## Slide 1
Al McBride
manager, area transmission planning
Transmission Interface Transfer Capabilities: 2015 Regional System Plan Assumptions, Presentation 1 –
External Interface Import Capability
December 18, 2014 | Westborough, MA
Planning Advisory Committee

## Slide 2: Agenda
Describe the provisions that govern the development and use of import transfer capability for existing external ties
Describe the evaluations that will be performed for external interface import transfer capabilities for use in the 2015 Regional System Plan (RSP15) and Resource Adequacy/FCM studies

## Slide 3: Provisions that govern the calculation of Import Transfer Capability of external ties

## Slide 4
FAC-013-2
NERC Standard FAC-013-2 ensures that Planning Coordinators have a methodology for, and perform an annual assessment to identify potential future Transmission System weaknesses and limiting facilities that could impact the Bulk Electric System’s ability to reliably transfer energy in the Near-Term Transmission Planning Horizon
  In New England, when identifying potential future Transmission System weaknesses, consideration will be given to rejected delist bids, generation retirements or other changes in system conditions

## Slide 5: Alignment of Planning Processes
NERC FAC-013-2 activities are in alignment with
  Regional System Plan (Attachment K):
    The Regional System Plan shall include the results of the annual assessment of transmission transfer capability, conducted pursuant to applicable NERC, NPCC and ISO New England standards and criteria and the identification of potential future transmission system weaknesses and limiting facilities that could impact the transmission system’s ability to reliably transfer energy in the planning horizon
    Each annual assessment will identify those portions of the New England system, along with the associated interface boundaries, that should be considered in the assessment of Capacity Zones to be modeled in the Forward Capacity Market pursuant to ISO Tariff Section III.12
  FERC 715 reporting of various aspects of the transmission system and the transmission planning process

## Slide 6: External import capability determinations – for use in FCM (Tariff Section III.12.9.2.4)
The import capability of all external interconnections with New England will be determined using studies of system conditions expected during the Capacity Commitment Period:
    Forecast 90/10 peak load
    Existing Generating Capacity Resources at their CNR Capability
    Existing Demand Resources reflecting their Capacity Supply Obligation
    Stressed Transfers
The system will be modeled in a manner that reflects the design of the interconnection
    If an interconnection and its supporting system upgrades were designed to provide incremental capacity into the New England Control Area, simulations will assume imports up to the level that the interconnection was designed to support
    If the interconnection was not designed to be comparably integrated, simulations will determine the amount of power that can be delivered into New England over the interconnection

## Slide 7: Analysis of the Delivery of Capacity
To analyze the potential for the delivery of capacity over an existing external interface into New England:
  For the study year and load level:
    Turn on New England Existing Generating Capacity Resources to their Capacity Network Resource Capability (CNRC)
    Turn on Existing Demand Resources
    Identify how much can be transferred into New England over the existing interface before reaching a constraint
To analyze the potential to qualify new capacity within New England (overlapping impacts of new internal resources):
  For the study year and load level:
    Turn on Existing Generating Capacity Resources to their CNRC
    Turn on Existing Demand Resources
    Increase imports to their limit or until an interface constrains
    Identify if there is any remaining headroom to qualify new internal capacity

## Slide 8: RSP14 A Review of previous results

## Slide 9: RSP14 External Interface Import Capability (The values below will be updated for RSP15)
Notes are discussed on the following pages

## Slide 10: External Interface Import Capability, continued
Limits are for the summer period, except where noted to be winter
  The limits may not include possible simultaneous impacts, and should not be considered as “firm” (the bases for these limits are subject to more detailed review in the future)
The electrical limit of the New Brunswick-New England (NB-NE) Tie is 1,000 MW
  When adjusted for the ability to deliver capacity to the greater New England Control area, the NB-NE transfer capability for RSP14 was 700 MW
    This is because of downstream constraints; in particular Orrington South
The capability for the Highgate facility is listed at the New England AC side of the Highgate terminal

## Slide 11: External Interface Import Capability, continued
The Hydro-Quebec Phase II interconnection is a DC tie with equipment ratings of 2,000 MW. Due to the need to protect for the loss of this line at full import level in the PJM and NY Control Areas’ systems, ISO-NE has assumed its transfer capability for capacity and reliability calculation purposes to be 1,400 MW
  This assumption is based on the results of loss-of-source analyses conducted by PJM and NY
Import capability on the Cross Sound Cable (CSC) is dependent on the level of local generation
New York interface limits
  These are without CSC and with the Northport Norwalk Cable at 0 MW flow
  Simultaneously importing into NE and SWCT or CT can lower the NY-NE capability (very rough decrease = 200 MW)

## Slide 12: RSP15 scope of review of external interface import transfer capability

## Slide 13: RSP15 Scope of Review of External Interface Import Transfer Capability
New Brunswick-New England
  Recent resource retirements and recent reductions in load in the Northern Maine area will be considered
Other external interfaces will be evaluated based on a review of Network Model updates that become certified for use in Forward Capacity Auction 10