## Net CONE Summary
Project: | ISO-NE Net CONE for Demand Curve
Date: | March 2014
Worksheet: | Net CONE Summary
|  | LMS100 | 187.8 | 333 | 1711 | 15yr MACRS | 8% | 15.5997 | 2.85 | 18.45 | 1.69 | -0.37 | 17.1358
Net CONE Estimates for Potential Reference Technologies (2018$)
|  | Reference | Installed | Total Plant | Overnight | Depreciation | After-Tax | Capital | Fixed | Gross | E&AS | PER/PFP Offsets | Net
|  | Technology | Capacity | Capital Cost | Cost | Schedule | WACC | Costs | O&M | CONE | Offsets |  | CONE
|  | Rest of Pool | MW | $m | $/kW |  | % | $/kW-mo | $/kW-mo | $/kW-mo | $/kW-mo | $/kW-mo | $/kW-mo
|  | 2x0 LM6000 | 173 | 352 | 1965 | 15yr MACRS | 8% | 17.9127 | 3.26 | 21.18 | 1.67 | -0.37 | 19.8757
|  | 2x0 LMS100 | 187.8 | 333 | 1711 | 15yr MACRS | 8% | 15.5997 | 2.85 | 18.45 | 1.69 | -0.37 | 17.1327
|  | 2x0 Frame CT | 416.6 | 389 | 902 | 15yr MACRS | 8% | 8.2085 | 1.55 | 9.76 | 1.66 | -0.37 | 8.4696
|  | 2x1 CC | 715 | 900 | 1178 | 20yr MACRS | 8% | 11.5926 | 2.44 | 14.04 | 3.33 | -0.37 | 11.0752

## CONE Calcs
Assumptions
1 | Select Options
| Select Technology >>> | LMS100 | CT | CC | LM6000 | LMS100
| FCA Year >>> | FCA9 | FCA9 | FCA10 | FCA11
| Performance Incentives | Yes | Yes | No
| Plant Capacity (MW) | 187.84
| Installed Cost ($m) | 332.6581
| Installed Cost ($/kW) | 1770.9654
| Depreciable Cost ($m) | 319.8989
| Depreciable Cost ($/kW) | 1703.0392
| Overnight Cost ($m) | 321.4473
| Overnight Cost ($/kW) | 1711.2823
| Fixed O&M ($/kW-yr) | 34.2366
2 | Financial Assumptions
| Economic Life (years) | 20
| Tax Depreciation Schedule | 15yr MACRS
| E&AS Margins ($/kW-mo) | 1.6869
| Peak Energy Rate Deduction ($/kW-mo) | 0.43
| Performance Incentives ($/kW-mo) | 0.06
| PV of Fuel Inventory at end of Economic Life ($m) | 0.88808
|  |  | Net CONE | ORTP
| Debt Fraction (%) | 60% | 50% | 50%
| Debt Rate (%) | 7% | 7% | 5.2%
| Equity Rate (%) | 13.8% | 11.9% | 11.3%
| Federal Tax Rate (%) | 35% | 35% | 35%
| State Tax Rate (%) | 8% | 8% | 8.93%
| Total Income Tax Rate (%) | 40.2% | 40.5% | 40.5%
| Annual Inflation Rate (%) | 2.25% | 2.25% | 2.25%
| Escalation Rate | 2.25% | 2.25% | 2.25%
| ATWACC Nominal (%) | 8.032% | 8.032% | 7.197%
| ATWACC Real (%) | 5.654% | 5.655% | 4.838%
| Interest During Construction (%) | 7%
| Construction Debt Fraction (%) | 60%
Calculations
Note: All dollar numbers are in nominal $.
|  | (1+ATWACC)/(1+Price_Growth)-1 = | 5.654%
| Components | Present Value | First Year Revenue Req. | First Year Revenue Req. | First Year Revenue Req.
|  | EOY 0 | MOY 1 | MOY 1 | MOY 1
|  | ($m) | ($m/yr) | ($/kW-yr) | ($/kW-mo)
| Investment Costs | 331.7701 | 46.2579 | 246.2623 | 20.5219
| Depreciation Tax Shield | -79.5755 | -11.095 | -59.0664 | -4.9222
| Operating Costs | 46.1243 | 6.431 | 34.2366 | 2.853
| Gross CONE | 298.3188 | 41.5939 | 221.4325 | 18.4527
| E&A/S Margins | --- | 3.8023 | 20.2424 | 1.6869
| PER/PFP | --- | -0.83401 | -4.44 | -0.37
| Revenue Offsets | --- | 2.9683 | 15.8024 | 1.3169
| Net CONE | --- | 38.6256 | 205.6301 | 17.1358
Summary of Operating Cash Flows
| Project Year | EOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY | MOY
|  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50
| E&A/S Margins ($m) |  | 3.8023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Performance Incentives ($m) |  | -0.83401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capacity Payment ($m) |  | 38.6256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Revenue ($m) |  | 41.5939 | 42.5297 | 43.4867 | 44.4651 | 45.4656 | 46.4886 | 47.5345 | 48.6041 | 49.6977 | 50.8159 | 51.9592 | 53.1283 | 54.3237 | 55.546 | 56.7958 | 58.0737 | 59.3803 | 60.7164 | 62.0825 | 63.4793 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fuel Costs ($m) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Variable O&M ($m) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fixed O&M ($m) |  | 6.431 | 6.5757 | 6.7237 | 6.8749 | 7.0296 | 7.1878 | 7.3495 | 7.5149 | 7.684 | 7.8568 | 8.0336 | 8.2144 | 8.3992 | 8.5882 | 8.7814 | 8.979 | 9.181 | 9.3876 | 9.5988 | 9.8148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating Costs ($m) |  | 6.431 | 6.5757 | 6.7237 | 6.8749 | 7.0296 | 7.1878 | 7.3495 | 7.5149 | 7.684 | 7.8568 | 8.0336 | 8.2144 | 8.3992 | 8.5882 | 8.7814 | 8.979 | 9.181 | 9.3876 | 9.5988 | 9.8148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Tax Depreciation (%) |  | 8.75% | 9.13% | 8.21% | 7.39% | 6.65% | 5.99% | 5.9% | 5.91% | 5.9% | 5.91% | 5.9% | 5.91% | 5.9% | 5.91% | 5.9% | 0.74% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Tax Depreciation ($m) |  | 27.9912 | 29.2068 | 26.2637 | 23.6405 | 21.2733 | 19.1619 | 18.874 | 18.906 | 18.874 | 18.906 | 18.874 | 18.906 | 18.874 | 18.906 | 18.874 | 2.3673 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Gross Income Tax ($m) ALL-EQUITY |  | 2.883 | 2.7124 | 4.2207 | 5.6078 | 6.8994 | 8.0958 | 8.567 | 8.9176 | 9.3021 | 9.6693 | 10.0707 | 10.4552 | 10.8743 | 11.2768 | 11.7144 | 18.7844 | 20.1801 | 20.6342 | 21.0984 | 21.5731 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| All-Equity Cash Flow ($m) | -331.7701 | 32.2798 | 33.2416 | 32.5423 | 31.9824 | 31.5366 | 31.205 | 31.618 | 32.1716 | 32.7116 | 33.2897 | 33.8549 | 34.4587 | 35.0502 | 35.681 | 36.2999 | 30.3102 | 30.0192 | 30.6946 | 31.3852 | 32.0914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Net Present Value Discounted at ATWACC ($m) | 0: 331.7701
TRUE

## Construction Cashflows
| Months To Completion |  |  | Construction Assumptions
| 20 |  |  | Technology >>> | LMS100
|  |  |  | Debt Ratio >>> | 60%
|  |  |  | Interest During Construction >>> | 7% | Debt Rate
|  |  |  | Years to Escalate Overnight Costs to 2018$ >>> | 0.58333
|  |  |  | ATWACC >>> | 8.032% | ATWACC nominal
|  | Project: | ISO-NE Net CONE for Demand Curve
|  | Date: | March 2014
|  | Worksheet: | Construction Cashflows
Note: All dollar numbers are in nominal $.
Summary of LMS100 Construction Cash Flows
|  |  | Construction Month | Total | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40
|  |  | Cash Flow (%) | 100% | 0.3635% | 0.4325% | 2.61% | 0.8045% | 1.755% | 1.111% | 2.176% | 2.887% | 4.029% | 6.697% | 8.136% | 10.41% | 11.57% | 12.27% | 11.49% | 10.16% | 7.709% | 4.285% | 0.9052% | 0.2016% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
|  |  | Capital Costs ($m) | 317.302 | 1.1533 | 1.3722 | 8.2801 | 2.5526 | 5.568 | 3.524 | 6.9059 | 9.1597 | 12.7842 | 21.25 | 25.8152 | 33.0215 | 36.712 | 38.9451 | 36.4544 | 32.2364 | 24.4599 | 13.5952 | 2.8724 | 0.63977 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Monthly Debt Rate = | 0.5654% |  | Interest During Construction ($m) |  | 0 | 0.0038478 | 0.0084393 | 0.036094 | 0.044734 | 0.063463 | 0.075436 | 0.098734 | 0.12963 | 0.17272 | 0.24421 | 0.33117 | 0.44247 | 0.56646 | 0.69832 | 0.82232 | 0.93267 | 1.0174 | 1.0663 | 1.0795 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Non-Depreciable Assets ($m) | 5.237 | 0.019034 | 0.022648 | 0.13666 | 0.042131 | 0.091899 | 0.058162 | 0.11398 | 0.15118 | 0.211 | 0.35073 | 0.42607 | 0.54501 | 0.60592 | 0.64278 | 0.60167 | 0.53205 | 0.40371 | 0.22439 | 0.047408 | 0.010559 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | IDC + Depreciable Assets ($m) |  | 1.1342 | 1.3534 | 8.1519 | 2.5466 | 5.5209 | 3.5293 | 6.8674 | 9.1073 | 12.7028 | 21.072 | 25.6334 | 32.8077 | 36.5486 | 38.8688 | 36.5511 | 32.5267 | 24.9889 | 14.3882 | 3.8912 | 1.7087 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Cumulative Dollars Spent ($m) |  | 1.1342 | 2.4876 | 10.6395 | 13.1861 | 18.707 | 22.2363 | 29.1037 | 38.2109 | 50.9138 | 71.9857 | 97.6191 | 130.4268 | 166.9754 | 205.8442 | 242.3953 | 274.9219 | 299.9108 | 314.299 | 318.1902 | 319.8989 | 319.8989 | 319.8989 | 319.8989 | 319.8989 | 319.8989 | 319.8989 | 319.8989 | 319.8989 | 319.8989 | 319.8989 | 319.8989 | 319.8989 | 319.8989 | 319.8989 | 319.8989 | 319.8989 | 319.8989 | 319.8989 | 319.8989 | 319.8989
|  |  | Overnight Cost ($m) | 321.4473
Monthly ATWACC nominal = | 0.6459% |  | Installed Cost ($m) | 332.6581
|  |  | Depreciable Cost ($m) | 319.8989

## Annual Updates Calcs
[8 empty] | CT | CC | LM6000 | LMS100
Project: | ISO-NE Net CONE for Demand Curve
Date: | March 2014
Worksheet: | Annual Updates Calcs
| Update Year: | FCA9
|  |  | Delivery Year | Dollars Year
|  | FCA9 | 2018/19 | 2018
|  | FCA10 | 2019/20 | 2019
|  | FCA11 | 2020/21 | 2020
| Annual Update Factors | FCA9 Value | FCA9 Value | Update Factor
| PPI Turbines | 225.8833 | 225.8833 | 1
| PPI Equipment | 216.5917 | 216.5917 | 1
| Utility Const Wage_MA | 107296 | 107296 | 1
| Utility Const Wage_ME | 61084 | 61084 | 1
| Power Gen Wage_MA | 119283 | 119283 | 1
| Power Gen Wage_ME | 85261 | 85261 | 1
| PPI Materials | 221.15 | 221.15 | 1
| PPI - Elect. Dist. | 136.75 | 136.75 | 1
| PPI - Gas Dist. | 112.3583 | 112.3583 | 1 |  |  |  | Notes:
| GDPD | 105.8393 | 105.8393 | 1 |  |  |  | Costs in red calculated based on percentage of other costs.
|  | Index |  |  | Update Factor |  |  | 2018/19 Capital Costs (2018$)
Depreciable (1 = Yes) |  | Frame-Type Combustion Turbine | Combined Cycle Gas Turbine | LMS100 Combustion Turbine | Frame-Type Combustion Turbine | Combined Cycle Gas Turbine | LMS100 Combustion Turbine | Frame-Type Combustion Turbine | Combined Cycle Gas Turbine | LM6000 Combustion Turbine | LMS100 Combustion Turbine
EPC Costs
Equipment
1 | Gas Turbines | PPI Turbines | PPI Turbines | PPI Turbines | 1 | 1 | 1 | 101021000 | 99491000 | 96531000 | 86990000
1 | Boiler / Heat Recovery Steam Generator | PPI Equipment | PPI Equipment | PPI Equipment | 1 | 1 | 1 | 19194000 | 47535000 | 24245000 | 15714000
1 | Condenser | - | PPI Equipment | - | n.a. | 1 | n.a. | n.a. | 29737000 | n.a. | n.a.
1 | Steam Turbines | - | PPI Turbines | - | n.a. | 1 | n.a. | n.a. | 39797000 | n.a. | n.a.
1 | Other Equipment | PPI Equipment | PPI Equipment | PPI Equipment | 1 | 1 | 1 | 24757000 | 55376000 | 26446000 | 32566000
| Equipment Subtotal | [6 empty] | 144972000 | 271936000 | 147222000 | 135270000
1 | Construction Labor | Utility Const Wage_MA | Utility Const Wage_MA | Utility Const Wage_MA | 1 | 1 | 1 | 65873000 | 193100000 | 51726000 | 49421000
1 | Other Labor (Eng, Procurement, Proj Mgt, Commissioning, etc.) | Power Gen Wage_MA | Power Gen Wage_MA | Power Gen Wage_MA | 1 | 1 | 1 | 18186000 | 43752000 | 15498000 | 17138000
1 | Materials | PPI Materials | PPI Materials | PPI Materials | 1 | 1 | 1 | 9067000 | 36812000 | 8652000 | 7889000
1 | Sales Tax | [6 empty] | 9627000 | 19297000 | 9742000 | 8947000
1 | EPC Contractor Fee | [6 empty] | 24773000 | 67788000 | 23284000 | 21867000
1 | EPC Contingency | [6 empty] | 27250000 | 63269000 | 25612000 | 24053000
| Subtotal - EPC Costs | [6 empty] | 299748000 | 695954000 | 281736000 | 264585000
Non-EPC Costs
1 | Owner's Costs (Services) | [6 empty] | 17985000 | 41757000 | 16904000 | 15875000
1 | Electrical Interconnection | PPI - Elect. Dist. | PPI - Elect. Dist. | PPI - Elect. Dist. | 1 | 1 | 1 | 17735000 | 28963000 | 8082000 | 8643000
1 | Gas Interconnection | PPI - Gas Dist. | PPI - Gas Dist. | PPI - Gas Dist. | 1 | 1 | 1 | 11786000 | 11607000 | 11786000 | 11786000
1 | Emission Reduction Credits | - | - | - |  |  |  | n.a. | n.a. | n.a. | n.a.
0 | Land | - | - | - |  |  |  | n.a. | n.a. | n.a. | n.a.
0 | Fuel Inventories | GDPD | GDPD | GDPD | 1 | 1 | 1 | 6689000 | 7682000 | 2557000 | 2591000
0 | Working Capital | [6 empty] | 2997000 | 6960000 | 2817000 | 2646000
1 | Owner's Contingency | [6 empty] | 5147000 | 8727000 | 3793000 | 3739000
| Subtotal - Non-EPC Costs w/o Financing Fees | [6 empty] | 62339000 | 105696000 | 45939000 | 45280000
1 | Financing Fees | [6 empty] | 8690000 | 19240000 | 7864000 | 7437000
| Subtotal - Non-EPC Costs | [6 empty] | 71029000 | 124936000 | 53803000 | 52717000
| Overnight Capital Costs ($) | [6 empty] | 370777000 | 820890000 | 335539000 | 317302000
| Overnight Capital Costs ($/kW) | [6 empty] | 889.9068 | 1148.0931 | 1939.5318 | 1689.2142
| Non-Depreciable Costs ($) | [6 empty] | 9686000 | 14642000 | 5374000 | 5237000
Fixed O&M Costs
| Labor | Power Gen Wage_MA | Power Gen Wage_MA | Power Gen Wage_MA | 1 | 1 | 1 | 1272000 | 3877000 | 1164000 | 1164000
| Materials and Contract Services | PPI Materials | PPI Materials | PPI Materials | 1 | 1 | 1 | 655000 | 4579000 | 376000 | 351000
| Administrative and General | Power Gen Wage_MA | Power Gen Wage_MA | Power Gen Wage_MA | 1 | 1 | 1 | 609000 | 992000 | 426000 | 419000
| Site Leasing Costs | GDPD | GDPD | GDPD | 1 | 1 | 1 | 212000 | 425000 | 276000 | 212000
| Property Taxes | [6 empty] | 2782000 | 6160000 | 2519000 | 2381000
| Insurance | [6 empty] | 2225000 | 4925000 | 2013000 | 1904000
| Total Fixed O&M ($) | [6 empty] | 7755000 | 20958000 | 6774000 | 6431000
| Total Fixed O&M ($/kW-year) | [6 empty] | 18.6129 | 29.3118 | 39.1561 | 34.2366

## Unit Specifications
|  | CT | CC | LM6000 | LMS100
Project: | ISO-NE Net CONE for Demand Curve
Date: | March 2014
Worksheet: | Unit Specifications
| Unit Specifications | Frame-Type Combustion Turbine | Combined Cycle Gas Turbine | LM6000 Combustion Turbine | LMS100 Combustion Turbine
| Turbine Model | Siemens SGT6-5000F(5) | Siemens SGT6-5000F(5) | GE LM6000 PC SPRINT | GE LMS100 PA
| Configuration | 2 x 0 | 2 x 2 x 1 | 4 x 0 | 2 x 0
| Net Plant Capacity (MW) | 416.647 | 715.003 | 173 | 187.84
| without Duct Firing (MW) | --- | 617.119 | - | -
| Cooling System | N/A | Dry | N/A | Dry Fin-Fan Intercooler
| Power Augmentation | Evaporative Cooling No inlet chillers | Evaporative Cooling No inlet chillers | Evaporative Cooling No inlet chillers | Evaporative Cooling No inlet chillers
| Net Heat Rate (Btu/kWh,HHV) | 10576.5 | 7437 | 9737.5 | 9088.5
| without Duct Firing (Btu/kWh, HHV) | --- | 7128 | --- | ---
| Environmental Controls | Dry Low NOx Burners Water Injection NOx Control Inlet Air Filters SCR with Tempering Air System CO Catalyst | Dry Low NOx Burners Water Injection NOx Control Inlet Air Filters SCR CO Catalyst | Water Injection NOx Control Inlet Air Filters SCR with Tempering Air System CO Catalyst | Water Injection NOx Control Inlet Air Filters SCR CO Catalyst
| Dual Fuel Capability | ULSD | ULSD | ULSD | ULSD
| Blackstart Capability | No | No | No | No
| On-Site Gas Compression | No | No | Yes | Yes
| Interconnection | 345 kV | 345 kV | 345 kV | 345 kV
| Plot Size (acres) | 10 | 20 | 13 | 10
| Location | Worcester, MA | Worcester, MA | Worcester, MA | Worcester, MA

## Capital Costs
[9 empty] | CT | CC | LM6000 | LMS100
|  |  | 2013 | [6 empty] | 2018
[8 empty] | Escalate to middle of drawdown schedule | 4.4167 | 3.8333 | 4.4167 | 4.4167 | 5
|  | CT_2013$ | CC_2013$ | LM6000_2013$ | LMS100_2013$ |  |  |  | CT_2018$ | CC_2018$ | LM6000_2018$ | LMS100_2018$
Project: | ISO-NE Net CONE for Demand Curve
Date: | March 2014
Worksheet: | Capital Costs
| Units | Reference Year Overnight Costs (2013$) | Reference Year Overnight Costs (2013$) | Reference Year Overnight Costs (2013$) | Reference Year Overnight Costs (2013$) |  |  |  | Reference Year Overnight Costs (2018$) | Reference Year Overnight Costs (2018$) | Reference Year Overnight Costs (2018$) | Reference Year Overnight Costs (2018$)
| Technology | Frame-Type Combustion Turbine | Combined Cycle Gas Turbine | LM6000 Combustion Turbine | LMS100 Combustion Turbine | Annual Escalation Rate | Inflation Adder |  | Frame-Type Combustion Turbine | Combined Cycle Gas Turbine | LM6000 Combustion Turbine | LMS100 Combustion Turbine |  | Comments
| Plant Capacity (MW) | 416.647 | 715.003 | 173 | 187.84 |  |  |  | 416.647 | 715.003 | 173 | 187.84
EPC Costs
Equipment
| Gas Turbines | 90000000 | 90000000 | 86000000 | 77500000 | 2.65% | 0.4% |  | 101021000 | 99491000 | 96531000 | 86990000
| HRSG / SCR | 17100000 | 43000000 | 21600000 | 14000000 | 2.65% | 0.4% |  | 19194000 | 47535000 | 24245000 | 15714000
| Condenser | 0 | 26900000 | 0 | 0 | 2.65% | 0.4% |  | 0 | 29737000 | 0 | 0
| Steam Turbines | 0 | 36000000 | 0 | 0 | 2.65% | 0.4% |  | 0 | 39797000 | 0 | 0
| Other Equipment | 22056000 | 50093000 | 23561000 | 29013000 | 2.65% | 0.4% |  | 24757000 | 55376000 | 26446000 | 32566000
| Equipment Subtotal | 129156000 | 245993000 | 131161000 | 120513000 | --- | --- |  | 144972000 | 271936000 | 147222000 | 135270000
| Construction Labor | 55988000 | 167685000 | 43964000 | 42005016.3488 | 3.75% | 1.5% |  | 65873000 | 193100000 | 51726000 | 49421000
| Other Labor | 15457000 | 37994000 | 13172000 | 14566103.0598 | 3.75% | 1.5% |  | 18186000 | 43752000 | 15498000 | 17138000 |  | Engineering, Procurement, Proj Mgt, Commissioning, etc.
| Materials | 8078000 | 33300000 | 7708000 | 7028528.827 | 2.65% | 0.4% |  | 9067000 | 36812000 | 8652000 | 7889000
| Sales Tax | 8577000 | 17456000 | 8679000 | 7971000 | --- | --- |  | 9627000 | 19297000 | 9742000 | 8947000
| EPC Contractor Fee | 21726000 | 60291000 | 20468000 | 19208000 | --- | --- |  | 24773000 | 67788000 | 23284000 | 21867000
| EPC Contingency | 23898000 | 56272000 | 22515000 | 21129000 | --- | --- |  | 27250000 | 63269000 | 25612000 | 24053000
| Total EPC Costs | 262880000 | 618991000 | 247667000 | 232421000 |  | --- |  | 299748000 | 695954000 | 281736000 | 264585000
Non-EPC Costs
| Owner's Costs (Services) | 15773000 | 37139000 | 14860000 | 13945000 | --- | --- |  | 17985000 | 41757000 | 16904000 | 15875000 |  | Permitting, Legal, Owner's Project Mgmt. & Engineering, Development Costs, & Studies.
| Electrical Interconnection | 15800000 | 26200000 | 7200000 | 7700000 | 2.65% | 0.4% |  | 17735000 | 28963000 | 8082000 | 8643000
| Gas Interconnection | 10500000 | 10500000 | 10500000 | 10500000 | 2.65% | 0.4% |  | 11786000 | 11607000 | 11786000 | 11786000
| Emission Reduction Credits | 0 | 0 | 0 | 0 | --- | --- |  | 0 | 0 | 0 | 0 |  | If applicable.
| Land | 0 | 0 | 0 | 0 | --- | --- |  | 0 | 0 | 0 | 0 |  | Included as site leasing costs in Fixed O&M.
| Fuel Inventories | 6346000 | 7339000 | 2426000 | 2458000 | 1.2% | -1.05% |  | 6689000 | 7682000 | 2557000 | 2591000
| Working Capital | 2629000 | 6190000 | 2477000 | 2324000 | --- | --- |  | 2997000 | 6960000 | 2817000 | 2646000 |  | Includes spare parts inventories, and other.
| Owner's Contingency | 4594000 | 7863000 | 3372000 | 3323000 | --- | --- |  | 5147000 | 8727000 | 3793000 | 3739000
| Subtotal - Non-EPC Costs w/o Financing Fees | 55642000 | 95231000 | 40835000 | 40250000 | --- | --- |  | 62339000 | 105696000 | 45939000 | 45280000
| Financing Fees | 7645000 | 17141000 | 6924000 | 6544000 | --- | --- |  | 8690000 | 19240000 | 7864000 | 7437000
| Total Non-EPC Costs | 63287000 | 112372000 | 47759000 | 46794000 | --- | --- |  | 71029000 | 124936000 | 53803000 | 52717000
| Overnight Capital Costs ($) | 326167000 | 731363000 | 295426000 | 279215000 |  |  |  | 370777000 | 820890000 | 335539000 | 317302000
| Overnight Capital Costs ($/kW) | 782.8377 | 1022.881 | 1707.6647 | 1486.4512 |  |  |  | 889.9068 | 1148.0931 | 1939.5318 | 1689.2142

## O&M Costs
|  |  | 2013 | [5 empty] | 2018
|  | CT | CC | LM6000 | LMS100 |  |  | CT | CC | LM6000 | LMS100
Project: | ISO-NE Net CONE for Demand Curve
Date: | March 2014
Worksheet: | O&M Costs
|  | Reference Year Costs (2013$) | [5 empty] | Reference Year Costs (2018$)
| O&M Costs | Frame-Type Combustion Turbine | Combined Cycle Gas Turbine | LM6000 Combustion Turbine | LMS100 Combustion Turbine | Annual Escalation Rate | Inflation Adder | Frame-Type Combustion Turbine | Combined Cycle Gas Turbine | LM6000 Combustion Turbine | LMS100 Combustion Turbine | Comments
Fixed O&M
| Labor | 1058000 | 3225000 | 968000 | 968000 | 3.75% | 1.5% | 1272000 | 3877000 | 1164000 | 1164000
| Materials and Contract Services | 575000 | 4018000 | 330000 | 308000 | 2.65% | 0.4% | 655000 | 4579000 | 376000 | 351000
| Administrative and General | 534000 | 870000 | 374000 | 368000 | 2.65% | 0.4% | 609000 | 992000 | 426000 | 419000
| Site Leasing Costs | 190000 | 380000 | 247000 | 190000 | 2.25% | 0% | 212000 | 425000 | 276000 | 212000
| Property Taxes | 2448000 | 5488000 | 2218000 | 2096000 |  |  | 2782000 | 6160000 | 2519000 | 2381000
| Insurance | 1957000 | 4388000 | 1773000 | 1675000 |  |  | 2225000 | 4925000 | 2013000 | 1904000
| Total Fixed O&M ($) | 6762000 | 18369000 | 5910000 | 5605000 |  |  | 7755000 | 20958000 | 6774000 | 6431000
| Total Fixed O&M ($/kW-year) | 16.2296 | 25.6908 | 34.1618 | 29.8392 |  |  | 18.6129 | 29.3118 | 39.1561 | 34.2366
Variable O&M
| Major Maintenance - Hours Based | 2.01 | 1.32 | 3.43 | 2.86 | 2.65% | 0.4% | 2.2908 | 1.5044 | 3.9092 | 3.2596 | CT and CC value is zero if starts-based major maintenance.
| Consumables, Waste Disposal, and Other VOM | 1.65 | 1.03 | 2.52 | 2.52 | 2.65% | 0.4% | 1.8805 | 1.1739 | 2.8721 | 2.8721
| Variable O&M - Hours Based ($/MWh) | 3.66 | 2.35 | 5.95 | 5.38 |  |  | 4.1713 | 2.6783 | 6.7813 | 6.1316
| Variable O&M - Starts Based ($/factored start, per turbine) | 9164 | 9201 | - | - | 2.65% | 0.4% | 10444.3123 | 10486.4816 | - | - | CT and CC value is zero if hours-based major maintenance.

## Capital Drawdown Schedule
| Project: | ISO-NE Net CONE for Demand Curve
| Date: | March 2014
| Worksheet: | Capital Drawdown Schedule
|  | Technology | Mon. Until | 50% of | Construction Month
|  |  | Completion | Drawdown | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | Total
CT |  | Frame-Type Combustion Turbine | 20 | 13 | 0.3635% | 0.4325% | 2.61% | 0.8045% | 1.755% | 1.111% | 2.176% | 2.887% | 4.029% | 6.697% | 8.136% | 10.41% | 11.57% | 12.27% | 11.49% | 10.16% | 7.709% | 4.285% | 0.9052% | 0.2016% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 100%
CC |  | Combined Cycle Gas Turbine | 36 | 22 | 0.01452% | 0.04211% | 0.04211% | 1.419% | 1.39% | 0.1962% | 0.314% | 1.223% | 1.289% | 1.081% | 1.138% | 1.209% | 2.115% | 2.312% | 3.273% | 3.574% | 4.073% | 4.478% | 5.244% | 5.345% | 5.219% | 5.381% | 5.109% | 5.064% | 5.233% | 5.219% | 5.262% | 4.937% | 4.858% | 4.152% | 3.767% | 3.014% | 2.178% | 0.5983% | 0.1388% | 0.09983% | 0% | 0% | 0% | 0% | 100%
LM6000 |  | LM6000 Combustion Turbine | 20 | 13 | 0.3635% | 0.4325% | 2.61% | 0.8045% | 1.755% | 1.111% | 2.176% | 2.887% | 4.029% | 6.697% | 8.136% | 10.41% | 11.57% | 12.27% | 11.49% | 10.16% | 7.709% | 4.285% | 0.9052% | 0.2016% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 100%
LMS100 |  | LMS100 Combustion Turbine | 20 | 13 | 0.3635% | 0.4325% | 2.61% | 0.8045% | 1.755% | 1.111% | 2.176% | 2.887% | 4.029% | 6.697% | 8.136% | 10.41% | 11.57% | 12.27% | 11.49% | 10.16% | 7.709% | 4.285% | 0.9052% | 0.2016% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 100%

## Cost Assumptions
|  |  | CT | CC | LM6000 | LMS100
Project: | ISO-NE Net CONE for Demand Curve
Date: | March 2014
Worksheet: | Capital Cost Assumptions
| Assumptions | Units | Frame-Type Combustion Turbine | Combined Cycle Gas Turbine | LM6000 Combustion Turbine | LMS100 Combustion Turbine
Plant Characteristics
| Net Plant Capacity - ICAP (with duct firing) | MW | 416.647 | 715.003 | 173 | 187.84
| (without duct firing) | MW | - | 617.119 | - | -
| Net Plant Heat Rate - Summer/Winter Average | Btu/kWh, HHV | 10576.5 | 7128 | 9737.5 | 9088.5
| Equivalent Forced Outage Rate - Demand Based | EFORd | 2.2% | 2% | 2.2% | 2.2%
Capital Costs
| EPC Contractor Fee | % of other EPC costs | 10% | 12% | 10% | 10%
| EPC Contingency | % of other EPC costs | 10% | 10% | 10% | 10%
| Owner's Cost | % of EPC costs | 6% | 6% | 6% | 6%
| Working Capital | % of EPC costs | 1% | 1% | 1% | 1%
| Owner Contingency | % of other Owner's costs | 9% | 9% | 9% | 9%
| Financing Fees | % | 4% | 4% | 4% | 4%
| Electric Interconnection | $m | 15.8 | 26.2 | 7.2 | 7.7
| Network Upgrades |  | 8.7 | 19.1 | 0.1 | 0.6
| Substation Upgrades | $m | 6 | 6 | 6 | 6
| Transmission Line Length | miles | 0.5 | 0.5 | 0.5 | 0.5
| Transmission Line Cost | $m/mile | 2.2 | 2.2 | 2.2 | 2.2
| Gas Interconnection | $m | 10.5 | 10.5 | 10.5 | 10.5
| Pipeline Cost | $/mile | 3.9 | 3.9 | 3.9 | 3.9
| Miles | miles | 2 | 2 | 2 | 2
| Substation | $m | 2.7 | 2.7 | 2.7 | 2.7
| Sales Tax Rates | % | 6.25% | 6.25% | 6.25% | 6.25%
| State Income Tax Rates | % | 8% | 8% | 8% | 8%
| Fuel Oil Inventory Cost | $ | 6345600.4735 | 7339019.593 | 2425806 | 2458344.7296
| Days of Fuel Oil Inventory | days | 3 | 3 | 3 | 3
| Capacity Factor for Inventory Days | % | 100% | 100% | 100% | 100%
| Fuel Oil Price | $/mmBtu | 20 | 20 | 20 | 20
| Fuel Oil Heating Value | Btu/gallon | 140000 | 140000 | 140000 | 140000
| Fuel Oil Inventory | gallons | 2266285.8834 | 2621078.4261 | 866359.2857 | 877980.2606
| Fuel Oil Price | $/gallon | 2.8 | 2.8 | 2.8 | 2.8
| Depreciation Schedule |  | 15yr MACRS | 20yr MACRS | 15yr MACRS | 15yr MACRS
| Tax Credits |  | --- | --- | --- | ---
O&M Costs
| Land | $m/yr | 0.19 | 0.38 | 0.247 | 0.19
| Land Leasing Cost | $/acre-year | 19000 | 19000 | 19000 | 19000
| Acreage | acre | 10 | 20 | 13 | 10
| Natural Gas Consumed During Start * | mmBtu/start, per Unit | 215 | 1688 | 27 | 215
| Property Tax - Land | % of Leasing Costs | 0.75% | 0.75% | 0.75% | 0.75%
| Property Tax - Plant | % of Overnight Capital Costs | 0.75% | 0.75% | 0.75% | 0.75%
| Insurance | % of Overnight Capital Costs | 0.6% | 0.6% | 0.6% | 0.6%
Note: All dollar numbers are in 2013$.

## Tax Depreciation
Project: | ISO-NE Net CONE for Demand Curve
Date: | March 2014
Worksheet: | Tax Depreciation
Source: | MACRS from IRS website
http://www.irs.gov/publications/p946/ar02.html
Year | 5yr MACRS | 10yr MACRS | 15yr MACRS | 20yr MACRS | 5yr SLD | 10yr SLD | 20yr SLD | 30yr SLD | 40yr SLD | 50yr SLD
1 | 35% | 17.5% | 8.75% | 6.563% | 20% | 10% | 5% | 3.333% | 2.5% | 2%
2 | 26% | 16.5% | 9.13% | 7% | 20% | 10% | 5% | 3.333% | 2.5% | 2%
3 | 15.6% | 13.2% | 8.21% | 6.482% | 20% | 10% | 5% | 3.333% | 2.5% | 2%
4 | 11.01% | 10.56% | 7.39% | 5.996% | 20% | 10% | 5% | 3.333% | 2.5% | 2%
5 | 11.01% | 8.45% | 6.65% | 5.546% | 20% | 10% | 5% | 3.333% | 2.5% | 2%
6 | 1.38% | 6.76% | 5.99% | 5.13% | 0% | 10% | 5% | 3.333% | 2.5% | 2%
7 | 0% | 6.55% | 5.9% | 4.746% | 0% | 10% | 5% | 3.333% | 2.5% | 2%
8 | 0% | 6.55% | 5.91% | 4.459% | 0% | 10% | 5% | 3.333% | 2.5% | 2%
9 | 0% | 6.56% | 5.9% | 4.459% | 0% | 10% | 5% | 3.333% | 2.5% | 2%
10 | 0% | 6.55% | 5.91% | 4.459% | 0% | 10% | 5% | 3.333% | 2.5% | 2%
11 | 0% | 0.82% | 5.9% | 4.459% | 0% | 0% | 5% | 3.333% | 2.5% | 2%
12 | 0% | 0% | 5.91% | 4.46% | 0% | 0% | 5% | 3.333% | 2.5% | 2%
13 | 0% | 0% | 5.9% | 4.459% | 0% | 0% | 5% | 3.333% | 2.5% | 2%
14 | 0% | 0% | 5.91% | 4.46% | 0% | 0% | 5% | 3.333% | 2.5% | 2%
15 | 0% | 0% | 5.9% | 4.459% | 0% | 0% | 5% | 3.333% | 2.5% | 2%
16 | 0% | 0% | 0.74% | 4.46% | 0% | 0% | 5% | 3.333% | 2.5% | 2%
17 | 0% | 0% | 0% | 4.459% | 0% | 0% | 5% | 3.333% | 2.5% | 2%
18 | 0% | 0% | 0% | 4.46% | 0% | 0% | 5% | 3.333% | 2.5% | 2%
19 | 0% | 0% | 0% | 4.459% | 0% | 0% | 5% | 3.333% | 2.5% | 2%
20 | 0% | 0% | 0% | 4.46% | 0% | 0% | 5% | 3.333% | 2.5% | 2%
21 | 0% | 0% | 0% | 0.565% | 0% | 0% | 0% | 3.333% | 2.5% | 2%
22 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 3.333% | 2.5% | 2%
23 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 3.333% | 2.5% | 2%
24 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 3.333% | 2.5% | 2%
25 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 3.333% | 2.5% | 2%
26 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 3.333% | 2.5% | 2%
27 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 3.333% | 2.5% | 2%
28 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 3.333% | 2.5% | 2%
29 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 3.333% | 2.5% | 2%
30 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 3.333% | 2.5% | 2%
31 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 2.5% | 2%
32 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 2.5% | 2%
33 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 2.5% | 2%
34 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 2.5% | 2%
35 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 2.5% | 2%
36 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 2.5% | 2%
37 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 2.5% | 2%
38 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 2.5% | 2%
39 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 2.5% | 2%
40 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 2.5% | 2%
41 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 2%
42 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 2%
43 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 2%
44 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 2%
45 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 2%
46 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 2%
47 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 2%
48 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 2%
49 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 2%
50 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 2%
TOTAL | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%

## Revenue Offsets
|  |  | CT | CC | LM6000 | LMS100
Project: | ISO-NE Net CONE for Demand Curve
Date: | March 2014
Worksheet: | Revenue Offsets
| Update Year: | FCA9
| Value | Units | Frame-Type Combustion Turbine | Combined Cycle Gas Turbine | LM6000 Combustion Turbine | LMS100 Combustion Turbine
| E&AS | $/kW-mo | 1.6596 | 3.3302 | 1.675 | 1.6869
| PER | $/kW-mo | 0.43 | 0.43 | 0.43 | 0.43
| PFP | $/kW-mo | 0.06 | 0.06 | 0.06 | 0.06
Note: All dollar numbers are in 2018$.
Note on B14: John Michael Hagerty: H = 5.8
Note on B15: John Michael Hagerty: H = 5.8

## Cost Index Data
|  |  | Project: | ISO-NE Net CONE for Demand Curve
|  |  | Date: | March 2014
|  |  | Worksheet: | Cost Index Data
|  |  | Instructions: | To set FCA10 and FCA11 Net CONE values, access the source of the indices through the link provided.
Be sure to check that the Series ID on this spreadsheet matches with the Series ID of the source of the index.
Enter all data currently available from the index in the yellow cells.
Modify the FCA10 or FCA 11 cell to the right based on the data available for the most recent 12 months for each index.
|  |  | Index Inputs | [12 empty] | Index Values
Construction Labor Cost Indexing
|  |  | Source: | BLS Quarterly Census of Employment and Wages
|  |  | Industry: | 2371 Utility System Construction
|  |  | Area: | 25013 Hampden County, Massachusetts
|  |  | Owner: | 5 Private
|  |  | Type: | 5 Average Annual Pay
|  |  | Size: | 0 All Establishment Sizes
|  |  | Series ID: | ENU250135052371
|  |  | Access: | http://data.bls.gov/cgi-bin/dsrv?en
|  |  | Date Updated: | 2013-08-28
ID | Index Name | Index Value | Year | Annual | [11 empty] | Auction | Index Value
Utility Const Wage_MA_FCA9 | Utility Const Wage_MA | 107296 | 2012 | 107296 | [11 empty] | FCA9 | 107296
Utility Const Wage_MA_FCA10 | Utility Const Wage_MA | 108000 | 2013 | 108000 | [11 empty] | FCA10 | 108000
Utility Const Wage_MA_FCA11 | Utility Const Wage_MA | 109000 | 2014 | 109000 | [11 empty] | FCA11 | 109000
|  |  | Source: | BLS Quarterly Census of Employment and Wages
|  |  | Industry: | 2371 Utility System Construction
|  |  | Area: | 23005 Cumberland Country, Maine
|  |  | Owner: | 5 Private
|  |  | Type: | 5 Average Annual Pay
|  |  | Size: | 0 All Establishment Sizes
|  |  | Series ID: | ENU230055052371
|  |  | Access: | http://data.bls.gov/cgi-bin/dsrv?en
|  |  | Date Updated: | 2013-08-28
ID | Index Name | Index Value | Year | Annual | [11 empty] | Auction | Index Value
Utility Const Wage_ME_FCA9 | Utility Const Wage_ME | 61084 | 2012 | 61084 | [11 empty] | FCA9 | 61084
Utility Const Wage_ME_FCA10 | Utility Const Wage_ME | 65000 | 2013 | 65000 | [11 empty] | FCA10 | 65000
Utility Const Wage_ME_FCA11 | Utility Const Wage_ME | 66000 | 2014 | 66000 | [11 empty] | FCA11 | 66000
Other Labor Cost Indexing
|  |  | Source: | BLS Quarterly Census of Employment and Wages
|  |  | Industry: | 2211 Power Generation and Supply
|  |  | Area: | 25013 Hampden County, Massachusetts
|  |  | Owner: | 5 Private
|  |  | Type: | 5 Average Annual Pay
|  |  | Size: | 0 All Establishment Sizes
|  |  | Series ID: | ENU250135052211
|  |  | Access: | http://data.bls.gov/cgi-bin/dsrv?en
|  |  | Date Updated: | 2013-08-28
ID | Index Name | Index Value | Year | Annual | [11 empty] | Auction | Index Value
Power Gen Wage_MA_FCA9 | Power Gen Wage_MA | 119283 | 2012 | 119283 | [11 empty] | FCA9 | 119283
Power Gen Wage_MA_FCA10 | Power Gen Wage_MA | 120000 | 2013 | 120000 | [11 empty] | FCA10 | 120000
Power Gen Wage_MA_FCA11 | Power Gen Wage_MA | 123000 | 2014 | 123000 | [11 empty] | FCA11 | 123000
|  |  | Source: | BLS Quarterly Census of Employment and Wages - 2211 Power Generation and Supply Average Annual Pay
|  |  | Industry: | 2211 Power Generation and Supply
|  |  | Area: | 23005 Cumberland Country, Maine
|  |  | Owner: | 5 Private
|  |  | Type: | 5 Average Annual Pay
|  |  | Size: | 0 All Establishment Sizes
|  |  | Series ID: | ENU230055052211
|  |  | Access: | http://data.bls.gov/cgi-bin/dsrv?en
|  |  | Date Updated: | 2013-08-28
ID | Index Name | Index Value | Year | Annual | [11 empty] | Auction | Index Value
Power Gen Wage_ME_FCA9 | Power Gen Wage_ME | 85261 | 2012 | 85261 | [11 empty] | FCA9 | 85261
Power Gen Wage_ME_FCA10 | Power Gen Wage_ME | 90000 | 2013 | 90000 | [11 empty] | FCA10 | 90000
Power Gen Wage_ME_FCA11 | Power Gen Wage_ME | 92000 | 2014 | 92000 | [11 empty] | FCA11 | 92000
Materials Cost Indexing
|  |  | Source: | BLS Producer Price Index Commodity Data
|  |  | Seasonal: | Not Seasonally Adjusted
|  |  | Group: | SOP Stage of Processing
|  |  | Item: | 2200 Materials and Components for Construction
|  |  | Series ID: | WPUSOP2200
|  |  | Access: | http://data.bls.gov/cgi-bin/dsrv?wp
|  |  | Date Updated: | 2013-08-28
|  |  | Year | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Auction | Index Value
PPI Materials_FCA9 | PPI Materials | 221.15 | 2012 | 215.3 | 216.8 | 217.4 | 218.3 | 219.1 | 219.1 | 218.5 | 218.7 | 219.2 | 219.1 | 219.5 | 219.9 | FCA9 | 221.15
PPI Materials_FCA10 | PPI Materials | 230 | 2013 | 221.2 | 222.2 | 222.7 | 223.1 | 223 | 222.6 | 222.6 | 230 | 230 | 230 | 230 | 230 | FCA10 | 230
PPI Materials_FCA11 | PPI Materials | 240 | 2014 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 240 | 240 | 240 | 240 | 240 | FCA11 | 240
|  |  | 2015 | 240 | 240 | 240 | 240 | 240 | 240 | 240
Electric Interconnection Cost Indexing
|  |  | Source: | BLS Producer Price Index Industry Data
|  |  | Industry: | 22112- Electric power transmission, control, and distribution
|  |  | Product: | 22112- Electric power transmission, control, and distribution
|  |  | Series ID: | PCU22112-22112-
|  |  | Access: | http://data.bls.gov/cgi-bin/dsrv?pc
|  |  | Date Updated: | 2013-08-28
|  |  | Year | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Auction | Index Value
PPI - Elect. Dist._FCA9 | PPI - Elect. Dist. | 136.75 | 2012 | 132.4 | 132.6 | 132.2 | 132.1 | 134 | 136.7 | 139.2 | 139.2 | 139.6 | 136 | 134.6 | 135.5 | FCA9 | 136.75
PPI - Elect. Dist._FCA10 | PPI - Elect. Dist. | 142 | 2013 | 134.7 | 134.5 | 134.6 | 134.2 | 136.6 | 140.3 | 141.2 | 142 | 142 | 142 | 142 | 142 | FCA10 | 142
PPI - Elect. Dist._FCA11 | PPI - Elect. Dist. | 145 | 2014 | 142 | 142 | 142 | 142 | 142 | 142 | 142 | 145 | 145 | 145 | 145 | 145 | FCA11 | 145
|  |  | 2015 | 145 | 145 | 145 | 145 | 145 | 145 | 145
Gas Interconnection Cost Indexing
|  |  | Source: | BLS Producer Price Index Industry Data
|  |  | Industry: | 2212-- Natural gas distribution
|  |  | Product: | 2212-- Natural gas distribution
|  |  | Series ID: | PCU2212--2212--
|  |  | Access: | http://data.bls.gov/cgi-bin/dsrv?pc
|  |  | Date Updated: | 2013-08-28
|  |  | Year | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Auction | Index Value
PPI - Gas Dist._FCA9 | PPI - Gas Dist. | 112.3583 | 2012 | 112.6 | 110 | 109.4 | 105.1 | 101.3 | 104.3 | 106.1 | 107.1 | 105.4 | 106.8 | 111.4 | 112.8 | FCA9 | 112.3583
PPI - Gas Dist._FCA10 | PPI - Gas Dist. | 120 | 2013 | 112.3 | 112.6 | 111.8 | 114.2 | 116.5 | 119.3 | 118.1 | 120 | 120 | 120 | 120 | 120 | FCA10 | 120
PPI - Gas Dist._FCA11 | PPI - Gas Dist. | 125 | 2014 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 125 | 125 | 125 | 125 | 125 | FCA11 | 125
|  |  | 2015 | 125 | 125 | 125 | 125 | 125 | 125 | 125
Gas and Steam Turbine Cost Index
|  |  | Source: | BLS Producer Price Index Commodity Data
|  |  | Seasonal: | Not Seasonally Adjusted
|  |  | Group: | 11 Machinery and equipment
|  |  | Item: | 97 Turbines and turbine generator sets
|  |  | Series ID: | WPU1197
|  |  | Access: | http://data.bls.gov/cgi-bin/dsrv?wp
|  |  | Date Updated: | 2013-08-28
|  |  | Year | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Auction | Index Value
PPI Turbines_FCA9 | PPI Turbines | 225.8833 | 2012 | 218.9 | 220 | 222.1 | 222.3 | 224.3 | 225.2 | 225.4 | 224.4 | 222.9 | 225.1 | 226.2 | 225.7 | FCA9 | 225.8833
PPI Turbines_FCA10 | PPI Turbines | 230 | 2013 | 225.4 | 225.4 | 226.3 | 226.6 | 228 | 227.3 | 227.3 | 230 | 230 | 230 | 230 | 230 | FCA10 | 230
PPI Turbines_FCA11 | PPI Turbines | 235 | 2014 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 235 | 235 | 235 | 235 | 235 | FCA11 | 235
|  |  | 2015 | 235 | 235 | 235 | 235 | 235 | 235 | 235
Other Equipment Cost Index
|  |  | Source: | BLS Producer Price Index Commodity Data
|  |  | Seasonal: | Not Seasonally Adjusted
|  |  | Group: | 11 Machinery and equipment
|  |  | Item: | 4 General purpose machinery and equipment
|  |  | Series ID: | WPU114
|  |  | Access: | http://data.bls.gov/cgi-bin/dsrv
|  |  | Date Updated: | 2013-08-28
|  |  | Year | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Auction | Index Value
PPI Equipment_FCA9 | PPI Equipment | 216.5917 | 2012 | 211.1 | 212.8 | 213 | 213.4 | 213.5 | 213.8 | 214.1 | 214.6 | 214.6 | 214.8 | 215.1 | 215.7 | FCA9 | 216.5917
PPI Equipment_FCA10 | PPI Equipment | 220 | 2013 | 216.4 | 217.3 | 217.9 | 217.9 | 218.4 | 218 | 218.4 | 220 | 220 | 220 | 220 | 220 | FCA10 | 220
PPI Equipment_FCA11 | PPI Equipment | 230 | 2014 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 230 | 230 | 230 | 230 | 230 | FCA11 | 230
|  |  | 2015 | 230 | 230 | 230 | 230 | 230 | 230 | 230
Land and Fuel Inventories
|  |  | Source: | Gross Domestic Product: Implicit Price Deflator (GDPDEF), Index 2009=100, Quarterly, Seasonally Adjusted - Choose last four quarters available.
|  |  | Access: | http://research.stlouisfed.org/fred2/graph/?s%5b1%5d%5bid%5d=GDPDEF
|  |  | Updated: | 2013-08-28
|  |  | Date Updated: Year: Year; 2013-08-28 Jan: Jan; 2013-08-28 Feb: Apr; 2013-08-28 Mar: Jun; 2013-08-28 Apr: Dec | Auction | Index Value
GDPD_FCA9 | GDPD | 105.8393 | Date Updated: Year: 2012; 2013-08-28 Jan: 104.291; 2013-08-28 Feb: 104.75; 2013-08-28 Mar: 105.292; 2013-08-28 Apr: 105.667 | FCA9 | 105.8393
GDPD_FCA10 | GDPD | 107 | Date Updated: Year: 2013; 2013-08-28 Jan: 106.105; 2013-08-28 Feb: 106.293; 2013-08-28 Mar: 107; 2013-08-28 Apr: 107 | FCA10 | 107
GDPD_FCA11 | GDPD | 108 | Date Updated: Year: 2014; 2013-08-28 Jan: 107; 2013-08-28 Feb: 107; 2013-08-28 Mar: 108; 2013-08-28 Apr: 108 | FCA11 | 108
|  |  | 2015 | 108 | 108

## Annual Results
|  |  | CT | CC | LM6000 | LMS100
| Project: | ISO-NE Net CONE for Demand Curve
| Date: | March 2014
| Worksheet: | Historical and Future E&AS Margin Results
Estimates of Historical and Future E&AS Margins
|  | Year | CT | CC | LM6000 | LMS100
|  |  | ($/kW-mo) | ($/kW-mo) | ($/kW-mo) | ($/kW-mo)
|  | 2010 | 2.3053 | 3.7542 | 1.9028 | 2.3544
|  | 2011 | 2.2 | 4.2955 | 2.2277 | 2.249
|  | 2012 | 0.9075 | 2.9272 | 0.91138 | 0.91439
|  | 2013 | 2.0346 | 4.0467 | 2.0543 | 2.0695
|  | 2014 | 2.8244 | 5.5514 | 2.8535 | 2.8759
|  | 2015 | 2.2096 | 4.3644 | 2.2321 | 2.2495
|  | 2016 | 1.9751 | 3.9102 | 1.9952 | 2.0107
|  | 2017 | 1.7182 | 3.4454 | 1.7346 | 1.7472
|  | 2018 | 1.683 | 3.3782 | 1.6991 | 1.7115
2019
2020
FCA9 |  | 2018/2019 | 1.6596 | 3.3302 | 1.675 | 1.6869
FCA10 |  | 2019/2020
FCA11 |  | 2020/2021

## Margin Forecast
Years Used | First of Mo | Project: | ISO-NE Net CONE for Demand Curve
2010 | 1 | Date: | March 2014
2011 |  | Worksheet: | E&AS Margin Forecast Calculations
2012
Forecasted E&AS Margins ($/kW-mo)
[5 empty] | Frame CT |  |  | CC |  |  | LM6000 |  |  | LMS100
|  |  | Date | Mass Hub On-Peak Electricity Price ($/MWh) | Actual Energy Margin / Elec Pric | Actual Energy Margin ($/kW-mo) | Forecasted Energy Margin ($/kW-mo) | Actual Energy Margin / Elec Pric | Actual Energy Margin ($/kW-mo) | Forecasted Energy Margin ($/kW-mo) | Actual Energy Margin / Elec Pric | Actual Energy Margin ($/kW-mo) | Forecasted Energy Margin ($/kW-mo) | Actual Energy Margin / Elec Pric | Actual Energy Margin ($/kW-mo) | Forecasted Energy Margin ($/kW-mo)
2010 | 10 |  | 2010-10-01 | 40.9455 | 0.031921 | 1.307 | 0.85859 | 0.062112 | 2.5432 | 3.3053 | 0.031983 | 1.3096 | 0.86151 | 0.032031 | 1.3115 | 0.86377
2010 | 11 |  | 2010-11-01 | 48.2802 | 0.036821 | 1.7777 | 1.2793 | 0.040086 | 1.9354 | 2.2326 | 0.037126 | 1.7924 | 1.2883 | 0.037361 | 1.8038 | 1.2952
2010 | 12 |  | 2010-12-01 | 73.1726 | 0.021111 | 1.5447 | 1.4034 | 0.047123 | 3.4481 | 3.0388 | 0.021292 | 1.558 | 1.4176 | 0.021431 | 1.5682 | 1.4287
2011 | 1 |  | 2011-01-01 | 78.5676 | 0.036626 | 2.8776 | 1.9724 | 0.070061 | 5.5045 | 3.3229 | 0.0375 | 2.9463 | 2.017 | 0.038176 | 2.9994 | 2.0516
2011 | 2 |  | 2011-02-01 | 64.1858 | 0.032041 | 2.0566 | 1.2772 | 0.069283 | 4.447 | 2.6034 | 0.032411 | 2.0803 | 1.2954 | 0.032697 | 2.0987 | 1.3096
2011 | 3 |  | 2011-03-01 | 52.266 | 0.040487 | 2.1161 | 1.3257 | 0.065966 | 3.4478 | 2.6681 | 0.040878 | 2.1365 | 1.3355 | 0.041181 | 2.1523 | 1.343
2011 | 4 |  | 2011-04-01 | 48.2601 | 0.04633 | 2.2359 | 1.168 | 0.068059 | 3.2846 | 2.4135 | 0.04671 | 2.2542 | 1.1752 | 0.047004 | 2.2684 | 1.1808
2011 | 5 |  | 2011-05-01 | 48.2027 | 0.028524 | 1.375 | 2.0444 | 0.058286 | 2.8095 | 2.8874 | 0.02862 | 1.3796 | 2.0578 | 0.028695 | 1.3832 | 2.0682
2011 | 6 |  | 2011-06-01 | 51.4381 | 0.061048 | 3.1402 | 2.5094 | 0.069148 | 3.5568 | 3.6623 | 0.061477 | 3.1623 | 2.5197 | 0.061809 | 3.1793 | 2.5278
2011 | 7 |  | 2011-07-01 | 71.6313 | 0.065856 | 4.7173 | 4.1178 | 0.12945 | 9.2724 | 9.5814 | 0.067061 | 4.8037 | 4.1589 | 0.067993 | 4.8704 | 4.1907
2011 | 8 |  | 2011-08-01 | 49.2983 | 0.039096 | 1.9274 | 2.5153 | 0.11236 | 5.5391 | 5.7322 | 0.03962 | 1.9532 | 2.5316 | 0.040026 | 1.9732 | 2.5442
2011 | 9 |  | 2011-09-01 | 45.7967 | 0.056509 | 2.5879 | 2.1577 | 0.083698 | 3.8331 | 3.6019 | 0.057208 | 2.62 | 2.1744 | 0.05775 | 2.6447 | 2.1874
2011 | 10 |  | 2011-10-01 | 46.3255 | 0.021006 | 0.97311 | 0.9714 | 0.099315 | 4.6008 | 3.7396 | 0.021101 | 0.97751 | 0.97471 | 0.021174 | 0.98091 | 0.97727
2011 | 11 |  | 2011-11-01 | 40.0987 | 0.02952 | 1.1837 | 1.0625 | 0.076966 | 3.0862 | 1.8543 | 0.029746 | 1.1928 | 1.07 | 0.02992 | 1.1998 | 1.0757
2011 | 12 |  | 2011-12-01 | 39.9084 | 0.030308 | 1.2095 | 0.7654 | 0.054238 | 2.1645 | 1.6574 | 0.030712 | 1.2257 | 0.77318 | 0.031025 | 1.2381 | 0.7792
2012 | 1 |  | 2012-01-01 | 44.8468 | 0.017304 | 0.77602 | 1.1258 | 0.018619 | 0.83501 | 1.8967 | 0.017359 | 0.77848 | 1.1513 | 0.017401 | 0.78037 | 1.171
2012 | 2 |  | 2012-02-01 | 32.8053 | 0.021042 | 0.69029 | 0.65276 | 0.038815 | 1.2733 | 1.3306 | 0.021083 | 0.69164 | 0.66209 | 0.021115 | 0.69269 | 0.66931
2012 | 3 |  | 2012-03-01 | 28.9904 | 0.022964 | 0.66572 | 0.73532 | 0.064351 | 1.8656 | 1.4799 | 0.022987 | 0.66639 | 0.74074 | 0.023004 | 0.6669 | 0.74492
2012 | 4 |  | 2012-04-01 | 29.5522 | 0.01918 | 0.56681 | 0.71524 | 0.044416 | 1.3126 | 1.4779 | 0.019206 | 0.56758 | 0.71966 | 0.019226 | 0.56818 | 0.72307
2012 | 5 |  | 2012-05-01 | 29.866 | 0.083826 | 2.5036 | 1.2667 | 0.065897 | 1.9681 | 1.789 | 0.084422 | 2.5213 | 1.275 | 0.084883 | 2.5351 | 1.2814
2012 | 6 |  | 2012-06-01 | 46.2571 | 0.011263 | 0.52097 | 2.2566 | 0.10093 | 4.6685 | 3.2934 | 0.011271 | 0.52137 | 2.266 | 0.011278 | 0.52168 | 2.2732
2012 | 7 |  | 2012-07-01 | 52.047 | 0.016255 | 0.84602 | 2.992 | 0.13877 | 7.2227 | 6.9618 | 0.016283 | 0.84749 | 3.0218 | 0.016305 | 0.84862 | 3.0449
2012 | 8 |  | 2012-08-01 | 47.1351 | 0.047232 | 2.2263 | 2.4049 | 0.14997 | 7.069 | 5.4807 | 0.047581 | 2.2427 | 2.4205 | 0.047851 | 2.2555 | 2.4325
2012 | 9 |  | 2012-09-01 | 37.1484 | 0.015538 | 0.57722 | 1.7502 | 0.087776 | 3.2607 | 2.9217 | 0.015579 | 0.57873 | 1.7638 | 0.015611 | 0.57991 | 1.7743
2012 | 10 |  | 2012-10-01 | 38.8129 | 0.0099801 | 0.38736 | 0.81387 | 0.080745 | 3.134 | 3.1331 | 0.010038 | 0.38959 | 0.81664 | 0.010082 | 0.39131 | 0.81878
2012 | 11 |  | 2012-11-01 | 62.7276 | 0.013154 | 0.8251 | 1.6622 | 0.021676 | 1.3597 | 2.9007 | 0.013178 | 0.8266 | 1.6738 | 0.013196 | 0.82776 | 1.6827
2012 | 12 |  | 2012-12-01 | 49.7915 | 0.0061179 | 0.30462 | 0.95495 | 0.023229 | 1.1566 | 2.0678 | 0.0061179 | 0.30462 | 0.96465 | 0.0061179 | 0.30462 | 0.97216
2013 | 1 |  | 2013-01-01 | 94.7927 | 0.021382 | 2.0269 | 2.3797 | 0.0382 | 3.621 | 4.0091 | 0.022158 | 2.1005 | 2.4335 | 0.022759 | 2.1574 | 2.4752
2013 | 2 |  | 2013-02-01 | 135.2854 | 0.0066113 | 0.89442 | 2.6919 | 0.013585 | 1.8378 | 5.4873 | 0.0070536 | 0.95425 | 2.7304 | 0.0073957 | 1.0005 | 2.7602
2013 | 3 |  | 2013-03-01 | 61.4129 | 0.012643 | 0.77644 | 1.5577 | 0.022829 | 1.402 | 3.135 | 0.012789 | 0.7854 | 1.5692 | 0.012902 | 0.79233 | 1.578
2013 | 4 |  | 2013-04-01 | 47.6193 | 0.0070976 | 0.33798 | 1.1525 | 0.037558 | 1.7885 | 2.3815 | 0.00714 | 0.34 | 1.1596 | 0.0071728 | 0.34156 | 1.1651
2013 | 5 |  | 2013-05-01 | 47.3613 | 0.014887 | 0.70507 | 2.0087 | 0.055522 | 2.6296 | 2.837 | 0.015031 | 0.71188 | 2.0219 | 0.015142 | 0.71715 | 2.0321
2013 | 6 |  | 2013-06-01 | 42.4022 | 0.074045 | 3.1396 | 2.0686 | 0.043522 | 1.8454 | 3.019 | 0.07421 | 3.1467 | 2.0771 | 0.074339 | 3.1521 | 2.0837
2013 | 7 |  | 2013-07-01 | 65.458 | 0.090349 | 5.914 | 3.763 | 0.13306 | 8.7098 | 8.7556 | 0.090836 | 5.9459 | 3.8005 | 0.091212 | 5.9706 | 3.8295
2013 | 8 |  | 2013-08-01 | 41.7319 | 0.066735 | 2.785 | 2.1292 | 0.086497 | 3.6097 | 4.8524 | 0.066854 | 2.7899 | 2.143 | 0.066945 | 2.7938 | 2.1537
2013 | 9 |  | 2013-09-01 | 49.9288 | 0.069297 | 3.4599 | 2.3524 | 0.064477 | 3.2193 | 3.9269 | 0.069653 | 3.4777 | 2.3706 | 0.069928 | 3.4914 | 2.3847
2013 | 10 |  | 2013-10-01 | 39.3335 |  |  | 0.82478 |  |  | 3.1752 |  |  | 0.82759 |  |  | 0.82976
2013 | 11 |  | 2013-11-01 | 51.165 |  |  | 1.3558 |  |  | 2.366 |  |  | 1.3652 |  |  | 1.3725
2013 | 12 |  | 2013-12-01 | 111.1189 |  |  | 2.1311 |  |  | 4.6147 |  |  | 2.1528 |  |  | 2.1696
2014 | 1 |  | 2014-01-01 | 204.0486 |  |  | 5.1224 |  |  | 8.6299 |  |  | 5.2384 |  |  | 5.3281
2014 | 2 |  | 2014-02-01 | 184.3757 |  |  | 3.6687 |  |  | 7.4785 |  |  | 3.7212 |  |  | 3.7617
2014 | 3 |  | 2014-03-01 | 139.4414 |  |  | 3.5369 |  |  | 7.1183 |  |  | 3.5629 |  |  | 3.583
2014 | 4 |  | 2014-04-01 | 65.3714 |  |  | 1.5822 |  |  | 3.2693 |  |  | 1.5919 |  |  | 1.5995
2014 | 5 |  | 2014-05-01 | 49.8929 |  |  | 2.1161 |  |  | 2.9887 |  |  | 2.13 |  |  | 2.1407
2014 | 6 |  | 2014-06-01 | 69.1857 |  |  | 3.3752 |  |  | 4.9259 |  |  | 3.3891 |  |  | 3.3999
2014 | 7 |  | 2014-07-01 | 72.4929 |  |  | 4.1674 |  |  | 9.6966 |  |  | 4.2089 |  |  | 4.2411
2014 | 8 |  | 2014-08-01 | 63 |  |  | 3.2143 |  |  | 7.3254 |  |  | 3.2352 |  |  | 3.2513
2014 | 9 |  | 2014-09-01 | 47.5143 |  |  | 2.2386 |  |  | 3.737 |  |  | 2.256 |  |  | 2.2694
2014 | 10 |  | 2014-10-01 | 48.1286 |  |  | 1.0092 |  |  | 3.8851 |  |  | 1.0126 |  |  | 1.0153
2014 | 11 |  | 2014-11-01 | 71.9929 |  |  | 1.9077 |  |  | 3.3291 |  |  | 1.921 |  |  | 1.9313
2014 | 12 |  | 2014-12-01 | 101.9143 |  |  | 1.9546 |  |  | 4.2325 |  |  | 1.9745 |  |  | 1.9898
2015 | 1 |  | 2015-01-01 | 147.7429 |  |  | 3.7089 |  |  | 6.2485 |  |  | 3.7929 |  |  | 3.8579
2015 | 2 |  | 2015-02-01 | 143.8786 |  |  | 2.8629 |  |  | 5.8359 |  |  | 2.9038 |  |  | 2.9355
2015 | 3 |  | 2015-03-01 | 77.8214 |  |  | 1.9739 |  |  | 3.9727 |  |  | 1.9884 |  |  | 1.9997
2015 | 4 |  | 2015-04-01 | 48.95 |  |  | 1.1847 |  |  | 2.448 |  |  | 1.192 |  |  | 1.1977
2015 | 5 |  | 2015-05-01 | 44.4571 |  |  | 1.8855 |  |  | 2.6631 |  |  | 1.8979 |  |  | 1.9075
2015 | 6 |  | 2015-06-01 | 48.6143 |  |  | 2.3716 |  |  | 3.4613 |  |  | 2.3814 |  |  | 2.389
2015 | 7 |  | 2015-07-01 | 60.4214 |  |  | 3.4734 |  |  | 8.082 |  |  | 3.5081 |  |  | 3.5349
2015 | 8 |  | 2015-08-01 | 56.8714 |  |  | 2.9016 |  |  | 6.6128 |  |  | 2.9204 |  |  | 2.935
2015 | 9 |  | 2015-09-01 | 42.9 |  |  | 2.0212 |  |  | 3.3741 |  |  | 2.0369 |  |  | 2.049
2015 | 10 |  | 2015-10-01 | 38.35 |  |  | 0.80416 |  |  | 3.0958 |  |  | 0.8069 |  |  | 0.80902
2015 | 11 |  | 2015-11-01 | 56.25 |  |  | 1.4905 |  |  | 2.6011 |  |  | 1.5009 |  |  | 1.509
2015 | 12 |  | 2015-12-01 | 95.7857 |  |  | 1.8371 |  |  | 3.9779 |  |  | 1.8557 |  |  | 1.8702
2016 | 1 |  | 2016-01-01 | 131.4429 |  |  | 3.2997 |  |  | 5.5591 |  |  | 3.3744 |  |  | 3.4322
2016 | 2 |  | 2016-02-01 | 131.4429 |  |  | 2.6155 |  |  | 5.3315 |  |  | 2.6529 |  |  | 2.6818
2016 | 3 |  | 2016-03-01 | 64.2 |  |  | 1.6284 |  |  | 3.2773 |  |  | 1.6404 |  |  | 1.6497
2016 | 4 |  | 2016-04-01 | 41.3 |  |  | 0.99957 |  |  | 2.0655 |  |  | 1.0057 |  |  | 1.0105
2016 | 5 |  | 2016-05-01 | 38.9571 |  |  | 1.6523 |  |  | 2.3336 |  |  | 1.6631 |  |  | 1.6715
2016 | 6 |  | 2016-06-01 | 42.9786 |  |  | 2.0967 |  |  | 3.06 |  |  | 2.1054 |  |  | 2.112
2016 | 7 |  | 2016-07-01 | 56.8786 |  |  | 3.2698 |  |  | 7.6081 |  |  | 3.3024 |  |  | 3.3276
2016 | 8 |  | 2016-08-01 | 56.8786 |  |  | 2.902 |  |  | 6.6136 |  |  | 2.9208 |  |  | 2.9354
2016 | 9 |  | 2016-09-01 | 39.1071 |  |  | 1.8425 |  |  | 3.0758 |  |  | 1.8568 |  |  | 1.8679
2016 | 10 |  | 2016-10-01 | 33.2143 |  |  | 0.69647 |  |  | 2.6812 |  |  | 0.69884 |  |  | 0.70068
2016 | 11 |  | 2016-11-01 | 47.1643 |  |  | 1.2498 |  |  | 2.181 |  |  | 1.2585 |  |  | 1.2652
2016 | 12 |  | 2016-12-01 | 75.5143 |  |  | 1.4483 |  |  | 3.1361 |  |  | 1.463 |  |  | 1.4744
2017 | 1 |  | 2017-01-01 | 95.75 |  |  | 2.4037 |  |  | 4.0496 |  |  | 2.4581 |  |  | 2.5002
2017 | 2 |  | 2017-02-01 | 95.75 |  |  | 1.9052 |  |  | 3.8837 |  |  | 1.9325 |  |  | 1.9535
2017 | 3 |  | 2017-03-01 | 44.2571 |  |  | 1.1226 |  |  | 2.2593 |  |  | 1.1308 |  |  | 1.1372
2017 | 4 |  | 2017-04-01 | 44.3071 |  |  | 1.0723 |  |  | 2.2158 |  |  | 1.079 |  |  | 1.0841
2017 | 5 |  | 2017-05-01 | 38.4571 |  |  | 1.6311 |  |  | 2.3036 |  |  | 1.6418 |  |  | 1.6501
2017 | 6 |  | 2017-06-01 | 41.6643 |  |  | 2.0326 |  |  | 2.9664 |  |  | 2.041 |  |  | 2.0475
2017 | 7 |  | 2017-07-01 | 50.35 |  |  | 2.8944 |  |  | 6.7348 |  |  | 2.9233 |  |  | 2.9456
2017 | 8 |  | 2017-08-01 | 50.3 |  |  | 2.5664 |  |  | 5.8487 |  |  | 2.583 |  |  | 2.5959
2017 | 9 |  | 2017-09-01 | 37.8571 |  |  | 1.7836 |  |  | 2.9775 |  |  | 1.7975 |  |  | 1.8082
2017 | 10 |  | 2017-10-01 | 48.1071 |  |  | 1.0088 |  |  | 3.8834 |  |  | 1.0122 |  |  | 1.0149
2017 | 11 |  | 2017-11-01 | 48.1071 |  |  | 1.2748 |  |  | 2.2246 |  |  | 1.2836 |  |  | 1.2905
2017 | 12 |  | 2017-12-01 | 48.1071 |  |  | 0.92265 |  |  | 1.9979 |  |  | 0.93202 |  |  | 0.93927
2018 | 1 |  | 2018-01-01 | 94.2571 |  |  | 2.3662 |  |  | 3.9864 |  |  | 2.4198 |  |  | 2.4612
2018 | 2 |  | 2018-02-01 | 94.4071 |  |  | 1.8785 |  |  | 3.8293 |  |  | 1.9054 |  |  | 1.9262
2018 | 3 |  | 2018-03-01 | 43.2357 |  |  | 1.0966 |  |  | 2.2071 |  |  | 1.1047 |  |  | 1.111
2018 | 4 |  | 2018-04-01 | 43.2857 |  |  | 1.0476 |  |  | 2.1648 |  |  | 1.0541 |  |  | 1.0591
2018 | 5 |  | 2018-05-01 | 37.2857 |  |  | 1.5814 |  |  | 2.2335 |  |  | 1.5918 |  |  | 1.5998
2018 | 6 | FCA9 | 2018-06-01 | 39.9857 |  |  | 1.9507 |  |  | 2.8469 |  |  | 1.9587 |  |  | 1.965
2018 | 7 |  | 2018-07-01 | 48.7571 |  |  | 2.8029 |  |  | 6.5217 |  |  | 2.8308 |  |  | 2.8525
2018 | 8 |  | 2018-08-01 | 48.8071 |  |  | 2.4902 |  |  | 5.6751 |  |  | 2.5063 |  |  | 2.5188
2018 | 9 |  | 2018-09-01 | 37.5857 |  |  | 1.7708 |  |  | 2.9561 |  |  | 1.7846 |  |  | 1.7952
2018 | 10 |  | 2018-10-01 | 48.1357 |  |  | 1.0094 |  |  | 3.8857 |  |  | 1.0128 |  |  | 1.0155
2018 | 11 |  | 2018-11-01 | 48.1857 |  |  | 1.2768 |  |  | 2.2282 |  |  | 1.2857 |  |  | 1.2926
2018 | 12 |  | 2018-12-01 | 48.2357 |  |  | 0.92511 |  |  | 2.0032 |  |  | 0.93451 |  |  | 0.94178
2019 | 1 |  | 2019-01-01 | 82.8214 |  |  | 2.0791 |  |  | 3.5028 |  |  | 2.1262 |  |  | 2.1626
2019 | 2 |  | 2019-02-01 | 82.8214 |  |  | 1.648 |  |  | 3.3593 |  |  | 1.6715 |  |  | 1.6898
2019 | 3 |  | 2019-03-01 | 44.6857 |  |  | 1.1334 |  |  | 2.2811 |  |  | 1.1418 |  |  | 1.1482
2019 | 4 |  | 2019-04-01 | 44.6857 |  |  | 1.0815 |  |  | 2.2348 |  |  | 1.0882 |  |  | 1.0934
2019 | 5 |  | 2019-05-01 | 41.1857 |  |  | 1.7468 |  |  | 2.4671 |  |  | 1.7583 |  |  | 1.7671
2019 | 6 | FCA10 | 2019-06-01 | 0
2019 | 7 |  | 2019-07-01 | 0
2019 | 8 |  | 2019-08-01 | 0
2019 | 9 |  | 2019-09-01 | 0
2019 | 10 |  | 2019-10-01 | 0
2019 | 11 |  | 2019-11-01 | 0
2019 | 12 |  | 2019-12-01 | 0
2020 | 1 |  | 2020-01-01 | 0
2020 | 2 |  | 2020-02-01 | 0
2020 | 3 |  | 2020-03-01 | 0
2020 | 4 |  | 2020-04-01 | 0
2020 | 5 |  | 2020-05-01 | 0
2020 | 6 | FCA11 | 2020-06-01 | 0
2020 | 7 |  | 2020-07-01 | 0
2020 | 8 |  | 2020-08-01 | 0
2020 | 9 |  | 2020-09-01 | 0
2020 | 10 |  | 2020-10-01 | 0
2020 | 11 |  | 2020-11-01 | 0
2020 | 12 |  | 2020-12-01 | 0
2021 | 1 |  | 2021-01-01 | 0
2021 | 2 |  | 2021-02-01 | 0
2021 | 3 |  | 2021-03-01 | 0
2021 | 4 |  | 2021-04-01 | 0
2021 | 5 |  | 2021-05-01 | 0

## Historical Prices
Project: | ISO-NE Net CONE for Demand Curve
Date: | March 2014
Worksheet: | Historical Electricity Prices
Historical Electricity Prices at Mass Hub
| Term | Mass Hub On-Peak Electricity Price ($/MWh)
| 2010-01-01 | 67.124
| 2010-02-01 | 57.415
| 2010-03-01 | 41.9935
| 2010-04-01 | 41.9179
| 2010-05-01 | 50.7018
| 2010-06-01 | 55.8562
| 2010-07-01 | 78.2443
| 2010-08-01 | 66.6588
| 2010-09-01 | 53.9358
| 2010-10-01 | 40.9455
| 2010-11-01 | 48.2802
| 2010-12-01 | 73.1726
| 2011-01-01 | 78.5676
| 2011-02-01 | 64.1858
| 2011-03-01 | 52.266
| 2011-04-01 | 48.2601
| 2011-05-01 | 48.2027
| 2011-06-01 | 51.4381
| 2011-07-01 | 71.6313
| 2011-08-01 | 49.2983
| 2011-09-01 | 45.7967
| 2011-10-01 | 46.3255
| 2011-11-01 | 40.0987
| 2011-12-01 | 39.9084
| 2012-01-01 | 44.8468
| 2012-02-01 | 32.8053
| 2012-03-01 | 28.9904
| 2012-04-01 | 29.5522
| 2012-05-01 | 29.866
| 2012-06-01 | 46.2571
| 2012-07-01 | 52.047
| 2012-08-01 | 47.1351
| 2012-09-01 | 37.1484
| 2012-10-01 | 38.8129
| 2012-11-01 | 62.7276
| 2012-12-01 | 49.7915
| 2013-01-01 | 94.7927
| 2013-02-01 | 135.2854
| 2013-03-01 | 61.4129
| 2013-04-01 | 47.6193
| 2013-05-01 | 47.3613
| 2013-06-01 | 42.4022
| 2013-07-01 | 65.458
| 2013-08-01 | 41.7319
| 2013-09-01 | 49.9288
| 2013-10-01 | 39.3335
| 2013-11-01 | 51.165
| 2013-12-01 | 111.1189
| 2014-01-01 | 204.0486
Note: Calculated by taking simple average of hourly on-peak electricity prices. Hourly on-peak electricity prices provided by Ventyx

## Futures Prices
| Project: | ISO-NE Net CONE for Demand Curve
| Date: | March 2014
| Worksheet: | Current and Projected Electricity and Gas Futures Prices
| Instructions: | Insert the most recent Mass Hub On-Peak data for the next 12 months available.
Electricity Futures
|  | Term | Mass Hub On-Peak Electricity Price ($/MWh)
[1]
|  | 2013-08-01 | 41.7319
|  | 2013-09-01 | 49.9288
10 |  | 2013-10-01 | 39.3335
11 |  | 2013-11-01 | 51.165
12 |  | 2013-12-01 | 111.1189
1 |  | 2014-01-01 | 204.0486
2 |  | 2014-02-01 | 184.3757
3 |  | 2014-03-01 | 139.4414
4 |  | 2014-04-01 | 65.3714
5 |  | 2014-05-01 | 49.8929
6 |  | 2014-06-01 | 69.1857
7 |  | 2014-07-01 | 72.4929
8 |  | 2014-08-01 | 63
9 |  | 2014-09-01 | 47.5143
10 |  | 2014-10-01 | 48.1286
11 |  | 2014-11-01 | 71.9929
12 |  | 2014-12-01 | 101.9143
1 |  | 2015-01-01 | 147.7429
2 |  | 2015-02-01 | 143.8786
3 |  | 2015-03-01 | 77.8214
4 |  | 2015-04-01 | 48.95
5 |  | 2015-05-01 | 44.4571
6 |  | 2015-06-01 | 48.6143
7 |  | 2015-07-01 | 60.4214
8 |  | 2015-08-01 | 56.8714
9 |  | 2015-09-01 | 42.9
10 |  | 2015-10-01 | 38.35
11 |  | 2015-11-01 | 56.25
12 |  | 2015-12-01 | 95.7857
1 |  | 2016-01-01 | 131.4429
2 |  | 2016-02-01 | 131.4429
3 |  | 2016-03-01 | 64.2
4 |  | 2016-04-01 | 41.3
5 |  | 2016-05-01 | 38.9571
6 |  | 2016-06-01 | 42.9786
7 |  | 2016-07-01 | 56.8786
8 |  | 2016-08-01 | 56.8786
9 |  | 2016-09-01 | 39.1071
10 |  | 2016-10-01 | 33.2143
11 |  | 2016-11-01 | 47.1643
12 |  | 2016-12-01 | 75.5143
1 |  | 2017-01-01 | 95.75
2 |  | 2017-02-01 | 95.75
3 |  | 2017-03-01 | 44.2571
4 |  | 2017-04-01 | 44.3071
5 |  | 2017-05-01 | 38.4571
6 |  | 2017-06-01 | 41.6643
7 |  | 2017-07-01 | 50.35
8 |  | 2017-08-01 | 50.3
9 |  | 2017-09-01 | 37.8571
10 |  | 2017-10-01 | 48.1071
11 |  | 2017-11-01 | 48.1071
12 |  | 2017-12-01 | 48.1071
1 |  | 2018-01-01 | 94.2571
2 |  | 2018-02-01 | 94.4071
3 |  | 2018-03-01 | 43.2357
4 |  | 2018-04-01 | 43.2857
5 |  | 2018-05-01 | 37.2857
6 | FCA9 | 2018-06-01 | 39.9857
7 |  | 2018-07-01 | 48.7571
8 |  | 2018-08-01 | 48.8071
9 |  | 2018-09-01 | 37.5857
10 |  | 2018-10-01 | 48.1357
11 |  | 2018-11-01 | 48.1857
12 |  | 2018-12-01 | 48.2357
1 |  | 2019-01-01 | 82.8214
2 |  | 2019-02-01 | 82.8214
3 |  | 2019-03-01 | 44.6857
4 |  | 2019-04-01 | 44.6857
5 |  | 2019-05-01 | 41.1857
6 | FCA10 | 2019-06-01
7 |  | 2019-07-01
8 |  | 2019-08-01
9 |  | 2019-09-01
10 |  | 2019-10-01
11 |  | 2019-11-01
12 |  | 2019-12-01
1 |  | 2020-01-01
2 |  | 2020-02-01
3 |  | 2020-03-01
4 |  | 2020-04-01
5 |  | 2020-05-01
6 | FCA11 | 2020-06-01
7 |  | 2020-07-01
8 |  | 2020-08-01
9 |  | 2020-09-01
10 |  | 2020-10-01
11 |  | 2020-11-01
12 |  | 2020-12-01
1 |  | 2021-01-01
2 |  | 2021-02-01
3 |  | 2021-03-01
4 |  | 2021-04-01
5 |  | 2021-05-01

## ICE - Mass Hub Futures
Source: https://www.theice.com/marketdata/reports/ReportCenter.shtml
|  |  |  | Category: | End of Day Reports
|  |  |  | Market: | ICE Futures U.S. - Energy Div
|  |  |  | Report: | DMR - IFED Futures
|  |  |  | Contract: | NEP-ISO NEW ENGLAND MASSACHUSETTS HUB DAY-AHEAD PEAK FIXED PRICE FUTURE
Year |  | Month | July/Aug |  | Term | 2014-02-20 | 2014-02-21 | 2014-02-24 | 2014-02-25 | 2014-02-26 | 2014-02-27 | 2014-02-28 | Avg
[6 empty] | Settlement | Settlement | Settlement | Settlement | Settlement | Settlement | Settlement | Settlement
2014 | 2014 | 2 | 0 |  | 2014-02-01 | 185.84 | 187.99 | 187.52 | 183.05 | 182.05 | 182.09 | 182.09 | 184.3757
2014 |  | 3 | 0 |  | 2014-03-01 | 144.85 | 150 | 125 | 127.5 | 133.5 | 135 | 160.24 | 139.4414
2014 |  | 4 | 0 |  | 2014-04-01 | 64.15 | 66.15 | 63.5 | 63.9 | 64.5 | 67 | 68.4 | 65.3714
2014 |  | 5 | 0 |  | 2014-05-01 | 50.25 | 50.95 | 49.5 | 49.75 | 49 | 49.4 | 50.4 | 49.8929
2014 |  | 6 | 0 |  | 2014-06-01 | 69.15 | 69.8 | 68.6 | 68.75 | 68.25 | 69.4 | 70.35 | 69.1857
2014 |  | 7 | 1 |  | 2014-07-01 | 72.55 | 73 | 71.2 | 72.05 | 71.5 | 73 | 74.15 | 72.4929
2014 |  | 8 | 1 |  | 2014-08-01 | 63.2 | 63.6 | 62 | 62.75 | 61.95 | 63.25 | 64.25 | 63
2014 |  | 9 | 0 |  | 2014-09-01 | 47.45 | 48 | 47.25 | 47.55 | 47 | 47.5 | 47.85 | 47.5143
2014 |  | 10 | 0 |  | 2014-10-01 | 48.2 | 48.95 | 48.05 | 48.35 | 47.5 | 47.7 | 48.15 | 48.1286
2014 |  | 11 | 0 |  | 2014-11-01 | 71.7 | 72.25 | 71.75 | 72.1 | 72.05 | 71.75 | 72.35 | 71.9929
2014 |  | 12 | 0 |  | 2014-12-01 | 102 | 102.3 | 102.15 | 102.15 | 101.85 | 101.3 | 101.65 | 101.9143
2015 | 2015 | 1 | 0 |  | 2015-01-01 | 148.25 | 148.85 | 147.9 | 147.85 | 147.35 | 146.85 | 147.15 | 147.7429
2015 |  | 2 | 0 |  | 2015-02-01 | 144.4 | 144.95 | 144.05 | 144 | 143.5 | 143 | 143.25 | 143.8786
2015 |  | 3 | 0 |  | 2015-03-01 | 77.55 | 77.9 | 77.7 | 77.8 | 77.55 | 77.9 | 78.35 | 77.8214
2015 |  | 4 | 0 |  | 2015-04-01 | 49.1 | 48.75 | 48.75 | 48.85 | 48.75 | 49.05 | 49.4 | 48.95
2015 |  | 5 | 0 |  | 2015-05-01 | 44.6 | 44.2 | 44.35 | 44.35 | 44.25 | 44.55 | 44.9 | 44.4571
2015 |  | 6 | 0 |  | 2015-06-01 | 49.05 | 49.05 | 48.65 | 48.55 | 48.25 | 48.35 | 48.4 | 48.6143
2015 |  | 7 | 1 |  | 2015-07-01 | 60.45 | 60.5 | 60.45 | 60.45 | 60.2 | 60.35 | 60.55 | 60.4214
2015 |  | 8 | 1 |  | 2015-08-01 | 56.9 | 56.95 | 56.9 | 56.9 | 56.65 | 56.8 | 57 | 56.8714
2015 |  | 9 | 0 |  | 2015-09-01 | 43.15 | 43.15 | 42.7 | 42.75 | 42.7 | 42.8 | 43.05 | 42.9
2015 |  | 10 | 0 |  | 2015-10-01 | 38.6 | 38.55 | 38.1 | 38.15 | 38.15 | 38.4 | 38.5 | 38.35
2015 |  | 11 | 0 |  | 2015-11-01 | 56.3 | 56.3 | 56.1 | 56.1 | 56.15 | 56.4 | 56.4 | 56.25
2015 |  | 12 | 0 |  | 2015-12-01 | 95.7 | 95.7 | 95.65 | 95.7 | 95.75 | 96 | 96 | 95.7857
2016 | 2016 | 1 | 0 |  | 2016-01-01 | 131.6 | 131.6 | 131.55 | 131.5 | 131.25 | 131.2 | 131.4 | 131.4429
2016 |  | 2 | 0 |  | 2016-02-01 | 131.6 | 131.6 | 131.55 | 131.5 | 131.25 | 131.2 | 131.4 | 131.4429
2016 |  | 3 | 0 |  | 2016-03-01 | 63.7 | 63.45 | 63.4 | 64.55 | 64.55 | 64.8 | 64.95 | 64.2
2016 |  | 4 | 0 |  | 2016-04-01 | 40.8 | 40.55 | 40.5 | 41.65 | 41.65 | 41.9 | 42.05 | 41.3
2016 |  | 5 | 0 |  | 2016-05-01 | 39.25 | 39 | 38.95 | 38.9 | 38.75 | 38.85 | 39 | 38.9571
2016 |  | 6 | 0 |  | 2016-06-01 | 43.3 | 43 | 42.95 | 42.9 | 42.75 | 42.9 | 43.05 | 42.9786
2016 |  | 7 | 1 |  | 2016-07-01 | 57.3 | 56.9 | 56.85 | 56.8 | 56.6 | 56.75 | 56.95 | 56.8786
2016 |  | 8 | 1 |  | 2016-08-01 | 57.3 | 56.9 | 56.85 | 56.8 | 56.6 | 56.75 | 56.95 | 56.8786
2016 |  | 9 | 0 |  | 2016-09-01 | 39.4 | 39.15 | 39.1 | 39.05 | 38.9 | 39 | 39.15 | 39.1071
2016 |  | 10 | 0 |  | 2016-10-01 | 33.3 | 33.25 | 33.25 | 33.2 | 33.05 | 33.15 | 33.3 | 33.2143
2016 |  | 11 | 0 |  | 2016-11-01 | 47.25 | 47.2 | 47.2 | 47.15 | 47 | 47.1 | 47.25 | 47.1643
2016 |  | 12 | 0 |  | 2016-12-01 | 75.6 | 75.55 | 75.55 | 75.5 | 75.35 | 75.45 | 75.6 | 75.5143
2017 | 2017 | 1 | 0 |  | 2017-01-01 | 95.9 | 95.65 | 95.6 | 95.8 | 95.6 | 95.75 | 95.95 | 95.75
2017 |  | 2 | 0 |  | 2017-02-01 | 95.9 | 95.65 | 95.6 | 95.8 | 95.6 | 95.75 | 95.95 | 95.75
2017 |  | 3 | 0 |  | 2017-03-01 | 44.35 | 44.2 | 44.15 | 44.3 | 44.15 | 44.25 | 44.4 | 44.2571
2017 |  | 4 | 0 |  | 2017-04-01 | 44.4 | 44.25 | 44.2 | 44.35 | 44.2 | 44.3 | 44.45 | 44.3071
2017 |  | 5 | 0 |  | 2017-05-01 | 38.55 | 38.4 | 38.35 | 38.5 | 38.35 | 38.45 | 38.6 | 38.4571
2017 |  | 6 | 0 |  | 2017-06-01 | 41.8 | 41.6 | 41.55 | 41.7 | 41.55 | 41.65 | 41.8 | 41.6643
2017 |  | 7 | 1 |  | 2017-07-01 | 50.5 | 50.25 | 50.2 | 50.4 | 50.2 | 50.35 | 50.55 | 50.35
2017 |  | 8 | 1 |  | 2017-08-01 | 50.45 | 50.2 | 50.15 | 50.35 | 50.15 | 50.3 | 50.5 | 50.3
2017 |  | 9 | 0 |  | 2017-09-01 | 37.95 | 37.8 | 37.75 | 37.9 | 37.75 | 37.85 | 38 | 37.8571
2017 |  | 10 | 0 |  | 2017-10-01 | 48.2 | 48.05 | 48 | 48.15 | 48 | 48.1 | 48.25 | 48.1071
2017 |  | 11 | 0 |  | 2017-11-01 | 48.2 | 48.05 | 48 | 48.15 | 48 | 48.1 | 48.25 | 48.1071
2017 |  | 12 | 0 |  | 2017-12-01 | 48.2 | 48.05 | 48 | 48.15 | 48 | 48.1 | 48.25 | 48.1071
2018 | 2018 | 1 | 0 |  | 2018-01-01 | 94.45 | 94.2 | 94.15 | 94.35 | 94.05 | 94.2 | 94.4 | 94.2571
2018 |  | 2 | 0 |  | 2018-02-01 | 94.6 | 94.35 | 94.3 | 94.5 | 94.2 | 94.35 | 94.55 | 94.4071
2018 |  | 3 | 0 |  | 2018-03-01 | 43.35 | 43.2 | 43.15 | 43.3 | 43.1 | 43.2 | 43.35 | 43.2357
2018 |  | 4 | 0 |  | 2018-04-01 | 43.4 | 43.25 | 43.2 | 43.35 | 43.15 | 43.25 | 43.4 | 43.2857
2018 |  | 5 | 0 |  | 2018-05-01 | 37.4 | 37.25 | 37.2 | 37.35 | 37.15 | 37.25 | 37.4 | 37.2857
2018 |  | 6 | 0 |  | 2018-06-01 | 40.1 | 39.95 | 39.9 | 40.05 | 39.85 | 39.95 | 40.1 | 39.9857
2018 |  | 7 | 1 |  | 2018-07-01 | 48.95 | 48.7 | 48.65 | 48.85 | 48.55 | 48.7 | 48.9 | 48.7571
2018 |  | 8 | 1 |  | 2018-08-01 | 49 | 48.75 | 48.7 | 48.9 | 48.6 | 48.75 | 48.95 | 48.8071
2018 |  | 9 | 0 |  | 2018-09-01 | 37.7 | 37.55 | 37.5 | 37.65 | 37.45 | 37.55 | 37.7 | 37.5857
2018 |  | 10 | 0 |  | 2018-10-01 | 48.25 | 48.1 | 48.05 | 48.2 | 48 | 48.1 | 48.25 | 48.1357
2018 |  | 11 | 0 |  | 2018-11-01 | 48.3 | 48.15 | 48.1 | 48.25 | 48.05 | 48.15 | 48.3 | 48.1857
2018 |  | 12 | 0 |  | 2018-12-01 | 48.35 | 48.2 | 48.15 | 48.3 | 48.1 | 48.2 | 48.35 | 48.2357
2019 | 2019 | 1 | 0 |  | 2019-01-01 | 83 | 82.8 | 82.75 | 82.9 | 82.65 | 82.75 | 82.9 | 82.8214
2019 |  | 2 | 0 |  | 2019-02-01 | 83 | 82.8 | 82.75 | 82.9 | 82.65 | 82.75 | 82.9 | 82.8214
2019 |  | 3 | 0 |  | 2019-03-01 | 44.8 | 44.65 | 44.6 | 44.75 | 44.55 | 44.65 | 44.8 | 44.6857
2019 |  | 4 | 0 |  | 2019-04-01 | 44.8 | 44.65 | 44.6 | 44.75 | 44.55 | 44.65 | 44.8 | 44.6857
2019 |  | 5 | 0 |  | 2019-05-01 | 41.3 | 41.15 | 41.1 | 41.25 | 41.05 | 41.15 | 41.3 | 41.1857
2019 |  | 6 | 0 |  | 2019-06-01 | 45 | 44.8 | 44.75 | 44.9 | 44.65 | 44.75 | 44.9 | 44.8214
2019 |  | 7 | 1 |  | 2019-07-01 | 52.75 | 52.5 | 52.45 | 52.65 | 52.35 | 52.5 | 52.7 | 52.5571
2019 |  | 8 | 1 |  | 2019-08-01 | 52.7 | 52.45 | 52.4 | 52.6 | 52.3 | 52.45 | 52.65 | 52.5071
2019 |  | 9 | 0 |  | 2019-09-01 | 47.25 | 47.05 | 47 | 47.15 | 46.9 | 47 | 47.15 | 47.0714
2019 |  | 10 | 0 |  | 2019-10-01 | 52.05 | 51.9 | 51.85 | 52 | 51.8 | 51.9 | 52.05 | 51.9357
2019 |  | 11 | 0 |  | 2019-11-01 | 52.05 | 51.9 | 51.85 | 52 | 51.8 | 51.9 | 52.05 | 51.9357
2019 |  | 12 | 0 |  | 2019-12-01 | 52.05 | 51.9 | 51.85 | 52 | 51.8 | 51.9 | 52.05 | 51.9357
2020 | 2020 | 1 | 0 |  | 2020-01-01 | 83.5 | 83.3 | 83.25 | 83.4 | 83.15 | 83.25 | 83.4 | 83.3214
2020 |  | 2 | 0 |  | 2020-02-01 | 83.5 | 83.3 | 83.25 | 83.4 | 83.15 | 83.25 | 83.4 | 83.3214
2020 |  | 3 | 0 |  | 2020-03-01 | 45.55 | 45.4 | 45.35 | 45.5 | 45.3 | 45.4 | 45.55 | 45.4357
2020 |  | 4 | 0 |  | 2020-04-01 | 45.55 | 45.4 | 45.35 | 45.5 | 45.3 | 45.4 | 45.55 | 45.4357
2020 |  | 5 | 0 |  | 2020-05-01 | 41.85 | 41.7 | 41.65 | 41.8 | 41.6 | 41.7 | 41.85 | 41.7357
2020 |  | 6 | 0 |  | 2020-06-01 | 45.6 | 45.4 | 45.35 | 45.5 | 45.25 | 45.35 | 45.5 | 45.4214
2020 |  | 7 | 1 |  | 2020-07-01 | 54.7 | 54.45 | 54.4 | 54.6 | 54.3 | 54.45 | 54.65 | 54.5071
2020 |  | 8 | 1 |  | 2020-08-01 | 54.7 | 54.45 | 54.4 | 54.6 | 54.3 | 54.45 | 54.65 | 54.5071
2020 |  | 9 | 0 |  | 2020-09-01 | 47.45 | 47.25 | 47.2 | 47.35 | 47.15 | 47.25 | 47.4 | 47.2929
2020 |  | 10 | 0 |  | 2020-10-01 | 52.65 | 52.5 | 52.45 | 52.6 | 52.4 | 52.5 | 52.65 | 52.5357
2020 |  | 11 | 0 |  | 2020-11-01 | 52.65 | 52.5 | 52.45 | 52.6 | 52.4 | 52.5 | 52.65 | 52.5357
2020 |  | 12 | 0 |  | 2020-12-01 | 52.65 | 52.5 | 52.45 | 52.6 | 52.4 | 52.5 | 52.65 | 52.5357