## Slide 1
October 15, 2013 | Reliability committee meeting
Mariah Winkler
Engineer, Resource Analysis & Integration
2017-2018 Capacity Commitment Period
Evaluation of Non-Price Retirements
Submitted between 8/27/2013 – 9/26/2013

## Slide 2: FCA #8 Non-Price Retirement Details
The Non-Price Retirement Request (NPR) submission window for the 2017-2018 CCP opened on June 3, 2013 and closed on October 6, 2013
98 NPRs have been submitted
  5 have been discussed and approved at the August Reliability Committee (RC) meeting
  7 will be discussed today
  86 will be discussed at the December RC Meeting
Today’s meeting shall focus on the below seven resources that have submitted NPRs between 8/27/2013 and 9/26/2013
Capacity Commitment Period | Non-Price Retirement Type (Full or Partial) | Resource ID | Resource Name | Resource Type | Resource Sub-Type | Relevant FCA Summer QC (MW) | Load Zone | Date of Request Receipt | October 15th RC Action
2017-2018 | Full | 611 | VT YANKEE NUCLEAR PWR STATION | Generator | Non-Intermittent | 604.250 | VT | 8/27/2013 | Vote
2017-2018 | Full | 332 | Bar Harbor Diesels 1-4 | Generator | Non-Intermittent | 4.075 | ME | 9/16/2013 | Notification
2017-2018 | Full | 475 | Medway Diesels 1-4 | Generator | Non-Intermittent | 7.950 | ME | 9/16/2013 | Vote
2017-2018 | Full | 339 | Bridgeport Harbor 2 | Generator | Non-Intermittent | 0.000 | CT | 9/20/2013 | Notification
2017-2018 | Full | 13664 | John Street #3 | Generator | Non-Intermittent | 2.000 | CT | 9/26/2013 | Notification
2017-2018 | Full | 13665 | John Street #4 | Generator | Non-Intermittent | 2.000 | CT | 9/26/2013 | Notification
2017-2018 | Full | 12528 | John Street #5 | Generator | Non-Intermittent | 1.900 | CT | 9/26/2013 | Notification

## Slide 3: Overview of the Reliability Analysis
The reliability analysis for NPRs is done in accordance with ISO New England Planning Procedure No. 10 (PP-10) – Planning Procedure to Support the Forward Capacity Market (FCM)
  Obligates the ISO to analyze the thermal, voltage and, if appropriate, the stability impacts of NPRs
  Assumptions for the analysis specified in Appendix A of PP-10
A reliability need constitutes a rejection of the NPR
Consultation with Transmission Owners and ISO Operations
Included as a supplement to this presentation, as part of today’s meeting materials, are the following:
  The Needs Assessments for each of the submitted NPRs

## Slide 4: Background information

## Slide 5: De-List History
Capacity Commitment Period | Resource ID | Resource Name | De-list Type | Retained for Reliability During FCA? | ISO Re-evaluation Determination | Date of Re-evaluation Determination | ISO Re-evaluation Determination
2013-14 | 611 | VT YANKEE NUCLEAR PWR STATION | Dynamic | Yes | Approved | 5/10/2012 | Approved
2014-15 | 611 | VT YANKEE NUCLEAR PWR STATION | Dynamic | Yes | Approved | 11/15/2012 | Approved
2015-16 | 611 | VT YANKEE NUCLEAR PWR STATION | Dynamic | No |  |  | 
Vermont Yankee has sought to de-list in 3 previous auctions
Capacity Commitment Period | Resource ID | Resource Name | De-list Type | Retained for Reliability During FCA?
2015-16 | 475 | MEDWAY DIESELS 1-4 | Dynamic | No
2016-17 | 475 | MEDWAY DIESELS 1-4 | Dynamic | No
Medway Diesels 1-4 has de-listed in 2 previous auctions

## Slide 6: System Upgrades in the Vermont Yankee Region
In addition to new resources procured in the region through the Forward Capacity Market, several transmission upgrades have been recently completed which are helpful to the operation of a system without Vermont Yankee:
  RSP Project #1171 – West Rutland Capacitor Rebuild (Completed 12/2011)
  RSP Project #1256 – Flagg Pond Upgrades (Completed 5/2012)
  RSP Project #1172 – Vermont Shunt Reactors (Completed 3/2013)
  RSP Project #680 – Bellows Falls Rebuild (Completed 9/2013)

## Slide 7: NPR Transmission Operability Analysis
Vermont Yankee and Medway Diesels 1-4

## Slide 8
Voltage Results
  Results of the N-1 and N-1-1 voltage analysis indicated that there are no voltage violations in the respective local study areas caused by the retirement of Vermont Yankee* or Medway Diesels 1-4
Thermal Results
  Results of the N-1 and N-1-1 thermal analysis indicated that there are no thermal violations in the respective local study areas caused by the retirement of Vermont Yankee* or Medway Diesels 1-4
ISO recommends that the NPRs for these resources be accepted
*The recent New Hampshire/Vermont Needs Assessments and Solution Studies included cases that assumed Vermont Yankee as retired.
NPR Transmission Operability Analysis Results

## Slide 9: Advisory Vote
Planning Procedure No. 10, Section 7.5.2 states
“The Reliability Committee shall provide formal input and advice to the ISO through an advisory vote regarding the review of Non-Price Retirement Requests prior to the ISO making a formal determination regarding the reliability impacts of a given Non-Price Retirement Request where, pursuant to Section III.13.2.5.2.5.(a)(i) of Market Rule 1, notification to the requesting Lead Market Participant will be made within 90 days of the submission of the Non-Price Retirement Request.”
The ISO will seek an advisory vote today on the review of Vermont Yankee and Medway Diesels 1-4 NPRs