© ISO New England Inc.

November 2, 2012

2012 Regional System Plan

Preface

ISO New England Inc. (ISO) is the not-for-profit corporation responsible for the reliable operation of New England’s power generation and transmission system. It also administers the region’s wholesale electricity markets and manages the comprehensive planning of the regional power system. The planning process includes the preparation of an annual Regional System Plan (RSP) in accordance with the ISO’s Open Access Transmission Tariff (OATT) and other parts of the Transmission, Markets, and Services Tariff (ISO tariff), approved by the Federal Energy Regulatory Commission (FERC). Regional System Plans meet the tariff requirements by including the following:

- Forecasts of future annual energy use and peak loads (i.e., the demand for electricity) for a five- to 10-year planning horizon and the need for resources (i.e., capacity)

- Information about the amounts, locations, and characteristics of market responses (e.g., generation or demand resources or merchant transmission facilities) that can meet the defined system needs to satisfy demand—systemwide and in specific areas

- Descriptions of transmission projects for the region that could meet the identified needs, as summarized in an RSP Project List, which includes information on project status and cost estimates and is updated several times each year.

RSPs also must summarize the ISO’s coordination of its short- and long-term system plans with those of neighboring systems, the results of economic studies of the New England system, and information that can be used for improving the design of the regional power markets. In addition to these requirements, the RSPs identify the initiatives and other actions the ISO, state officials, regional policymakers, participating transmission owners (PTOs), and other New England Power Pool (NEPOOL) market participants and stakeholders can take to meet the needs of the system.

The 2012 Regional System Plan (RSP12) and the regional system planning process, which identifies the region’s electricity needs and plans for meeting these needs for 2012 through 2021, were developed in full accordance with the requirements established in the OATT.

Regional Transmission Planning Results

New England’s transmission owners have constructed transmission projects throughout the region to provide solutions to the needs identified through the regional planning process, as detailed in past RSPs and supporting reports. These projects have reinforced the transmission facilities serving areas that have experienced load growth, such as Vermont, southern Maine, and the New Hampshire seacoast area. The projects also have reinforced the system in critical “load pockets,” such as Southwest Connecticut (SWCT) and Boston, allowing the import of power from other parts of the system. New interconnections with neighboring power systems also have been placed in service. From 2002 through June 2012, 400 projects were put into service, totaling approximately $4.8 billion of new infrastructure investment.

In addition to the need for transmission development, the region has responded to the need for electric energy and capacity resources. New generating projects totaling 14,432 megawatts (MW) have been interconnected with the system since generators first submitted requests to the ISO to be interconnected to the New England power system in November 1997. Demand resources currently totaling 2,106 MW are part of the regional power system, and 3,646 MW are expected by 2015.

Past RSPs and recent ISO studies also have identified risks to the future economic and reliability performance of the system. This information has continued to assist stakeholders with formulating policies for the region. The information also has been used to identify needed changes to the markets, which must encourage the development of resources where and when needed, such as “fast-start” resources in load pockets. These resources can quickly reach rated capability to help meet reliability requirements and reduce the amount of time generators operate out of economic-merit order.

RSP12 Review and Approval

The regional system planning process in New England is open and transparent and reflects advisory input from regional stakeholders, particularly members of the Planning Advisory Committee (PAC), according to the requirements specified in the OATT. The PAC is open to all parties interested in regional system planning activities in New England.

The ISO and the PAC have discussed study proposals, scopes of work, assumptions, and draft and final results and other materials appearing in RSP12. From September 2011 through August 2012, the ISO hosted 14 PAC meetings, which were attended by 175 stakeholder representatives from 101 entities. The total stakeholder attendance of 714 signifies over 4,400 workforce hours of participation. The ISO also posted to its website PAC presentations, meeting minutes, reports, databases, and other materials. In addition, a public meeting was held on September 13, 2012, to discuss RSP12 and other planning issues facing the New England region.

As required by the OATT Attachment K, the ISO New England Board of Directors has approved the 2012 Regional System Plan.

Contents

Preface	i

Figures	viii

Tables	x

Section 1
Executive Summary	1

1.1 Overview of the Current System and Planning Process	2

1.2 Major Findings and Observations	4

1.2.1 Forecasts of the Peak Demand and Annual Use of Electric Energy and the Effects of
Energy-Efficiency Measures	5

1.2.2 Needs for Capacity and Operating Reserves	7

1.2.3 Transmission System Needs and Solutions	9

1.2.4 Development and Integration of Resources	11

1.2.5 Interregional Planning	16

1.2.6 State, Regional, and Federal Initiatives that Affect System Planning	17

1.3 Conclusions	18

Section 2
Introduction	19

2.1 The Regional System Planning Process	20

2.1.1 Working with the Planning Advisory Committee	20

2.1.2 Forecasting Demand and Determining System Needs	21

2.1.3 Developing Market Resource Alternatives to Address System Needs	21

2.1.4 Planning Transmission Upgrades	21

2.1.5 Providing Information to Stakeholders	22

2.1.6 Coordinating with Neighboring Areas	22

2.1.7 Meeting All Requirements	23

2.1.8 Accounting for Uncertainty	23

2.2 Overview of the New England Electric Power System	23

2.3 Overview of the New England Wholesale Electricity Market Structure	25

2.4 RSP Subareas	28

Section 3
Forecasts of New England’s Peak Demand, Annual Use of Electric Energy, and Energy Efficiency	29

3.1 ISO New England Load Forecasts	29

3.1.1 Economic and Demographic Factors and Electric Energy Use	31

3.1.2 The CELT Forecast and Passive Demand Resources	33

3.1.3 Subarea Use of Electric Energy	34

3.1.4 Summary of Key Findings of the Load Forecast	36

3.2 Energy-Efficiency Forecast for New England	36

3.2.1 Background and Update	36

3.2.2 Methodology and Data Collection	37

3.2.3 Results	39

3.2.4 Summary of the Energy-Efficiency Forecast and Methodology	42

Section 4
Resources—Adequacy, Capacity, and Reserves	43

4.1 Determining and Meeting Resource Adequacy Needs	43

4.1.1 Systemwide Installed Capacity Requirement	43

4.1.2 Local Resource Requirements and Limits	45

4.1.3 Capacity Supply Obligations	47

4.1.4 Systemwide Resource Needs	50

4.2 Analyzing Operable Capacity	51

4.2.1 Approach	51

4.2.2 Results	52

4.3 Determining Operating Reserves and Regulation	53

4.3.1 Systemwide Operating-Reserve Requirements	54

4.3.2 Forward Reserve Market Requirements for Major Import Areas	55

4.4 Identifying New England’s Generating Resources	58

4.4.1 Existing Generating Resources in New England	59

4.4.2 Generating Units in the ISO Generator Interconnection Queue	60

4.5 Analyzing Market Resource Alternatives	62

4.5.1 Pilot Studies	63

4.5.2 Stakeholder Input	64

4.5.3 Next Steps	64

4.6 Summary	65

Section 5
Transmission Security and Upgrades	67

5.1 The Need for Transmission Security	67

5.2 Transmission Planning Process	68

5.2.1 Needs Assessments and Solutions Studies	69

5.2.2 Project Timing	69

5.3 Types of Transmission Upgrades	70

5.3.1 Reliability Transmission Upgrades	70

5.3.2 Market Efficiency Transmission Upgrades	70

5.3.3 Generator Interconnection Upgrades and Generator Interconnection-Related Upgrades	71

5.3.4 Elective Transmission Upgrades and Merchant Transmission Facilities	71

5.4 RSP Project List and Projected Transmission Project Costs	72

5.5 Transmission System Performance Needs Assessments and Upgrade Approvals	74

5.5.1 Northern New England	75

5.5.2 Southern New England	85

5.6 Information on Critical Load Levels	98

5.7 Transmission Improvements to Load and Generation Pockets Addressing Reliability Issues	98

5.8 Out-of-Merit Operating Situations	99

5.9 Other Needed and Elective Transmission Upgrades	100

5.9.1 Needed Market-Efficiency-Related Transmission Upgrades	100

5.9.2 Transmission Improvements to Mitigate Congestion	100

5.9.3 Reliability Transmission Upgrade Improvements to Load and Generation Pockets	100

5.9.4 Required Generator-Interconnection-Related Upgrades	101

5.9.5 Elective Transmission Upgrades and Merchant Transmission	101

5.10 Summary	102

Section 6
Strategic Planning Initiative	104

6.1 The SPI Risks and Challenges	104

6.1.1 Risk 1: Resource Performance and Flexibility	105

6.1.2 Risk 2: Increased Reliance on Natural-Gas-Fired Capacity	106

6.1.3 Risk 3: Potential Retirement of Generators	107

6.1.4 Risk 4: Integration of a Greater Level of Variable Energy Resources	108

6.1.5 Risk 5: Alignment of Markets with Planning	108

6.1.6 Summary of Risk Interactions	109

6.2 Analyses and Updates to Studies and Other Actions Supporting the Strategic Planning Initiative	109

6.2.1 Improvements in System Operations (Risk 1)	110

6.2.2 Integration of Renewable Resources (Risks 1, 4, and 5)	110

6.2.3 Economic Performance and Related Studies (Risks 1 to 5)	110

6.2.4 Fuel Diversity and Supply Studies and Actions to Address the Issues (Risk 2)	111

6.2.5 Impacts of Environmental Regulations on Generating Units and the Power System (Risk 3)	112

6.2.6 Transmission System and Market Resource Alternative Analyses (Risks 1 to 5)	112

6.2.7 Strategic Transmission Analysis (Risks 3 and 4)	113

6.3 Summary	116

Section 7
Fuel Supply and Diversity	117

7.1 Capacity Mix and Electric Energy Production by Fuel Type	117

7.2 2011/2012 Overview of System Operations Events	123

7.3 Natural Gas Supply and Infrastructure Update	124

7.3.1 Natural Gas Development and Infrastructure	124

7.3.2 The ISO’s 2011 Natural Gas Study	125

7.4 Nuclear Supply Update	128

7.5 Hydroelectric Update	130

7.6 Renewable Portfolio Standards and Renewable Project Development	131

7.6.1 Renewable Resources in the ISO Generation Queue	131

7.6.2 Project Development Uncertainty	133

7.6.3 Update of Renewable Projects Indicated by NESCOE	134

7.6.4 Update on Meeting State RPSs and Other Targets	134

7.6.5 Wind	142

7.6.6 Distributed Generation	143

7.7 Conclusions	150

Section 8
Environmental and Economic Performance of the System	151

8.1 Environmental Performance of the System	151

8.1.1 Potential Regional Impacts of EPA Regulations	151

8.1.2 Generator Emissions	156

8.1.3 Greenhouse Gas Reduction Programs	158

8.1.4 Environmental Summary	160

8.2 Economic Performance Studies	160

8.2.1 Update of the 2011 Economic Study	161

8.2.2 Economic Study Requests, 2012	168

8.2.3 Generic Capital Costs of New Supply-Side Resources	169

8.3 Conclusions	170

Section 9
Planning Coordination, Studies, and Initiatives	172

9.1 Federal Initiatives	172

9.1.1 FERC Order 1000 and Order 764	172

9.1.2 Metrics Report	172

9.1.3 US Department of Energy Congestion Studies	173

9.2 Interregional Coordination and Initiatives	173

9.2.1 EIPC Studies of the Eastern Interconnection	174

9.2.2 NERC Activities	175

9.2.3 IRC Activities	176

9.2.4 Northeast Power Coordinating Council Studies and Activities	176

9.2.5 Northeastern ISO/RTO Planning Coordination Protocol	176

9.3 Regional Initiatives	177

9.3.1 Coordination among the New England States	178

9.3.2 NESCOE Updates	178

9.3.3 New England Governors Eastern Canadian Premiers/Northeast International Committee
on Energy	178

9.3.4 Forward Capacity Market Updates	179

9.3.5 Price-Responsive Demand	180

9.3.6 Consumer Liaison Group	180

9.4 ISO Initiatives	181

9.4.1 Updates on Developing and Integrating Smart Grid and Other New Technologies	181

9.4.2 Improvements to Transmission Cost Estimate Tracking	184

9.4.3 Improvements to System Restoration and Black Start	184

9.5 State Initiatives, Activities, and Policies	185

9.5.1 Connecticut	185

9.5.2 Maine	186

9.5.3 Massachusetts	186

9.5.4 New Hampshire	188

9.5.5 Rhode Island	189

9.5.6 Vermont	189

9.6 Summary of Initiatives	190

Section 10
Key Findings and Conclusions	191

Appendix A
Glossary	197

Appendix B
Acronyms and Abbreviations	209

# Figures

Figure 2-1: 	Key facts about New England’s electric power system and wholesale electricity markets.	24

Figure 2-2: 	Active-demand-resource dispatch zones in the ISO New England system.	27

Figure 2-3: 	RSP12 geographic scope of the New England electric power system.	28

Figure 3-1: 	The ISO’s actual summer peak loads (i.e., reconstituted for OP 4 and FCM passive demand resources) and the 50/50 and 90/10 forecasts (MW).	31

Figure 3-2: 	“Economy.com” forecasts of New England gross state product (indexed to 1980 = 100)
from November 2011 and October 2010 forecasts.	33

Figure 3-3: 	RSP12 annual energy-use load forecast (diamond), load forecast minus FCM results (square),
and load forecast minus the FCM and minus the energy-efficiency forecast (triangle) for 2015
to 2021 (GWh).	41

Figure 3-4: 	RSP12 summer peak demand forecast (90/10) (diamond), load forecast minus FCM results
(square), and load forecast minus the FCM and minus the energy-efficiency forecast (triangle)
for 2015 to 2021 (MW).	41

Figure 4-1: 	Projected summer operable capacity analysis, 2012 to 2021.	52

Figure 4-2: 	Capacity of generation-interconnection requests by RSP subarea from November 1997
to April 2012.	60

Figure 4-3: 	Resources in the ISO Generator Interconnection Queue, by state and fuel type,
as of April 1, 2012 (MW and %).	61

Figure 4-4: 	Resources in the ISO Generator Interconnection Queue, by RSP subarea and fuel type,
as of April 1, 2012 (MW).	62

Figure 4-5: 	Percentage of resources in the ISO Generator Interconnection Queue, by RSP subarea
and fuel type, as of April 1, 2012.	62

Figure 5-1: 	Map of constraints in southern New England.	87

Figure 6-1: 	The five challenges of the Strategic Planning Initiative.	105

Figure 6-2: 	Conceptual transmission plan for the delivery of 2 GW of wind resources.	115

Figure 7-1: 	New England’s 2012 summer generation capacity mix by primary fuel type (MW and %).	118

Figure 7-2: 	New England electric energy production in 2011 by fuel type (GWh and %).	121

Figure 7-3: 	New England energy imports and exports by balancing authority area in 2011 (GWh).	121

Figure 7-4: 	New England’s generating capacity and electric energy by fuel type, 2000 and 2011.	122

Figure 7-5: 	ICF Natural Gas Study Reference Case scenario run for the existing generation fleet,
winter peak-day gas supply surplus and deficits.	127

Figure 7-6: 	Proposed New England capacity from renewable resources in the ISO Generation
Interconnection Queue, including non-FERC jurisdictional projects,
as of April 1, 2012 (MW and %)	132

Figure 7-7: 	Estimated annual electric energy from proposed New England renewable resources
in the ISO’s Generator Interconnection Queue, including non-FERC-jurisdictional projects,
as of April 1, 2012 (GWh).	133

Figure 7-8: 	RPS state targets for "new" renewable resources in 2021.	135

Figure 7-9: 	Passive demand resources in the 2012 CELT, 2012 to 2021 (includes energy-efficiency
forecast, 2015 to 2021) (GWh).	138

Figure 7-10: 	Total projected RPS targets (all classes) and goals for New England, 2012 to 2021 (GWh).	139

Figure 7-11: 	Incremental growth in the RPS class targets for the "new" renewable resources
for the New England states, net of 2011 RPS targets, 2012 to 2021 (GWh).	140

Figure 7-12: 	Estimated incremental electric energy from meeting new RPS targets (2012 to 2021)
compared with estimated electric energy from various percentages of new renewable
projects in the ISO queue as of April 1, 2012 (GWh).	141

Figure 7-13: 	Solar PV energy generated in New England by quarter, 2005 to 2011,
based on NEPOOL GIS data.	149

Figure 8-1: 	Existing or planned advanced pollution control technologies at New England generators, 2011.	156

Figure 8-2: 	Annual CO2 emissions—New England historical (2000 to 2011) and RGGI compliance period
(2009 to 2011)—by state (million short tons).	158

Figure 8-3: 	Renewable energy clusters evaluated in the 2011 economic study.	163

Figure 8-4: 	The New England transmission system “pipes and bubbles” as modeled in this study.	164

Figure 9-1: 	Existing and planned FACTS devices in New England	183

# Tables

Table 3-1 	Summary of Annual Electric Energy Use and Peak Demand for New England and the States	30

Table 3-2 	New England Economic and Demographic Forecast Summary	32

Table 3-3 	Forecasts of Annual Use of Electric Energy and Peak Demand in RSP Subareas, 2012 and 2021	34

Table 3-4 	Forecasts of RSP Subarea Peak Demand, 2012	35

Table 3-5  	ISO New England’s Final Energy-Efficiency Forecast for 2015 to 2021 (GWh, MW)	40

Table 4-1 	Actual and Representative New England Net Installed Capacity Requirements and Resulting Reserves, 2012 to 2021 (MW, %)	45

Table 4-2 	Actual LSRs and MCLs for the 2012/2013 to 2015/2016 Capacity Commitment Periods	46

Table 4-3 	Summary of the FCA Obligations at the Conclusion of Each Auction (MW)	48

Table 4-4 	Results of the FCA by Capacity Zone at the Conclusion of Each Auction (MW, $/kW-month)	49

Table 4-5 	Capacity Supply Obligation for New Capacity Procured during the Forward Capacity
Auctions (MW)	50

Table 4-6 	Future Systemwide Needs (MW)	51

Table 4-7 	Projected New England Operable Capacity Analysis for Summer, 2012 to 2021,
Assuming 50/50 Loads (MW)	52

Table 4-8 	Projected New England Operable Capacity Analysis for Summer, 2012 to 2021,
Assuming 90/10 Loads (MW)	53

Table 4-9  	Representative Future Operating-Reserve Requirements in Major New England
Import Areas (MW)	56

Table 4-10 	2012 Seasonal Claimed Capability for ISO New England Generating Resources
by Assumed Operating Classification, Systemwide and by RSP Subarea (MW)	58

Table 4-11 	RSP12 Generating Capacity by Subarea, SMD Load Zone, and State, 2012	59

Table 4-12 	Summary of Queue Projects as of April 1, 2012	61

Table 5-1 	Cost of Reliability Projects as of June 2012 Plan Update (Millions of $)	73

Table 5-2 	Actual and Forecast Regional Network Service Rates, 2011 to 2016	74

Table 5-3 	Net Commitment-Period Compensation by Type and Year (Million $)	101

Table 7-1  	New England’s 2012 Summer Generation Capacity Mix by Fuel Type Compared with the 2010 Nationwide Summer Capacity Mix (%)	119

Table 7-2  	New England’s 2011 Electric Energy Generation Mix by Fuel Type Compared with the 2011 Nationwide Energy Mix (%)	120

Table 7-3 	New England’s 2012 Summer Generation Capacity Mix by Fuel Type
and In-Service Dates (MW, %)	122

Table 7-4 	New England Operating Nuclear Power Plants	128

Table 7-5 	Estimated Energy from New England Renewable Energy Projects in the ISO Queue,
as of April 1, 2012	132

Table 7-6 	Summary of All Projects and Wind Projects in the ISO Queue as of April 1, 2012	133

Table 7-7 	Technologies Designated in Renewable Portfolio Standards in New England,
as of April 1, 2012	136

Table 7-8 	Annual Percentages of Electric Energy Provided by Affected Load-Serving Entities
for Meeting the State’s RPS Classes, 2012-2021, as of April 1, 2012	137

Table 7-9 	State Net-Metering Rules for Distributed Generation	145

Table 7-10 	Summary of Estimates for Potential PV Development in 2021 by State	148

Table 8-1 	New and Upcoming EPA Environmental Regulations, Targeted Pollutants or Actions,
and Control Options	153

Table 8-2 	New England Capacity Potentially Affected by EPA’s Proposed Cooling Water Intake Rule
and the Amount of Once-Through Water Cooling Technology Used, 2010 (MW, %)	154

Table 8-3 	System Emissions Rates, 2009 and 2010 (lb/MWh)	157

Table 8-4 	Marginal Emissions Rates, 2009 and 2010 (lb/MWh)	157

Table 8-5  	Single-Value Summer-Peak Transmission Interface Limits for 2016 Used in the IREMM Model	165

Table 8-6 	Capacity and Energy Assumed for the Three Primary Wind-Penetration Scenarios	166

Table 8-7  	Generic Capital Costs of New Supply-Side Resources	170

# Executive Summary

The ISO New England (ISO) 2012 Regional System Plan (RSP12) presents the results of load, resource, and transmission analyses of New England’s electric power system for the 10-year planning period through 2021. The report describes the major factors influencing the development of the electric power system for these future years and how the region can provide a reliable and economical system in compliance with federal and state regulations and guidelines. In addition to complying with all applicable sections of the ISO’s Transmission, Markets, and Services Tariff (ISO tariff), approved by the Federal Energy Regulatory Commission (FERC), RSP12 and the system planning process satisfy the relevant criteria and requirements established by the North American Electric Reliability Corporation (NERC), the Northeast Power Coordinating Council (NPCC), participating transmission owners (PTOs), and the ISO.

Over the past decade, the system planning process and market design have fostered significant improvements to the region’s generation and demand resources and transmission system. Almost one-third of the region’s existing generation was built during the last 11 years, and more than half of the region’s electric energy production now comes from efficient, gas-fired combined-cycle generators. Additionally, the amount of demand resources in the region has grown significantly. The transmission system, which for decades saw little investment, has been upgraded to better serve the region’s load. Building on the results and recommendations of previous Regional System Plans, RSP12 presents the results of newly completed studies and summarizes the new and planned infrastructure for all areas of New England. RSP12 also discusses ongoing, new, and pending analyses based on the current system. In addition, RSP12 discusses state and federal policies that affect the planning process, system reliability, and the economic performance of the system.

Notwithstanding the region’s recent improvements, challenges remain across the 10-year planning horizon for maintaining the reliable and efficient operation of the New England power system. These challenges include the following:

- Improving resource performance and flexibility

- Maintaining reliability given the region’s increased reliance on natural-gas-fired capacity

- Planning for the potential retirement of generators

- Integrating a greater level of intermittent resources (i.e., variable energy resources; VERs)

- Aligning wholesale market design with regional transmission planning

To address these challenges and prepare for changes likely to confront the New England power system, the region is conducting a Strategic Planning Initiative. Through the initiative, the ISO and regional stakeholders have defined the region’s key issues and risks and currently are assessing potential enhancements to the planning process and wholesale markets to help ensure a reliable system and efficient marketplace in the long term. As part of this process, the region is assessing the tools available to ensure system reliability, such as various market mechanisms and system operating procedures, and is determining whether to improve and better integrate these tools, develop and implement new approaches, or undertake a combination of both approaches. The region is well poised to meet the upcoming challenges identified by the Strategic Planning Initiative and through other stakeholder efforts, such as the Planning Advisory Committee (PAC) and the New England Power Pool (NEPOOL) committee structure.

This section provides an overview of the current system, highlights of the planning process, and major findings and observations of system studies and regional activities.

## Overview of the Current System and Planning Process

The regional planning process, as summarized in the Regional System Plan, is comprehensive, providing information to stakeholders on the load and energy-efficiency (EE) forecasts, resource and transmission development needs, infrastructure improvements, interregional coordination, and the results of economic studies and other initiatives, as highlighted below.

The regional forecasts show modest growth in peak demand and annual energy use during a gradual recovery from the widespread recession. The newly developed energy-efficiency forecast of demand-side resources shows that state efficiency programs slow load growth further.

Historically, supply and demand resources have responded to the wholesale electricity markets and public policies, and the region has considerable potential for developing new resources where and when needed. The ISO New England Generation Interconnection Queue (the queue) and energy-efficiency forecast indicate this potential for the future development of resources. However, the region is at risk of losing resources to retirements and, as identified in a study of the region’s natural gas supply, of becoming increasingly reliant on natural gas to generate electric energy. To begin to address these issues, the region is examining modifications to the markets that would improve resource performance and development. The region also is revising operating procedures that address the reliability issues. Improved communications between the electric power and natural gas system operators are in place and have improved operational coordination. Additional efforts are underway to better coordinate electricity and gas markets and develop and provide incentives for generators to have reliable fuel arrangements that would, for example, encourage investment in oil inventory or the commitment to firm pipeline transportation contracts.

RSP assessments, including those on resource adequacy, operating reserves, and transmission security, have shown the amounts, locations, and types of resources and transmission infrastructure the system requires for complying with criteria and standards. While transmission upgrades continue to progress throughout the region, certain projects are being deferred or modified because of the reduction in net loads indicated by the load and EE forecasts and the addition of new market resources. However, additional infrastructure improvements may be required in the long term to accommodate the likely resource retirements, integrate remote renewable resources, and continue meeting reliability needs. Evolving system conditions may require updates to the planning process and identified needs. For example, the efficient and cost-effective development of needed system infrastructure could be improved by better aligning the market resource procurement process with the system planning process.

Under the Strategic Planning Initiative, the ISO and regional stakeholders currently are examining ways to better coordinate the market structure and planning processes. The initiative also has defined other current and potential tools for preserving reliable and efficient system operations and maintaining system security. The current tools include committing and dispatching resources out-of-merit, procuring more reserves, issuing “gap” requests for proposals to meet short-term reliability needs, procuring emergency capacity through operating procedures, and conducting other special operator actions during fuel shortages.

Potential new tools for improving reliable operations and system security include market rules that can achieve the following:

- Increase economic incentives for resource performance, assess penalties for failing to perform, and more fully value needed operating resource characteristics

- Coordinate the ISO’s Day-Ahead Energy Market schedule with the natural gas industry’s intraday nomination schedules, which would allow gas-fired generators to submit energy supply offers in the wholesale energy market with more information about their fuel procurements for generating electric energy

- Allow resources to update their electric energy offers hourly to reflect changing fuel prices

- Provide supplemental compensation for needed resources

- Incent dual-fuel capability

- Improve the process for coordinating the timing of developing market resource alternatives to transmission development (i.e., market resource alternatives; MRAs)

- Facilitate the integration of intermittent resources

The ISO also is conducting studies to support the Strategic Planning Initiative’s longer-term vision of the system. Current analyses are identifying possible changes in the performance characteristics, obligations, and flexibility of the region’s resources. Additional studies are more fully identifying the exposure to potential regional and interregional natural gas shortfalls that could limit electric energy production.

An examination of possible generator retirements shows that the units most likely to retire have poor economic performance and could require major capital improvements for complying with pending and final US Environmental Protection Agency (EPA) and state environmental regulations. A Strategic Transmission Analysis is evaluating how the retirement of “at-risk” units will affect reliability. This analysis also is developing a conceptual system buildout that would be necessary for combinations of unit retirements, repowering, and integrating remote wind generators.

The integration of intermittent resources, however, presents challenges for operating the system and developing transmission. Economic studies of various system-expansion scenarios have shown potential production costs, transmission congestion, and a number of other metrics. Other analyses have identified operational issues and solutions to facilitate the integration and large-scale use of intermittent resources. Additional studies are evaluating the ability of merchant and elective transmission projects to access renewable energy sources within New England and in neighboring regions.

The ISO is implementing many of the recommendations of a prior study, the New England Wind Integration Study (NEWIS), such as the development of a centralized wind power forecast of the region’s wind generation. Solar photovoltaic resources have grown in the region, and their continued growth is anticipated. The ISO will continue to track these resources and resolve any potential operational and planning issues that may emerge as the use of these resources expands.

Interregional planning and environmental assessments have become increasingly important for the ISO and stakeholders, who together are addressing issues raised within the region and with neighboring regions. New England is positioning itself to integrate clean and renewable resources and import additional hydroelectric and wind energy from neighboring Canadian provinces. The Northeast Coordinated System Plan 2011 (NCSP11) demonstrates coordinated planning with the New York ISO (NYISO), PJM Interconnection (PJM), and other interregional organizations, such as the NPCC and NERC. Compliance with FERC Order 1000 on transmission planning and cost allocation, however, will require improvements in the regional planning process. These improvements must consider public policies, enhance interregional planning, and allocate transmission project costs for public-policy projects and interregional projects. The ISO supports other interregional planning efforts, such as the Eastern Interconnection Planning Collaborative (EIPC) and the US Department of Energy (DOE) congestion studies.

To address the issues raised during the regional system planning process and the results of studies and initiatives underway, the region is considering updating the regional planning process; improving the wholesale electricity markets for energy, capacity, and ancillary services; and revising operating procedures.

## Major Findings and Observations

This section presents an overview of the major findings of the RSP12 load forecast and energy-efficiency forecast; supply and demand resource and transmission planning efforts; market outcomes; economic studies; and other programs, projects, and initiatives that are part of the system planning process. The sections of the report that contain more details of these findings and observations are indicated.

For all RSP12 analyses, the ISO used a number of assumptions, which are subject to uncertainty over the course of the planning period. Some factors, as follows, are subject to change, which may vary RSP12 results and conclusions and ultimately influence the future development of transmission and generation and demand resources:

Demand and energy-efficiency forecasts, which are dependent on the economy, new building and federal appliance-efficiency standards, state EE goals and program implementation, and other considerations

Resource availability, which is dependent on physical and economic parameters that affect the performance, development, and retirement of resources

Environmental regulations and compliance strategies, which can vary with changes in public policies, economic parameters, and technology development

Fuel price forecasts, which change with world markets and infrastructure development

Market rules and public policies, which can alter the development of market resources

Technology development and its deployment, which may improve the physical ability and the economic viability of new types of power system equipment and the efficiency of operating the power system

Timing of planned system improvements, which can be subject to siting and construction delays and changes to the system

The ISO considers these factors for developing a robust plan. While each RSP is a snapshot in time, the planning process is continuous, and results are updated as needed, accounting for the status of ongoing activities and new initiatives.

### Forecasts of the Peak Demand and Annual Use of Electric Energy and the Effects of Energy-Efficiency Measures

The amount and location of the net system load may affect the need for new resources and the required timing of some transmission projects. For the 10-year planning period, RSP12 summarizes the growth of electric energy usage, both annually and at the peak hour—for the entire system, individual states, and smaller areas of the power system. RSP12 also summarizes a new method to forecast the long-term annual and peak energy-efficiency savings for 2015 to 2021. (Section 3.2)

#### Peak Demand and Annual Use of Electric Energy and Load Growth

For RSP12, the 50/50 “reference case” summer peak forecast is 27,440 megawatts (MW) for 2012, which grows to 31,255 MW for 2021. The 90/10 “extreme case” summer peak forecast, which represents summer heat waves, is 29,620 MW for 2012 and grows to 33,765 MW in 2021. The actual load has been near or above the 50/50 forecast 10 times during the last 20 years because of weather conditions; six of these 10 times, the load has been near or has exceeded the 90/10 forecast. The ISO forecasts the 10-year growth rate to be 1.5% per year for the summer peak demand, 0.6% per year for the winter peak demand, and 0.9% per year for the annual use of electric energy. The annual load factor (i.e., the ratio of the average hourly load during a year to peak hourly load) continues to decline from 57.5% in 2012 to 54.9% in 2021. (Section 3.1)

The RSP12 forecasts for the annual use of electric energy and winter peaks are not materially different from the RSP11 forecast. The RSP12 forecast of summer peak demand is lower than the RSP11 forecast by approximately 660 MW in 2012 and 290 MW by 2021. (Section 3.1)

The load forecast is highly dependent on the economic forecast, which reflects (1) the recent recession ending in 2009, followed by weak economic growth beginning in 2010, and (2) a projected moderate rebound in 2014 through 2016, followed by sustained economic growth. The RSP12 forecasts also incorporate the expected effects of federal EE standards for appliances and commercial equipment, which will go into effect in 2013, and the historical energy-efficiency savings (i.e., reductions in past loads resulting from energy-efficiency measures). Another factor for developing the forecasts is that demand resources that cleared the Forward Capacity Market (FCM) are considered to be sources of supply and not demand-side measures. The forecast of the energy savings attributable to federal appliance standards is 1.6% of the total gross electric energy consumption for 2021; the forecasted energy-efficiency savings from FCM passive demand resources is 11.4% for 2021. These represent a total energy savings of 13.0% of the gross consumption of electric energy projected for 2021. (Section 3.1)

#### Energy-Efficiency Forecast

In response to stakeholder requests, an EE forecast was developed for estimating long-term energy savings and reductions in peak demand not otherwise attributed to savings from FCM passive demand resource or reflected in the ISO load forecast. The EE forecast will be used in conjunction with the passive demand resources that cleared the Forward Capacity Market for 2012 through 2014.

The ISO first met with state energy-efficiency program administrators, other Independent System Operators and Regional Transmission Organizations (ISO/RTOs), various state agencies, and regional stakeholders to identify and discuss issues associated with developing a method of improving EE forecasts and incorporating EE savings from state programs into the ISO’s planning process. Through an open stakeholder process, the ISO developed a methodology for forecasting the amount of energy and peak load savings that can be obtained from energy-efficiency programs. This methodology is based on projections of funding levels for state-sponsored energy efficiency, the amount of energy savings per dollar spent, and the amount of peak load savings per megawatt-hour of energy saved. The EE forecast accounts for uncertainty factors, such as the amounts and spend rates of future budgets and decreases in the energy savings per dollar spent, which may affect the amounts of EE successfully developed. The methodology developed was the first of its kind nationally because it captures and compiles data for six states to create a regional EE forecast. The EE investment is expected to be approximately $8 billion from 2012 through 2021. (Section 3.2)

The EE forecast for 2015 through 2021 shows an annual average regionwide energy savings of approximately 1,343 gigawatt-hours (GWh), an average reduction in peak loads of 206 MW per year. The EE forecast shows savings of 1,619 MWh in 2015, declining to 1,092 MWh in 2021. Similarly, the peak load savings from EE declines from 249 MW in 2015 to 168 MW in 2021. The EE forecast also shows results for each New England state. (Section 3.2.3)

### Needs for Capacity and Operating Reserves

RSP12 quantifies the system needs for capacity and operating reserves and the amounts procured through the Forward Capacity Market and the locational Forward Reserve Market (FRM). The RSP also discusses pilot analyses of market resource alternatives.

#### Capacity

The current development of generation, demand, and import capacity resources in the region is expected to provide the capacity needed to meet the requirements for resource adequacy (i.e., the minimum amount of capacity the region will require, called the Installed Capacity Requirement [ICR]). The net ICR is expected to grow from 32,010 MW in 2012 to a representative value of 35,600 MW by 2021. (Section 4.1.1)

Resources are projected to be sufficient for the 2015/2016 capacity commitment period. The region would have a surplus of 2,660 MW in 2017/2018, which would decrease to 1,903 MW in 2021/2022, accounting for the load and energy-efficiency forecasts and assuming all resources with capacity supply obligations for FCA #6 remain in service. (Section 4.1.4)

The amount of capacity resources in the Northeast Massachusetts (NEMA)/Boston capacity zone is projected to marginally meet the resource adequacy requirements for that area. The fifth Forward Capacity Auction (FCA #5) recognized the “nonprice” retirement request of Salem Harbor units #1, #2, #3, and #4 (near Boston), representing nearly 750 MW. In FCA #6, the local sourcing requirement (LSR) for NEMA/Boston was 3,289 MW, and the resources in that area totaled 3,348 MW. Additional load growth or retirements in NEMA/Boston would create the need to develop new resources. Recent developments in NEMA/Boston associated with reduced liquefied natural gas (LNG) supplies further highlighted reliability concerns in this zone. (Section 4.1.3.2 and Section 7)

Other resources throughout the region, particularly demand resources, have submitted nonprice retirement requests, and approximately 1,662 MW of one-year dynamic and static delist bids were approved in FCA #6. The high likelihood of resource retirements at future auctions also will likely accelerate the need for new resources, and the region already is beginning to lose old, relatively inefficient generating facilities. Additionally, coal and oil resource owners could choose not to invest in environmental remediation measures called for in pending or required regulations, which could force these units to shut down. (Section 4.1.3, Section 7, and Section 8.1.1)

Changes directed by FERC also will improve the market incentives for developing resources when and where needed, and the Strategic Planning Initiative is assessing ways to enhance the efficient development of resources. In general, the development of new resources near the system load centers in NEMA/Boston and Connecticut and in other load pockets throughout the system mitigates reliability risks associated with resource retirements, improves system performance, and allows for a more optimal use of the existing infrastructure. Resources in the ISO queue, which included 6,600 MW as of April 1, 2012; new demand resources; and new import capacity from neighboring regions are in various stages of development and could address these issues. (Sections 4.1, 6.1, and 9.1)

#### Operating Reserves and Resource Flexibility

Operating reserve is the megawatt capability of a power system greater than system demand, which the system requires to preserve system reliability—such as by providing frequency regulation, correcting errors in load forecasting, and handling forced outages—when resources or transmission facilities are lost because of a contingency. The need for operating reserves is a performance-based requirement. Resources participating in the locational Forward Reserve Market and other committed and on-line resources are helping satisfy the operating-reserve requirements of the region overall and in major load pockets to cover contingencies.

As a result of transmission upgrades and other resource additions, the Greater Southwest Connecticut area is not expected to need any additional local operating reserve for 2013 to 2016. Over the same period, the forecasted need for the Greater Connecticut area is 400 to 1,100 MW during the summer, and the need for the BOSTON area ranges from 0 to 200 MW. The addition of in-merit generation or demand resources within the major import areas, improvements to the transmission system, or some combination of all measures would decrease the need to locate operating reserves within these areas. (Section 4.3)

Unit retirements, limited energy resources, and the addition of intermittent resources, particularly wind, will likely increase the need for flexible operations and resources to provide reserves, regulation service, and ramping in the most effective locations. The ISO is considering a review of the requirements for operating reserve and an evaluation of potential enhancements to the wholesale electricity markets to better meet operational needs and improve the long-term efficiency and reliability of the system. (Section 6.1)

#### Analysis of Market Resources as an Alternative to Transmission Investment

Regional System Plans provide considerable information on the desired amounts, types, locations, and performance requirements of resources for meeting system needs. In general, developing resources in load pockets is beneficial, especially the load pockets with exposure to potential generator retirements. However, assessing the suitability of resources during the planning process can be challenging because of the wide variability of the characteristics, locations, and possible combinations of resources, such as central station and distributed generation resources, end-use efficiency, and storage technologies.

In response to PAC requests for more details about resources that could meet system needs, the ISO performed a pilot study for the Vermont/New Hampshire (VT/NH) area, which demonstrated how resources of various sizes and at various locations could meet thermal system performance requirements for 2020. The analysis identified the critical load levels and hypothetical supply-side units, which could eliminate thermal overloads for normal and contingency conditions. The ISO has applied the lessons learned from the VT/NH study to the next pilot study of the Greater Hartford and Central Connecticut area and has updated the PAC on this pilot. Under the scope of the Strategic Planning Initiative, the region will consider modifying the wholesale electricity market design to better align the process for identifying market resource alternatives with the planning process that identifies transmission solutions. (Section 4.5.1 and Section 6)

### Transmission System Needs and Solutions

The performance of the transmission system must meet reliability requirements in accordance with applicable NERC, NPCC, and ISO criteria and standards. To meet these requirements, RSP12 identifies the transmission development needed in the region and summarizes the status of ongoing transmission studies and projects in various stages of implementation. Transmission projects placed in service over the past 10 years have reduced congestion and decreased dependence on generating units located in load pockets. In 2011, systemwide congestion-related costs totaled approximately $18 million, and payments for generators in “must-run” situations that provided second-contingency coverage and voltage control totaled just under $12 million (Section 5.2)

#### Transmission Projects

The ISO regularly discusses system needs and the justification for transmission improvements with the PAC, which provides guidance and comments on study scopes, assumptions, and results. All transmission projects are coordinated with other regions as warranted. The ISO also has advised the PAC of the regional network service (RNS) rate and projections developed by the PTOs. (Section 5.3)

The RSP Project List is a summary of transmission projects under various stages of development (i.e., concept, planned, proposed, and under construction), as required under the Open Access Transmission Tariff (OATT) to meet regional system needs. It also includes information on project status and cost estimates. The descriptions of transmission projects in RSP12 are based on the June 2012 update, which includes 256 projects at a total cost of approximately $6.0 billion. The ISO updates the RSP Project List at least three times per year, capturing improvements identified and changes in project status. In addition, the ISO makes available to stakeholders the databases used for simulating the power system. The status of several major projects under development is as follows: (Section 5.4)

- The Maine Power Reliability Program (MPRP), for which the Maine Public Utilities Commission (MPUC) has approved most of the components, establishes a second 345 kilovolt (kV) path in northern Maine from Surowiec to Orrington and adds new 345 kV lines in southern Maine, creating a third parallel path from Surowiec to Eliot. Many components of these new paths are under construction. When completed, they will provide basic infrastructure needed for increasing the ability to move power into Maine from New Hampshire and will improve the ability of the transmission system within Maine to move power into the local load pockets as necessary. The ISO is conducting an analysis of the extent to which transfer capability through Maine has been changed because of the MPRP project. The MPRP project is scheduled for completion by early 2015. (Section 5.4)

- The New England East–West Solution (NEEWS) series of projects has been identified to improve system reliability: (Section 5.4)

- The ISO conducted the needs assessments and solutions studies, and the affected states (Massachusetts, Connecticut, and Rhode Island) completed the siting proceedings; the Springfield and Rhode Island components of NEEWS are scheduled for service by 2014.

- The Interstate Reliability Project has been reevaluated to account for updated load and energy-efficiency forecasts; system operating constraints; and resources acquired, delisted, or retired through the Forward Capacity Auctions, such as the impact of the unavailability of the Salem Harbor facility. The need for the Interstate Reliability Project has been reconfirmed, and the preferred solution is unchanged.

- The need for the Central Connecticut Reliability component of NEEWS remains under consideration as part of the Greater Hartford–Central Connecticut (GHCC) study.

- The Long-Term Lower SEMA project addresses system reliability concerns in the lower southeastern Massachusetts (LSM) area, which includes Cape Cod, and is scheduled for completion in September 2013. The project includes adding a new 345 kV transmission line from the Carver substation to a new 345/115 kV substation west of Barnstable on Cape Cod. The project received siting approval in May 2012. (Section 5.4)

Several major transmission planning studies have been completed, and others are underway to address system issues in all six New England states. Some studies have developed preferred solutions to serve major portions of the system, including Vermont and New Hampshire, the Merrimack Valley, the Pittsfield and Greenfield area, and the Greater Boston area. However, certain projects are being deferred because the RSP12 load forecast is lower than the RSP11 forecast and because the new energy-efficiency forecast reduces load further. All studies examine the system comprehensively and account for the electrical characteristics of the tightly integrated New England network.

Generation helps ensure the reliability of area load pockets. These load pockets include portions of Maine, the Boston area, southeastern Massachusetts (SEMA), western Massachusetts, the Springfield area, and portions of Connecticut. In addition to enhancing reliability, transmission improvements placed in service have reduced load costs associated with second-contingency and voltage-control payments to generators. The Lower Southeastern Massachusetts (Lower SEMA) short-term upgrades are one example of transmission upgrades that have improved reliability, reduced dependencies on generating units, and reduced “make-whole” payments to market participants whose resources had operating costs higher than their energy market revenues over a 24-hour dispatch day. (Section 5)

Transmission expansion may be required to meet future challenges facing the New England region to accomplish the following actions: (Section 5.2)

- Preserve the reliability of service to those areas of the system that could face generator retirements within the planning horizon

- Provide access to renewable resources, some of which are likely to be located remotely from load centers

- Provide access to a diversity of generator types using different fuels and having varying operating characteristics

The regional planning process is robust, and the New England region stands ready to develop any required infrastructure through the partnership of the ISO with the states, market participants, and other stakeholders.

#### Elective and Merchant Transmission Development

Several developers have proposed elective or merchant transmission upgrades, which are in various stages of study and development. These projects could increase New England’s tie capability with its neighbors and improve access to renewable sources of energy. The ISO will continue to monitor the outcomes of these upgrades and their impacts on system conditions and needs. (Section 5)

### Development and Integration of Resources

In addition to identifying the need for capacity and operating reserves, the ISO assesses the potential impacts of fuel availability and public policies, including environmental initiatives, on the system’s need for certain amounts, types, and locations of resources and transmission improvements. The ISO also identifies possible regional solutions to meet these needs and resolves issues concerning the development and integration of renewable resources and smart grid technologies.

#### Natural Gas Supply and Fuel Diversity Issues

New England is increasingly dependent on natural gas as a primary fuel for generating electric energy and decreasing its dependence on oil. In 2000, 17.7% of the region’s capacity was natural-gas-fired generation, which produced 14.7% of the region’s electric energy, whereas in 2011, natural gas plants represented 42.6% of the region’s capacity and provided 51.3% of the system’s electrical energy. In 2000, oil units represented 34.0% of the region’s capacity and produced 22.0% of the region’s electric energy that year, but in 2011, oil units represented 22.0% of the capacity and produced 0.6% of the region’s electric energy. (Section 7.1)

The overall use of natural gas has been increasing because of increased residential and commercial consumption, international demand, and use by electric power generators. The increase in the use of natural gas to generate electricity is the result of the addition of new efficient natural-gas-fired units over the past decade; the recent relatively low price of natural gas; and the displacement of old, less efficient oil and coal units in economic dispatch. The reliance on natural gas could be increased by the loss of other types of generation subject to risks, such as nuclear and hydro units that may not be relicensed. Accompanying the increased use of natural gas are concerns regarding the region’s need for sufficient natural gas pipeline capacity and gas supply in the pipelines—summer and winter and during all types of natural and geopolitical events that could interrupt supplies of gas and other fuels, such as oil and coal.

Several actual and possible operational circumstances have shown the need for market and planning improvements to enhance the reliability and security of the region’s gas- and oil-fuel supplies for generating electricity. To understand the potential vulnerabilities to the disruption in natural gas supply, particularly in severe winter or other stressed system conditions, the ISO completed a study of regional natural gas issues, which accomplished a number of tasks: (Section 7.3.2)

- Assessed the effects of generator retirements on fuel supply and diversity concerns

- Determined the quantities of gas-fired capacity available after all firm, priority deliveries are accounted for

- Reviewed natural gas infrastructure contingencies affecting reliable electric power operation

- Determined the need for additional natural gas system supply to reliably serve New England generating resources

- Identified the required amounts of resources that could be used in lieu of natural-gas-fired generation, such as dual-fuel and oil-fired generation

- Considered the effects of several natural gas pipeline infrastructure outages

Recent improvements to the regional and interregional natural gas infrastructure have helped address the increased demand for natural gas. Additional planned enhancements will continue to expand the sources of natural gas for the region’s power generators. For example, six regional pipeline projects became commercially available during 2011. Spectra Energy’s Algonquin Incremental Market (AIM) project is under consideration, with a tentative schedule for completion by 2016. If fully developed, this project could bring up to an additional 350 thousand dekatherms of natural gas per day from the Marcellus gas fields. Also, the implementation of operating procedures and improved communications between electric power and natural gas system operators has decreased certain near-term operational risks. (Section 7.3)

The ISO is considering several additional actions to improve the reliability of the region’s fuel supply to generating units, which will be reviewed through the stakeholder process, such as Markets Committee meetings:

- Obtaining additional information on the fuel arrangements of gas and oil generators

- Coordinating the timing of day-ahead electricity markets with the nomination times of the natural gas industry

- Requiring supplementary fuel procurements to ensure that gas and oil generators have a secure fuel supply

- Making longer-term changes to the product definition and obligations in the Forward Capacity Market

Adding renewable resources would help diversify the region’s fuel supply, but the reliable integration of intermittent renewable resources could stress natural gas generators, which would face increased regulation and reserve requirements. Many natural-gas-fired units lack the electrical (physical) ability to provide this flexible operation, and potential adverse interactions with the natural gas system must be addressed. Many units also do not have economical or effective dual-fuel capability (in terms of the amount of time they need to switch to using oil or the availability of secondary fuel inventory). (Section 7)

Many of these natural gas supply and fuel diversity issues have been identified under the Strategic Planning Initiative. Additionally, the scoping of a follow-up natural gas study has begun for determining the potential risks of energy shortfalls for the region under a variety of scenarios. (Sections 6 and 7)

#### The Potential Impacts of Water and Environmental Emissions Regulations on the Power System

For more than 10 years, the region’s average and marginal emission rates for sulfur dioxide (SO2), nitrogen oxides (NOX), and carbon dioxide (CO2) have been declining. This is a result of natural-gas-fired generators in the region emitting fewer pollutants than the generating units they displaced in economic dispatch and of oil- and coal-fired units adding emission controls. New transmission upgrades have reduced the dependence on older, less efficient oil and coal units, which had been needed to address reliability concerns. Compared with 2001, the 2010 average emission rate for SO2 has declined by 64%; the rate for NOX, by 54%; and the rate for CO2, by 11%. Total emissions for SO2 and NOX also have decreased from 2001 levels, by 60% and 52%, respectively. (Section 8.1.2)

However, the region and neighboring areas face extensive and stricter state and federal environmental regulations to protect public health and the environment. These regulations address air emissions, including air toxics; cooling water intake requirements; wastewater discharges; and the handling of coal combustion waste products. When promulgated, these regulations will increase the operating costs for affected generating plants, add capital costs for environmental controls, and require the use of low-emitting fuels. These regulations may lead to the retirement of some aging units before 2021 (the last year of this 10-year plan) and may limit energy production and generation capacity. Because this could lead to new generation dispatch and commitment patterns and shifting costs, the ISO will monitor and evaluate environmental initiatives as they are proposed and implemented for incorporating valid assumptions in system planning studies. (Section 8)

The ISO reviewed several modeling assessments and reports that evaluated the impact of existing and proposed EPA regulations and identified fossil and steam thermal units in the region that would need to comply with these regulations. Drawing on these studies and conducting an independent analysis, the ISO identified the amount of generation across New England that could be affected by the environmental requirements:

- A total of 12.1 gigawatts (GW) of fossil fuel and nuclear capacity could be subject to potential cooling water intake requirements, of which 5.6 GW could be subject to more restrictive requirements associated with adding control options to protect aquatic life no later than 2021. Owners of most of the at-risk capacity would face compliance or retirement decisions—and FCM positioning decisions—starting late in this decade. (Section 8.1.1.1)

- A total of 7.9 GW of existing coal steam or oil/gas steam units could be subject to the proposed final Mercury and Air Toxics Standards (MATS), with full compliance likely by 2015. Because infrequently operated units would be exempt from MATS, less than 1 GW of retirements are anticipated as a direct result of these regulations, but the long-term, economic viability of these units remains doubtful. (Section 8.1.1.2)

ISO analyses for the Strategic Planning Initiative and other planning efforts also will continue to identify generators at risk for retirement and generators that already have environmental remediation measures in place or may require relatively minor upgrades. The actual compliance timelines will depend on the timing and substance of the final regulations and site-specific circumstances of the electric generating facilities. (Section 6)

#### Renewable Portfolio Standards and the Integration of Renewable Resources

Environmental regulations and policies mentioned above, Renewable Portfolio Standards (RPSs), and similar state goals are stimulating the need for and development of renewable resources and energy efficiency in the region. Other regional and industry efforts are assisting in integrating renewable resources, demand resources, and smart grid technologies into the system.

Meeting State Targets for Renewable Energy. The New England states have targets for the proportion of electric energy that load-serving entities (LSEs) must serve with renewable resources, such as wind, solar, and energy efficiency. By 2021, EE and renewable resources would supply 31.8% of the region’s projected electric energy. This percentage includes an 11.6% reduction in the region’s projected electric energy consumption in 2021 resulting from passive demand resources and the forecasted energy-efficiency savings, as reported in the 2012–2021 Forecast Report of Capacity, Energy, Loads, and Transmission (2012 CELT Report). It also includes 20.2% of Renewable Portfolio Standards and policies addressing renewable supply goals. Possible solutions for meeting or exceeding the region’s RPSs include developing the renewable resources in the ISO queue; importing renewable resources from adjacent balancing authority areas; building new renewable resources in New England not yet in the queue; “behind-the-meter” projects; and using eligible renewable fuels in existing generators, such as biomass. Further, achievements in energy efficiency in the region that exceed the levels in the EE forecast could reduce the amount of new renewable resources required to meet state RPSs. If the development of renewable resources falls short of providing sufficient Renewable Energy Certificates (RECs) to meet the RPSs, load-serving entities can make state-established alternative compliance payments (ACPs). ACPs also can serve as a price cap on the cost of Renewable Energy Certificates. (Section 7.6)

Analysis of the ISO queue shows that the electric energy these resources could produce alone would exceed the increase of the RPS requirements through 2018. For example, the development of 40% of the renewable resources in the queue would meet the RPS goals through 2014. (Section 7.6)

Integrating Intermittent Renewable Resources. The ISO completed the New England Wind Integration Study, a major study of integrating wind resources into the New England system. This study analyzed various planning, operating, and market aspects of wind integration and the conceptual development of a transmission system that would be able to integrate large amounts of wind generation resources (i.e., up to 12,000 MW). The study found that New England would be able to accommodate the large-scale integration of wind resources but identified a number of issues if this were to occur. These issues include the need for conducting detailed transmission analyses to maintain reliable system performance; the need for increased system flexibility, operating reserves, and regulation service; and reduced net energy market revenues for natural-gas-fired resources. The study also identified the need for improved methods for calculating capacity values and forecasting wind generation, transmission development for interconnecting new wind resources, and updated interconnection requirements for voltage control and operating data. (Section 7.6.5)

New England states have a combination of goals, policies, and funding that promote the development of distributed resources, such as combined heat and power (CHP) systems and photovoltaic solar power capacity. Because solar resources are intermittent, integrating a large amount of megawatts from small-scale solar developments across the system could present issues similar to those for wind resources. The effects on the overall power system, however, would likely be less significant because the expected amount of solar resource development currently is much smaller than the planned wind development in the region. (Section 7.6.6.1)

Developing New England’s Smart Grid. Smart grid technologies can improve data acquisition, analysis, control, and efficiency of the electric power grid and distribution systems. In 2010, DOE approved funding for the ISO and the New England transmission owners to install phasor measurement units (PMUs) at 40 substations, which will be used to upgrade the monitoring and operation of the system. The region is a leader in the smart grid application of high-voltage direct-current (HVDC) facilities and flexible alternating-current transmission systems (FACTS). Smart grid technologies also can facilitate dynamic pricing, if implemented by the states, and the integration of variable energy resources. The ISO and stakeholders also have supported research and development efforts and the establishment of industry standards for integrating smart grid technologies, such as dispatching active demand resources. The ISO will monitor the development of these resources, which are affected by the installation of smart meters and changes in retail rate structures. (Section 9.4.1)

#### Economic Studies of Resource Integration and Interregional Coordination

In response to stakeholder requests received in 2011, the ISO completed economic studies to examine various wind development scenarios, particularly in northern New England. The studies quantify the near-term economic performance of the system for 2016, assuming the realization of renewable resources in the interconnection queue. While the study showed that transmission development could enable different combinations of wind resources, it also recommended further analysis of operational issues. (Section 8.2)

The economic studies analyzed several of the strategic issues the region is considering. Accessing the onshore wind energy located in northern New England, which is remote from load centers, will require transmission expansion. Replacing older high-emitting coal- and oil-fired units with cleaner-burning natural gas generation will decrease environmental emissions but increase New England’s dependence on natural gas and potentially require the expansion of the natural gas system infrastructure. The addition of resources with low energy costs decreases electric energy expenses for LSEs but also decreases energy market revenues to resources, which may then require increases in other revenue sources to remain economical. (Section 8.2)

The ISO presently is conducting economic studies in response to stakeholder requests received in 2012. These studies will examine the effects of adding and retiring resources at various locations. These effects include congestion costs, locations where resource or transmission development could be needed, and resources’ potential energy revenues and capital costs based on run times. The studies also will quantify several system metrics for the expansion of renewable resources and energy efficiency, various amounts of price-responsive demand, and the addition of load. (Section 8.2)

The ISO also is preparing a transmission system study of integrating wind resources within New England and renewable resource imports from Canada. This Strategic Transmission Analysis includes a number of retirement scenarios for aging coal- and oil-fired generating units. The study is developing conceptual transmission buildouts to inform stakeholders and government officials as they establish policies that affect the future planning and development of the system. (Section 6)

### Interregional Planning

ISO New England’s planning activities are closely coordinated at several levels:

- Among the six New England states

- With neighboring systems through a Northeastern ISO/RTO Planning Coordination Protocol and the NPCC

- Across the interconnection through the Eastern Interconnection Planning Collaborative (EIPC)

- Nationally through NERC and DOE

The ISO has developed coordinated system plans and has proactively initiated planning studies with other regions. The Northeast Coordinated System Plan summarizes several key interregional issues and activities: (Section 9.2)

- Market efficiency analyses, including the development of coordinated production cost models of the three ISO/RTOs and neighboring regions, which will serve as guidance for future interregional transmission studies

- The effects of environmental regulations and the integration of wind and other renewable resources

- Fuel diversity issues, including the current and future dependency on natural gas and how the interregional electric power system provides “fuel diversity by wire”

- The effects of demand-side resources on the system and how each of the ISO/RTOs reflects these resources in its respective system operations and planning

- Coordinated tracking and discussion of FERC’s Notice of Proposed Rulemaking (NOPR) on Transmission Planning and Cost Allocation, which became a final rule (FERC Order 1000) in 2011

Sharing more supply and demand resources with other systems most likely will be needed, particularly to meet environmental regulations and successfully integrate variable energy resources. Identifying interregional system needs and the potential impacts that proposed generating units and transmission projects could have on neighboring systems is beneficial to support interregional reliability and economic performance. ISO New England will continue conducting joint studies with NYISO and PJM to identify transmission constraints limiting interregional power transfers and show the effects of relieving these constraints throughout the ISO/RTO regions. The ISO also will continue to coordinate other efforts with neighboring systems to explore the ability to import power from and export power to the eastern Canadian provinces and New York and participate in national and regional planning activities. (Section 9.2 )

In August 2009, a coalition of the regional planning authorities within the Eastern Interconnection formed the Eastern Interconnection Planning Collaborative, a first-of-its-kind effort. The EIPC addresses its portion of North American planning issues, coordinates plans, and conducts studies for the entire Eastern Interconnection through a transparent and collaborative process with input from a broad base of interested stakeholders. ISO New England and other planning authorities throughout the Eastern Interconnection are principal investigators in the EIPC process.

During Phase I, the EIPC analyzed eight macroeconomic futures and 72 associated sensitivities based on input variables of each future. This phase resulted in the selection of three final scenarios and the identification of resource-expansion options for these scenarios, which will be analyzed in more detail during a second phase. Phase II, scheduled for completion by December 2012, also will summarize the results of production cost analyses for the transmission buildouts. (Section 9.2)

The ISO participates in several other national and regional system planning forums, such as the Electric Reliability Organization, the ISO/RTO Council, and the Northeast Power Coordinating Council. Through the NPCC and NERC, the ISO has participated in interregional assessments, which coordinate planning studies and demonstrate compliance with all required planning standards, criteria, and procedures. (Section 9.2)

### State, Regional, and Federal Initiatives that Affect System Planning

The ISO continuously works with a wide variety of state policymakers and other regional and interregional stakeholders through its planning process. Regional initiatives have improved the transparency of transmission cost estimates, provided critical load levels and other information included in needs assessments, and developed an energy-efficiency forecasting methodology for the region. The ISO has continued to provide technical support to a number of state agencies and groups, such as the New England Conference of Public Utilities Commissioners (NECPUC), the New England Governors’ Conference (NEGC), the New England Governors and Eastern Canadian Premiers (NEG/ECP), the Consumer Liaison Group (CLG), the New England States Committee on Electricity (NESCOE), and others. The planning process will continue to evolve in response to FERC orders and other policy developments. (Section 9)

Active involvement and participation by all stakeholders, including public officials, state agencies, NESCOE, participating transmission owners, market participants, and other PAC members, are key elements of an open, transparent, and successful planning process. As needed, the ISO will work with these groups to support regional and federal policy initiatives, such as the Strategic Planning Initiative and FERC Order No. 1000 on transmission planning and cost allocation. The ISO will continue to provide required technical support to the New England states and the federal government as they formulate policies for the region. (Section 9)

## Conclusions

The ISO’s 2012 Regional System Plan provides information on the timing, location, and type of system resources and the transmission projects needed for reliably serving load throughout the region through 2021. The economic recession has slowed the growth of the summer peak demand, while wholesale electricity markets and other factors have stimulated the development of supply and demand resources and transmission infrastructure to meet the needs of the New England region. Operational challenges, such as LNG supply issues to NEMA/Boston, are being addressed, and the issues for further analysis are being incorporated into the planning process. To meet future system needs, the planning process will need to consider the likelihood of power plant retirements, the expected development and integration of the region’s renewable resources, the impact of public policies, and the close interaction between the natural gas and electric power system infrastructure.

The region’s heavy dependence on natural-gas-fired generation to meet its electricity needs is expected to grow, with the likely retirement of old coal and oil units and their replacement, in whole or in part, with generators in the queue, and with the possibility of nuclear outages or retirements. At the same time, environmental and economic incentives provided by governmental policies are encouraging the development of low-emitting, renewable resources, such as wind and solar. Passive demand resources are expected to increase as well, as shown by the ISO’s energy-efficiency forecast for this planning period. Economic studies are showing the effects of these types of resources and possible new imports from Canada, providing useful information for policymakers and resource developers. Also, smart grid technologies are being developed to improve the electric power system’s performance and operating flexibility and its potential to grow active demand resources.

RSP12 and its associated RSP Project List, needs assessments, and solutions studies provide detailed information about the system changes needed to reliably serve load in New England for the next 10 years. Transmission projects are in various stages of development, and many have begun or have completed the siting process. Elective and merchant transmission facilities, in various stages of development, have the potential to provide access to renewable resources in remote areas of the region and in neighboring areas.

In its Strategic Planning Initiative, the ISO has identified risks to the regional electric power system; the likelihood, timing, and potential consequences of these risks; and possible mitigating actions. Through an open process, regional stakeholders and the ISO are developing an approach to address these issues, which could include further infrastructure development as well as changes to the wholesale electricity market design and the system planning process. Through current and planned activities, the region is well positioned to meet all challenges to reliable and economic system performance.

# Introduction

As the Regional Transmission Organization (RTO) for New England, ISO New England (ISO) operates the region’s electric power system, administers the region’s competitive wholesale electricity markets, and conducts the regional planning process. It also coordinates planning efforts with neighboring areas. To carry out its planning responsibilities, the ISO works closely with members of the Planning Advisory Committee (PAC). PAC membership is open to all and currently includes representatives from state and federal governmental agencies; participating transmission owners (PTOs); market participants; other New England Power Pool (NEPOOL) members; consulting companies; manufacturers; and other organizations, such as universities and environmental groups.

In compliance with all portions of the ISO’s Transmission, Markets, and Services Tariff (ISO tariff), including the Open Access Transmission Tariff (OATT), and to provide information to stakeholders for developing resources and transmission solutions to meet system needs, the 2012 Regional System Plan (RSP12) describes the ISO’s annual system resource and transmission planning activities for the 10-year period to 2021. It also summarizes the results of regional and local-area studies, as follows:

- Load forecasts for peak demand and the average annual use of electric energy and the regional energy-efficiency (EE) forecast

- Analyses of the amount, characteristics, and locations of needed capacity and operating reserves

- Assessments of systemwide and local-area needs and solutions to meet these needs:

- Market resource solutions (i.e., supply or demand resources at one or multiple locations in an area to meet a transmission system reliability need in that area)

- Transmission solutions

- Simulations of the estimated economic and environmental performance of various future resource- and transmission-expansion scenarios

RSP12 also summarizes information and activities concerning the status of the region’s fuel diversity and supply; resource development and integration, including renewable resources; new technologies; and environmental issues associated with power plant air emissions and water withdrawals and discharges. In addition, the RSP reports on state, regional, federal, and eastern Canadian initiatives relevant to New England’s power system planning and joint planning efforts with New York and other neighboring power systems.

Where applicable, RSP12 provides the link to the RSP Project List, which includes the status of transmission upgrades during a project’s lifecycle. RSP12 incorporates information from the June 2012 list. Italicized terms indicate that a definition for the term is included within the text, footnotes, or Glossary (Appendix A); links to other documents that more fully define the more complex terms are provided. Links to relevant technical materials also are included throughout the report; all website addresses are current as of the time of publication. Appendix B is a list of acronyms and abbreviations used in RSP12.

This section summarizes the ISO’s regional system planning process required by the ISO’s tariff. As background, the section provides an overview of the power system and the RSP subareas used in system planning studies. The section also summarizes the wholesale market structure in New England and how the information in the RSP is used to identify possible improvements to the markets.

## The Regional System Planning Process

The main objectives of the ISO’s regional system planning process are as follows:

- Identify system needs and associated system improvements to ensure the reliability of the system for the short and long terms

- Facilitate the efficient operation of the markets through resource additions and transmission upgrades that serve to reliably move power from various internal and external sources to the region’s load centers

- Provide information to regional stakeholders, who can further develop system improvements

The major steps of the planning process are described in the following sections.

### Working with the Planning Advisory Committee

The primary means of conducting the system planning process is through the open and transparent stakeholder forum with the PAC. For RSP12, the PAC has met 14 times from fall 2011 to summer 2012. PAC sessions have discussed draft scopes of work, assumptions, and draft and final study results on a wide range of issues. In addition, subgroups of the PAC met to discuss economic studies, the energy-efficiency forecast (see below), and environmental issues. PAC agendas; minutes; materials; draft reports, including stakeholder questions and ISO responses; and final reports are posted on the ISO website.

For RSP12, as in past years, feedback from the PAC has been referred to other stakeholder committees, which have discussed system needs and other items identified in the RSP. The Reliability Committee recommends approvals of planning procedures, final proposed plan applications, regional transmission cost allocations, and other activities that affect the overall operations and planning of the power system. The Markets Committee recommends approval of changes to Market Rule 1 and market procedures.

### Forecasting Demand and Determining System Needs

Key drivers for determining whether and where system improvements are needed are the forecasts of the peak demand and annual use of electric energy over a five- to 10-year planning period. RSP12 projects electric energy use for 2012 to 2021. RSP12 also includes an energy-efficiency forecast for 2015 to 2021, which shows the potential effect of EE projections on peak demand and annual energy use. The EE forecast was produced using a new methodology the ISO developed with stakeholders through the Energy-Efficiency Forecast Working Group (EEFWG) and the PAC.

To assess how to maintain the reliability of the New England power system, while promoting the operation of efficient wholesale electricity markets, the ISO and its stakeholders analyze the system and its components as a whole. They account for the performance of these individual elements and the many varied and complex interactions that occur among the components and affect the overall performance of the system. Specifically, the electric power planning process in New England assesses the amounts and general locations of resources the overall system and individual areas of the system need, the types of resources that can satisfy these needs and any critical time constraints for addressing them, and the impacts of public policies on existing resources and potential resource development. RSP12 discusses these needs and other factors and reports on the status of projects to address them.

### Developing Market Resource Alternatives to Address System Needs

Using information on defined system needs, a variety of established signals from ISO-administered markets, and other factors, stakeholders responsible for developing needed resources can assess their options for satisfying these needs and commit to developing projects. For example, stakeholders can build a new power plant to provide additional system capacity, participate in ISO programs to reduce the amount of electric energy used, or provide merchant transmission upgrades. These merchant transmission and supply and demand resource alternatives could result in modifying, offsetting, or deferring proposed regulated transmission upgrades.

### Planning Transmission Upgrades

To the extent that stakeholder responses to market signals are not forthcoming or adequate to meet identified system needs, the planning process requires the ISO, through the open stakeholder process, to conduct subsequent planning of transmission upgrades. The aim of these efforts is to develop regulated transmission solutions for transmission infrastructure that can meet the identified needs. However, the ISO does not have the authority to build needed resources or transmission.

With input from stakeholders, the ISO prepares needs assessments, which identify needs on the system, and solutions studies, which describe transmission options for meeting the identified needs. Subsequent assessments report on the status of these solutions, which typically are implemented over several years. These transmission projects are part of the ISO’s RSP Project List (see Section 5.4), which is updated several times per year. Stakeholders may elect to develop some market resources once regulated transmission projects have been identified or built.

### Providing Information to Stakeholders

To provide the needed information to stakeholders, the ISO issues the Regional System Plan, the RSP Project List, and specific needs assessments and solutions studies. In addition, the ISO posts on its website detailed information supplemental to the RSP process, such as the Annual Markets Report (AMR), Wholesale Markets Project Plan (WMPP), presentations, and other reports. The ISO also makes available databases used in its analyses and related information required to perform simulations consistent with FERC policies and the ISO Information Policy requirements pertaining to both confidential information and critical energy infrastructure information (CEII) requirements. Stakeholders can use this information and data to conduct their own independent studies.

The information contained in RSP12 is a status report of several planning initiatives and studies, many of which may take years to complete.

### Coordinating with Neighboring Areas

In developing the Regional System Plans, the ISO also is required to coordinate study efforts with surrounding RTOs and balancing authority areas and to analyze information and data presented in neighboring plans. This is achieved through a number of interregional agreements and joint studies with neighboring regions and across the entire Eastern Interconnection. Section 9 summarizes several of these efforts.

### Meeting All Requirements

In addition to complying with the ISO tariff, which reflects the requirements of FERC orders such as the planning principle requirements of FERC Order 890, RSP12 complies with North American Electric Reliability Corporation (NERC) and Northeast Power Coordinating Council (NPCC) criteria and standards, as well as ISO planning and operating procedures. RSP12 also conforms to transmission owner criteria, rules, standards, guides, and policies consistent with NERC, NPCC, ISO criteria, standards, and procedures. In spring 2012, the region successfully passed an NPCC audit that shows the region fully meets reliability standards. RSP12 reflects the impacts that federal government and New England state policies have on system planning. The region is working toward compliance with FERC Order 1000, which requires enhancements to the planning process.

### Accounting for Uncertainty

Regional system planning must account for the uncertainty in assumptions made about the next 10 years stemming from changing demand, fuel prices, technologies, market rules, and environmental requirements; other relevant events; and the physical conditions under which the system might be operating. The development and retirement of resources and changes in the load and energy-efficiency forecasts are major factors affecting the development and timing of needed transmission facilities and market resources options. While each RSP represents a snapshot in time, the planning process is continuous, and the results are revisited as needed when new information becomes available.

## Overview of the New England Electric Power System

New England’s electric power grid has been planned and operated as a unified system of its NEPOOL members. The New England system integrates resources with the transmission system to serve all regional load regardless of state boundaries. Most of the transmission lines are relatively short and networked as a grid. Therefore, the electrical performance in one part of the system affects all areas of the system.

As shown in Figure 2-1, the New England regional electric power system serves 14 million people living in a 68,000 square-mile area. More than 300 generating units, representing approximately 32,000 megawatts (MW) of total generating capacity, produce electric energy, measured in megawatt-hours (MWh). Most of these facilities are connected through over 8,000 miles of high-voltage transmission lines. Thirteen tie lines interconnect New England with neighboring New York State and the provinces of New Brunswick and Québec, Canada. Demand resources now play a significant role in operating the New England power system. As of summer 2012, approximately 2,100 MW of demand resources representing load reductions and “behind-the-meter” generators were registered as part of ISO’s Forward Capacity Market.

|  | - 6.5 million households and businesses; population 14 million - Over 300 generators - 32,000 MW of total generation - Over 8,000 miles of transmission lines - 13 interconnections to electricity systems in New York and Canada - Approximately 2,100 MW of demand resources for 2012 - All-time peak demand of 28,130 MW, set on August 2, 2006 - Approximately 500 participants in the marketplace (those who generate, buy, sell, transport, and use wholesale electricity and implement demand resources) - $7.63 billion total market value— $6.17 billion energy market, $1.35 billion capacity market, and approximately $0.11 billion for ancillary services - Approximately $5.0 billion in transmission investment since 2002; approximately $6 billion planned over the next 10 years |
| --- | --- |

Figure 2-1: Key facts about New England’s electric power system and wholesale electricity markets.

Note: The total load on August 2, 2006, would have been 28,770 MW had it not been reduced by approximately 640 MW, which included a 490 MW demand reduction in response to ISO Operating Procedure No. 4 (OP 4), Action during a Capacity Deficiency; a 45 MW reduction of other interruptible OP 4 loads; and a 107 MW reduction of load as a result of price-response programs, which are outside of OP 4 actions. More information on OP 4 is available at http://www.iso-ne.com/rules_proceds/operating/isone/op4/index.html. Also see Section 3.1.

The ISO’s all-time actual summer peak demand was 28,130 MW on August 2, 2006, which was due to extreme temperatures and humidity regionwide. In accordance with ISO operating procedures, demand-response programs were activated during this period, which lowered this peak by approximately 640 MW. Without these programs, the peak would have been approximately 28,770 MW. The 2011 summer peak, on July 22, 2011, was 27,707 MW, the second-highest peak on record. This load was lower than the 2006 historical peak, primarily because of the use of 1,817 MW of passive and active demand resources during weather that was even more extreme than in 2006. Without these demand resources, the 2011 peak would have been approximately 29,524 MW. The ISO’s all-time actual winter peak of 22,818 MW occurred on January 15, 2004. The 2011/2012 winter peak was lower, at 19,905 MW, because of mild weather conditions and 1,428 MW of passive demand resources. Without these resources, the 2011/2012 winter peak would have been approximately 21,333 MW.

## Overview of the New England Wholesale Electricity Market Structure

New England’s wholesale electricity markets facilitate the buying, selling, and transporting of wholesale electricity, as well as ensure proper system frequency and voltage, sufficient future capacity, seasonal and real-time reserve capacity, and system restoration capability after a blackout. Stakeholders also have the opportunity to hedge against the costs associated with transmission congestion. As shown in Figure 2-1, in 2011, approximately 500 market participants completed transactions in New England’s wholesale electricity markets totaling $7.63 billion. The wholesale electricity markets and market products in New England are as follows:

- Day-Ahead Energy Market—allows market participants to secure prices for electric energy the day before the operating day and hedge against price fluctuations that can occur in real time.

- Real-Time Energy Market—coordinates the dispatch of generation and demand resources to meet the instantaneous demand for electricity.

- Forward Capacity Market (FCM)—ensures the sufficiency of installed capacity, which includes demand resources, to meet the future demand for electricity by sending appropriate price signals to attract new investment and maintain existing investment both where and when needed.

- Financial Transmission Rights (FTRs)—allows participants to hedge against the economic impacts associated with transmission congestion and provides a financial instrument to arbitrage differences between expected and actual day-ahead congestion.

- Ancillary services

- Regulation Market—compensates resources that the ISO instructs to increase or decrease output moment by moment to balance the variations in demand and system frequency to meet industry standards.

- Forward Reserve Market (FRM)—compensates generators for the availability of their unloaded operating capacity that can be converted into electric energy within 10 or 30 minutes when needed to respond to system contingencies, such as unexpected outages.

- Real-time reserve pricing—compensates on-line generators that offer their electric energy above the marginal cost for the increased value of their energy when the system or portions of the system are short of reserves. It also provides efficient price signals to generators when redispatch is needed to provide additional reserves to meet requirements.

- Voltage support—compensates resources for maintaining voltage-control capability, which allows system operators to maintain transmission voltages within acceptable limits.

The market structure for conducting wholesale electric energy transactions in New England is Standard Market Design (SMD). One key feature of SMD is locational marginal pricing, which is a way for electric energy prices to reflect the variations in supply, demand, and transmission system limitations effectively at every location where electric energy enters or exits the wholesale power network. In New England, wholesale electricity prices are set at approximately 900 pricing points (i.e., pnodes) on the power grid. If the system were entirely unconstrained and had no losses, all locational marginal prices (LMPs) would be the same, reflecting only the cost of serving the next megawatt increment of load by the generator with the lowest-cost electric energy available, which would be able to flow to any point on the transmission system. LMPs would differ among the pnodes if each location’s marginal cost of congestion and marginal cost of line losses differed.

Transmission system constraints, which limit the flow of the least-cost generation and create the need to dispatch more costly generation, give rise to the congestion component of an LMP. Line losses are caused by physical resistance in the transmission system as electricity travels through transformers, reactors, and other types of equipment; this produces heat and results in less power being withdrawn from the system than was injected. Line losses and their associated marginal costs are inherent to transmission lines and other grid infrastructure as electric energy flows from generators to loads. As with the marginal cost of congestion, the marginal cost of losses affects the amount of generation that must be dispatched. The ISO operates the system to minimize total system costs, while recognizing physical limitations of the system.

The pricing points on the system include individual generating units, load nodes, load zones (i.e., aggregations of load pnodes within a specific area), and the Hub. The Hub is a collection of locations that has a price intended to represent an uncongested price for electric energy, facilitate energy trading, and enhance transparency and liquidity in the marketplace. In New England, generators are paid the LMP for electric energy at their respective nodes, and participants serving demand pay the price at their respective load zones.

Import-constrained load zones are areas within New England that do not have enough local resources and transmission-import capability to serve local demand reliably or economically. Export-constrained load zones are areas within New England where the available resources, after serving local load, exceed the areas’ transmission capability to export the excess electric energy. New England is divided into the following eight load zones used for wholesale market billing: Maine (ME), New Hampshire (NH), Vermont (VT), Rhode Island (RI), Connecticut (CT), Western/Central Massachusetts (WCMA), Northeast Massachusetts and Boston (NEMA), and Southeast Massachusetts (SEMA).

A capacity zone is a geographic subregion of the New England Balancing Authority Area that may represent load zones that are export constrained, import constrained, or contiguous—neither export nor import constrained. Capacity zones are used in the Forward Capacity Auctions (FCAs) (see Sections 4.1.2 and 4.1.3). The region also currently has four reserve zones—Connecticut (CT), Southwest Connecticut (SWCT), NEMA/Boston, and the rest of the system (Rest-of-System, ROS) (i.e., the area excluding the other, local reserve zones).

Additionally, the region is divided into 19 demand-resource dispatch zones, which are groups of nodes used to dispatch real-time demand-response resources or real-time emergency generation (RTEG) resources. These allow for a more granular dispatch of active demand resources at times, locations, and quantities needed to address potential system problems without unnecessarily calling on other active demand resources. Figure 2-2 shows the dispatch zones the ISO uses to dispatch FCM active demand resources.

Figure 2-2: Active-demand-resource dispatch zones in the ISO New England system.

## RSP Subareas

To assist in modeling and planning electricity resources in New England, the ISO established 13 subareas of the region’s electric power system. These subareas form a simplified model of load areas connected by the major transmission interfaces across the system. The simplified model illustrates possible physical limitations to the reliable and economic flow of power that can evolve over time as the system changes.

Figure 2-3 shows the ISO subareas and three external balancing authority areas. While more detailed models are used for transmission planning studies and for the real-time operation of the system, the subarea representation shown in Figure 2-3 is suitable for RSP12 studies of production cost and environmental emissions.

|  | Subarea Designation | Region or State |
| --- | --- | --- |
|  | BHE | Northeastern Maine |
|  | ME | Western and central Maine/ Saco Valley, New Hampshire |
|  | SME | Southeastern Maine |
|  | NH | Northern, eastern, and central New Hampshire/eastern Vermont and southwestern Maine |
|  | VT | Vermont/southwestern New Hampshire |
|  | Boston (all capitalized) | Greater Boston, including the North Shore |
|  | CMA/NEMA | Central Massachusetts/ northeastern Massachusetts |
|  | WMA | Western Massachusetts |
|  | SEMA | Southeastern Massachusetts/ Newport, Rhode Island |
|  | RI | Rhode Island/bordering Massachusetts |
|  | CT | Northern and eastern Connecticut |
|  | SWCT | Southwestern Connecticut |
|  | NOR | Norwalk/Stamford, Connecticut |
|  | NB, HQ, and NY | New Brunswick (Maritimes), Hydro­Québec, and New York external balancing authority areas |

Figure 2-3: RSP12 geographic scope of the New England electric power system.

Notes: Some RSP studies investigate conditions in Greater Connecticut, which combines the NOR, SWCT, and CT subareas. This area has similar boundaries to the State of Connecticut but is slightly smaller because of electrical system configurations near the border with western Massachusetts. Greater Southwest Connecticut includes the southwest and western portions of Connecticut and consists of the NOR and SWCT subareas. NB includes New Brunswick, Nova Scotia, and Prince Edward Island (i.e., the Maritime provinces) plus the area served by the Northern Maine Independent System Administrator (USA).

# Forecasts of New England’s Peak Demand, Annual Use of Electric Energy, and Energy Efficiency

Load forecasts provide key inputs for evaluating the reliability and economic performance of the electric power system under various conditions and for determining whether and when improvements are needed. This section summarizes the forecasts for the annual use of electric energy and peak loads, New England-wide and in the states and subareas. It also describes the economic and demographic factors that drive the forecasts and explains the forecasting methodology. For RSP12, no changes have been made to the methodology for forecasting annual energy use and peak loads.

This section also provides information on the ISO’s newly developed energy-efficiency (EE) projections for the region. It summarizes information gathered from utility program administrators and state agency representatives and describes the ISO’s stakeholder process and methodology used to forecast EE resources over the 10-year RSP planning horizon.

## ISO New England Load Forecasts

The ISO load forecasts are estimates of the total amounts of electric energy that will be needed in the New England states annually and during seasonal peak hours. This year’s forecast horizon runs from 2012 through winter 2021/2022. Each forecast cycle updates the data for the region’s historical annual use of electric energy and peak loads by including an additional year of data, the most recent economic and demographic forecasts, and resettlement adjustments that include meter corrections.

The recent economic recession dominated the changes in the annual use of electric energy and seasonal peak load forecasts reported in the 2011 Regional System Plan (RSP11) and correspondingly influences the 2012 forecasts. Compared with the economic forecast used in RSP11, the RSP12 outlook for the recession and recovery shows less growth in 2011 through 2013, higher growth in 2014 through 2016 with a more moderate rebound, and similar growth for the remaining years. Both outlooks show the low point of the recent recession occurring in 2009, with the recovery beginning in 2010. The short-term outlook for 2012 to 2021 shows the growth in the gross domestic product (GDP) of 3.4% in 2012, rising to a high of 3.9% in 2014, and declining to about 2% by 2017 through 2021.

RSP12 predicts approximately the same growth in the use of electric energy as RSP11. The long-term summer peak load forecasts for RSP12 are less than 300 MW below those published in RSP11.

Table 3-1 summarizes the ISO’s forecasts of annual electric energy use and seasonal peak load (50/50 and 90/10) for New England overall and for each state. Net energy for load (NEL) is the generation output within an area, accounting for electric energy imports from other areas and electric energy exports to other areas. It also accounts for system losses and excludes the electric energy consumed to operate pumped-storage hydroelectric plants. The compound annual growth rate (CAGR) for the ISO’s electric energy use is 0.9% for 2012 through 2021, 1.5% for the summer peak, and 0.6% for the winter peak. The systemwide load factor (i.e., the ratio of the average hourly load during a year to peak hourly load) continues to decrease, from 57.5% in 2012 to 54.9% in 2021, but at a slower rate than in the past, and it begins to flatten by the end of forecast.

Table 3-1
Summary of Annual Electric Energy Use and Peak Demand for New England and the States

| State(a) | Net Energy for Load (1,000 MWh) |  |  | Summer Peak Loads (MW) |  |  |  |  | Winter Peak Loads (MW) |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | 50/50 |  | 90/10 |  |  | 50/50 |  | 90/10 |  |  |
|  | 2012 | 2021 | CAGR(b) | 2012 | 2021 | 2012 | 2021 | CAGR(b) | 2012/13 | 2021/22 | 2012/13 | 2021/22 | CAGR(b) |
| CT | 34,545 | 37,060 | 0.8 | 7,240 | 8,060 | 7,870 | 8,745 | 1.2 | 5,725 | 5,870 | 5,880 | 6,020 | 0.3 |
| ME | 12,190 | 13,230 | 0.9 | 2,065 | 2,295 | 2,195 | 2,455 | 1.3 | 1,900 | 1,975 | 1,975 | 2,045 | 0.4 |
| MA | 63,730 | 69,960 | 1.0 | 12,735 | 14,700 | 13,735 | 15,865 | 1.6 | 10,255 | 11,005 | 10,535 | 11,240 | 0.8 |
| NH | 12,300 | 13,670 | 1.2 | 2,425 | 2,870 | 2,605 | 3,080 | 1.9 | 2,030 | 2,185 | 2,135 | 2,290 | 0.8 |
| RI | 8,780 | 9,465 | 0.8 | 1,895 | 2,150 | 2,100 | 2,400 | 1.5 | 1,385 | 1,425 | 1,435 | 1,475 | 0.3 |
| VT | 6,650 | 6,990 | 0.6 | 1,085 | 1,175 | 1,120 | 1,220 | 1.0 | 1,065 | 1,110 | 1,135 | 1,180 | 0.5 |
| New England | 138,195 | 150,375 | 0.9 | 27,440 | 31,255 | 29,620 | 33,765 | 1.5 | 22,355 | 23,565 | 23,095 | 24,250 | 0.6 |

- A variety of factors cause state growth rates to differ from the overall growth rate for New England. For example, New Hampshire has the fastest-growing economy in New England, and Maine has the slowest-growing economy in the region.

- CAGR stands for compound annual growth rate.

Figure 3-1 shows a comparison of the ISO’s actual summer peak demand (i.e., the load reconstituted to include the megawatts that had been reduced because of OP 4 and FCM passive demand resources) with the 50/50 load forecast and with the 90/10 load forecast. The actual load has been near or has exceeded the 90/10 forecast six times over the last 20 years because of hot and humid weather conditions, and it has been near or above the 50/50 forecast 10 times during same period.

Figure 3-1: The ISO’s actual summer peak loads (i.e., reconstituted for OP 4 and FCM passive demand resources) and the 50/50 and 90/10 forecasts (MW).

Note: The forecasted load values are the first-year values of the CELT forecast for each year. For example, the forecasted loads for 2011 are the loads for the first year of the 2011 CELT report.

### Economic and Demographic Factors and Electric Energy Use

The price of electricity and other economic and demographic factors (see Sections 3.1.1.1 and 3.1.1.2) drive the annual use of electric energy and the growth of the seasonal peak. In addition to net energy for load, the forecasts account for the effects of future federal long-term energy-efficiency goals, as well as the historical effects of energy efficiency, but do not reflect the peak and electric energy savings attributable to passive demand resources (see Section 3.1.2).

The ISO’s forecasts of electric energy use in New England and each state are based on a total energy-use concept, which sums the total electric energy used residentially (about 38%), commercially (about 42%), and industrially (about 20%). Real gross state product (RGSP) and the real price of electricity serve as proxies for overall economic and demographic conditions. (For Connecticut, real personal income is used in place of RGSP because it produced a more credible energy forecast than the RGSP.) These variables are the primary forces driving the model of electric energy use. Table 3-2 summarizes these and other indicators of the New England economy.

Table 3-2
New England Economic and Demographic Forecast Summary

| Factor | 1980 | 2011 | CAGR | 2012 | 2021 | CAGR |
| --- | --- | --- | --- | --- | --- | --- |
| Summer peak (MW) | 14,539 | 27,240 | 2.0 | 27,440 | 31,255 | 1.5 |
| Net energy for load (1,000 MWh) | 82,927 | 136,121 | 1.6 | 138,195 | 150,375 | 0.9 |
| Population (thousands) | 12,378 | 14,517 | 0.5 | 14,552 | 14,865 | 0.2 |
| Real price of electricity (¢/kWh, 1996 $)(a) | 17.289 | 14.596 | -0.5 | 14.596 | 14.596 | 0.0 |
| Employment (thousands) | 5,483 | 6,843 | 0.7 | 6,880 | 7,568 | 1.1 |
| Real income (millions, 2005 $) | 280,918 | 649,394 | 2.7 | 666,671 | 837,924 | 2.6 |
| Real gross state product (millions, 2005 $) | 310,452 | 742,124 | 2.9 | 767,158 | 982,601 | 2.8 |
| Energy per household (MWh) | 18.954 | 23.857 | 0.7 | 24.085 | 25.124 | 0.5 |
| Real income per household (thousands) (2005 base year) | 64.207 | 113.817 | 1.9 | 116.189 | 139.995 | 2.1 |

(a) kWh stands for kilowatt-hour.

#### Electricity Prices

The forecast of the retail electricity prices assumes that the prices will grow at the rate of inflation (2.7% average annual growth) and have fully incorporated the capacity costs from the Forward Capacity Market.

#### Economic Factors

The Economy.com November 2011 economic forecast of real gross state product (and for Connecticut, real personal income) was used to represent overall economic activity in the RSP12 forecast models. Compared with the October 2010 Economy.com economic forecast, the November 2011 Economy.com forecast of real gross state product shows less growth in 2011 through 2013; higher growth in 2014 through 2016, but with a more moderate rebound than the RSP11 forecast; and the same growth for the remaining years. Figure 3-2 compares the RGSP forecasts from November 2011 with the forecasts from October 2010.

Figure 3-2: “Economy.com” forecasts of New England gross state product (indexed to 1980 = 100) from November 2011 and October 2010 forecasts.

Source: Moody’s Analytics, Economy.com.

Notes: Years 1980 to 2010 reflect actual gross state product. The blue bars highlight the three years for which the RSP11 and RSP12 forecasts differ.

### The CELT Forecast and Passive Demand Resources

The seasonal peak load and energy-use forecast, as published in the 2012–2021 Forecast Report of Capacity, Energy, Loads, and Transmission (2012 CELT Report) and used for calculating the Installed Capacity Requirement (ICR), fully accounts for historical energy efficiency, passive demand resources, and future federal appliance standards. The forecast does not expressly reflect the future reduction in peak demand and energy use that will result from the passive demand resources that clear the Forward Capacity Auctions and the energy-efficiency forecast (described in detail in Section 3.2). Historical reductions in load from “other demand resources” in the transition period leading up to the FCM and the historical reductions in load from the passive demand resources in the FCM have been added back into the historical loads used for load forecasting, to avoid double counting them.

### Subarea Use of Electric Energy

Much of the RSP12 reliability and production cost analysis depends on the forecasts of annual electric energy use and peak demand in the subareas. Table 3-3 summarizes these forecasts and provides important market information to stakeholders. Table 3-4 shows the forecast for the RSP subareas and their relationship to the load zones and states. The forecasts for the peak demand and annual energy use in the subareas are based on allocating the ISO’s state forecasts to distribution companies within the states (on the basis of historical shares), allocating the distribution company forecasts to buses using the ISO model of the transmission network, and then aggregating the busses for each of the subareas.

Table 3-3
Forecasts of Annual Use of Electric Energy and Peak Demand in RSP Subareas, 2012 and 2021

| Area | Net Energy for Load (1,000 MWh) |  |  | Summer Peak Loads (MW) |  |  |  |  | Winter Peak Loads (MW) |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | 50/50 Load |  | 90/10 Load |  |  | 50/50 Load |  | 90/10 Load |  |  |
|  | 2012 | 2021 | CAGR | 2012 | 2021 | 2012 | 2021 | CAGR | 2012/13 | 2021/22 | 2012/13 | 2021/22 | CAGR |
| BHE | 1,872 | 2,032 | 0.9 | 316 | 352 | 336 | 376 | 1.3 | 293 | 304 | 304 | 315 | 0.4 |
| ME | 5,799 | 6,408 | 1.1 | 947 | 1,074 | 1,007 | 1,149 | 1.5 | 938 | 989 | 975 | 1,024 | 0.6 |
| SME | 4,188 | 4,430 | 0.6 | 732 | 793 | 778 | 849 | 1.0 | 630 | 640 | 655 | 663 | 0.2 |
| NH | 10,790 | 11,950 | 1.1 | 2,109 | 2,481 | 2,261 | 2,658 | 1.8 | 1,767 | 1,898 | 1,859 | 1,990 | 0.8 |
| VT | 7,317 | 7,814 | 0.7 | 1,258 | 1,396 | 1,312 | 1,463 | 1.2 | 1,172 | 1,237 | 1,245 | 1,310 | 0.6 |
| BOSTON | 28,175 | 30,633 | 0.9 | 5,634 | 6,421 | 6,076 | 6,929 | 1.5 | 4,528 | 4,831 | 4,653 | 4,936 | 0.7 |
| CMA/NEMA | 8,419 | 9,145 | 0.9 | 1,690 | 1,938 | 1,822 | 2,091 | 1.5 | 1,347 | 1,427 | 1,385 | 1,459 | 0.6 |
| WMA | 11,002 | 11,885 | 0.9 | 2,132 | 2,435 | 2,298 | 2,625 | 1.5 | 1,814 | 1,907 | 1,867 | 1,952 | 0.6 |
| SEMA | 14,411 | 16,018 | 1.2 | 2,903 | 3,374 | 3,136 | 3,648 | 1.7 | 2,312 | 2,518 | 2,376 | 2,574 | 1.0 |
| RI | 12,149 | 13,507 | 1.2 | 2,582 | 3,038 | 2,836 | 3,351 | 1.9 | 1,913 | 2,028 | 1,976 | 2,089 | 0.6 |
| CT | 16,603 | 17,818 | 0.8 | 3,487 | 3,885 | 3,791 | 4,215 | 1.2 | 2,746 | 2,815 | 2,820 | 2,887 | 0.3 |
| SWCT | 11,311 | 12,164 | 0.8 | 2,362 | 2,634 | 2,568 | 2,858 | 1.2 | 1,882 | 1,935 | 1,933 | 1,984 | 0.3 |
| NOR | 6,158 | 6,571 | 0.7 | 1,291 | 1,430 | 1,404 | 1,552 | 1.1 | 1,019 | 1,040 | 1,047 | 1,067 | 0.2 |
| ISO total(a, b) | 138,195 | 150,375 | 0.9 | 27,440 | 31,255 | 29,620 | 33,765 | 1.5 | 22,355 | 23,565 | 23,095 | 24,250 | 0.6 |

(a) The total load-zone projections are similar to the state load projections and are available at the ISO’s “2012 Forecast Data File,” http://www.iso-ne.com/trans/celt/fsct_detail/index.html; tab #2, “ISO-NE Control Area, States, Regional System Plan (RSP12) Subareas and SMD Load Zones Energy and Seasonal Peak-Load Forecast.”

(b) Totals may not equal the sum because of rounding and may not exactly match the results for other tables in this section.

Table 3-4
Forecasts of RSP Subarea Peak Demand, 2012(a)

| RSP Subarea | Load Zone | State | 50/50 Summer Peak Load |  |  | 90/10 Summer Peak Load |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | MW | % of RSP Subarea | % of State | MW | % of RSP Subarea | % of State |
| BHE | ME | Maine | 315 | 100.0 | 15.3 | 335 | 100.0 | 15.3 |
| ME | ME | Maine | 945 | 100.0 | 45.8 | 1,005 | 100.0 | 45.8 |
| SME | ME | Maine | 730 | 100.0 | 35.4 | 780 | 100.0 | 35.5 |
| NH | ME | Maine | 70 | 3.3 | 3.4 | 75 | 3.3 | 3.4 |
|  | NH | New Hampshire | 1,955 | 92.7 | 80.6 | 2,100 | 92.9 | 80.6 |
|  | VT | Vermont | 85 | 4.0 | 7.8 | 90 | 4.0 | 8.0 |
|  |  |  | 2,110 |  |  | 2,260 |  |  |
| VT | NH | New Hampshire | 325 | 25.8 | 13.4 | 345 | 26.3 | 13.2 |
|  | VT | Vermont | 935 | 74.2 | 86.2 | 965 | 73.7 | 86.2 |
|  |  |  | 1,260 |  |  | 1,310 |  |  |
| BOSTON | NH | New Hampshire | 80 | 1.4 | 3.3 | 85 | 1.4 | 3.3 |
|  | NEMA/ Boston | Massachusetts | 5,555 | 98.6 | 43.6 | 5,990 | 98.6 | 43.6 |
|  |  |  | 5,635 |  |  | 6,075 |  |  |
| CMA/NEMA | NH | New Hampshire | 70 | 4.1 | 2.9 | 75 | 4.1 | 2.9 |
|  | WCMA | Massachusetts | 1,620 | 95.9 | 12.7 | 1,750 | 96.2 | 12.7 |
|  |  |  | 1,690 |  |  | 1,820 |  |  |
| WMA | VT | Vermont | 65 | 3.1 | 6.0 | 65 | 2.8 | 5.8 |
|  | CT | Connecticut | 100 | 4.7 | 1.4 | 110 | 4.8 | 1.4 |
|  | WCMA | Massachusetts | 1,970 | 92.5 | 15.5 | 2,125 | 92.4 | 15.5 |
|  |  |  | 2,130 |  |  | 2,300 |  |  |
| SEMA | RI | Rhode Island | 155 | 5.3 | 8.2 | 170 | 5.4 | 8.1 |
|  | SEMA | Massachusetts | 2,750 | 94.7 | 21.6 | 2,965 | 94.6 | 21.6 |
|  |  |  | 2,905 |  |  | 3,135 |  |  |
| RI | RI | Rhode Island | 1,740 | 67.4 | 91.8 | 1,930 | 68.1 | 91.9 |
|  | SEMA | Massachusetts | 840 | 32.6 | 6.6 | 905 | 31.9 | 6.6 |
|  |  |  | 2,580 |  |  | 2,835 |  |  |
| CT | CT | Connecticut | 3,485 | 100.0 | 48.1 | 3,790 | 100.0 | 48.2 |
| SWCT | CT | Connecticut | 2,360 | 100.0 | 32.6 | 2,570 | 100.0 | 32.7 |
| NOR | CT | Connecticut | 1,290 | 100.0 | 17.8 | 1,405 | 100.0 | 17.9 |

(a) Totals may not equal the sum because of rounding and may not exactly match the results for other tables in this section.

### Summary of Key Findings of the Load Forecast

The RSP12 forecasts of annual net energy use and peak loads are key inputs in establishing the system needs discussed in Sections 4 through 15. The RSP12 forecasts for the annual use of electric energy and winter peak are essentially the same as in RSP11, but the summer peak forecasts are lower than in RSP11. The key points of the forecast are as follows:

- The recent recession ended in 2009, followed by relatively weak economic growth beginning in 2010. The economy is forecast to rebound through 2014 and then return to a long-run sustainable growth rate.

- The forecasts for annual energy use and the winter peaks are not materially different from the RSP11 forecast.

- The 50/50 and 90/10 summer peak forecasts are lower than in RSP11 by about 660 MW in 2012 but only by 290 MW in 2021.

- The ISO will continue examining ways to improve the load forecast further.

- The compound annual growth rate for the ISO’s electric energy use is 0.9% for 2012 through 2021, 1.5% for the summer peak, and 0.6% for the winter peak.

## Energy-Efficiency Forecast for New England

This section provides information on the ISO’s ongoing efforts to analyze the long-term impacts of state-sponsored energy-efficiency programs and the development of an energy-efficiency forecast. It summarizes the ISO’s outreach to the states, other Independent System Operator/Regional Transmission Organizations (ISO/RTOs), and program administrators (PAs) and describes the ISO’s efforts to develop and implement a methodology to forecast EE resources over the 10-year RSP planning horizon.

### Background and Update

By statute, rule, and policy, the New England states have made EE a priority for the region, and in recent years, the New England state-sponsored EE programs have grown to unprecedented levels. Generally, the state public utilities commissions (PUCs) are responsible for approving EE program scope, costs, and implementation. Utilities often serve as PAs and manage the state-sponsored EE programs.

The FCM provides the ISO with information about the commitments to deliver EE (also known as passive demand resources) to the region over a four-year period into the future. Historically, ISO planners held this level of EE constant when analyzing future years beyond the FCM timeframe. Thus, no incremental growth in EE was forecasted beyond the latest known amounts of FCM passive demand resources. In the past, the ISO gathered information on these state-sponsored EE programs to better understand their aggregate impact on the power system. However, quantifying the long-range incremental impacts of the diverse state-sponsored EE programs became a challenge.

The levels of state-sponsored EE investments and the magnitude of EE programs prompted the ISO and the region’s energy-efficiency stakeholders to undertake an intensive, multiyear research, data collection, and analysis process. These efforts resulted in a comprehensive assessment of historical spending on EE programs by PAs and resulting energy savings in the region, the development of an energy-efficiency forecast methodology, and the release of the ISO’s energy-efficiency forecast—the first multistate energy-efficiency forecast in the United States. The goal of the forecast is to equip system planners and stakeholders with information about the long-term impacts of state-sponsored EE programs. The ISO was able to show, for example, that in 2010 alone, the region spent nearly $500 million on EE efforts.

In 2012, the ISO established and now chairs the Energy-Efficiency Forecast Working Group (EEFWG), to provide ongoing input into the EE forecast process. In addition to the ISO, this stakeholder group consists of state representatives with expertise in energy-efficiency programs, PAs, and other interested parties who provide guidance on EE forecast assumptions, methodologies, and data inputs.

### Methodology and Data Collection

In concept, the forecast methodology developed is similar to a method originally developed by the New York ISO. Both forecasts primarily are based on EE program budgets, production costs (annualized unit of energy per unit of cost, expressed as megawatt-hours per dollar; MWh/$), and the ratios of peak demand savings to annual energy use savings (MW/MWh) (i.e., the inverse of the load factor; see Section 3.1). With this type of EE data, future energy reductions and peak demand savings can be calculated.

The ISO bases its forecast methodology estimates of future EE budgets on projections of current EE revenue sources, including system benefits charges, revenues from Regional Greenhouse Gas Initiative (RGGI) auctions (see Section 8.1.3.1), the FCM (Section 4.1.3), and other sources. Projections of future production costs can be based on historical costs as reported by the PAs and reviewed by PUC staff.

In 2011, the ISO developed a “proof-of-concept” EE forecast methodology to give regional EE stakeholders a chance to provide input on possible mechanisms for the EE forecast methodology. The initial proof-of-concept EE forecast results were generated using estimates of budgets funded from known sources and a fixed production cost taken from regional data (NYISO). The calculation for the ISO’s EE forecast methodology is as follows:

MW = (Budget $) (% Spent) (MWh/$) (RR) (MW/MWh)

Where:

- MW refers to the peak megawatt reduction.

- Budget $ refers to an estimate of the dollars to be spent on EE (including budget uncertainty).

- % Spent is the percentage of dollars that can be spent on EE programs in that time period, developed from historical data.

- MWh/$ refers to the production cost megawatt-hour savings per dollar spent, developed from historical data and derived as an average of program administrator data from 2009 and 2010.

- RR refers to the realization rate of observed or measured savings to estimated savings, developed from historical data.

- MW/MWh refers to the ratio of peak demand savings to annual energy use savings, developed from historical data (developed from the load forecast for the proof of concept) and derived as an average of program administrator data from 2009 and 2010.

After the methodology was developed, detailed data on state-sponsored EE programs were needed to populate the methodology and produce an EE forecast for 2015 through 2021. Data collection for the EE forecast began in January 2012 using a newly developed EE data-gathering worksheet. These data would be used for evaluating production costs and allowing ongoing trending of changes to the technologies used by EE programs and their performance characteristics. After stakeholder discussions, the ISO sent the worksheet to all PAs in New England.

Via the worksheet, the ISO received data from all the region’s 14 regulated PAs, who reported on approximately 130 unique EE programs aimed at commercial/industrial, residential, and low-income customers. Of these programs, lighting measures and mixed lighting constitute a majority of the energy and demand savings, and the commercial and industrial sectors provide most of the overall savings.

The EE forecast methodology and the results of the proof-of-concept EE forecast were developed by the ISO with stakeholder input. After the proof-of-concept forecast was vetted, a draft EE forecast was released for stakeholder review on February 24, 2012. This draft used budget data and production costs provided by the PAs and included a range of scenarios for addressing various levels of uncertainty for consideration by the EEFWG. After consultation with the EEFWG, a final draft was released on March 19, 2012.

As a result of input provided by the EEFWG, the ISO revised the EE forecast methodology to incorporate the states’ near-term approved EE budgets and ensure that the most current and accurate information is available for the EE forecast. The ISO applied uncertainty factors to future budgets to reflect the challenges facing PAs in Massachusetts and Rhode Island where programs are expanding rapidly. Specifically, budgets were discounted by 10% in each budget year for these two states. The ISO also adjusted the final EE forecast for 2015 to 2021 to account for the impacts of inflation on the program costs and assumed increases in production costs. For all states except Maine, production costs were escalated by 7.5% each year to account for both the increasing costs of energy-efficiency measures and 2.5% inflation. Because the Maine production costs historically were low, they were escalated by 7.5% in the first year and were increased annually until reaching 10% growth in the last year of the forecast. This made Maine’s production costs more consistent with the region’s forecast.

### Results

The final EE forecast for 2015 to 2021, which was posted on April 12, 2012, contains forecasted savings in average, total, and peak energy use for the region and each state for this timeframe. The results show a regional annual average energy savings of 1,343 gigawatt-hours (GWh) and are based on an average annual spending rate of approximately $800 million per year. Total energy savings were 9,399 GWh from 2015 to 2021. The states’ annual average energy savings ranged from a low of 71 GWh in Maine to a high of 786 GWh in Massachusetts.

The regional average peak demand savings amounts to 206 MW. Total peak savings was 1,444 MW from 2015 to 2021. The states’ annual average peak savings ranged from a low of 8 MW in Maine to a high of 122 MW in Massachusetts. Table 3-5 shows the results of ISO’s final EE forecast for 2015 to 2021.

Table 3-5
 ISO New England’s Final Energy-Efficiency Forecast for 2015 to 2021 (GWh, MW)(a)

| Forecast of Electric Energy Savings (GWh) |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Year | Sum of States | States |  |  |  |  |  |
|  |  | ME | NH | VT | CT | RI | MA |
| 2015 | 1,619 | 89 | 65 | 110 | 244 | 163 | 948 |
| 2016 | 1,518 | 82 | 62 | 102 | 230 | 153 | 889 |
| 2017 | 1,423 | 77 | 59 | 95 | 216 | 143 | 833 |
| 2018 | 1,333 | 71 | 56 | 88 | 204 | 134 | 780 |
| 2019 | 1,247 | 65 | 53 | 82 | 191 | 125 | 731 |
| 2020 | 1,167 | 60 | 50 | 77 | 180 | 117 | 684 |
| 2021 | 1,092 | 55 | 48 | 71 | 169 | 109 | 640 |
| Total | 9,399 | 499 | 393 | 625 | 1434 | 944 | 5,505 |
| Average | 1,343 | 71 | 56 | 89 | 205 | 135 | 786 |
| Forecast of Peak Demand Savings (MW) |  |  |  |  |  |  |  |
| Year | Sum of States | States |  |  |  |  |  |
|  |  | ME | NH | VT | CT | RI | MA |
| 2015 | 249 | 10 | 11 | 20 | 33 | 28 | 147 |
| 2016 | 233 | 9 | 10 | 19 | 31 | 26 | 138 |
| 2017 | 218 | 8 | 10 | 18 | 29 | 25 | 129 |
| 2018 | 205 | 8 | 9 | 16 | 27 | 23 | 121 |
| 2019 | 192 | 7 | 9 | 15 | 26 | 22 | 113 |
| 2020 | 179 | 7 | 8 | 14 | 24 | 20 | 106 |
| 2021 | 168 | 6 | 8 | 13 | 23 | 19 | 99 |
| Total | 1,444 | 55 | 65 | 115 | 193 | 163 | 853 |
| Average | 206 | 8 | 9 | 16 | 28 | 23 | 122 |

(a) The forecast results are available at http://www.iso-ne.com/committees/comm_wkgrps/othr/enrgy_effncy_frcst/frcst/2012/iso_ne_ee_forecast_2015_2021.pdf.

Figure 3-3 and Figure 3-4 depict the data presented in Table 3-5, incorporating the EE forecast with the RSP 2012 annual energy use and summer peak forecasts. The forecast of annual energy use shows essentially no growth in energy use from 2015 to 2021 compared with the RSP energy forecast for 2015 to 2021, minus the results for the existing FCM passive resources. Over a similar timeframe, the summer peak 90/10 forecast, including the EE forecast, is projected to increase at a more modest rate, approximately half the projected growth rate of the 90/10 without the EE forecast.

Figure 3-3: RSP12 annual energy-use load forecast (diamond), load forecast minus FCM results (square), and load forecast minus the FCM and minus the energy-efficiency forecast (triangle) for 2015 to 2021 (GWh).

Note: Additional information is available at http://www.iso-ne.com/committees/comm_wkgrps/othr/enrgy_effncy_frcst/frcst/2012/draft_final_ee_forecast_3_16_12.pdf.

Figure 3-4: RSP12 summer peak demand forecast (90/10) (diamond), load forecast minus FCM results (square), and load forecast minus the FCM and minus the energy-efficiency forecast (triangle) for 2015 to 2021 (MW).

Note: Additional information is available at http://www.iso-ne.com/committees/comm_wkgrps/othr/enrgy_effncy_frcst/frcst/2012/draft_final_ee_forecast_3_16_12.pdf.

### Summary of the Energy-Efficiency Forecast and Methodology

The FCM provides the ISO with a comprehensive understanding of the short-term savings in energy use over the FCM horizon. Since 2009, the ISO has been analyzing energy-efficiency programs and studying how to model incremental, future long-term EE savings for five to 10 years. This deliberate and analytic effort advanced the ISO’s understanding of energy efficiency from anecdotal to empirical. The result is the nation’s first regional (multistate) long-term forecast of energy efficiency. Similar to any forecast, some level of uncertainty exists in the EE forecast. But as the region gains experience using this EE forecast methodology, the ISO and regional stakeholders will consider making adjustments to the methodology to ensure that the results are as accurate as possible. When incorporated into the ISO’s planning activities, this forecast should ensure that the impacts from the region’s large investments in EE are appropriately reflected in regional transmission decisions.

# Resources—Adequacy, Capacity, and Reserves

The ISO’s system planning process identifies the amounts, locations, and types of resources the system needs and how the region is meeting these needs in the short term through the Forward Capacity Market (FCM) and the locational Forward Reserve Market (FRM). Long-term needs can be met through projects proposed through the ISO’s Generator Interconnection Queue (the queue), energy-efficiency resources reflected in the ISO EE forecast, imports from neighboring systems, and the development of other resources.

This section describes the requirements for resource adequacy over the planning period; the analyses conducted to determine the systemwide and local-area needs for resource adequacy; and the region’s efforts to meet the need for resources through the FCM, the FRM, the queue, and energy-efficiency resources planned by the states. This section also discusses the results of the net operable capability assessments of the system under a variety of deterministic, stressed-system conditions and the status of studies of market resource alternatives to transmission development.

## Determining and Meeting Resource Adequacy Needs

To ensure resource adequacy for the system, the amount of capacity the system requires in a given year is determined through the Installed Capacity Requirement (ICR) calculation, which accounts for uncertainties, contingencies, and resource performance under a wide range of existing and future system conditions. The ICR is the amount of capacity that must be obtained through supply-side and demand-side resources in the Forward Capacity Market. Through the FCM, which consists of a series of auctions and bilateral trading periods, specific resources are procured and committed for meeting the ICR, and other key values are identified. Purchased capacity resources must be available in the specified timeframe to ensure the region has adequate resources. To be able to handle contingencies, such as unplanned outages, the system also must procure operating reserves. Collectively, the forecasts of future electricity demand (as discussed in Section 3), the ICR calculation, the procurement of capacity and reserves, and the operable capacity analyses that consider future scenarios of load forecasts and operating conditions (see Section 4.2) are referred to as the resource adequacy process. The specific mix of resources committed to the New England system for any particular delivery period changes over time, so no static report such as the RSP can possibly capture the “latest” available information. Data in this report are accurate as of the date they were presented to the PAC.

### Systemwide Installed Capacity Requirement

The Installed Capacity Requirement is determined using the well-established probabilistic loss-of-load-expectation (LOLE) analysis. The LOLE analysis identifies the amount of installed capacity (in MW) the system needs to meet the NPCC and ISO resource adequacy planning criterion to not disconnect firm load more than once in 10 years. To meet this “once-in-10-years” LOLE requirement, the region’s power system needs installed capacity in an amount equal to the expected demand plus additional capacity to handle any uncertainties associated with load or the performance of the capacity resources. Thus, the ICR forms the basis of the systemwide total amount of new and existing resources the annual Forward Capacity Auctions must procure as part of the FCM.

The analysis for calculating the ICR for New England examines system resource adequacy using assumptions for the load forecast, existing resources and their availability, imports, and possible tie-reliability benefits (i.e., the receipt of emergency electric energy from neighboring regions). The model also accounts for the load and capacity relief that can be obtained from implementing operating procedures, including demand-response programs. The ICR calculation, which uses a single-bus model, does not consider the transmission system constraints within New England.

RSP12 presents the established ICR values for the 2012 through 2015 capacity commitment periods (CCPs) and shows representative net ICR values for the 2017 through 2021 periods. The projected net ICR values do not indicate the definitive amount of capacity the region must purchase for that period but provide stakeholders with a general forecast of the likely resource needs of the region. The assumptions used to develop the ICR values published in RSP12 were discussed at meetings of the Power Supply Planning Committee (PSPC), the Reliability Committee (RC), and the PAC.

The results of the ICR calculation are summarized in Table 4-1 with the 50/50 peak load forecast (see Section 3.1). The net ICR values for the 2012/2013 through 2015/2016 capacity commitment periods reflect the latest ICR values established for these years. FERC has approved the ICR and Hydro-Québec Interconnection Capability Credits (HQICC) values for the 2012/2013 through 2015/2016 commitment periods, which were based on the 2011 CELT load forecast, except for the 2014/2015 values, which were based on the 2010 CELT load forecast. With stakeholder input, the ISO calculated the representative net ICR values for 2017/2018 and beyond, assuming the 2012 CELT load forecast and applying a 14% reserve to the 50/50 load forecast. This 14% reserve is based on the actual required average value determined for 2012/2013 through 2015/2016.

Table 4-1
Actual and Representative New England Net Installed Capacity Requirements
and Resulting Reserves, 2012 to 2021 (MW, %)

| Years | 2012 CELT Forecast 50/50 Peak (MW) | Actual and Representative Future Net ICR(a) (MW) | Resulting Reserves(b) (%) |
| --- | --- | --- | --- |
| 2012/2013 | 27,440 | 32,010 | 16.7 |
| 2013/2014 | 27,765 | 32,547 | 17.2 |
| 2014/2015 | 28,275 | 33,200 | 17.4 |
| 2015/2016 | 28,840 | 33,456 | 16.0 |
| 2016/2017 | 29,400 | TBD(c) | TBD(c) |
| 2017/2018 | 29,895 | 34,100(d) | 14.1 |
| 2018/2019 | 30,275 | 34,500(d) | 14.0 |
| 2019/2020 | 30,605 | 34,900(d) | 14.0 |
| 2020/2021 | 30,930 | 35,300(d) | 14.1 |
| 2021/2022 | 31,255 | 35,600(d) | 13.9 |

- Net ICR values for 2012/2013 to 2015/2016 are the latest values approved by FERC. These net ICR values were developed using 2011 CELT report loads, except for the 2014/2015 values, which were developed using the 2010 CELT report loads.

- The resulting reserves, when calculated using their respective CELT load forecasts, showed an average of approximately 14% resulting reserves for 2012/2013 to 2015/2016. The resulting reserve percentages shown in the table for this four-year period, however, are higher than 14% because they were calculated with the lower 50/50 peak load forecasts of the 2012 CELT Report and not with the 2011 CELT Report, which the net ICRs originally were calculated with.

- The ICR and net ICR will be filed with the FERC in November 2012.

- The 2017/2018 through 2021/2022 capability years’ representative net ICR values needed to meet the resource adequacy planning criterion are calculated based on the assumed average 14% resulting reserves for the 2012/2012 through 2015/2016 period, rounded to the nearest hundred. The rounding of the resulting-reserves values to the nearest hundred causes slight variation of plus or minus 0.1%.

The assumed percentage of resulting reserves shown in Table 4-1 for the future years is consistent with the results of past studies, assumed system conditions, and probabilistic calculation methodologies. As of the RSP12 publication date, the net ICR for 2016/2017 was under development and scheduled to be filed with FERC in November 2012. In December 2012 or early 2013, the ISO plans on recalculating the representative net ICR values using the same probabilistic calculation techniques and assumptions as used for determining the 2016/2017 net ICR values.

### Local Resource Requirements and Limits

While the ICR addresses New England’s total capacity requirement assuming the system overall has no transmission constraints, certain subareas are limited in their ability to export or import power. To address the impacts of these constraints on subarea reliability, before each FCA, the ISO determines the maximum capacity limit (MCL) and local sourcing requirement (LSR) for certain subareas within New England. An MCL is the maximum amount of capacity that can be procured in an export-constrained load zone to meet the total ICR for the New England region. An LSR is the minimum amount of capacity that must be electrically located within an import-constrained load zone to meet the ICR. Areas that have either an LSR or an MCL and that meet other tests in the market are designated in the Forward Capacity Auction as capacity zones. These designations help ensure that the appropriate amount of capacity is procured within these capacity zones to satisfy the ICR and contribute effectively to total system reliability.

On March 30, 2012, FERC issued an order that approved the January 31, 2012, ISO and NEPOOL filing on setting the floor price for FCA #7 at $3.15/kW-month and modeling four capacity zones. On April 13, 2011, FERC issued an order concerning the FCM redesign effort, by which eight capacity zones may be modeled in the FCA for future capacity commitment periods. The final design is yet to be completed. In addition, the ISO was directed to implement the changes defined in the April 13, 2011, order for FCA #8 and to file market rules to that effect by December 3, 2012.

The LSR and MCL values are included in Table 4-2 for the 2012/2013 through the 2015/2016 capacity commitment periods. The LSR and MCL values for FCA #7 were under development at the time of the RSP12 publication and will be filed with FERC in November 2012. In December 2012, the ISO will evaluate methods to calculate the representative LSR and MCL values for 2017/2018 through 2021/2022, with the goal of providing this information to the PAC in 2013.

Table 4-2
Actual LSRs and MCLs for the 2012/2013 to 2015/2016 Capacity Commitment Periods(a)

| Capacity Commitment Period |  | LSR (MW) |  | MCL (MW) |
| --- | --- | --- | --- | --- |
|  |  | CT | NEMA/Boston | Maine |
| 2012/2013 | FCA #3 | 7,312 | 3,013 | 3,707 |
| 2013/2014 | FCA #4 | 7,489 | 3,118 | 3,584 |
| 2014/2015 | FCA #5 | 7,478 | 3,046 | 3,702 |
| 2015/2016 | FCA #6 | 7,542 | 3,289 | 3,888 |

(a) 	Sources: “Summary of ICR, LSR, and MCL for FCM and the Transition Period,” available at http://www.iso-ne.com/markets/othrmkts_data/fcm/doc/summary_of_icr_values.pdf. Annual Reconfiguration Auction (ARA) values (see Section 4.1.3) were used for the 2010/2011, 2011/2012, 2012/2013, and 2013/2014 capacity commitment periods.

### Capacity Supply Obligations

The FCM’s Forward Capacity Auctions are designed to procure capacity roughly three years (40 months) in advance of the commitment period. This lead time allows capacity suppliers to develop new capacity resources and enables the ISO to plan for these new resources. Six annual auctions for FCM resources have taken place to address the region’s capacity needs through May 31, 2016.

All capacity resources, supply side and demand side (and including intermittent, variable energy resources [VERs], such as wind and solar), must comply with the qualification and financial-assurance requirements of the FCM. Existing capacity resources are required to participate in the FCA and automatically are entered into the capacity auction. However, these resources may indicate a desire to be removed from the FCA by submitting a delist bid before the qualification deadline for existing capacity. For example, high-priced capacity resources may choose to submit delist bids, indicating that the resources do not want the capacity supply obligation (CSO) below a certain price. Because the obligation to participate in the New England energy market is assigned only to resources with a capacity supply obligation, delisted resources are not obligated to supply electric energy, although they are allowed to voluntarily supply energy at market prices. Reconfiguration auctions also may procure any quantities not purchased in the FCA because of delisting at specific price thresholds. These monthly and annual auctions allow adjustments that reflect changes in the ICR, and they facilitate the trading of individual commitments made in the previous FCA. Unless an existing capacity resource follows specific criteria to become delisted each year, it will be assigned a one-year capacity supply obligation. New capacity that bids in the FCA can choose an initial capacity commitment period obligation between one and five years. In addition to the reconfiguration auctions, updates to the CSOs are based on bilateral transactions.

The FCM requires all new and existing capacity resources that obtain a capacity supply obligation (i.e., that clear the auction) to perform during shortage events, which occur only if the region is not able to meet its load and operating-reserve requirements in real time (see Section 4.3). Purchased resources that fail to perform during a shortage event receive a significantly reduced capacity payment, a measure intended to improve the alignment between system needs and available capacity.

This section presents the results of the first six Forward Capacity Auctions, including the amount of capacity that will be supplied by generation, import, and demand resources in the region.

#### Capacity Supply Obligations for the First Six FCAs

Table 4-3 shows the results of the six FCAs held so far for 2010/2011 through 2015/2016 and provides the capacity supply obligation totals procured for FCA #1 thru FCA #6 at the conclusion of each auction. This table also includes some details on the types of CSOs procured, including the total real-time emergency generation (RTEG) (see Section 2.3), self-supply obligation values that reflect bilateral capacity arrangements, and import capacity supply obligations from neighboring balancing authority areas.

Table 4-3
Summary of the FCA Obligations at the Conclusion of Each Auction (MW)(a)

| Commitment Period | ICR | HQICC | Net ICR(b) | Capacity Supply Obligation | RTEG Capacity Supply Obligation | RTEG Utilization Ratio | Self-Supply Obligation | Import Capacity Supply Obligation |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 2010/2011 | 33,705 | 1,400 | 32,305 | 34,077 | 875 | 0.686 | 1,593 | 934 |
| 2011/2012 | 33,439 | 911 | 32,528 | 37,283 | 759 | 0.791 | 1,696 | 2,298 |
| 2012/2013 | 32,879 | 914 | 31,965 | 36,996 | 630 | 0.952 | 1,935 | 1,900 |
| 2013/2014 | 33,043 | 916 | 32,127 | 37,501 | 688 | 0.872 | 2.698 | 1,993 |
| 2014/2015 | 34,154 | 954 | 33,200 | 36,918 | 722 | 0.831 | 3,176 | 2,011 |
| 2015/2016 | 34,498 | 1,042 | 33,456 | 36,309 | 617 | 0.972 | 4,164 | 1,924 |

  - Information regarding the results of annual reconfiguration auctions is available at http://www.iso-ne.com/markets/othrmkts_data/fcm/doc/summary_of_icr_values.pdf.

  - The ICR minus the Hydro-Québec Interconnection Capability Credits (see Section 4.1.1) equals the net ICR. The ICR applies to the FCA, not the reconfiguration auction.

#### FCA Results for Capacity Zones

Table 4-4 summarizes the detailed CSOs for the capacity zones modeled for each capacity commitment period, which are published in the 2012 CELT Report. The CSOs have been adjusted to reflect the market rule’s real-time emergency-generation limit of 600 MW, which is the maximum quantity of this capacity resource type that can be counted toward the ICR. Two capacity zones, Maine and the Rest-of-Pool, are used in the FCM to address Maine’s designation as an export-limited capacity zone. The potential import-constrained capacity zones were determined to have sufficient existing capacity to meet the local sourcing requirements.

Table 4-4
Results of the FCA by Capacity Zone at the Conclusion of Each Auction (MW, $/kW-month)(a)

| Commitment Period | Modeled Capacity Zone | Maximum Capacity Limit | Capacity Supply Obligation | RTEG Capacity Supply Obligation | Self-Supply Obligation | Capacity Clearing Price | Payment Rate | RTEG Payment Rate |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | (MW) |  |  |  | ($/kW-month) |  |  |
| 2010/2011 | Rest-of-Pool | N/A | 30,572 | 838 | 1,584 | 4.500 | 4.254 | 2.918 |
|  | Maine | 3,855 | 3,505 | 37 | 9 | 4.500 | 4.254 | 2.918 |
| 2011/2012 | Rest-of-Pool | N/A | 33,468 | 727 | 1,687 | 3.600 | 3.119 | 2.467 |
|  | Maine | 3,395 | 3,815 | 32 | 9 | 3.600 | 3.119 | 2.467 |
| 2012/2013 | Rest-of-Pool | N/A | 33,099 | 597 | 1,925 | 2.951 | 2.535 | 2.413 |
|  | Maine | 3,257 | 3,897 | 33 | 9 | 2.951 | 2.465 | 2.347 |
| 2013/2014 | Rest-of-Pool | N/A | 33,476 | 655 | 2,693 | 2.951 | 2.516 | 2.194 |
|  | Maine | 3,187 | 4,025 | 33 | 6 | 2.951 | 2.336 | 2.036 |
| 2014/2015 | Rest-of-Pool | N/A | 32,960 | 691 | 3,171 | 3.209 | 2.855 | 2.374 |
|  | Maine | 3,702 | 3,958 | 31 | 5 | 3.209 | 2.855 | 2.374 |
| 2015/2016 | Rest-of-Pool | N/A | 32,374 | 582 | 4,157 | 3.434 | 3.129 | 3.044 |
|  | Maine | 3,888 | 3,935 | 35 | 7 | 3.434 | 3.129 | 3.044 |

    - Values are rounded and do not reflect proration.

Available capacity resources in the NEMA/Boston capacity zone satisfy resource adequacy requirements for the area through FCA #6, with a local sourcing requirement of 3,289 MW for NEMA/Boston and 3,348 MW in available resources. However, additional retirements beyond those announced for Salem Harbor, additional load growth in NEMA/Boston, or issues with the availability of resources in the area will likely create the need for additional resource development. Available capacity resources in the Connecticut capacity zone exceed the resource adequacy requirements for the area after FCA #6, by 1,363 MW. In this zone for the 2015/2016 capacity commitment period, 8,905 MW of capacity resources will be used to meet the local sourcing requirement of 7,542 MW.

#### Capacity Supply Obligations for New Capacity

Overall, after adjusting for the repowering of existing generating capacity resources, which are treated as new capacity in the FCA, the contributions from new generating capacity resources toward meeting the ICR have been significantly less than the contributions from new demand and import capacity resources. Table 4-5 shows the new incremental additions of capacity by each type of resource—generation, demand, and imports.

Table 4-5
Capacity Supply Obligation for New Capacity
Procured during the Forward Capacity Auctions (MW)(a)

| Capacity Resource | FCA #1 | FCA #2 | FCA #3 | FCA #4 | FCA #5 | FCA #6 |
| --- | --- | --- | --- | --- | --- | --- |
| Generation resources | 40 | 1,157 | 199 | 114 | 42 | 79 |
| Demand-resource total | 860 | 447 | 309 | 515 | 263 | 313 |
| Active demand resources | 576 | 185 | 98 | 257 | 42 | 66 |
| Passive demand resources | 284 | 262 | 211 | 258 | 221 | 247 |
| Import resources | 0 | 1,529 | 817 | 831 | 871 | 1,648 |

(a) 	New RTEG capacity is not included in the table values because it is treated as existing capacity in the FCA. Repowered existing generating capacity (i.e., capacity that has undergone environmental upgrades), which is treated as new capacity in the FCA, has been removed as well. Refer to the full auction results at http://www.iso-ne.com/markets/othrmkts_data/fcm/cal_results/index.html.

More new demand and import capacity resources than new generation resources have been acquired through the FCM thus far. To date, nonprice retirements have been accepted for Salem Harbor units #1 through #4 (748 MW in FCA #5), and these units will be retired by June 1, 2014. Other resources, including demand resources, have submitted nonprice retirement requests, and the ISO continues to track the effects of retirements. In addition, approximately 1,662 MW of one-year dynamic and static delist bids were submitted and approved in FCA #6, which are resources that may reenter the FCM in later auctions. The retirement of older generating capacity resources without their replacement by new generating resources could result in the increased need to rely on both demand and import capacity to meet the requirements for resource adequacy and system operations.

### Systemwide Resource Needs

The systemwide capacity needs are shown by the representative net ICR values for future years (see Section 4.1.1). Table 4-6 compares these systemwide needs with the resources procured in FCA #6 plus the energy-efficiency forecast (see Section 3.2) that projects the future levels of passive demand resources. This projection assumes that all resources with supply obligations through FCA #6 are in commercial service by the start of the sixth capacity commitment period commencing in June 2015 and that they remain in service for the 10-year planning horizon. The resource surpluses from 2017 through 2021 show the maximum amounts of resource retirements the region can withstand systemwide. Individual retirements of resources, however, may not be permissible because of transmission security constraints that must be respected to serve load reliably.

Table 4-6
Future Systemwide Needs (MW)

| Year | 50/50 Peak Load | Representative Net ICR (Need) | FCA #6 (Known Resources)(a) | EE Forecast (New Resource) | Resource Surplus/Shortage |
| --- | --- | --- | --- | --- | --- |
| 2017/2018 | 29,895 | 34,100 | 36,309 | 451 | 2,660 |
| 2018/2019 | 30,275 | 34,500 | 36,309 | 655 | 2,464 |
| 2019/2020 | 30,605 | 34,900 | 36,309 | 847 | 2,256 |
| 2020/2021 | 30,930 | 35,300 | 36,309 | 1,026 | 2,035 |
| 2021/2022 | 31,255 | 35,600 | 36,309 | 1,194 | 1,903 |

(a) FCA #6 resource numbers are based on FCA #6 auction results. Imports were assumed at 314.8 MW. Details are available at http://www.iso-ne.com/regulatory/ferc/filings/2012/apr/er12-1678-000_04-30-12_6th_fca_results_filing.pdf.

## Analyzing Operable Capacity

Using a deterministic approach, the ISO analyzes the systemwide operable capacity to estimate the net capacity that will be available under two scenarios (i.e., using the 50/50 and 90/10 forecasts of peak load). The analysis identifies operable capacity margins (i.e., the amount of resources that must be operational to meet peak demand plus operating-reserve requirements) under assumed peak-load conditions. The results of these examinations show either a positive or negative operating margin in meeting system operating requirements. A negative margin for a specific scenario indicates the extent that possible mitigation actions would be required through predefined protocols, as prescribed in the ISO’s Operating Procedure No. 4, Action during a Capacity Deficiency, or Operating Procedure No. 7 (OP 7), Action in an Emergency.

For RSP12, the ISO conducted a systemwide operable capacity analysis for 2012 to 2021, which does not take into account operable capacity needs for RSP subareas. This section discusses the methodology used to conduct this analysis and summarizes its results.

### Approach

The operable capacity analysis was performed with both the 50/50 and 90/10 peak-load forecasts, adjusted with a total of 2,000 MW of operating reserves assumed to reflect the largest loss-of-source (LOS) contingency at 1,400 MW plus one-half of a large (1,200 MW) generating unit operating equivalent to 600 MW. The systemwide capacity assumed was the actual or the representative net ICR values for the region (described in Table 4-1), assuming 2,100 MW of resource outages, which is consistent with the historical performance of supply-side generating resources. The results are a direct comparison of the operable capacity requirements of the system with the total capacity assumed to be available (in this case, the net ICR values minus assumed unavailable capacity).

### Results

Figure 4-1, Table 4-7, and Table 4-8 show the results of the systemwide operable capacity analysis. The results show that if the loads associated with the 50/50 forecast were to occur, the ISO would not expect New England to experience any negative operable capacity margin during the study period.

Figure 4-1: Projected summer operable capacity analysis, 2012 to 2021.

Note: Each year indicates the starting year for the respective capacity commitment period. Total net capacity values for 2012/2013 to 2015/2016 are based on the net ICR filed with FERC. The net capacity for 2017/2018 to 2021/2022 is based on representative net ICR values. The net capacity for 2016/2017 is under development and will be determined after the net ICR for 2016/2017 is filed with FERC in November 2012.

Table 4-7
Projected New England Operable Capacity Analysis for Summer, 2012 to 2021,
Assuming 50/50 Loads (MW)

| Capacity Situation (Summer MW) | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Load (50/50 forecast) | 27,440 | 27,765 | 28,275 | 28,840 | 29,400 | 29,895 | 30,275 | 30,605 | 30,930 | 31,255 |
| Operating reserves | 2,000 | 2,000 | 2,000 | 2,000 | 2,000 | 2,000 | 2,000 | 2,000 | 2,000 | 2,000 |
| Total requirement | 29,440 | 29,765 | 30,275 | 30,840 | 31,400 | 31,895 | 32,275 | 32,605 | 32,930 | 33,255 |
| Installed capacity (net ICR) | 32,010 | 32,547 | 33,200 | 33,456 | N/A | 34,100 | 34,500 | 34,900 | 35,300 | 35,600 |
| Assumed unavailable capacity | −2,100 | −2,100 | −2,100 | −2,100 | −2,100 | −2,100 | −2,100 | −2,100 | −2,100 | −2,100 |
| Total net capacity(a) | 29,910 | 30,447 | 31,100 | 31,356 | N/A | 32,000 | 32,400 | 32,800 | 33,200 | 33,500 |
| Operable capacity margin(b) | 470 | 682 | 825 | 516 | N/A | 105 | 125 | 195 | 270 | 245 |

(a)	The net capacity values are consistent with Table 4-1.

(b) “Operable capacity margin” equals “total net capacity” minus “total requirement.”

Table 4-8
Projected New England Operable Capacity Analysis for Summer, 2012 to 2021,
Assuming 90/10 Loads (MW)

| Capacity Situation (Summer MW) | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Load (90/10 forecast) | 29,620 | 29,980 | 30,530 | 31,130 | 31,725 | 32,255 | 32,675 | 33,040 | 33,405 | 33,765 |
| Operating reserves | 2,000 | 2,000 | 2,000 | 2,000 | 2,000 | 2,000 | 2,000 | 2,000 | 2,000 | 2,000 |
| Total requirement | 31,620 | 31,980 | 32,530 | 33,130 | 33,725 | 34,255 | 34,675 | 35,040 | 35,405 | 35,765 |
| Installed capacity (net ICR) | 32,010 | 32,547 | 33,200 | 33,456 | N/A | 34,100 | 34,500 | 34,900 | 35,300 | 35,600 |
| Assumed unavailable capacity | −2,100 | −2,100 | −2,100 | −2,100 | −2,100 | −2,100 | −2,100 | −2,100 | −2,100 | −2,100 |
| Total net capacity(a) | 29,910 | 30,447 | 31,100 | 31,356 | N/A | 32,000 | 32,400 | 32,800 | 33,200 | 33,500 |
| Operable capacity margin(b) | −1,710 | −1,533 | −1,430 | −1,774 | N/A | −2,255 | −2,275 | −2,240 | −2,205 | −2,265 |

(a)	The net capacity values are consistent with Table 4-1.

(b) 	“Operable capacity margin” equals “total net capacity” minus “total requirement.”

Figure 4-1 and Table 4-8 show that New England could experience larger negative operable capacity margins of approximately 1,710 MW as early as summer 2012 if the 90/10 peak loads occurred. Thus, throughout the study period, New England would need to rely on load and capacity relief from OP 4 actions under the projected 90/10 peak loads. Assuming the exact amount of resources needed to meet the once-in-10-years LOLE is purchased in the FCA, this negative operable capacity margin would decrease to approximately 1,430 MW by 2014 and then increase back to the 1,774 MW range by 2015. Using an indicative reserve margin of approximately 14%, the operable capacity margin stays relatively constant from 2017 through 2021 in the negative 2,250 MW range.

## Determining Operating Reserves and Regulation

In addition to capacity resources being available to meet the region’s actual demand for electricity, as discussed in Section 4.1, the system needs a certain amount of resources that can provide operating reserves and system regulation. The overall mix of resources providing operating reserves must be able to respond quickly to system contingencies stemming from equipment outages. These resources also may be called on to provide regulation service for maintaining system frequency and external transactions with neighboring balancing authority areas or to serve load during peak demand conditions. A suboptimal mix of resources overall, with limited amounts of flexible operating characteristics, could result in the dependence of the system on more costly resources to provide these services. In the worst case, reliability would be degraded.

Several types of resources in New England have the operating characteristics to respond to contingencies, provide regulation service, and serve peak demand. The generating units that provide operating reserves can respond to contingencies within 10 or 30 minutes and can either be synchronized or not synchronized to the power system. Synchronized (i.e., spinning) operating reserves are on-line resources that can increase output. Nonsynchronized (i.e., nonspinning) operating reserves are off-line, “fast-start” resources that can be electrically synchronized to the system quickly and reach claimed capability (i.e., a generator’s maximum production or output) within 10 to 30 minutes to respond to a contingency and serve demand.

During daily operations, the ISO determines operating-reserve requirements for the system as a whole and for major import-constrained areas. The requirement for systemwide operating reserves is based on the largest loss-of-source contingency and half of the next-largest loss-of-source contingency within New England, which typically consist of some combination of the two largest on-line generating units or imports on the Phase II interconnection with Québec. The operating reserves required within the major importing subareas of the system depend on many factors, including the economic dispatch of generation systemwide, the operating characteristics of the generation within the subarea, the projected peak load of the subarea, the most critical contingencies that determine the transmission import capability into the subarea, and possible resource outages. The ISO analyzes and determines how the generating resources within the load pockets must be committed to meet the following day’s operational requirements and withstand possible contingencies. The locational Forward Reserve Market is in place to procure these required operating reserves.

This section discusses the need for operating reserves, both systemwide and in major import areas, and the use of specific types of fast-start resources to fill these needs. An overview of the FRM and a forecast of representative future operating-reserve requirements for Greater Southwest Connecticut, Greater Connecticut, and BOSTON are provided. This section also discusses the likely need for additional flexible resources identified by the Strategic Planning Initiative.

### Systemwide Operating-Reserve Requirements

A certain amount of the power system’s resources must be available to provide operating reserves to assist in addressing systemwide contingencies, as follows:

- Loss of generating equipment within the ISO New England Balancing Authority Area or within any other NPCC balancing authority area

- Loss of transmission equipment within or between NPCC balancing authority areas, which might reduce the capability to transfer electric power within New England or between the New England balancing authority area and any other area

The ISO’s operating-reserve requirements, as established in Operating Procedure No. 8, Operating Reserve and Regulation (OP 8), are used to protect the system from the impacts associated with a loss of generating or transmission equipment within New England. As documented in OP 8, the ISO must maintain sufficient reserves during normal conditions in the ISO New England Balancing Authority Area to be able to replace within 10 minutes the first-contingency loss (N−1) (see Section 2.3). Typically, the largest first-contingency loss is between 1,300 and 1,700 MW. In addition, OP 8 requires the ISO to maintain sufficient reserves to be able to replace at least 50% of the next-largest contingency loss (N−1−1) within 30 minutes. Typically, 50% of the next-largest contingency loss is between 600 and 750 MW.

In accordance with NERC and NPCC criteria for power system operation, ISO Operating Procedure No. 19 (OP 19), Transmission Operations, requires the system to operate such that when any power system element is lost (N−1), power flows remain within applicable emergency limits of the remaining power system elements. This N−1 limit may be a thermal, voltage, or stability limit of the transmission system. OP 19 further stipulates that within 30 minutes of the loss of the first-contingency element, the system must be able to return to a normal state that can withstand a second contingency. To implement these OP 19 requirements, and as set forth in OP 8, operating reserves must be distributed throughout the system. This requirement is designed to ensure that the ISO can activate all reserves without exceeding transmission system limitations and that the operation of the system remains in accordance with NERC, NPCC, and ISO New England criteria and guidelines.

### Forward Reserve Market Requirements for Major Import Areas

To maintain system reliability, OP 8 mandates the ISO to maintain certain reserve levels within major importing subareas that rely on imports of power from outside the area. The amount and type of operating reserves a subarea needs depend on the system’s reliability constraints and the characteristics of the generating units within the subarea. Subarea reserve requirements also vary as a function of load levels, unit commitment and dispatch, system topology, special operational considerations, and other system conditions. If maximizing the use of transmission import capability to meet demand is more economical, the subarea will require more local operating reserves to protect for contingencies. If using import capability to meet demand is less economical, generation located outside the subarea could be used to provide operating reserves, thus reducing operating-reserve support needed within the subarea.

Table 4-9 shows representative future operating-reserve requirements for Greater Southwest Connecticut, Greater Connecticut, and BOSTON. These estimated requirements are based on the same methodology used to calculate the requirements for the locational FRM. The estimates account for representative future system conditions for load, economic generation, generation availability, N−1 and N−1−1 transfer limits, and normal criteria contingencies for generation and transmission in each subarea. The representative values show a range to reflect the load and resource uncertainties associated with future system conditions. Table 4-9 also shows the existing amount of fast-start capability located in each subarea resulting from the fast-start resource offers into past FRM auctions.

Table 4-9 
Representative Future Operating-Reserve Requirements
in Major New England Import Areas (MW)

| Area/Improvement | Market Period(a) | Range of Fast-Start Resources Offered into the Past Forward Reserve Auctions (MW)(b) | Representative Future Locational Forward Reserve Market Requirements (MW) |  |
| --- | --- | --- | --- | --- |
|  |  |  | Summer(c) (Jun to Sep) | Winter(c) (Oct to May) |
| Greater Southwest Connecticut(d) | 2012 | 199–515 | 0(e) | 50(e) |
|  | 2013 |  | 0 | 0 |
|  | 2014 |  | 0 | 0 |
|  | 2015 |  | 0 | 0 |
|  | 2016 |  | 0 | 0 |
| Greater Connecticut(f, g) Greater Springfield Reliability Project (GSRP), and Interstate Reliability Project (IRP) of the New England East–West Solution (NEEWS)(f) | 2012 | 614–1,563(h) | 765(e) | 837(e) |
|  | 2013 |  | 400–1,100 | 0–200 |
|  | 2014 |  | 400–1,100 | 0–200 |
|  | 2015 |  | 400–1,100 | 0–200 |
|  | 2016 |  | 400–1,100 0–300 with IRP of NEEWS | 0–200 0 with IRP of NEEWS |
| BOSTON(g, i) | 2012 | 0–441 | 0(e) | 0(e) |
|  | 2013 |  | 0–200 | 0 |
|  | 2014 |  | 0–200 | 0 |
|  | 2015 |  | 0–200 | 0 |
|  | 2016 |  | 0–200 | 0 |

- The market period is from June 1 through May 31 of the following year.

- These values are the range of the megawatts of resources offered into the past forward-reserve auctions. The amount offered into the auctions for BOSTON decreased in recent years as the reserve requirements for the market decreased. A summary of the forward-reserve offers for the past auctions is available at http://www.iso-ne.com/markets/othrmkts_data/res_mkt/summ/2012/forward_reserve_auction_results.pdf.

- “Summer” means June through September of a capability year; “winter” means October of the associated year through May of the following year (e.g., the 2012 winter values are for October 2012 through May 2013). The representative values show a range to reflect uncertainties associated with the future system conditions.

- The assumed N−1 and N−1−1 values to reflect transmission import limits into Greater Southwest Connecticut are 3,200 MW and 2,300 MW, respectively.

- These values are actual locational forward-reserve requirements. The projections of the requirements for future years are based on assumed contingencies.

- For Greater Connecticut, the assumed import limits reflect an N−1 value of 2,500 MW and an N−1−1 value of 1,300 MW before 2014. These limits are assumed to increase to 2,600 MW and 1,400 MW, respectively, in 2014 when the Greater Springfield Reliability Project component of the New England East–West Solution is in-service. The limits are assumed to increase to 3,400 MW, and 2,500 MW, in 2016 when the Interstate Reliability Project of NEEWS is in-service. Refer to Section 5.5.2 for more information on NEEWS.

- In some circumstances when transmission contingencies are more severe than generation contingencies, shedding some nonconsequential load (i.e., load shed that is not the direct result of the contingency) may be acceptable.

- These values include resources in Greater Southwest Connecticut.

- The assumed N−1 and N−1−1 values reflecting transmission import limits into BOSTON are 4,900 MW and 3,700 MW, respectively. These limits are assumed to change to 4,850 MW and 4,175 MW, respectively, starting in 2014, to reflect the impacts of the retirement of Salem Harbor units #1–#4 and the North Shore Upgrade. The operating-reserve values for BOSTON would be lower with transmission upgrades or without consideration of the common-mode failure of Mystic units #8 and #9 that were assumed to trip up to 1,400 MW because of exposure to a common failure of the fuel supply to the units.

While the estimates for operating-reserve requirements are based on expected future operating conditions, annual market requirements are based on historical data that reflect the actual previous seasonal system conditions; actual market requirements are calculated immediately before each locational FRM procurement period.

Because the local contingency requirements in Greater SWCT are nested within CT (i.e., operating reserves meeting the Greater SWCT requirement also meet the Greater Connecticut requirement), resources installed in the Greater SWCT area also would satisfy the need for resources located anywhere in Greater Connecticut.

#### Greater Southwest Connecticut

As shown in Table 4-9, Greater SWCT has sufficient fast-start resources to meet its 2012 requirements for operating reserves. For future years, economic energy transfers to serve load and the reserve support necessary to cover the second contingencies can be provided from outside the Greater SWCT area because transmission improvements have increased the transfer capability into the area (see Section 5.5.2).

#### Greater Connecticut

Past RSPs and market signals had identified the need for in-merit and fast-start resources in Greater Connecticut to meet reliability requirements and reduce out-of-merit market costs. As a result of resource development, Greater Connecticut is projected to have adequate fast-start resources, and the economic performance of this area is expected to improve. Up to 1,563 MW of fast-start resources were offered into the past summer auctions for Greater Connecticut, which exceeds the 765 MW of the reserve requirement established for the FRM. The decrease of the local reserve requirements is the result of planned additions of economical baseload generation within Greater Connecticut procured through the FCM and the increase of import capability into Greater Connecticut resulting from the transmission projects of the New England East–West Solution (see Section 5.5.2) expected to be completed in 2014 and 2016.

#### BOSTON

The FRM requirements for the BOSTON subarea shown in Table 4-9 reflect the possible simultaneous contingency loss of Mystic units #8 and #9. With the increased import limits resulting from the completion of the NSTAR 345 kilovolt (kV) Transmission Reliability Project in 2008, operators should be able to optimize the use of regional generation to meet both load and reserve requirements.

The FRM requirements for the BOSTON subarea also reflect the retirements of the Salem Harbor units in 2014. These retirements affect the reserve requirements because they will reduce the total ability to serve load in the BOSTON subarea. Although the North Shore transmission upgrades increase the transmission transfer capabilities into BOSTON, this capability is more than offset by the reduced amount of Salem Harbor generation available to serve the BOSTON subarea loads. (Refer to Table 4-9, note i.)

If the transmission lines were fully utilized to import lower-cost generation into BOSTON, this subarea would need to provide operating reserves to protect against the larger of (1) the loss of the largest generation source within the subarea and a transmission line or (2) the loss of two transmission lines into the subarea. Up to 441 MW of fast-start resources were offered into the past FRM auctions. The expected amount of existing fast-start resources located in BOSTON will likely meet the 0 to 200 MW of representative local reserve requirements for BOSTON during the study timeframe.

#### Summary of Forward Reserve Market Requirements in Major Load Pockets

New England must meet its overall operating-reserve requirements and have sufficient reserves in load pockets to meet reliability requirements. The recent additions of fast-start resources in Greater Connecticut provide needed operating flexibility as well as operating reserves. Planned fast-start resources as well as baseload resources on line most of the time (see below) also would decrease the amounts of reserves required within the subareas of Greater Connecticut. Existing fast-start resources likely will be used to meet the locational reserve requirements for BOSTON. Any reduction in traditional baseload resources in either area would increase the locational FRM requirement.

The potential retirement of generating units could affect the definition of the zones for operating-reserve requirements.

## Identifying New England’s Generating Resources

The system’s generating units have different production costs and abilities to change output. Baseload generating units satisfy all or part of the minimum load of the system, producing economical electric energy continuously and at a constant rate close to maximum output. Baseload units usually are not flexible and typically are on line more than 70% of the year. Intermediate-load generating units are used during the transition between baseload and peak-load requirements and typically operate from 10% to 70% of the year. These units come on line during intermediate load levels and ramp up and down to follow the system load that peaks during the day and is at its lowest in the middle of the night. Intermediate units often provide regulation and spinning reserve. Peaking units operate less than 10% of the year (i.e., a few hundred hours per year). These units usually are on line during very high, peak-day load periods and may be used in response to system contingencies because they can start quickly on demand and operate for only a few hours.

Table 4-10 shows the megawatt amount of seasonal claimed capability by assumed operating classification of the generating resources, both systemwide and for each RSP subarea.

Table 4-10
2012 Seasonal Claimed Capability for ISO New England Generating Resources
by Assumed Operating Classification, Systemwide and by RSP Subarea (MW)

| Area | Baseload | Intermediate | Peaking |
| --- | --- | --- | --- |
| BHE | 163 | 515 | 143 |
| BOSTON | 1,407 | 1,659 | 237 |
| CMA/NEMA | 46 | 111 | 30 |
| CT | 3,904 | 729 | 548 |
| ME | 297 | 385 | 123 |
| NH | 2,808 | 1,224 | 83 |
| NOR | 330 | 0 | 184 |
| RI | 1,551 | 3,674 | 46 |
| SEMA | 1,880 | 1,323 | 148 |
| SME | 890 | 574 | 32 |
| SWCT | 525 | 987 | 772 |
| VT | 803 | 41 | 111 |
| WMA | 376 | 1,383 | 1,927 |
| Total | 14,981 | 12,605 | 4,383 |

### Existing Generating Resources in New England

Generating units located close to load centers typically reduce the need for transmission system improvements. Table 4-11 tabulates the existing generating amounts and locations by RSP subarea, load zone, and state.

Table 4-11
RSP12 Generating Capacity by Subarea, SMD Load Zone, and State, 2012

| RSP Subarea | State | Load Zone | Summer |  |  | Winter |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | MW | % of RSP Subarea | % of State | MW | % of RSP Subarea | % of State |
| BHE | Maine | ME | 821 | 100 | 26 | 877 | 100 | 26 |
| ME | Maine | ME | 804 | 100 | 26 | 931 | 100 | 28 |
|  | New Hampshire | NH | 0 | 0 | 0 | 0.4 | 0 | 0 |
|  |  |  | 804 |  |  | 931 |  |  |
| SME | Maine | ME | 1,495 | 100 | 48 | 1,559 | 100 | 46 |
| NH | Massachusetts | WCMA | 16 | 0 | 0 | 17 | 0 | 0 |
|  | New Hampshire | ME | 0 | 0 | 0 | 0.5 | 0 | 0 |
|  |  | NH | 4,074 | 99 | 100 | 4,309 | 99 | 100 |
|  | Vermont | NH | 1 | 0 | 0 | 1 | 0 | 0 |
|  |  | VT | 25 | 1 | 2 | 34 | 1 | 3 |
|  |  |  | 4,116 |  |  | 4,361 |  |  |
| VT | New Hampshire | NH | 1 | 0 | 0 | 3 | 0 | 0 |
|  | Vermont | NH | 90 | 9 | 8 | 90 | 9 | 8 |
|  |  | VT | 864 | 91 | 82 | 964 | 91 | 83 |
|  |  |  | 955 |  |  | 1,057 |  |  |
| BOSTON | Massachusetts | NEMA | 3,294 | 100 | 25 | 3,716 | 100 | 26 |
|  |  | SEMA | 0 | 0 | 0 | 1 | 0 | 0 |
|  |  | WCMA | 8 | 0 | 0 | 15 | 0 | 0 |
|  |  |  | 3,302 |  |  | 3,731 |  |  |
| CMA/NEMA | Massachusetts | NEMA | 1 | 0 | 0 | 0 | 0 | 0 |
|  |  | WCMA | 187 | 100 | 1 | 200 | 100 | 1 |
|  |  |  | 188 |  |  | 200 |  |  |
| WMA | Massachusetts | WCMA | 3,608 | 98 | 27 | 3,887 | 98 | 27 |
|  | Vermont | WCMA | 78 | 2 | 7 | 77 | 2 | 7 |
|  |  |  | 3,686 |  |  | 3,963 |  |  |
| SEMA | Massachusetts | SEMA | 3,107 | 93 | 24 | 3,368 | 92 | 23 |
|  | Rhode Island | RI | 244 | 7 | 13 | 279 | 8 | 13 |
|  |  |  | 3,351 |  |  | 3,647 |  |  |
| RI | Connecticut | RI | 745 | 14 | 9 | 845 | 15 | 9 |
|  | Massachusetts | SEMA | 2,926 | 56 | 22 | 3,175 | 55 | 22 |
|  | Rhode Island | RI | 1,601 | 30 | 87 | 1,800 | 31 | 87 |
|  |  |  | 5,272 |  |  | 5,820 |  |  |
| CT | Connecticut | CT | 5,181 | 100 | 59 | 5,175 | 100 | 57 |
| SWCT | Connecticut | CT | 2,284 | 100 | 26 | 2,542 | 100 | 28 |
| NOR | Connecticut | CT | 514 | 100 | 6 | 546 | 100 | 6 |
| Total(a) |  |  | 31,969 |  |  | 34,408 |  |  |

(a) Totals may vary because of rounding.

As part of the FCA-qualification process, generators are subject to a review that evaluates whether transmission upgrades are needed to ensure that the new generating capacity is incrementally useful within each capacity zone. Previous RSP and FCM studies have confirmed that interconnecting new resources close to the Connecticut, Boston, and lower SEMA load centers would improve the overall reliability of the system and could potentially defer the need for transmission improvements. Additionally, system studies show that generation near Burlington, Vermont; Manchester, New Hampshire; and in the New Hampshire seacoast may be beneficial, depending on the size and location of the generation. Furthermore, some areas of the system are showing significant system limitations that prevent the concurrent operation of existing resources. These areas include western Maine; north of Orrington, Maine; and extreme Northern Vermont. Individual system impact studies are necessary to fully assess the electrical performance of the system and determine reliable interconnections of generation resources.

### Generating Units in the ISO Generator Interconnection Queue

The interconnection requests in the ISO’s Generator Interconnection Queue reflect the region’s interest in building new generation capacity. Figure 4-2 shows the capacity of the 70 active generation-interconnection requests in the queue by RSP subarea as of April 1, 2012. The areas with the most active proposed capacity additions are the SWCT, WMA, and SEMA subareas followed by ME, BOSTON, and CT. Together, these six subareas have about 5,349 MW under development out of a total of 6,574 MW of active projects for New England. A total of 2,126 MW is proposed for the three subareas in Connecticut.

Figure 4-2: Capacity of generation-interconnection requests by RSP subarea from November 1997 to April 2012.

Notes: All capacities are based on the projects in the ISO Generator Interconnection Queue as of April 1, 2012, that would interconnect with the ISO system. Projects involving only transmission or that did not increase an existing generator’s capacity were excluded. Projects with more than one listing in the queue, representing different interconnection configurations, were only counted once.

Table 4-12 shows a summary of the projects in the ISO Generator Interconnection Queue as of April 1, 2012. Since the first publication of the queue in November 1997, 87 generating projects (14,432 MW) out of 348 total generator applications (totaling 71,327 MW) have become commercial. Since the queue’s inception, proposed projects totaling approximately 50,321 MW have been withdrawn, reflecting a megawatt attrition rate of 71%. The 70 active projects in the queue total 6,574 MW. Figure 4-3 shows the resources in the ISO Generator Interconnection Queue, by state and fuel type, as of April 1, 2012. Figure 4-4 shows the total megawatts of the same resources by RSP subarea, and Figure 4-5 shows the percentages of the fuel types by subarea.

Table 4-12
Summary of Queue Projects as of April 1, 2012

| Category of Projects | Projects | Total Capacity (MW) |
| --- | --- | --- |
| Commercial | 87 | 14,432 |
| Active | 70 | 6,574 |
| Withdrawn | 191 | 50,321 |
| Total | 348 | 71,327 |

Figure 4-3: Resources in the ISO Generator Interconnection Queue, by state and fuel type, as of April 1, 2012 (MW and %).

Notes: The “other renewables” category includes wood, landfill gas (LFG), solar, and fuel cell capacity. The totals for all categories reflect all queue projects that would interconnect with the system and not all projects in New England.

Figure 4-4: Resources in the ISO Generator Interconnection Queue, by RSP subarea and fuel type, as of April 1, 2012 (MW).

Figure 4-5: Percentage of resources in the ISO Generator Interconnection Queue, by RSP subarea and fuel type, as of April 1, 2012.

## Analyzing Market Resource Alternatives

The RSP annually discusses the region’s reliability concerns and solutions to these concerns. Past discussions have provided information on the amounts, types, and locations of needed resources and on transmission solutions to these needs. At the request of ISO stakeholders, the ISO has identified hypothetical market resources that can relieve transmission system reliability needs in certain areas of the system. These market resources, which may consist of supply or demand resources at one or multiple locations, also may help meet the requirements for resource adequacy and operating reserves. This section describes market resources, the work done to date in the pilot studies, and next steps for evaluating market resource alternatives.

### Pilot Studies

In October 2010, the ISO introduced to stakeholders a conceptual approach to evaluating market resource alternatives. The approach used a steady-state thermal analysis to address the reliability concerns identified. The analysis served as an indication of the amounts, types, and locations of generation, demand resources, and transmission that could individually meet reliability requirements. A hybrid solution encompassing a combination of generation, demand response, and transmission was not evaluated, and no economic analysis of the market resources was performed. The analysis also did not assess the ability of the resources to deliver capacity or address detailed transmission planning issues, such as voltage performance, short-circuit levels, or system stability.

The ISO completed the first pilot study in May 2011. It assessed market resources for addressing the reliability concerns identified in the Vermont/New Hampshire Needs Assessment using analyses and assumptions stakeholders had already agreed on. The computer simulations created theoretical solutions that represent optimally located, perfectly balanced, and constantly available resources (e.g., generation or demand resources) without consideration of the transmission required to interconnect the theoretical generators. Changes to the size, location, or availability of these theoretical solutions could require additional megawatts to resolve the needs identified by the VT/NH Needs Assessment.

The study considered nine subareas in the VT/NH area for application of supply and demand market resources consistent with the nine subareas studied when determining the regulated transmission solution. FCA #4 resources (see Section 4.1.3) were represented in the cases, but potential resources in the ISO Generation Interconnection Queue (see Section 4.4) and in other stages of development were not assumed in the simulations. The transmission overloads identified in the needs assessment were brought within or below 100% of the applicable facility limits.

In the study, the VT/NH critical load-level analysis was used to determine the level of market demand resources that could alleviate the need for transmission improvements. This analysis identified the system load levels that could relieve each specific overload in the nine study subareas. Using the most limiting critical load level, the study estimated the effective load reduction in each dispatch zone (DZ).

To determine the conceptual supply-side market resources needed in lieu of transmission improvements, effective capacity in blocks of 500 MW were modeled at all 115 kV and 345 kV busses across the VT/NH areas. A security-constrained dispatch model was used to determine the location where added megawatts would relieve all the overloads for all the system conditions considered. This model also sought to minimize the megawatts of capacity dispatched.

The results represent only a theoretical solution of optimally located and dispatched resources assumed to be available 100% of the time. Any deviation from the solution or assumptions in the study may require more megawatts to eliminate the overloads. To assess the full impact of potential supply resources as market resource alternatives would require more detailed system studies. Future Strategic Planning Initiatives would need to address these issues when considering MRAs in lieu of transmission improvements and will provide further opportunity to discuss the role and cost allocation for market resource solutions.

### Stakeholder Input

Overall, the VT/NH pilot study was well received by stakeholders. Some stakeholders expressed a desire for a more granular analysis of market resource alternatives, specifically about locations of demand-response resources, while others indicated that the level of detail provided in the analysis surpassed their expectations. PAC stakeholders indicated that siting, permitting, and construction of generating facilities in certain identified areas would likely present many challenges. Stakeholders were particularly concerned about areas where a large supply-side resource would need to be constructed in a relatively small area. Study results highlighted that some market resource alternatives would be suitable for meeting some reliability needs but that other market resource solutions would require resources in multiple locations with an overly complex generator dispatch. For these cases, transmission solutions may be more practical. Study results also highlighted that some transmission upgrades likely would be required for the MRA solutions to pass the ISO’s “overlapping interconnection impacts test” that would allow them to qualify in the Forward Capacity Market.

### Next Steps

The ISO will continue to work with stakeholders to further refine market resource analysis in evaluating the role of market resources in meeting reliability needs. In late 2011, the ISO introduced the next pilot study, which will analyze the Greater Harford and Central Connecticut area. This pilot study is scheduled to be completed in late 2012.

The ISO will continue to focus on the technical aspects of such analyses but recognizes that some questions are outstanding, such as the following:

- Should the analysis consider the longevity of market resource alternatives?

- What is the appropriate level of coordination with current and proposed state processes?

- How do market resource alternatives comport with the wholesale market design and the principle of revenue recovery through the wholesale markets?

- How should the analysis consider the other values that the proposed market resources provide to the system, such as adding fast-start or load-following capability?

The ongoing Strategic Planning Initiative will further provide for a regional discussion about market resources as alternatives to transmission and about better aligning the timing of determining potential wholesale market resource solutions with the timing of determining system planning requirements and transmission solutions.

## Summary

The results of FCA #6 show that New England will have adequate resources through 2015/2016, assuming that resources meet their capacity supply obligations. Because additional retirements may occur, the ISO is working with stakeholders to identify issues and find the means of meeting future capacity needs. Most recent increases in capacity have come from both demand resources and imports from neighboring regions, and approximately 6,600 MW of proposed generation are in the ISO Generator Interconnection Queue. The ISO remains optimistic that adequate demand and supply resources will be procured and installed in time to meet the physical capacity needs that will be established by the ICRs for future years. Additional market incentives may be needed to further increase the likelihood of resource development where and when needed.

By design, the level of the ICR specified for New England could necessitate the use of specific OP 4 actions because the ICR calculation includes the load relief provided by these actions as resource offsets. Several factors would affect the frequency and extent of OP 4 actions, including the amount of resources procured to meet capacity needs, their availability, and actual system loads. Study results show that the need for load and capacity relief by OP 4 actions will be approximately 2,300 MW during extremely hot and humid summer peak-load conditions. This amount is likely achievable through OP 4 actions by depleting operating reserves, scheduling emergency transactions with neighboring systems, operating real-time emergency generators, and implementing 5% voltage reductions.

Fast-start resources with a short lead time for project development can satisfy near-term operating-reserve requirements while providing operational flexibility to major load pockets and the system overall. Properly locating and sizing economical baseload generation within major load pockets decreases the amount of reserves required within the load pocket and reduces the reliance on transmission facilities Transmission improvements also can allow for the increased use of reserves from outside these areas.

This section shows that representative operating-reserve requirements could be met for the system as currently planned. Additional pilot studies of market resource alternatives are underway that will further inform stakeholders.

Preserving the reliable operation of the system will become increasingly challenging with potential retirements and the need for operating flexibility. As a result of these factors, the need for new resources, especially those able to provide operating reserves and ramping capabilities, is expected to increase.

To address these challenges over the long term, the region has initiated a Strategic Planning Initiative (see Section 6) and other stakeholder efforts. Analysis and adjustments of markets may be required to establish reliable amounts and locations of needed new resources and operating reserves, including the appropriate levels of spinning and nonspinning reserves. Enhancements to the FCM and the locational FRM, which could include a reexamination of the capacity and reserve zones, also may be considered to better meet operational needs.

# Transmission Security and Upgrades

The ISO and regional stakeholders have made progress analyzing the transmission system in New England, developing “backstop” transmission solutions to address existing and projected transmission system needs and implementing these solutions. Sixteen major 345 kV projects have emerged from these efforts, all of which are critical for maintaining transmission system reliability. These transmission upgrades also have improved and will continue to improve the economic performance of the power system.

Eight of the 16 major 345 kV projects have been placed in service at a cost of over $2.5 billion. These include the two Southwest Connecticut Reliability Projects (Phase 1 and Phase 2), the Northeast Reliability Interconnection (NRI) Project, the Boston 345 kV Transmission Reliability Project (Phase 1 and Phase 2), the Short-Term Lower SEMA Upgrades, the Northwest Vermont (NWVT) Reliability Project, and the Vermont Southern Loop Project. The Springfield and Rhode Island components of the New England East–West Solution (NEEWS) series of projects, the Long-Term Lower SEMA Upgrades, and the Maine Power Reliability Program (MPRP) have received siting approval and are under construction. The Interstate Reliability Project component of NEEWS is in siting. Two new 345 kV projects have emerged as a result of the 2011 Vermont/New Hampshire assessment and the Greater Boston studies. The needs assessment currently is being updated for the last of the 16 projects—the Central Connecticut Reliability Project component of NEEWS. This assessment has been merged into the Greater Hartford–Central Connecticut (GHCC) study.

Also, the addition of the 345 kV substations in Wachusett, Ward Hill, Wakefield Junction, West Amesbury, and Plainfield (Berry Street), Massachusetts; the expansion and creation of the 345 kV substations in Scobie and Fitzwilliam, New Hampshire, respectively; the expansion of the 345 kV substations in Barbour Hill, Haddam, and Killingly, Connecticut; and the creation of the 345 kV Keene Road substation in northern Maine have improved the ability of the transmission system to meet load growth. All these and other projects will help maintain system reliability and enhance the region’s ability to support a robust, competitive wholesale power market by reliably moving power from various internal and external sources to the region’s load centers.

This section discusses the need for transmission security and the performance of the transmission system in New England. It addresses the need for transmission upgrades, accounting for known plans for resource additions and attritions, and updates the progress of the current major transmission projects in the region. Information regarding the detailed analyses associated with many of these efforts can be found in previous RSPs, various PAC presentations, and other ISO reports.

## The Need for Transmission Security

A reliable, well-designed transmission system is essential for complying with mandatory reliability standards and providing regional transmission service that provides for the secure dispatch and operation of generation and that delivers numerous products and services, as follows:

- Capacity

- Electric energy

- Operating reserves

- Load-following

- Automatic generation control

- Immediate contingency response to sudden generator or transmission outages

A secure transmission system also plays an important role in the following functions:

- Improving the reliability of and access to supply resources

- Regulating voltage and minimizing voltage fluctuations

- Stabilizing the grid after transient events

- Facilitating the efficient use of regional supply and demand resources

- Reducing the amount of reserves necessary for the secure operation of the system

- Facilitating the scheduling of equipment maintenance

- Assisting neighboring balancing authority areas, especially during major contingencies affecting their reliability, and ensuring the reliability of the interconnected system

## Transmission Planning Process

The electric power industry’s mandatory reliability standards, the ISO’s procedures and practices, and good utility practice define what constitutes adequate regional transmission system performance, the foundation for the ISO’s transmission planning responsibility. All system modifications to transmission, generation, and loads must be analyzed and designed to ensure systemwide coordination and continued system reliability in compliance with these standards.

Infrastructure throughout many parts of the system, which was planned, designed, and built many years ago, is becoming increasingly inadequate. The system contains relatively old, low-capacity 115 kV lines, some of which were converted from 69 kV design. Additionally, a number of aging 345/115 kV transformers are connected to the 115 kV system. The continued use of this aging equipment increases the risk of the system experiencing extended equipment outages that cannot be repaired or replaced quickly.

Many of the transmission system projects underway in the region are being designed to reduce the dependence on individual generating plants and improve the operation of those areas of the system currently facing some type of complication. These can include restrictions on generator dispatch, the use of special protection systems (SPSs), sensitivity to varying load levels, and facility outages resulting from unplanned contingencies and maintenance conditions. With the possibility of generator retirements, the need for transmission improvements will likely increase, as noted by the Strategic Planning Initiative.

The ISO has drafted a Transmission Planning Manual that discusses the assumptions used in transmission studies and the rationale behind the assumptions. Transmission owners and the states have provided comments on the document, which the ISO is reviewing. It expects to release the report to all stakeholders in early 2013.

### Needs Assessments and Solutions Studies

Through an open stakeholder process, the ISO develops plans for the region’s networked transmission facilities to address future system needs. Subject to the ISO’s Information Policy and the critical energy infrastructure information (CEII) requirements approved by FERC, all planning study efforts are discussed with the PAC, and opportunities are provided for comments ranging from the draft scope of work through the posting of final reports. Study base cases and contingencies, which are used to simulate the system, are posted and available to stakeholders who meet CEII requirements.

The transmission planning process begins by developing a study scope and identifying all key inputs for conducting a needs assessment. These assessments determine the adequacy of the power system, as a whole or in part, for maintaining the reliability of the system while promoting the operation of efficient wholesale electricity markets in New England. After the results of a needs assessment are made available for stakeholder input, the alternative transmission system solutions are identified and evaluated thoroughly to determine the most cost-effective proposed transmission solutions for the region. These study efforts and the proposed transmission solutions are documented in solutions studies, which also are subject to stakeholder review and input. These studies, in aggregate, provide the basis for upgrading the transmission system and updating the ISO’s 10-year Regional System Plan consistent with and in compliance with the ISO tariff and NERC, the NPCC, and ISO New England standards, criteria, and procedures.

Beginning in 2012, the ISO began including in needs assessments and resulting solutions studies the impact of future energy-efficiency programs beyond those participating in the Forward Capacity Market. Depending on the timing of the update, some studies, such as the New Hampshire/Vermont studies, have included future energy efficiency based on the values provided in the proof-of-concept for the energy-efficiency forecast (see Section 3.2). These studies will be adjusted further as necessary to account for the final 2012 energy-efficiency forecast. Other study updates, such as those for Greater Boston, are being reviewed using the final values of the energy-efficiency forecast.

### Project Timing

The ISO periodically reviews the need for and timing of projects. When stakeholders provide new information, and as system parameters change, the plans, including those described in this report, may change to ensure that they can be implemented without degrading the performance of the New England system, the NPCC region (see Section 9.2.4), or the remainder of the Eastern Interconnection. The ISO conducts sensitivity analyses to account for factors such as generation unavailability, maintenance-outage conditions, and potential retirement scenarios—all of which could advance the need for transmission improvements—as well as the development of generation and demand resources, which can delay the need for transmission improvements. The planning process identifies sufficient lead times for the construction of transmission solutions to ensure that the region meets planning and operating criteria.

## Types of Transmission Upgrades

Attachment N of the OATT, “Procedures for Regional System Plan Upgrades,” defines several categories of transmission upgrades that can be developed to address various types of defined system needs, such as reliability and market efficiency.

### Reliability Transmission Upgrades

Reliability Transmission Upgrades are necessary to ensure the continued reliability of the New England transmission system in compliance with applicable reliability standards. A Reliability Transmission Upgrade also may provide market-efficiency benefits. To identify the transmission system facilities required to maintain reliability and system performance, the ISO evaluates the following factors using reasonable assumptions for forecasted load and the availability of generation and transmission facilities (based on maintenance schedules, forced outages, or other unavailability factors):

- Known changes in available supply resources and transmission facilities, such as anticipated transmission enhancements considering Elective Transmission Upgrades and merchant transmission facilities (i.e., independently developed and funded facilities subject to the operational control of the ISO, pursuant to unit-specific operating agreements) (see below); the addition of demand-side resources or new or previously unavailable generators; or generator retirements

- Forecasted load, which accounts for growth, reductions, and redistribution throughout the grid

- Acceptable stability response

- Acceptable short-circuit performance

- Acceptable voltage levels

- Adequate thermal capability

- Acceptable system operability and responses (e.g., automatic operations, voltage changes)

### Market Efficiency Transmission Upgrades

Market Efficiency Transmission Upgrades (METUs) primarily are designed to reduce the total net production cost to supply the system load. The ISO categorizes a proposed transmission upgrade as a METU when it determines that the net present value of the net reduction in total cost to supply the system load is greater than the net present value of the carrying cost of the identified upgrade. A Reliability Transmission Upgrade may qualify for interim treatment as a Market Efficiency Transmission Upgrade if market efficiency is used to advance the schedule for the implementation of the upgrade.

In determining the net present value of power system resource costs, the ISO takes into account applicable projected economic factors, as follows:

- Energy costs

- Capacity costs

- Cost of supplying total operating reserve

- System losses

- Changes in available supply resources and transmission facilities, such as through anticipated transmission enhancements considering Elective Transmission Upgrades and merchant transmission facilities (see below); the addition of demand-side resources or new or previously unavailable generators; or generator retirements

- Load growth

- Fuel costs and availability

- Generator availability

- Release of locked-in generating resources

- Present-worth factors for each project specific to the owner of the project

- Present-worth period not to exceed 10 years

- Cost of the project

Analyses may include the use of historical information, such as information in market reports, and special studies, and they should report cumulative net present value annually over the study period.

### Generator Interconnection Upgrades and Generator Interconnection-Related Upgrades

A Generator Interconnection Upgrade is an addition or modification to the New England transmission system for interconnecting a new or existing generating unit whose energy or capacity capability is materially changing and increasing, whether or not the interconnection is for meeting the Network Capability Interconnection Standard or the Capacity Capability Interconnection Standard. Costs of Generator Interconnection-Related Upgrades typically are allocated to the generator owner in accordance with the OATT. Generator Interconnection-Related Upgrades to the New England transmission system are included in the RSP Project List for informational purposes (see Section 5.4).

### Elective Transmission Upgrades and Merchant Transmission Facilities

An Elective Transmission Upgrade (ETU) is an upgrade to the New England transmission system voluntarily funded by one or more participants that have agreed to pay all the costs of the upgrade and is not one of the following types of other upgrades:

- Generator Interconnection-Related Upgrade

- Reliability Transmission Upgrade

- Market Efficiency Transmission Upgrade

- Project proposed as an ETU but already identified as a transmission project in the RSP before its proposal as an ETU

The Elective Transmission Upgrade study process also is the mechanism available to integrate merchant transmission facilities into the regional transmission system.

## RSP Project List and Projected Transmission Project Costs

The RSP Project List is a summary of needed transmission projects for the region and includes information on project type, the primary owner, the transmission upgrades and their status, and the estimated cost of the pool transmission facility (PTF) portion of the project. The list is updated at least three times per year, although the ISO regularly discusses the justification for transmission improvements with the PAC and the Reliability Committee, which provide guidance and comment on study scopes, assumptions, and results. The RSP Project List classifies projects as they progress through the study and stakeholder planning processes as follows:

- Concept—a transmission project under consideration by its proponent as a potential solution to meet an identified need in a needs assessment or the RSP but for which little or no analysis is available to support the transmission project.

- Proposed—a regulated transmission solution that (1) has been proposed in response to a specific identified need in a needs assessment or the RSP and (2) has been evaluated or further defined and developed in a solutions study, as specified in the OATT, Attachment K, Section 4.2(b), but has not received ISO approval under Section I.3.9 of the tariff. The regulated transmission solution must include analysis sufficient to support an ISO determination, as communicated to the PAC, that it most likely would meet the identified need stated in the needs assessment or the RSP.

- Planned—a transmission upgrade the ISO has approved under Section I.3.9 of the tariff. Both a needs assessment and a solutions study have been completed for planned projects.

The ISO regularly updates the PAC on study schedules, scopes of work, assumptions, draft and final results, and project costs, with the status of all projects compiled in the RSP Project List. Projects are considered part of the Regional System Plan consistent with their status and are subject to transmission cost allocation for the region. RSP12 incorporates information from the June 2012 RSP Project List. As of June 2012, the total estimated cost of transmission upgrades proposed, planned, and under construction was approximately $6.0 billion, as shown in Table 5-1.

Table 5-1
Cost of Reliability Projects as of June 2012 Plan Update (Millions of $)

| Projects | Project Costs (millions of $)(a) |
| --- | --- |
| Major projects |  |
| Maine Power Reliability Program | 1,440 |
| Merrimack Valley/North Shore Reliability Project | 154 |
| Long-Term Lower SEMA Upgrades | 114 |
| New England East–West Solution (NEEWS) | 1,908 |
| NEEWS (Greater Springfield Reliability Project)—$747 million |  |
| NEEWS (Rhode Island Reliability Project)—$305 million |  |
| NEEWS (Central Connecticut Reliability Project)—$301 million |  |
| NEEWS (Interstate Reliability Project)—$510 million |  |
| NEEWS (other)—$45 million |  |
| Greater Rhode Island Transmission Reinforcements (including Advanced NEEWS) | 242 |
| Pittsfield/Greenfield Project | 131 |
| Greater Boston—North, South, Central, Western Suburbs | 711 |
| New Hampshire Solution—Southern, Central, Seacoast, Northern | 436 |
| Vermont Solution—Northwestern, Central, Southeastern | 260 |
| Subtotal(b) | 5,396 |
| Other projects | 5,649 |
| New projects | 0 |
| Projects whose cost estimates were previously reported as “to be determined” | 21 |
| Total(b) | 11,066 |
| Minus “concept” projects | −190 |
| Minus “in-service” projects | −4,871 |
| Aggregate estimate of active projects in the plan(b) | 6,006 |

(a) 	All costs were provided by transmission owners.

(b) 	Totals may not sum exactly because of rounding.

The participating transmission owner (PTO) Administrative Committee (AC) provides annual updates to the ISO and NEPOOL on projected regional network service (RNS) transmission rates, as shown in Table 5-2. The RNS transmission rate effective June 1, 2012, is $75/kW-year.

Table 5-2
Actual and Forecast Regional Network Service Rates, 2011 to 2016(a. b. c)

|  | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 |
| --- | --- | --- | --- | --- | --- | --- |
|  | Actual |  | Estimated |  |  |  |
| Additions in-service ($ millions) | 1,303 | 1,305 | 1,172 | 1,184 | 1,330 | 1,246 |
| Revenue requirement ($ millions) | 206 | 203 | 197 | 182 | 212 | 212 |
| RNS rate impact ($/kW-year) | 10 | 10 | 10 | 9 | 10 | 11 |
| RNS rate forecast ($/kW-year) | 64 | 75 | 85 | 94 | 104 | 115 |
| RNS rate forecast ($/kWh)(d) | 0.012 | 0.014 | 0.016 | 0.018 | 0.020 | 0.022 |

(a) 	The forecast is preliminary and for illustrative purposes only. It reflects gross costs and is based on a number of assumptions and variables, including, among others, estimated project need, design, scope, and labor and materials costs; inflation; site and permitting approvals; transmission in-service dates; estimated carrying charges; and coincident peak network loads. It does not include assumptions pertaining to savings (e.g., those associated with reduced congestion and unlocked capacity) or prior-year true-up adjustments. Therefore, such estimates and assumptions are expected to change as current data become available. Contact ISO Customer Service at (413) 540-4220 for additional information about the RNS rate forecast.

(b) 	The figures may not agree because of rounding.

(c) 	Source: RNS Rate Effective June 1, 2012,  and RNS Rates—Five-Year Forecast, PTO AC Rates Working Group presentation at the NEPOOL Reliability Committee/Transmission Committee Summer Meeting (August 13–15, 2012), http://www.iso-ne.com/committees/comm_wkgrps/trans_comm/tariff_comm/mtrls/2012/aug1314152012/a6_2012_rns_rate_presentation_revised_8_9.pdf and http://www.iso-ne.com/committees/comm_wkgrps/trans_comm/tariff_comm/mtrls/2012/aug1314152012/a6_rns_rates_forecast_2012_2016.ppt.

(d) 	The estimated RNS rate forecast assumes a 60% load factor.

## Transmission System Performance Needs Assessments and Upgrade Approvals

The New England power system provides electricity to a diverse region, ranging from rural agricultural areas to densely populated urban areas, and it integrates widely dispersed and varied types of power supply resources. The geographic distribution of peak loads in New England is approximately 20% in the northern states of Maine, New Hampshire, and Vermont and 80% in the southern states of Massachusetts, Connecticut, and Rhode Island. Although the land area in the northern states is larger than the land area in the southern states, the greater urban development in southern New England creates the relatively larger demand and corresponding transmission density.

The New England transmission system consists of mostly 115 kV, 230 kV, and 345 kV transmission lines, which in northern New England generally are longer and fewer in number than in southern New England. The New England area has nine interconnections with New York: two 345 kV ties, one 230 kV tie, one 138 kV tie, three 115 kV ties, one 69 kV tie, and one 330 MW, ±150 kV high-voltage direct-current (HVDC) tie.

Currently, New England and New Brunswick are connected through two 345 kV ties, the second of which was placed in service in December 2007. New England also has two HVDC interconnections with Québec: a 225 MW back-to-back converter at Highgate in northern Vermont and a ±450 kV HVDC line with terminal configurations allowing up to 2,000 MW to be delivered at Sandy Pond in Massachusetts.

The following sections summarize the June 2012 status of several transmission planning studies and projects and the need for upgrades.

### Northern New England

The northern New England (NNE) area encompasses the transmission system in Maine, New Hampshire, and Vermont. Studies of each of these states are being conducted to address the transmission system’s short- and long-term needs.

#### Northern New England Transmission

With the Northeast Reliability Interconnection in service, New England and New Brunswick now have two 345 kV interconnections leading into a 345 kV corridor at Orrington, Maine. The corridor spans hundreds of miles and eventually ties into Massachusetts. The transmission system throughout northern New England is limited in capacity; it is weak in places and faces numerous transmission security concerns. Underlying the limited number of 345 kV transmission facilities are a number of old, low-capacity, and long 115 kV lines. These lines serve a geographically dispersed load as well as the concentrated, more developed load centers in southern Maine, southern New Hampshire, and northwestern Vermont.

The two most significant issues facing the area have been to maintain the general performance of the long 345 kV corridor, particularly through Maine, and to maintain the reliability of supply to meet demand. The region faces thermal and voltage performance issues and stability concerns and is reliant on several SPSs that may be subject to incorrect or undesired operation. Rapid load growth has raised particular concerns in northwestern Vermont; the southern and seacoast areas of Maine and New Hampshire; various localized areas across Maine; and the tristate “Monadnock” area of southeastern Vermont, southwestern New Hampshire, and north-central Massachusetts. The system of long 115 kV lines, with weak sources and high real- and reactive-power losses, is exceeding its ability to integrate generation and efficiently and effectively serve load. Also, in many instances, the underlying systems of 34.5 kV, 46 kV, and 69 kV lines are exceeding their capabilities and are being upgraded, placing greater demands on an already stressed 115 kV system.

Over the past several years, the addition of generation in Maine and New Hampshire, in combination with the area’s limited transfer capability and limited transmission expansion, has increased the likelihood of many northern New England interfaces operating near their limits, creating restrictions on northern resources. Because these interface limits depend on generation dispatch, the operation of the system becomes more complex. Additional concerns in northern New England include limited system flexibility to accommodate maintenance outages, limited dynamic reactive-power resources, and high real- and reactive-power losses. However, load growth in the north, in combination with other system changes, is easing the stresses on some northern New England interfaces, such as the interface between Maine and New Hampshire. In fact, the power flows on some interfaces, which historically have been from north to south, at times have reversed and are moving from south to north, highlighting shifting market economics, generation dispatch patterns, and emerging system weaknesses in addition to those already identified on the interfaces. The recent operating data in this corridor shows that flows remain predominantly in the north to south direction.

Load growth also is causing reliability concerns and has led to new or worsening situations in areas with localized dependence on existing generation. Additionally, special protection system limitations in operating correctly are at times leading to requirements to operate generation out of merit to ensure adequate SPS functioning.

#### Northern New England Transmission System Studies

Study efforts are progressing in various portions of Maine, New Hampshire, and Vermont to address a number of transmission system concerns. Some of these studies have focused on defining short-term needs and developing solutions, while others have made significant progress in evaluating potential system conditions 10 years into the future.

Maine—The long-term system needs of Bangor Hydro Electric (BHE) and Central Maine Power (CMP) were identified in 2007. To improve the performance of the Bangor system, the Keene Road substation was completed and 115 kV upgrades have been placed into service. CMP has planned 115 kV expansions in western Maine to address area thermal and voltage issues. Upgrades north of Augusta and near Rumford have reduced some voltage concerns. Several 115 kV system reinforcements, including the addition of the new substation at Maguire Road in southern Maine, already have been placed into service and are helping to serve southern Maine load in the near term.

Projects planned as part of the Maine Power Reliability Program (MPRP) must meet reliability requirements and be consistent with long-term planning objectives in both the BHE and CMP service territories. These projects include the addition of significant new 345 kV and 115 kV transmission facilities and new 345 kV autotransformers at key locations.

The northern portion of the Maine transmission system continues to present challenges to reliable system planning and operations. Lengthy sections of 345 kV transmission in Maine connect the New Brunswick system to the greater New England network. Until the addition of the MPRP project (see Section 5.5.1.3), portions of this corridor consist of only one 345 kV line in parallel with weak 115 kV transmission serving relatively small amounts of load. To maintain reliable operations, this part of the system currently employs several SPSs, and a static VAR compensator (SVC) is used to dynamically support voltage. Certain contingencies have the potential to cause high voltages, low voltages, high frequencies, the loss of a large amount of generation, or system separation from New Brunswick. A number of new generation projects and elective transmission upgrades are seeking to interconnect to this part of the system. The technical complexities mentioned complicate the system’s ability to accommodate additional interconnections.

A transfer study is being conducted to identify the increase in transfer capability across the major interfaces in Maine and neighboring systems resulting from the addition of the MPRP project. The study, which is scheduled for completion in 2012, is evaluating thermal, voltage, and stability transfer limits. The overall limiting condition in setting the new transfer limits is the system’s stability response to faults in southern New England. The new transfer limits will be adopted in the appropriate planning and capacity market processes.

The preliminary transfer limits indicate that the constraints within Maine will likely continue to limit the ability of the system to deliver some existing and new capacity. Because of these continued constraining interface limits within Maine, subsequent study work will investigate the ability to further increase the north-to-south limits in Maine with the existing series capacitor at Orrington placed in service.

In addition to the Surowiec South and Orrington South interfaces, subarea export constraints will continue to be restrictive after the updated MPRP transfer limits are put in place. They include the Rumford Area, Bigelow/Upper Kennebec, and Northern Maine/Keene Road. The Strategic Transmission Analysis (see Section 6.2.7) may provide additional information on the transmission upgrades that could be needed to address these subarea export constraints as well as the Surrowiec South and Orrington South constraints.

New Hampshire—A number of studies of the New Hampshire portion of the system have been conducted. These studies have identified the need for additional 345/115 kV transformation capability and the need for additional 115 kV transmission support in various parts of the state. Existing and midterm concerns of northern and central New Hampshire have been improved by closing the Y-138 tie with Maine and the addition of a second 345/115 kV autotransformer at Deerfield.

As discussed below, a 10-year, two-phase study of the New Hampshire area has been completed as part of the Vermont/New Hampshire Transmission System Needs Assessment and Solutions Study.

Vermont— Vermont regulations require the Vermont Electric Power Company (VELCO), the owner and operator of Vermont's transmission system, to develop a 20-year Vermont Long-Range Transmission Plan every three years. As a follow-up to the 2006 Vermont Transmission System Long-Range Plan (2006 VT LRP), the 2009 Vermont Long-Range Plan and the Vermont Transmission Reliability Report Needs Analysis identified widespread thermal and voltage violations for key contingencies with critical facilities out of service.

The Vermont system was studied to assess and resolve potential reliability issues as part of the Vermont/New Hampshire Transmission System 2011 Needs Assessment. Collaborative efforts among the ISO, VELCO, National Grid, and Northeast Utilities have continued assessing the reliability of Vermont and New Hampshire’s transmission system.

New Hampshire and Vermont Combined—A combined study of the Vermont and New Hampshire area was completed in two phases. The first phase was to conduct the Vermont/New Hampshire Transmission System 2011 Needs Assessment, which identified and focused on transmission system needs for serving New Hampshire and Vermont loads while maintaining overall regional system performance. The second phase studied transmission solution alternatives and resulted in proposed regulated transmission solutions that address the violations identified within the needs assessment. In addition, a pilot study of market resource alternatives was conducted for the Vermont/New Hampshire system (see Section 4.5).

The Vermont/New Hampshire Transmission System 2011 Needs Assessment identified several areas of weak performance and demonstrated the following transmission system needs:

- The Vermont transmission system: The Vermont transmission system requires additional local reactive support to help maintain voltage within criteria. In addition, following the outage of critical facilities that serve the area, the remaining 115 kV lines serving the state become loaded above emergency limits. This indicates the need for locating additional resources within that area or adding transmission capacity to maintain reliable operations following these contingencies.

- Multiple outages: The combination of key line contingencies causes some thermal overloads and many low-voltage violations on the underlying 115 kV system.

- Concord–Manchester–Nashua: This area, stretching roughly from the Webster substation in the north to the Power Street substation in the south, shows many voltage and thermal violations for a wide range of first and second contingencies. These violations are more significant when certain generation connected to the system is unavailable.

- Central New Hampshire: The portion of New Hampshire’s transmission system near the Beebe River substation shows many post-contingency voltage violations, which in turn cause some thermal overloads on 115 kV lines.

- The New Hampshire seacoast: The New Hampshire seacoast area is in need of additional resources or transmission capability to serve the 115 kV network under both N-1 and N-1-1 conditions.

- Western New Hampshire: The New Hampshire western area shows many post-contingency voltage violations and thermal overloads on 115 kV lines under both N-1 and N-1-1 conditions.

- Other areas of the New Hampshire system: Other regions of the system show violations, illustrating a dependence on local generation and sensitivity to area load growth. As solutions are developed to meet the needs identified for the larger areas, the needs of these areas may be addressed; however, the smaller areas should continue to be monitored throughout the planning process to ensure their compliance with planning criteria.

The Vermont/New Hampshire Transmission System 2011 Needs Assessment identified the critical load level at which the voltage violations and thermal overloads would occur. Most of the voltage and thermal violations identified were found at or below existing peak load levels under various system conditions. The needs assessment, coupled with the critical load level analysis, indicates the need to examine substantial transmission system upgrades to improve system performance.

The study reflected several sensitivities to future assumptions within New Hampshire and Vermont, such as changes to the status of Vermont Yankee (VY), which may have an impact on the performance of both the New Hampshire and Vermont transmission systems. Additionally, NYISO has informed ISO New England and VELCO that it no longer expects the normal flow on the PV-20 line into Vermont to be between 70 MW and 140 MW because of reliability concerns in New York.

The New Hampshire/Vermont Solutions Study assessed alternatives for upgrading the New Hampshire and Vermont 345 kV and 115 kV transmission system. Transmission upgrades for ensuring the reliability of the transmission system in New Hampshire and Vermont were identified to address the reliability needs found in the needs assessment.

A follow-up analysis to the New Hampshire/Vermont Needs Assessments and Solutions Study included a reassessment of the preferred solutions developed in the solutions study. This reassessment incorporated an updated set of assumptions based on the 2011 “proof-of concept” long-term energy-efficiency forecast (see Section 3.2), as well as for load, generation and demand resources, transmission system topology, and the use of existing transmission system devices. A number of transmission system upgrades were identified, which are no longer required within the 10-year planning horizon and could be deferred from the preferred solution identified in the New Hampshire/Vermont Solutions Study. These deferred transmission system upgrades are located in almost every portion of the New Hampshire and Vermont transmission systems. Another study of the New Hampshire/Vermont area was initiated in 2012 to capture the final long-term energy-efficiency forecast, as well as the latest Forward Capacity Auction results and the latest load forecast for 2022.

The final set of transmission system upgrades, identified for each of the subareas in New England, is as follows:

- Northwestern Vermont—The following solution was developed to mitigate low voltages following certain contingencies in New York:

- Special protection system to cross-trip PV-20 line

Central Vermont/Connecticut River—The central Vermont area consists of the 345 kV and 115 kV corridors between Coolidge and West Rutland and includes the transmission lines connecting to the substations on either end of the corridor. The Connecticut River corridor consists of a series of substations along the Vermont–New Hampshire border, operated by both VELCO and National Grid. Four transmission lines feed this area from the east, west, north, and south. The following solutions were developed to mitigate thermal overloads and voltage violations:

- New Coolidge–West Rutland 345 kV line

- New Coolidge–Ascutney 115 kV line

Southwestern Vermont—The following solutions were developed to eliminate low voltages at Bennington:

- Adams 115 kV substation reconfiguration and the addition of two circuit breakers

- Two 12.5 MVAR capacitor banks at Bennington 115 kV substation

Southeastern Vermont and Western New Hampshire—The southeastern Vermont and western New Hampshire area focuses on the Vernon area in southern Vermont and the Fitzwilliam/Monadnock area in western New Hampshire. The Fitzwilliam/Monadnock area is centered on the Monadnock 115 kV bus. This area is bounded by the L163 Jackman–Keene, the I135N Bellows Falls–Monadnock tap, the J136N Bellows Falls–Flagg Pond, and the N186 Vernon Road tap–Chestnut Hill 115 kV lines, as well as the Fitzwilliam 345/115 kV autotransformer. The following solutions were developed to mitigate thermal overloads and voltage violations:

- New Fitzwilliam–Monadnock 115 kV line

- Two 25 MVAR capacitor banks at Amherst 345 kV substation

- Two 13.3 MVAR capacitor banks at Weare 115 kV substation

- A152 Chestnut Hill–Westport–Swanzey 115 kV line rebuild

- N186-2 Vernon Road tap–Chestnut Hill 115 kV line rebuild

- Terminal upgrades at Flagg Pond 115 kV substation

- 381–Northfield–New Hampshire/Vermont border 345 kV line upgrade

Northern New Hampshire and Northern Vermont—The northern Vermont area refers to the area associated with the 115 kV path along northern Vermont between the St. Johnsbury and Highgate 115 kV stations. The northern New Hampshire area represents the northern 115 kV loop including Whitefield, Lost Nation, and Berlin, and the Comerford/Moore/Littleton area. The following solutions were developed to mitigate thermal overloads and voltage violations:

- Second 230/115 kV autotransformer at Littleton

- A 230 kV C203 Comerford–Moore line tap into Littleton substation

Central New Hampshire—The central New Hampshire area stretches roughly from the Webster substation in the south to the Littleton substation in the north. The following solutions were developed to mitigate thermal overloads and voltage violations:

- Four 26 MVAR capacitor banks at Webster 115 kV substation

- Two 25 MVAR dynamic reactive devices at Saco Valley 115 kV substation

- Load transfer scheme

Southern New Hampshire—The southern New Hampshire area stretches roughly from the Webster substation in the north to the Power Street substation in the south. This area is fed from local generation and from the Deerfield and Scobie 345/115 kV stations from the east, from the Webster 115 kV station from the north, the L163 Keene–Jackman 115 kV line from the west, and the Y151 Power St–Tewksbury 115 kV line from the south. This area serves the Nashua, Manchester, and Concord area loads and contains a significant portion of the total New Hampshire load. The following solutions were developed to mitigate multiple thermal overloads and voltage violations:

- 345/115 kV autotransformer at Eagle

- 326-National Grid NH/MA border–Sandy Pond 345 kV line upgrade

- 326-NU Scobie Pond–NH/MA border 345 kV line upgrade

- Scobie series circuit breaker with breaker 802

- New Scobie–Huse Road 115 kV line

- Four 25 MVAR capacitor banks at Eagle 115 kV substation

- G146 Garvins–Deerfield 115 kV line upgrade

- P145 Oak Hill–Merrimack 115 kV line upgrade

- D118 Deerfield–Pine Hill 115 kV line rebuild

- H137 Merrimack–Garvins 115 kV line rebuild

- J114-2 Greggs–Rimmon 115 kV line upgrade

- Loop V182 line into Oak Hill substation

- Merrimack series circuit breaker with breakers BT12 and BT23

- Merrimack capacitor bank relocation to bus 1 and bus 3

- K165 Eagle–Bridge St.–Power St. 115 kV line upgrade

New Hampshire Seacoast—The New Hampshire Seacoast area is the area along the New Hampshire coastline, which is bordered by the Deerfield and Scobie 115 kV stations to the west and the Three Rivers 115 kV station to the north. There are no 115 kV connections to the south. This system serves load in the Portsmouth, Dover, and Rochester areas. The following solutions were developed to mitigate multiple thermal overloads and voltage violations:

- New Madbury–Portsmouth 115 kV line

- New Scobie–Chester 115 kV line

- Chester substation work associated with new 115 kV line

- Six 13.3 MVAR capacitor banks at Schiller 115 kV substation and series circuit breaker with breaker BT10

- H141 Chester–Great Bay 115 kV line upgrade

- R193 Scobie–Kingston tap 115 kV line upgrade

- Three Rivers series circuit breaker with breaker R1690

#### Northern New England Transmission Projects

The ISO has identified projects that address transmission system performance issues, either individually or in combination. Some of the projects, as described in the previous sections, address subregional reliability issues and also have the ancillary benefit of improving the performance of major transmission corridors and thus the overall performance of the system. The projects are as follows:

- Vermont 345 kV Reactor Additions—This project is needed to provide support for the long-term loss of equipment that provides reactive support; to compensate for the absence of voltage control from key generating units, possibly due to maintenance outages; to mitigate high-voltage violations; and to address operational concerns during light-load conditions. The projected in-service date is late October 2012. Elements of this project are as follows:

- New Haven substation—replace the existing fixed 60 MVAR reactor with a 34 to 60 MVAR variable reactor

- Coolidge substation—install two 34 to 60 MVAR variable reactors

- Vernon 345 kV substation—install the 60 MVAR fixed reactor relocated from the New Haven substation

- Bennington, Ascutney, and Georgia 115 kV Substation Rebuild Projects—These substation rebuild projects in Vermont are needed for resolving contingencies that could result in area voltage collapse. The existing straight-bus substations will be rebuilt to a ring-bus configuration and designed to accommodate future expansion to a breaker-and-a-half configuration. The projected in-service date for the Ascutney and Georgia rebuilds is December 2012. The projected in-service date for the Bennington rebuild is June 2013.

- Central Vermont Voltage Upgrade Project—This project is needed to improve voltage performance in the central and northwest Vermont area. It consists of closing switch #230 at the Essex substation and installing two 115 kV, 25 MVAR shunt capacitor banks at the West Rutland substation. The Essex switch was closed in January 2011. The entire project entered service in late 2011.

- Highgate Converter Station Refurbishment—Highgate provides both capacity and energy to the New England region. The Highgate converter was constructed in 1985, and it has begun to fail more frequently. To ensure that the converter continues to operate reliably, the control and cooling systems need to be replaced. Finding parts and industry expertise to perform repairs on this aging equipment has become difficult. Plus, repairing aging technology is more time consuming and more difficult than repairing newer equipment, which may eventually lead to nonrepairable failures of the outdated control systems. Because of its age, the cooling system requires increased maintenance, which exposes the converter to potential forced and extended outages. Failure of a cooling system would reduce or shut down power transfers through the converter. Other control components and devices also will need to be replaced. The Highgate converter is expected to provide the ability to import power at its full 225 MW capacity when the upgrade is completed, which is projected for March 2013.

- Deerfield Substation Expansion Project—This project adds a second 345/115 kV autotransformer at the Deerfield substation in New Hampshire, which entered service in November 2011. Three new 345 kV circuit breakers will be added to eliminate problematic contingencies. Five 115 kV circuit breakers will be replaced, and one new 115 kV circuit breaker will be added. To mitigate area overloads, the Madbury–Deerfield (L175) 115 kV line will be rebuilt, and the Dover–Madbury (M183) 115 kV line and Deerfield–Rochester (C129) 115 kV line will be reconductored. In addition, the Rochester substation will be expanded to accommodate a new radial line to a new North Rochester substation by 2015.

- Section 241 Heywood–Wyman Hydro Project—This project is part of what has been known as the Heywood Road (formerly Benton) Project. These transmission upgrades are required to mitigate low voltages and voltage collapse in the Skowhegan–Waterville–Winslow area in Maine that could result from the contingent loss of critical lines in the area. A new switchyard connecting the Winslow−Wyman Hydro, Coopers Mills–Rice Rips, and Heywood–Wyman Hydro lines (83, 67A, and 241, respectively) in a six-breaker ring-bus configuration will provide an additional path from Coopers Mills (formerly Maxcys) substation to the Waterville–Winslow area. This new switchyard configuration will improve system voltage. Section 241 line was placed in service in June 2012.

- Section 63 Area Voltage Support—Currently, all loads served by the Wyman–Livermore Falls 115 kV line (section 63) in western Maine are exposed to contingency outages. Additionally, area voltages fall to unacceptable levels because of contingencies. To mitigate violations observed, a new switching station at the 63B tap, referred to as the Starks switching station, will be constructed, and two 18 MVAR capacitor banks will be added to that station. These upgrades have a proposed in-service date of September 2012.

- Maine Power Reliability Program—The MPRP provides a 10-year look at the Maine transmission system and has identified the following inadequacies:

- Insufficient 345 kV transmission—Maine currently has two 345 kV transmission paths from southern to central Maine and two 345 kV ties from northern Maine to New Brunswick. In the central part of the system, Maine has a single 345 kV path.

- Insufficient 345/115 kV transformation capacity—The reliability of Maine’s 115 kV system depends on the capacity and availability of autotransformers at five locations. Overloads of the autotransformers under normal and contingency conditions illustrate insufficient transformation capacity.

- Insufficient 345 kV transmission support for Portland and southern Maine—The largest load pocket in Maine is subject to thermal and voltage reliability issues.

- Insufficient transmission infrastructure in western, central, and southern Maine regions—Each of these regions in Maine represents a major load pocket that depends on local generation to meet reliability standards.

- Insufficient transmission infrastructure in midcoast and “downeast” Maine regions—These regions in Maine (i.e., Bucksport−Eastport) represent load pockets that have no local generation and fully depend on the transmission system.

- MPRP Transmission Alternatives Study—This study identified transmission upgrades to serve load pockets and ensure that the system will meet national and regional transmission reliability criteria. These projects will provide the ancillary benefit of facilitating the maintenance of the system in Maine. The selected alternative, referred to in the transmission alternatives study as “N5S1,” consists of significant additions of new 345 kV lines, 115 kV lines, 115 kV capacitors, 345/115 kV autotransformers, and line rebuilds and the separation of circuits sharing common towers. The new 345 kV lines in the north will create a 345 kV path from Orrington to Surowiec, while the new 345 kV lines in the south will create a third parallel path from Surowiec to Eliot in southern Maine. While these new paths are expected to increase transfer capability out of Maine, they also will increase the ability to move power into Maine from New Hampshire and improve the ability of the transmission system within Maine to move power into the load pockets as necessary.

- On July 1, 2008, CMP submitted a siting application for these MPRP projects to the Maine Public Utilities Commission (MPUC). In June 2010, the MPUC issued an order approving most of the MPRP. The 345 kV portions of the MPRP not approved were the installation of the autotransformer at Raven Farm, the reconfiguration of Maine Yankee substation, and the elimination of the double-circuit tower (DCT) configuration, which exists on the Maine Yankee−Buxton and Coopers Mill−Maine Yankee (375/392) circuits. On July 26, 2010, PSNH and CMP filed a supplemental filing that provides additional information on the new Eliot switching station near Three Rivers per the June 2010 MPUC order. In addition, the permitting process for Section 3020 (Surowiec to Raven Farm) still is open for establishing siting details. The Eliot switching station has completed the siting process and has obtained its Certificate of Public Convenience and Necessity (CPCN) from the MPUC. Because of engineering design changes and the Maine Public Utilities Commission Order issued in June 2010, the “N5S1” alternative has been modified. The expected in-service date for the entire MPRP project is early 2015. The major 345 kV components of the current plan are as follows:

- New 345 kV line construction

    - Orrington–Albion Road

    - Albion Road–Coopers Mills

    - Coopers Mills–Larrabee Road

    - Larrabee Road–Surowiec

    - Surowiec–Raven Farm

    - South Gorham–Maguire Road

    - Maguire Road–Eliot (formally called Three Rivers)

- New 345/115 kV autotransformers

    - Albion Road

    - Cooper Mills (replace existing Maxcys T3)

    - Larrabee Road

    - Maguire Road

    - South Gorham

- Separation of double-circuit towers

- 345 kV Kennebec River Crossing by the Maine Yankee−Buxton and Maine Yankee−Surowiec circuits (375/377)

  - Rerating of 345 kV transmission lines

    - Section 378 (345 kV Maine Yankee–Mason)

- Chester Area Project—This project adds a 345/115 kV transformer at Keene Road in Chester, Maine, to provide necessary backup to the area load and allow for rebuilding the Keene–Enfield–Graham 115 kV section (line 64). Currently, section 64 needs to be rebuilt, and the area’s subtransmission system is incapable of supporting area loads while construction is underway. In addition, the section 64 rebuild and the installation of the Keene Road autotransformer provides area support following the loss of both autotransformers at Orrington. The autotransformer is in service, and the section 64 rebuild was placed in service in December 2011.

### Southern New England

The southern New England area encompasses the Massachusetts, Rhode Island, and Connecticut transmission system. Studies of these states are being conducted to address a wide range of transmission system concerns, both short and long term.

#### Southern New England Transmission

The 345 kV facilities that traverse southern New England comprise the primary infrastructure integrating southern New England, northern New England, and the Maritimes Balancing Authority Area with the rest of the Eastern Interconnection. This network serves the majority of New England demand, integrating a substantial portion of the region’s supply, demand, and import resources.

Although recent improvements have been made, the southern New England system continues to face thermal, low-voltage, high-voltage, and short-circuit concerns under some system conditions. The most significant concerns involve maintaining the reliability of supply to serve load and developing the transmission infrastructure to integrate generation throughout this area. In many areas, an aging low-capacity 115 kV system has been overtaxed and no longer is able to serve load and support generation reliably. Upgrades to the power system are being planned and developed to ensure the system can meet its current level of demand and prepare for future load growth (see Section 3).

#### Southern New England Transmission System Studies

Study efforts in southern New England have been progressing on a wide range of system concerns. As previously stated, initial efforts focused on load areas with the most significant risks to reliability and threats to the system, particularly Boston and southwest Connecticut. With upgrades in those areas under construction, plans were developed to address the reliability of other parts of the system, particularly Connecticut; the Springfield, Massachusetts, area; central and western Massachusetts; Rhode Island; and southeastern Massachusetts, including Cape Cod.

The need originally identified for a number of the upgrades associated with this “second tier” of studies has now been reconfirmed. This includes three of the four NEEWS components: the Rhode Island Reliability Project (RIRP), the Greater Springfield Reliability Project (GSRP), and the Interstate Reliability Project (Interstate). The Interstate reassessment effort also addressed the much broader requirements of the overall New England east–west and west–east transmission systems.

Preferred solutions were developed for the Boston area and the Pittsfield area of western Massachusetts.

A Greater Hartford–Central Connecticut study is in progress, which is the needs reassessment of the Central Connecticut Reliability Project (CCRP) component of NEEWS, the Hartford and Middletown studies, and the northwest Connecticut and Barbour Hill areas. In combination, this study and the Southwest Connecticut study cover the majority of load within the state. The needs assessment includes the impact of the energy-efficiency forecast for years beyond those covered by the Forward Capacity Auction commitment periods (see Section 3.2).

A needs assessment currently is being conducted for the Southeast Massachusetts/Rhode Island (SEMA/RI) area, referred to as Eastern REMVEC. Its major goal is to determine any long-term system needs required to integrally serve the broad SEMA, NEMA, and Rhode Island areas, and to ensure consistency and cohesiveness of the planning and design of these areas of the system. This study will assume as its starting point that the Long-Term Lower SEMA, Interstate, RIRP, and Greater Boston plans are all in service (see more below).

Southern New England Region—The reassessments of the needs for the first two components of NEEWS that entered the siting process—the Rhode Island Reliability Project and the Greater Springfield Reliability Project—were completed, and the projects are under construction. Conversely, as a result of new resources’ clearing in FCA #1 through FCA #4 (see Section 4.1.3) within Connecticut and to the west of the New England East–West interface and the updated load forecast, the need for the Interstate and the CCRP components required a significant amount of new analysis.

The updated needs assessment for the Interstate component of NEEWS was published in April 2011. The results of the reassessment show a substantial need for an integrated regional transmission solution to resolve system performance issues in eastern New England, western New England, and Greater Rhode Island (GRI). Addressing the transmission constraints along the Card Street–West Medway corridor (CT–RI–MA) will resolve both the aforementioned load-serving issues. This also would allow for the use of the approximately 2,000 MW of generation along this corridor in the Greater Rhode Island area to reliably serve load in both western and eastern New England over the long-term planning horizon. See Figure 5-1.

Figure 5-1: Map of constraints in southern New England.

The original need for the Interstate component of NEEWS primarily was based on a deficiency in the ability to move power from eastern New England to serve load in western New England and Connecticut. While this need still exists to some extent, the new analysis shows the increased need to move power from western New England to serve load in eastern New England as well.

The original analysis showed the need for a third 345 kV line into West Farnum to reliably serve load in Rhode Island. This need also exists in the updated needs assessment. The subsequent solutions study reviewed five different alternatives to resolve the remaining needs, and the preferred alternative was a modified version of the original Interstate project. The solutions study was published in February 2012.

The modifications reflected the reduced need to move power from eastern New England to western New England and the increased need to move power from west to east. The solutions studies show that the original interstate project is effective at resolving the majority of the overload issues in Rhode Island, western New England, Connecticut, and eastern New England. However, it did not resolve all criteria violations for serving eastern New England load. The necessary additional modifications are as follows:

- Upgrade the 345 kV line from ANP Blackstone, MA–NEA Bellingham, MA–West Medway, MA (336 line)

- Reconductor the 345 kV line from Sherman Road, RI, to West Farnum, RI (328 line)

- Eliminate the sag limit on the 115 kV line from Montville, CT, to Buddington, CT (1410 line)

- Upgrade the terminal equipment at Sherman Road (345 kV), West Medway (345 kV), and West Farnum (345 kV) substations

- Rebuild of the Sherman Road, RI (345 kV) switching station

As a consequence of the reassessment, the following upgrades included in the original Interstate Reliability Project are no longer needed:

- Upgrading the terminal equipment necessary to increase the ratings on the 345 kV line from ANP Blackstone, MA, to Sherman Road, RI (3361 line)

- Reconductoring a section of the 345 kV line from Sherman Road, RI, to Killingly, CT (347 line)

- Adding 480 MVARs of capacitors at the Montville 345 kV substation

- Adding a 345 kV circuit breaker at the Killingly substation

Another project originally part of the Interstate component of NEEWS, the looping of the Millstone–Manchester 345 kV line into the Card Street substation, is not needed as part of the Interstate Reliability Project. This project and the CCRP are being reassessed as part of the Greater Hartford–Central Connecticut study.

Because FCA #4 was the most recent auction at the initiation of the needs assessment, the results documented in the report do not incorporate changes as a result of FCA #5. However, a comparison of the results of the critical load level analysis performed for eastern New England, western New England, and Connecticut with the additional resources that cleared FCA #5 showed that the additional resources would not alter the need for the project and the preferred alternative.

The updated needs assessment conducted for RIRP and GSRP had indicated that the two projects are needed in 2013 and 2014, the respective in-service dates for these projects. Because the rate of energy-efficiency growth in New England does not exceed the rate of load growth, the projects still are needed, even considering the energy-efficiency forecast.

However, since the need for the Interstate Reliability Project was based on the transfer of power into eastern New England, western New England, Connecticut, and Rhode Island, the energy-efficiency forecast and the new load forecast, which when combined result in lower loads in these areas, could have had an impact on the need and the solution. An Interstate Needs Assessment update based on these changes and necessary updates in resources resulting from the FCM through FCA #6 has been completed. The results of this update have shown system needs similar to those found in the previous assessment and that all parts of the preferred solution are needed.

Massachusetts—The solutions study has been completed for the Berkshire County/Pittsfield area, and the final report has been posted.

- Greater Boston area: A long-term reliability needs assessment for 2013 and 2018 has been completed for the Greater Boston area, and solutions have been developed to address the criteria violations that resulted. The solution assessment focused on developing solutions for three study subareas: northern (New Hampshire border to Boston including the suburbs north of Boston), central (downtown Boston 115 kV system and the suburbs west of Boston), and southern (suburbs south of Boston). The solutions for the northern, southern, and central areas have been identified. In addition, these final transmission solutions account for the retirement of the Salem Harbor units, and the necessary 115 kV line reconductoring projects in the North Shore area have been advanced so that they will be in service before the Salem Harbor units retire.

- The preferred transmission solution for the northern area includes the following elements (all in Massachusetts except where indicated):

- New 345 kV circuit from Scobie, NH, to Tewksbury

- New 345 kV circuit from Tewksbury to Woburn

- New 345 kV circuit from Ward Hill to Wakefield Junction

- New 345 kV cable from Woburn to North Cambridge

- New 345/115 kV autotransformer at Woburn

- Line reconductorings on the 115 kV network in the North Shore area, which are being advanced to ensure that reliability will be maintained when the Salem units are retired by June 1, 2014 (see Section 5.8):

- Y-151: Tewksbury Junction–West Metheun

- B-154N and C-155N: King Street–South Danvers

- S-145 and T-146: Tewksbury–North Reading

- Line reconductorings on the 115 kV network in the North Shore Area:

- Y-151: Tewksbury–Tewksbury Junction

- S-145 and T-146: North Reading–Wakefield Junction

- Line reconductoring/upgrades on the 345 kV network in the North Area:

- 337: Sandy Pond–Tewksbury

- 394: Terminal upgrades at the Seabrook 345 kV station

- Line reconductorings in the Wakefield–Everett area:

- F158N and F158S lines: Wakefield–Everett

- 128-518/P168: Chelsea–Revere

- Reconductoring the 115 kV lines M 139 and N 140 from Tewksbury to Pinehurst

- New 36.7 MVAR capacitor bank at Chelsea

- Opening the Y-151 Line at Power St., NH, and retiring the Y-151 SPS

The final transmission solution for the southern area includes the following (all in Massachusetts):

- A new 115 kV line from Holbrook to West Walpole

- Reconductoring of the sections of the 115 kV line from Beaver Pond to Depot Street
(C-129 N/201-502) and the line from Depot Street to Medway (D-130/201-501)

The preferred transmission solution for the central area includes the following upgrades (all in Massachusetts):

- New 115 kV lines, as follows:

  - From Sudbury to Hudson

  - From Woburn to Hartwell

  - From Needham to Baker St.

  - From Mystic to Chelsea

  - From Mystic to Woburn

- A new 230/115 kV autotransformer at Sudbury

- A second Mystic 345/115 kV autotransformer at Mystic

- A new 36.7 MVAR capacitor at Hartwell

- Reconfiguration of the Waltham 115 kV substation

- Separation of the X-24/E-157W double-circuit tower instances

- Separation of the F-158N/Q-169 DCT instance

- Separation of the O-167/P-168 DCT instance

- Terminal upgrades at the West Medway substation to increase the 282-602 line capability

- K Street 115 kV breaker additions

- Replacement of the existing Woburn 345/115 kV autotransformer

- Line reconductorings on the 115 kV and 69 kV network in the central area

320-507/508: Lexington–Waltham

211-508: Woburn–Burlington

533-508: Lexington–Harwell

E-157W: East Main St.–Millbury

128-518: Chelsea–Revere

W23: Fitch Rd.–Woodside

W23W: Northboro–Woodside

Berkshire County/Pittsfield area: The completed solutions study for this area describes the area’s final transmission solution, which consists of the following upgrades:

- Expand and reconfigure Northfield Mountain 345 kV substation, and install a 345/115 kV autotransformer

- Build a three-breaker ring-bus switching station in Erving adjacent to the A127/B128 right-of-way

- Build a new 1.2 mile 115 kV single-circuit line connecting the new Northfield autotransformer to the new Erving switching station

- Rebuild the 115 kV 1361 line (Montague–Cumberland)

- Loop the 115 kV A127 (Harriman–Millbury 115 kV) line into the new Erving switching station, and reconductor the A127 line from Erving to the Cabot tap (on the way to Harriman substation)

- Disconnect Montague from the 115 kV B128 line at Cabot Junction, and reconnect to the A127 line (Harriman–Millbury)

- Reconductor the 115 kV 1371 line (Woodland–Pleasant)

- Remove the sag limitation on the 115 kV 1421 and 1512 lines (Pleasant–Blandford–Granville Junction)

- Rebuild the 115 kV A127/Y177 double-circuit line from Montague to Cabot Junction on single-circuit structures

- Reconnect the Y177 line into the 3T/4T position at Montague substation

- Install 115 kV capacitors at Podick, Amherst, and Cumberland substations

- Install a bus tie breaker between buses 1 and 2 and replace the E131 115 kV breaker at Harriman substation

- Replace five air-break disconnect switches on the A127E line between Erving and Barre

Massachusetts/Rhode Island—The Southeast Massachusetts/Rhode Island study (the Eastern REMVEC study) is in its early stages. The study will determine whether any additional needs exist that require further solutions to reliably serve the broad southeast Massachusetts, northeast Massachusetts, and Rhode Island load areas after the preferred solutions identified by the Greater Boston, Interstate, RIRP, and Lower SEMA analyses are placed in service. Past studies have indicated a need to further integrate the Brayton Point plant, perhaps via a new Brayton Point–Bridgewater 345 kV line, and to add transmission capacity to remove limits on moving generation into and around the West Medway substation. This study also will identify solutions to the high fault-duty availabilities at the West Medway station.

Connecticut—A long-term reliability needs assessment for 2018 has been completed for the Southwest Connecticut area, and solutions are being developed to address the criteria violations. The analysis of the solutions focused on developing solutions for six study subareas: Naugatuck Valley and the Frost Bridge–Devon Corridor, Housatonic Valley, Bridgeport, New Haven, Southington, and Glenbrook–South End. The Glenbrook–South End cable and the Mill River–Quinnipiac 8300 line reconfiguration included in the New Haven area solution alternatives (see Section 5.5.2.3, Southwest Connecticut Advanced Solutions) were developed to address independent subarea needs and were advanced. Other solution alternatives were developed in conjunction to address interdependent subarea needs.

The solutions alternatives for addressing the needs in the Naugatuck Valley and Frost Bridge–Devon Corridor subareas include a combination of the following components:

Separation of DCT configurations

Reconductoring of 115 kV transmission lines

Installation of capacitor banks

Reconfiguration of 115 kV substations

Addition of a 115 kV circuit series breaker

Paralleling of 115 kV transmission lines

The solution alternatives for addressing the needs in the Housatonic Valley subarea include a combination of the following components:

Addition of a 115 kV transmission line

Reconfiguration of 115 kV transmission lines

Relocation of existing capacitor banks

Installation of capacitor banks

Installation of one synchronous condenser

The preferred solution for addressing the needs in the Bridgeport area includes the following components:

- Reconductoring and rebuilding of the 115 kV transmission lines between Baird and Congress substations

- An upgrade of the 115 kV bus at Baird

- Installation of 345 kV series circuit breaker at East Devon

- Reconductoring and rebuilding of the 115 kV transmission lines between Devon Tie switching station and Barnum substation

- Reconductoring and rebuilding of 115 kV transmission lines between Baird and Barnum substations

- Installation of two 30 MVAR capacitor banks at the Hawthorne 115 kV substation

The alternatives for addressing the remaining needs in the Bridgeport area, still under evaluation, include the following:

- Recondutoring of two 115 kV lines from Pequonnock to Trumbull substations

- Installation of a series reactor in the 115 kV lines from Pequonnock to Trumbull substations

- Paralleling of two 115 kV lines from Pequonnock to Trumbull substations

These alternatives are being studied in conjunction with the solution alternatives being developed to address the needs in the Naugatuck Valley and Frost Bridge–Devon corridor.

The preferred solution for addressing the needs in the New Haven subarea includes the following components:

- Removal of the 115 kV phase-angle regulator at Sackett substation

- Reconductoring of the 115 kV lines between Cook Hill Junction and Southington and also between Glen Lake Junction and Mix Avenue substation

- Terminal uprates and control room expansion at Mix Avenue substation

- Installation of 42 MVAR capacitor banks at Mix Avenue and Grand Avenue substations

- Relay upgrades at June and North Haven 115 kV substations

- Replacement of a circuit switcher at Wallingford 115 kV substation

- Replacement of the capacitor bank at Sackett 115 kV substation

- Installation of a series reactor at Mix Avenue between Mix Avenue substation and Glen Lake Junction

- Recondutoring of the 115 kV lines between Wallingford and Walrec and Walrec to North Haven substations

- Reconductoring of the 115 kV lines between Devon Tie switching station and Milvon substation

The alternatives for addressing the remaining needs in the New Haven area, still under evaluation, include the following:

- Reliance on operator actions

- Elimination of line reclosing

- An upgrade or installation of a new 345 kV auto transformer

The comprehensive solution alternatives for addressing the needs in the Naugatuck Valley, Frost Bridge–Devon corridor and the Housatonic Valley subareas include a combination of the following components:

- Addition of 115 kV transmission lines

- Reconfiguration of 115 kV transmission lines

- Reconductoring of 115 kV transmission lines

- Reconfiguration of 115 kV substations

- Installation of capacitor banks

In parallel with the SWCT Solutions Study, the fault-duty interrupt at the Pequonnock 115 kV station was tested. The leading alternative for meeting transient stability criteria was determined to be delaying the circuit-breaker fault clearing time to reduce the interrupt duty. The leading alternative includes the complete replacement of the transmission control house and relays to incorporate the additional time delay in the tripping logic to achieve the delayed clearing.

Two other study efforts in Connecticut, the evaluation of the Hartford and Middletown areas, have now been combined with the Greater Hartford–Central Connecticut study. The Greater Hartford transmission system can experience flow-through issues when its 115 kV circuits are called on, under contingency conditions, to carry the power normally supplied via the 345 kV system. Additionally, load-supply issues exist under certain dispatch and transfer conditions. Both voltage and thermal issues have been identified in the Middletown area under future conditions when local generation is unavailable and when the Haddam 345/115 kV autotransformer is out of service.

Both these analyses have now been combined with the reassessment of the CCRP component of NEEWS, along with the Barbour Hill and northwest Connecticut area studies, to become the GHCC study. This needs assessment currently is being conducted for this study and will include the impact of the energy-efficiency forecast (see Section 3.2).

Finally, the eastern Connecticut area study is in its early stages. The eastern Connecticut area is defined from the east by the Connecticut and Rhode Island border, from the south by Long Island Sound, from the west by the eastern boundary of the western Connecticut transfer, and from the north by the border between Connecticut and Massachusetts. The study will evaluate the unavailability of the AES Thames generating unit among other issues.

#### Southern New England Transmission System Projects

A number of transmission projects in various stages are underway in southern New England. The system performance in southern New England is complicated by many factors, such as load levels, system transfers, and unit commitment. The projects identified for this area must function reliably under a wide variety of conditions, and their development must support the operation of the overall system.

NEEWS—Siting has been approved for two of the four components of the NEEWS project, and the projects are under construction. The Rhode Island Reliability Project addresses the need for additional 345/115 kV transformation and contingency coverage in the Rhode Island area, and the Greater Springfield Reliability Project addresses various thermal overloads under forecasted normal conditions and significant thermal overloads and voltage problems under numerous contingencies.

The Rhode Island component is estimated to be completed from late 2011 to mid-2013 and consists of, among others, the following upgrades:

- A second West Farnum–Kent County 345 kV line

- A third Kent County 345/115 kV autotransformer, placed into service in June 2011. (The second Kent County 345/115 kV transformer was placed into service in January 2011 as a part of the advanced NEEWS reinforcements for Greater Rhode Island.)

The Springfield component is estimated to be completed from late 2011 to December 2013 and consists of the following upgrades:

- Construction of a new Ludlow–Agawam–North Bloomfield 345 kV line

- Reconfiguration of the Barbour Hill–Manchester–North Bloomfield three-terminal 345 kV line into two separate two-terminal lines: Barbour Hill–Manchester and North Bloomfield–Manchester

- Reconfiguration and expansion of the Ludlow 345 kV substation

- Replacement of two existing 345 kV/115 kV autotransformers at Ludlow

- Construction of a new 345 kV switchyard and the installation of two 345/115 kV autotransformers at Agawam

- Construction of a new 345 kV switchyard at North Bloomfield and the addition of a second 345 kV autotransformer

- Construction of a new 115 kV switching station at Cadwell. The new 115 kV switching station at Cadwell was placed into service in December 2011.

- A combination of rebuilding, reconfiguring, and reconductoring numerous 115 kV circuits

Webster–Harriman 115 kV Refurbishment (A127/B128)—A rebuild similar to that of the E205 line has begun for the A127 and B128 115 kV lines that run westerly from the proximity of the Webster Street substation in Massachusetts to the Harriman substation in Vermont. This project currently is scheduled to be completed in 2014.

Central/Western Massachusetts Upgrades—Past studies developed a 10-year plan for central Massachusetts and portions of western Massachusetts. This plan calls for adding a second 230/115 kV autotransformer and replacing four 230 kV breakers at Bear Swamp, replacing a transformer at Pratts Junction substation, adding a new 115 kV line from Millbury to Webster, and implementing several other 115 kV upgrades. Some of the upgrades have been placed in service, with the remaining scheduled for 2012 through 2015.

Worcester Area Reinforcements—The major upgrade associated with this reliability improvement is the installation of a new, 3.6 mile, 115 kV cable that connects the Bloomingdale and Vernon Hill substations in Massachusetts. This cable, placed in service in June 2012, completes a 115 kV loop providing alternate supplies to two critical Worcester substations.

Merrimack Valley/North Shore Project—Engineering and construction of the last of the upgrades associated with the Merrimack Valley/North Shore Project in Massachusetts currently is in progress. The new Wakefield Junction substation was placed in service in late 2009, and the Golden Hills substation was removed in early 2010. The remaining upgrades will be completed in 2012. The replacement of the underground cables between the Salem Harbor and Railyard substations has been deferred until improved information on their proper sizing is available; therefore, this upgrade no longer is considered part of the Merrimack Valley/North Shore Project.

Auburn Reliability Project—Past studies of the area surrounding the Auburn Street substation in Massachusetts identified overloads of the existing 345/115 kV autotransformer and several 115 kV lines, voltage problems, and breaker overstresses. The solution to eliminate these reliability deficiencies includes rebuilding the 345 kV and 115 kV switchyards at the Auburn Street substation to accommodate new bay configurations, along with the installation of a second autotransformer and the replacement of a number of breakers. Reconductoring of the 115 kV Auburn Street–Parkview and Bridgewater–East Bridgewater lines have been completed. Additionally, a number of distribution substation changes are being discussed that could modify the original project and its subsequent cost. The Bridgewater–Easton 115 kV line (E1) will be extended to supply a new municipal substation in Mansfield. The new Avon substation will be constructed and tapped off the newly reconductored Auburn Street–Parkview line (A94). The addition of a second distribution transformer at Dupont requires associated terminal work. The project currently is scheduled to be completed in 2015.

Lower SEMA Short- and Long-Term Upgrades—Plans to improve system performance in the lower southeastern Massachusetts (LSM) area, which includes Cape Cod, were separated into two phases. Phase one included the projects that could be put in place in an expedited time frame. Phase two includes those projects that would serve as the long-term solution for reliable supply but would require state siting hearings. The short-term upgrades were completed in 2009, and the long-term upgrades received siting approval on April 27, 2012.

The long-term plan, scheduled for a May 2013 in-service date, includes adding a new 345 kV transmission line from the Carver substation to a new 345/115 kV substation. This new four-breaker ring-bus substation, which has been designated the Oak Street substation, will be located west of the Barnstable substation adjacent to the 115 kV line right-of-way. The Carver–Bourne section of the 345 kV line is new construction, and the Bourne–Barnstable portion of the new 345 kV line will use an existing 115 kV line built to 345 kV standards. The 115 kV line (the Mashpee–Barnstable 115 line) will be tapped into the new substation. The plan also involves placing the existing 345 kV Cape Cod Canal crossing on separate towers and reconductoring the 115 kV D21 line between Bell Rock and High Hill.

Greater Rhode Island (Advanced NEEWS) Project—Reliability concerns with the 115 kV system in the Bridgewater–Somerset–Tiverton areas of southeastern Massachusetts and the adjoining area in Rhode Island had been identified previously. The solutions to these concerns were a group of upgrades that had been combined with the advanced Rhode Island upgrades (associated with NEEWS studies) to become what is now known as the Greater Rhode Island transmission reinforcements. The advanced NEEWS upgrades, the new Berry Street 345/115 kV substation (MA) and the expansion of the Kent County substation (RI) with an additional 345/115 kV autotransformer, have been placed in service in 2011. The proposed non-NEEWS GRI solutions in the Massachusetts area include, among other projects, the construction of new 115 kV transmission circuits between Brayton Point and Bell Rock substations. These currently are scheduled for a 2014 in-service date and will be reexamined as part of the SEMA/RI (Eastern REMVEC) study (see above).

Grand Avenue Substation Rebuild—The Grand Avenue 115 kV substation rebuild was completed early in 2012. A detailed engineering review of the existing substation determined that it was past its useful life and that upgrades were not practical when considering the short-circuit capabilities of the bus work, the ground grid, disconnect switches, and other equipment. Maintenance of the existing equipment had become increasingly difficult with the clearances that existed and the extent of the outages that had to be secured for work to proceed.

Millstone Double-Circuit Separation—Four 345 kV circuits emanate from the Millstone switching station. The 310 line to Manchester and the 348 line to Haddam share the same towers for four miles. The 371 line to Montville and the 383 line to Card Street share the same towers for two miles. The severe-line-outage detection (SLOD) special protection system was installed to improve system stability performance under certain system conditions. This project will separate the double-circuit sections of the Millstone lines and eliminate the need for the SLOD SPS and the exposure to contingencies that can be limiting under some system conditions in moving power from east to west through Connecticut. The project is expected to be completed December 2013.

Southwest Connecticut Advanced Solutions—The advanced solutions for SWCT include the following elements:

- Reconfiguration of the 115 kV 8300 line from Mill River to Quinnipiac—The SWCT Needs Assessment analysis showed thermal issues due to the loss of the 8300 line on its own or as a contingency pair. These N-1 and N-1-1 contingencies are unrelated to other needs in the New Haven area. The solution to mitigate the thermal issues is to install a new 115 kV overhead line from Mill River to Grand Avenue and to extend the existing 8300 line from Mill River into a new Grand Avenue substation bay. The project is expected to be completed by September 2013.

- NU’s Glenbrook–South End cable—The SWCT Needs Assessment analysis showed thermal and voltage issues in the Stamford-Greenwich and Darien-Compo subareas due to line and cable outages followed by 115 kV stuck breaker and DCT contingencies. The solution to mitigate these issues is to install a new 115 kV underground cable between the Glenbrook and South End substations. The project is expected to be completed by December 2014.

## Information on Critical Load Levels

The ISO has been improving the information provided to stakeholders, especially the required timing of transmission projects. The load level most often drives the need for transmission improvements under the assumptions used in each of the studies. The load level at which a system problem could occur and, therefore a solution would be needed, is referred to as the critical load level. From this critical load level, an approximate year of need can be developed. However, the year of need can change as the load forecast and other influences, such as energy efficiency, vary.

The ISO provides information on critical load levels in the needs assessment and solutions study for each portion of the region investigated. In the March 2012 update to the New Hampshire/Vermont Needs and Solutions Studies (see Section 5.5.1.2), critical load levels have been provided, and virtually all upgrades are required at load levels that already have been surpassed. A similar assessment was performed for the Greater Boston area.  The results of this analysis also showed numerous system concerns for load levels that already have been surpassed.

## Transmission Improvements to Load and Generation Pockets
Addressing Reliability Issues

The performance of the transmission system is highly dependent on embedded generators operating to maintain reliability in several smaller areas of the system. Consistent with ISO operating requirements, the generators may be required to provide second-contingency protection or voltage support or to avoid overloads of transmission system elements. Reliability may be threatened when only a few generating units are available to provide system support, especially when considering normal levels of unplanned or scheduled outages of generators or transmission facilities. This transmission system dependence on local-area generating units typically can result in relatively high reliability payments associated with out-of-merit unit commitments.

Several areas currently depend on out-of-merit generating units to some degree to maintain reliability, or have been dependent on these units until recently. These areas and the status of transmission projects that have either reduced or eliminated the need to run units out of merit to respect reliability requirements, or are expected to do so when the projects are completed, are as follows:

- Maine—Generation is required for maintaining system reliability following second contingencies involving flows from New Hampshire to Maine. The MPRP project (see Sections 5.5.1.2 and 5.5.1.3) is expected to help reduce the requirement for running certain generators to support New Hampshire to Maine transfers. Net Commitment-Period Compensation (NCPC) charges in the Maine area were just under $3.0 million, owing to operating reserve requirements and the need to maintain second-contingency protection for the NH to ME interface.

- Massachusetts

- Boston area—Because of the shunt reactor installations in the 2009 to 2010 timeframe, which followed the completion of the Stoughton Cables project, NCPC for this area totaled less than $1.4 million for 2011.

- Southeastern Massachusetts—The completion of the short-term Lower SEMA project, coupled with the temporary operating measures put in place, resulted in NCPC payments in this area being less than $0.3 million.

- Western Massachusetts/Springfield area—A preferred solution for the Pittsfield–Greenfield area has been selected; however, some out-of-merit costs likely will continue until improvements are placed in service. Other out-of-merit costs in this area are associated with the construction of the GSRP component of NEEWS, which will accommodate load growth as well as reduce dependence on local generation. This area accounted for approximately $5.5 million of the 2011 NCPC charges.

- Connecticut—The new resources procured through the Forward Capacity Market helped keep the NCPC charges to just over $1.1 million for Connecticut. This minimal amount was due to operating reserve requirements and the need to maintain second-contingency protection for the CT interface.

## Out-of-Merit Operating Situations

As part of the FCM rules, the ISO reviews each delist bid to determine whether the capacity associated with the delist bid is needed for the reliability of the New England electric power system. Capacity determined not to be needed for reliability is allowed to delist.

For FCA #4, which was held in August 2010 for the 2013/2014 capacity commitment period, 281 delist bids were received, representing 2,410 MW. In accordance with Planning Procedure No. 10 (PP 10), Planning Procedure to Support the Forward Capacity Market, the ISO reviewed and analyzed these bids and determined that 587 MW, representing Salem Harbor units #3 and #4, and 604 MW, representing Vermont Yankee, were needed for reliability. In a December 16, 2010, order, FERC accepted the ISO’s determination. In May 2012, the ISO notified Entergy that Vermont Yankee is no longer needed for the FCA #4 capacity commitment period. Refer to Section 7.4 for more information on VY.

In February 2011, a nonprice retirement request (see Section 5.5.2.2) was submitted for Salem Harbor units #1, #2, #3, and #4 beginning June 1, 2014. The ISO found no reliability concerns associated with the retirement of Salem units #1 and #2. However, in May 2011, the ISO provided its determination to FERC that Salem Harbor units #3 and #4 were needed to ensure continued reliability of the system. Soon after the ISO’s determination was issued, Dominion Energy Marketing notified the ISO that it will proceed with the retirement of Salem units #3 and #4 on June 1, 2014.

For FCA #5, which was held in June 2011, for the 2014/2015 capacity commitment period, 201 delist bids were received, representing 1,775 MW. In accordance with PP 10, the ISO reviewed and analyzed these bids and determined that only Vermont Yankee was needed for reliability.

FCA #6 was held in April 2012 for the 2015/2016 capacity commitment period. The ISO reviewed and analyzed 191 delist bids, representing 1,968 MW. Several delist bids representing 79 MW were needed for reliability in the NEMA/Boston capacity zone. The final transmission solution for the Greater Boston area is expected to mitigate these concerns by increasing the ability of the transmission system to move power into the area.

## Other Needed and Elective Transmission Upgrades

This section discusses Market-Efficiency-Related Transmission Upgrades. It also provides information on several transmission upgrades developed and paid for by generator developers. The transmission upgrades must meet reliability performance requirements.

### Needed Market-Efficiency-Related Transmission Upgrades

The purpose of and requirements for Market-Efficiency Transmission Upgrades are described in Section 5.3.2. However, market-efficiency benefits also may be associated with Reliability Transmission Upgrades, particularly when out-of-merit operating costs are reduced.

### Transmission Improvements to Mitigate Congestion

Recent experience has demonstrated that the regional transmission system has little congestion. For most of the system in 2011, the average difference between the congestion component of the LMP at the Hub and the regional energy zones was less than $0.64/MWh. The congestion costs are not significant enough to warrant mitigation by a transmission upgrade; however, planned Reliability Transmission Upgrades might help reduce congestion costs further. Similarly, planned Reliability Transmission Upgrades also may reduce transmission system losses.

### Reliability Transmission Upgrade Improvements to Load and Generation Pockets

Transmission solutions continue to be put in place where proposed generating or demand-side resources have not relieved transmission system performance concerns. The ISO is studying many of these areas, and while transmission projects are still being planned for some areas, other areas already have projects under construction and in service to mitigate dependence on generating units. Reliability Transmission Upgrades were used to address these system performance concerns, which contributed to a substantial reduction in out-of-merit operating costs.

Generating units in load pockets may receive second-contingency or voltage-control payments for must-run situations. Table 5-3 shows the NCPC by type and year.

Table 5-3
Net Commitment-Period Compensation by Type and Year (Million $)

| Year | Second Contingency(a) | Voltage | Total |
| --- | --- | --- | --- |
| 2003(b) | 36.0 | 14.4 | 50.4 |
| 2004 | 43.9 | 68.0 | 111.9 |
| 2005 | 133.7 | 75.1 | 208.8 |
| 2006 | 179.9 | 19.0 | 198.9 |
| 2007 | 169.5 | 46.0 | 215.5 |
| 2008 | 182.5 | 29.4 | 211.9 |
| 2009 | 17.2 | 5.0 | 22.2 |
| 2010 | 3.9 | 5.1 | 9.0 |
| 2011 | 6.0 | 5.9 | 11.9 |

(a) 	NCPC for first-contingency commitment and distribution support is not included.

(b) 	NCPC under Standard Market Design began in March 2003.

The 2009, 2010, and 2011 figures show a significant drop-off from the preceding years, averaging less than $15 million per year. With NCPC reliability payments this low, the current incentives are limited for pursuing transmission upgrades solely to reduce dependence on these generating units and improve the economic performance of the system.

### Required Generator-Interconnection-Related Upgrades

No significant transmission system upgrades resulted from the interconnection of generators. Most of the Generator-Interconnection-Related Upgrades are fairly local to the point of interconnection of the generator. The PTF upgrades are identified in the RSP Project List (see Section 5.4).

### Elective Transmission Upgrades and Merchant Transmission

Currently, eleven projects are Elective Transmission Upgrades or merchant transmission facilities:

- Two-terminal, HVDC line between Maine Yankee substation and South Boston, MA

- HVDC line between Orrington, ME, and Boston

- 345/230 kV AC line between Plattsburgh, NY, and New Haven, VT, in series with a back-to-back HVDC facility

- 345 kV tie line connecting Houlton, ME, and the Maine Electric Power Company (MEPCO)

- 345 kV tie line connecting Bridgewater, ME, and MEPCO

- HVDC line from northern Maine to Boston

- HVDC line from Québec to New Hampshire

- HVDC tie from southern Connecticut to Long Island

- HVDC line from northern Maine to north of Boston

- HVDC line connecting offshore wind to south of Boston

- HVDC line connecting offshore wind to Cape Cod

All ETU projects listed above currently are in the study phase.

## Summary

To date, eight major 345 kV transmission projects have been completed in five states since 2002; four additional projects have completed siting and are under construction; and one other is in siting. These projects reinforce critical load pockets, such as in Southwest Connecticut and Boston, and areas that have experienced significant load growth, such as northwest Vermont. These projects also include a new interconnection to New Brunswick, which increases the ability of New England to import power from Canada.

The MPUC has approved the siting of most of the component projects of the Maine Power Reliability Program, and many components are under construction. The MPRP will establish a second 345 kV line in the north from Orrington to Surowiec and will add new 345 kV lines in southern Maine, creating a third parallel path from Surowiec to Eliot (Three Rivers) in southern Maine. This program will reinforce and augment the 345/115 kV transformation capability in various load centers of Maine for greater reliability to area loads. These new paths provide basic infrastructure to increase the ability to move power into Maine from New Hampshire and improve the ability of the transmission system within Maine to move power into the load pockets as necessary. The studies necessary to evaluate any changes in transfer capability from Maine to New Hampshire are expected to be complete in 2012.

To address potential system reliability concerns associated with the upcoming unavailability of Salem Harbor and the potential unavailability of Vermont Yankee, specific transmission upgrades have been advanced. For the retirement of the generation at Salem Harbor, 115 kV line reconductoring projects are moving ahead in the North Shore area. For Vermont Yankee, upgrades at Flagg Pond have been installed to address potential thermal overloads if Vermont Yankee is unavailable.

The New England East–West Solution series of projects has been identified to improve system reliability. RSP12 shows that the Springfield and Rhode Island components should be placed in-service as soon as possible. The updated review of the need for the Interstate Reliability Project component of NEEWS is complete, and the preferred solution is unchanged. The needs assessment for the Central Connecticut Reliability Project has been combined with the Greater Hartford–Central Connecticut study, presently underway.

Costs associated with second-contingency and voltage-control payments have been mitigated through transmission improvements. Additional transmission plans have been developed, which reduce the dependence on generating units needed for reliability. An example is the Lower SEMA projects, whereby short-term improvements already have reduced dependence on the Cape Cod Canal generating units; further long-term improvements will eliminate the need to commit generation for second-contingency protection.

From 2002 through June 2012, 400 projects have been put into service, with an investment totaling approximately $4.8 billion. Additional projects (proposed, planned, or under construction), totaling approximately $6.0 billion, are summarized in the RSP Project List, which is updated periodically.

All transmission projects are developed to serve the reliability of the entire region and are fully coordinated regionally and interregionally. Most projects on the RSP Project List remain subject to regional cost allocation. As a result of transmission expansion, the ISO meets all required transmission planning requirements, and little congestion currently is evident on the system.

# Strategic Planning Initiative

ISO New England has been planning and operating the power system successfully since 1997. As shown in this and prior Regional System Plans, power plant emissions are lower, transmission projects have been built to enhance the system’s reliability, demand resources have become part of the regional power system, and the wholesale markets have become more competitive. However, the regional energy landscape is changing rapidly with advances in generation, transmission, demand resources, and wholesale markets that all must respond to evolving economic and policy conditions. This transforming energy landscape is posing challenges for older fossil fuel resources, which may need to retire, and it is requiring technological advances for the region, such as for integrating variable energy resources (VERs) and utilizing advanced transmission system technologies. While these system changes are encouraging the development of natural-gas-fired generation, renewable resources, and energy efficiency, all of which will further reduce emissions and other adverse environmental impacts in the region, more challenges lie ahead.

To address these challenges, since early 2011, ISO New England, the New England states, and NEPOOL participants have engaged in a Strategic Planning Initiative focused on the future of the wholesale electricity sector in New England and the development of enhancements to the planning process and wholesale markets. ISO New England launched this initiative to proactively highlight and address several key risks to the long-term reliable and efficient operation of the wholesale electric markets and regional power system and to ensure the region’s continued compliance with all required NERC and regional planning and operating requirements.

This section discusses the risks identified for the Strategic Planning Initiative, studies being conducted to help address the risks, and potential mitigating solutions.

## The SPI Risks and Challenges

The challenges identified in the Strategic Planning Initiative, as shown in Figure 6-1, are as follows:

  - Resource Performance and Flexibility—the uncertain amounts, unclear performance, and operational challenges of using demand resources, less responsive resources, and resources with limited ability to supply electric energy, and the need to increase system flexibility

  - Increased Reliance on Natural-Gas-Fired Capacity—the reliance on natural-gas-only resources because the gas supply and infrastructure systems may not be sufficient to meet power system needs when seasonal demand is high or when the system is stressed in other ways or facing natural gas supply and distribution system contingencies

  - Retirement of Generators—economic and policy factors that could lead to the exit of a substantial portion of older fossil-fuel capacity

  - Integration of a Greater Level of Intermittent Resources—the need for a steady increase in reserves, regulation, and ramping capabilities as more intermittent resources, primarily renewable energy resources, are added to the system over the next several years

  - Alignment of Markets with Planning—the need to better align the timing and analysis of wholesale market procurements with the transmission planning processes to allow for meeting reliability needs through market resources or backstop transmission solutions

Figure 6-1: The five challenges of the Strategic Planning Initiative.

Throughout 2011, the ISO held a series of stakeholder discussions on the Strategic Planning Initiative, after which the region reached broad consensus regarding the nature and urgency of the identified risks. Discussions with state regulators and representatives, NEPOOL, and other regional stakeholders yielded valuable input, summarized in white papers, to address a number of issues. The white papers include a “roadmap” of potential solutions for mitigating the identified risks in the near and long terms, present possible changes to the Forward Capacity Market, and conceptualize a design for facilitating the participation of market-based resources in New England’s system planning process as alternatives to transmission reliability projects. The region now is working toward further developing solutions to help ensure a reliable system and efficient marketplace in the long term. The following sections describe the risks in more detail.

### Risk 1: Resource Performance and Flexibility

Recent experience has indicated that the operational characteristics of New England’s current fleet of resources present challenges for the system operator and do not fully match the operational needs of the existing and likely future system. Reserves may be called on if a transmission line or generator trips unexpectedly, or if supplies are running short because demand is peaking. Contingencies assumed in planning and operations are large relative to the size of the New England system. In practice, the availability of off-line reserve resources is limited, and at times, additional resources must be committed as on-line reserves. Moreover, the system’s resources have limited flexibility, given the current market incentives and performance characteristics of the types of units on the system.

The current circumstances include the following:

- Slow response and decreased reliability of older thermal units not designed to be used as flexible ramping resources

- Relatively narrow operational band of more responsive and newer gas-fired, combined-cycle units

- Frequent participation in the energy markets by capacity that is responsive but limited in the amount of electric energy it can provide, rendering it unavailable to serve as reserves or provide ramping functions

- Constrained operational ability to use certain classes of demand resources that can be dispatched in emergency conditions only

All these issues can lead to less efficient operation of the system, increased out-of-market costs, and reliability issues.

### Risk 2: Increased Reliance on Natural-Gas-Fired Capacity

The region has been increasing its dependence on natural gas to generate electric energy and provide operating reserves. (Refer to the data presented in Section 7.1.) Issues with the availability of natural gas for power generation have occurred, however, posing a risk to the reliability of the power supply. New England has faced the following challenging operating conditions resulting from the actual or anticipated unavailability of the region’s gas-fired generating capacity or energy production:

- Disruptions in the natural gas supply and transportation infrastructure (e.g., the 2004 “cold snap,” the 2009 Sable Island outage, and January 2011 cold weather)—New England’s peak electrical use is in the summer months, while its peak natural gas use—for space heating—is in the winter months. In the spring through the fall, local gas distribution companies in the region may “release” their unused firm gas entitlements to the gas-fired generation sector. However, during the winter, the local distribution companies (LDCs) exercise their firm pipeline (and storage) entitlements to service their core customers and satisfy the space heating needs of residences and businesses. Thus, during winter, New England’s gas-fired generators face the most risk of being unable to obtain gas for their units. On a very cold, winter peak day (i.e., peak “cold-snap” conditions), the demand for natural gas for both power generation and heating is high, but most of the natural gas within the regional pipelines is targeted for use by the core gas sector, which could leave most of the single-fuel, gas-only power plants without a fuel source to generate electricity. Additionally, at any time during the year, including the summer peak demand period, the loss of a major pipeline or compressor station, due to forced outages or maintenance for example, could temporarily constrain pipeline capacity and limit service to nonfirm customers in New England.

- Market conditions under which generating units could not capture volatile intraday gas pricing in their wholesale electricity market offers—These conditions create a disincentive for generators to use their nominated gas for electric power generation and thus allow them to profit more from selling their gas transportation and supply into the gas market than using the gas to generate electricity. Even when natural gas supply is available, if the generators cannot reflect the spot market price of that fuel in their electricity market offers, the suppliers and transporters may have economic incentives to sell their natural gas supplies and transportation services to higher-paying consumers. This is particularly true for liquefied natural gas (LNG) deliveries that are part of a worldwide market for natural gas. The interruption of LNG deliveries during April/May 2012 into the NEMA/Boston capacity zone required posturing of resources in preparation of 90/10 conditions.

- The apparent reversal of initial progress in increasing the amount of dual-fuel capability at the region’s natural-gas-fired facilities following the cold snap of 2004—Economic and operational factors have affected the operation of dual-fuel units that burn oil, including relative fuel prices, the cost of storing back-up fuel inventory, additional operations and maintenance expenses associated with fuel switching, and the time it takes for some units to switch over.

In addition to the efforts to add dual-fuel capability in the region after 2004, the region made other improvements to address its dependence on natural gas for power generation. These efforts include stronger communication with interstate natural gas pipeline facilities, better coordination with New England’s natural gas industry participants, and closer monitoring of natural gas system conditions. However, the ISO’s review of natural-gas-related power system events since 2004 and an evaluation of natural gas system capacities to support power generation under normal and outage conditions suggest that the region needs to mitigate the consequences of operational and economic risks to the power system, including the following:

- Vulnerability of electric power system reliability caused by natural gas infrastructure problems

- Inability of gas generators to reflect updated fuel prices in their wholesale electricity market offers or to schedule fuel deliveries in response to ISO dispatch instructions

- The reliability need to enhance the region’s dual-fuel capability and have generators with the flexibility to switch to a back-up fuel source when needed for energy production, particularly for cold-weather events and other forecast events

- The need for securing fuel for the gas-fired units the region relies on to meet energy needs, load following, and contingency response

The region is expected to continue its high dependence on natural-gas-fired generation because of the relatively low fuel cost and low emissions profile for natural gas and because electric power transmission improvements have reduced the region’s reliance on older, less economical oil- and coal-fired generators in load pockets. The likely retirements of these less economical generators (discussed below) will decrease fuel diversity and heighten the regional risks of relying on natural-gas-fired capacity, particularly during conditions of strained gas availability because the primary remaining and replacement capacity for the coal and oil units will be natural gas. The anticipated growth of intermittent resources (also discussed in Section 6.1.4) would pose additional operational challenges to both the natural gas and the electric power systems.

### Risk 3: Potential Retirement of Generators

One of the near-term risks is the potential for substantial unit retirements before the planned long-term market and system enhancements can influence resource development. Although the retirement of uneconomic capacity is an efficient market outcome contemplated in the FCM design, the potential magnitude of retirements in a relatively short timeframe, as identified by the ISO, and the effects of these retirements on the other identified challenges are concerns. The sections that follow contain more details about the interactions of the risks associated with system performance, flexibility, and high dependence on natural gas.

The capacity mix in New England, which has summer peak requirements of roughly 32 gigawatts (GW), operates with about 6 GW of fossil-fueled generating units (primarily coal or oil) that are older than 40 years and that convert fuel to electricity inefficiently (i.e., they run at heat rates exceeding 10,000 British thermal units/kilowatt-hour; Btu/kWh). In 2020, over 8.5 GW are expected to be older than 40 years. Oil-fired generation represents almost 22% of existing capacity in the region and last year supplied 15% of the peak load (see Section 7.1). However, oil-fired generation operates at an average capacity factor of less than 1%. Under the current market conditions of relatively low electric energy clearing prices and the favoring of efficient, new generating facilities, the oil-fired resources and, to some degree, coal resources face economic challenges trying to recover most of their variable and fixed costs, including any new capital investments. Thus, even without new capital investment, a significant portion of the region’s generating fleet is at risk of retirement.

Yet, existing and pending environmental initiatives that (could) require reduced air emissions and controlled water withdrawals and discharges are placing increased economic pressure on aging coal- and oil-fired units to add environmental controls or to reduce run times (see Section 8.1.1). Given their age and lack of operating revenues and the new capital investment that may be required, these coal and oil units are likely to retire in the latter half of the decade and be replaced with efficient and relatively clean-burning natural-gas-fired units. The region also could face the retirement of nuclear generators when their licenses come due for renewal.

### Risk 4: Integration of a Greater Level of Variable Energy Resources

All six New England states have goals for supplying load with renewable resources. A steady increase in system flexibility, as discussed in Section 6.1.1, will be required to ensure system reliability as the region adds more intermittent resources, primarily renewable energy resources, to the system over the next several years. The variable nature of intermittent resources will require the system to have increased reserves, regulation, and ramping capabilities. New England has almost 2,200 MW of wind generation in the queue, and state goals for funding photovoltaic generation has the potential to support the development of 800 MW by 2021. In addition to requiring system flexibility, transmission development likely will be needed for integrating New England’s potential wind power development.

### Risk 5: Alignment of Markets with Planning

The RSP and associated transmission studies contain a significant amount of information available to market participants on the locational and performance characteristics needed for reliable system operations. At present, the region develops transmission solutions to solve reliability issues and does not fully identify granular resource requirements that also meet all transmission system needs. These transmission analyses also may not be available with sufficient notice for the markets to receive adequate signals regarding transmission security requirements or for market resource proposals to respond fully to identified system needs. However, developing a market resource may be the more cost-effective choice depending on its location, cost, and other factors, such as ensuring resource adequacy and the efficient commitment and dispatch of resources.

Incorporating market resource alternative analyses into transmission planning has some challenges, as highlighted in an October 2011 ISO whitepaper, Aligning Planning and Markets. These challenges include coordinating the disconnected timing between markets and planning and standardizing analytical approaches and assumptions (see Section 4.5). For example, if system resources change significantly (e.g., through the retirement of a large number of key resources over a relatively short period of time), the FCM may not have time to induce market solutions before backstop transmission solutions are well underway to resolve the identified transmission security need.

### Summary of Risk Interactions

Natural-gas-fired generating units most likely could replace many of the old coal, oil, and nuclear units in locations requiring relatively little additional transmission system infrastructure. Although the addition of renewable resources would provide some diversity of the fuel supply, the increased regulation and reserve requirements needed to reliably integrate new intermittent resources could place new stresses on the natural gas system, which would need to flexibly provide fuel to generators on short notice. Exacerbating the problem, many existing natural-gas-fired units require extensive retrofitting to provide flexible operation and economical or effective dual-fuel capability (in terms of the amount of time it takes to switch to using oil, ramping rates, or the availability of secondary fuel inventory). Finally, the replacement of spinning reserve with new generating units that have less inertia than the retiring units or fast-start resources (see Section 4.3) reduces the inertia on the system, which has the potential to degrade system stability performance.

Several other components of the regional fuel supplies used to generate electricity can have an impact on New England’s electric power sector and wholesale markets. These impacts include natural and geopolitical events that create large price swings and disruptions in the supply of oil, both heavy and light, which affect regional oil markets; constraints on transporting and importing coal; challenges to the nuclear power industry; regional drought; or a combination of several of these problems.

## Analyses and Updates to Studies and Other Actions Supporting the Strategic Planning Initiative

The ISO is conducting several studies to address the risks identified through the Strategic Planning Initiative. These studies are assessing the economic and reliability effects of retiring aging, environmentally challenged generating units and their likely replacement with natural-gas-fired generation, renewable VERs, and imports from the neighboring Canadian regions. The ISO also is studying improved operations, the integration of renewable resources, economic performance and expansion of resources, the extent of fuel diversity risks and means of reducing these risks, natural gas system requirements, and other issues. The studies involve simulating production costs and conducting transmission planning studies for some of these scenarios. Because the five identified risks are interrelated, many of the studies are informing regional stakeholders on the extent of the overall risks facing the region and quantifying potential solutions that may address several risks. Some actions already are underway to address some of the identified risks.

### Improvements in System Operations (Risk 1)

To address resource performance and flexibility needs, the ISO periodically meets with plant managers and operators, transmission owners, and demand-response aggregators to review operating procedures. The ISO is examining the operation of the grid and the structure of the markets to identify tools the ISO control room can use to better manage operational issues, to better define system operating needs and incentives for resource performance, and to refine operating procedures to reflect resource performance characteristics (see Section 9.4.1).

### Integration of Renewable Resources (Risks 1, 4, and 5)

The ISO completed the New England Wind Integration Study (NEWIS), a major study of integrating large amounts of wind resources (up to 12,000 MW) into the New England system. This study analyzed various planning, operating, and market aspects of wind integration and the conceptual development of a transmission system that can integrate these resources.

NEWIS results showed that the large-scale integration of wind resources is feasible in the New England region, but the region will need to continue addressing a number of issues, including the methods for calculating capacity values and forecasting wind generation outputs and updated interconnection requirements. NEWIS also quantified the amount of increased system flexibility required to integrate large amounts of wind generation and the needed market design incentives for dispatchable resources to add this flexibility. Another result showed that adding large-scale wind generation would reduce net energy market revenues for natural-gas-fired resources, which could make these units uneconomical and not available to supply system needs if they retired. These units would need additional sources of revenue, possibly through market modifications, to allow them to charge for the reliability services they will be providing. Section 7.6.5 contains further details on NEWIS.

The ISO continues to analyze VER integration issues, both regionally and in interregional forums.

### Economic Performance and Related Studies (Risks 1 to 5)

As a follow-up analysis to NEWIS, the ISO completed the 2011 Economic Study that analyzed the impacts of varying amounts of wind integration on several system metrics, including production cost, load-serving entity (LSE) expenses, environmental emissions, and others (see Section 8.2.1). This study also showed the need for transmission development to interconnect the wind resources and to bring the energy to load centers in New England. Plans for further studies call for conducting follow-up analysis using the GridView program (Section 8.2.1.3) to provide more details of the effects of integrating wind generation.

New England states have goals for developing solar photovoltaic (PV) power capacity, either explicitly or as part of their Renewable Portfolio Standards (see Section 7.6). Although integrating a large amount of capacity from small-scale, intermittent solar developments across the system is challenging, the effects on the overall power system most likely would be less significant because the expected amount of solar resource development is much smaller than the planned wind development in the region. The ISO has begun to examine the potential effects of large-scale solar power development in the region. (Section 7.6.6.1)

The 2012 Economic Study (see Section 8.2.2) has the goal of showing the most suitable locations for developing generation for reducing congestion, including natural gas, wind, and photovoltaic solar resources. The study also will show the effects of energy efficiency and the least suitable locations for unit retirements. The study will compare a “business-as-usual scenario” of currently known system expansion plans with the effects of increases and decreases in several parameters, including load; energy efficiency; a mix of renewable resources based on the ISO Generator Interconnection Queue and “behind-the-meter,” distributed generators (see Section 7.6.6); and efficient natural gas, combined-cycle units. In addition to the typical metrics provided by ISO in past economic studies (e.g., production costs, LSE expenses, congestion, environmental emissions), the study will show the estimated dollars/kilowatt-year ($/kW-year) capital costs plus technology costs for each type of resource and its energy revenues. The simulation results also will show where the system may have potential transmission bottlenecks and the effects of relieving these transmission constraints. The scope of work and assumptions were discussed with the PAC, and the draft study results are under development.

The ISO plans to use the Electric Generation Expansion Analysis System (EGEAS) program to examine future system scenarios. For each scenario, the EGEAS simulation tool identifies the most economical expansion of future resources under various assumptions, such as the capital cost of new supply- and demand-side resources, the availability of planned and existing resources, the production costs of all resources, and load levels and shapes.

### Fuel Diversity and Supply Studies and Actions to Address the Issues (Risk 2)

Recent and planned improvements to the regional and interregional natural gas infrastructure have been analyzed and will expand natural gas sources to meet New England’s increasing demand for natural gas to produce electric power. Also, the implementation of operating procedures and improved communications between electric power and natural gas system operators have decreased operational risks and improved the reliability of natural gas supply and transportation.

To quantify the extent of the regional fuel-diversity risk, the ISO commissioned a study to assess the regional gas supply and delivery system’s ability to serve New England’s power supply gas demands under several scenarios. The study reviewed the amount of gas supply available for New England’s gas-fired power generation through 2020 on peak winter and peak summer days. While the results showed that the natural gas system is adequate to meet the region’s expected summer peak conditions through 2020 and is able to supply LDC demand, the existing natural gas infrastructure may not be able to meet the electric power system demand during peak winter conditions. These study results also showed the extent to which the region could require alternative sources of electrical power generation, such as dual-fuel capability, and additional gas transportation to generating units. Refer to Section 7.3.2 for more details about this study. Also refer to the ISO’s whitepaper, Addressing Gas Dependence, which reviews the reliability issues associated with the region’s increasing dependence on gas-fired generators and solutions to mitigate this risk.

To better understand the emerging vulnerabilities, particularly in severe winter or other stressed system conditions, the ISO will issue a follow-up request for proposals to further study regional natural gas issues. This study will examine natural gas system demand scenarios based on the demands of natural-gas-fired generating units to quantify the periods when these natural-gas-fired generators may be exposed to fuel shortages. In addition, the ISO is coordinating with NYSIO and PJM Interconnection (PJM) on a natural gas study of the interregional system.

### Impacts of Environmental Regulations on Generating Units and the Power System (Risk 3)

Because new environmental requirements are in flux and are being phased in over the next decade, assessing the potential impacts that the resulting regulations could have on generators and the power system poses some challenges. First, the capital investments some generation owners will need to make are uncertain for complying with the Mercury and Air Toxics Standards (MATS) of the US EPA Clean Air Act (CAA) and the Cooling Water Intake 316(b) Rule of the Clean Water Act (CWA) (see Section 8.1.1). Other unknowns include the timing, magnitude, and location of unit retirements that could result from generators opting not to comply with these regulations.

As part of the Strategic Planning Initiative, the ISO is collecting and analyzing data to identify the units expected to face significant capital investments because of upcoming regulatory requirements and to assess the potential resulting impacts on transmission system operations. The ISO also has initiated a study to better quantify the implications of the likely retirement of several generating units and their potential replacements. The ISO is identifying generators that already have environmental remediation measures in place or may require relatively minor upgrades and those at risk for retirement. The actual compliance timelines will depend on the timing and substance of the final regulations and site-specific circumstances of the electric generating facilities. Most of the at-risk capacity would face compliance or retirement decisions—and FCM positioning decisions—starting late in this decade, extending into the early part of the next decade.

### Transmission System and Market Resource Alternative Analyses (Risks 1 to 5)

To improve the alignment of the wholesale markets with transmission planning and enable markets to produce solutions to transmission security needs, the ISO began to study market resource alternatives using information obtained from the transmission needs assessments of the same areas. These studies aim to identify the generation and demand-resource amounts and locations that could resolve the needs signaled by the transmission needs assessments. The full implementation of these studies will require significant effort to define the timing, analytic approach, and description of system conditions.

As a case study, the ISO conducted a pilot study that analyzed market resource alternatives for the New Hampshire/Vermont area. The ISO now proposes the use of such analysis in the transmission planning process to facilitate the procurement of market resources to meet transmission security needs. A new pilot study is underway for the Greater Hartford Central Connecticut area (refer to Section 4.5.3).

To address the identified need for aligning markets and planning, enhancing the existing markets, and potentially developing new services or markets, the ISO has prepared several documents and is developing several more that frame the issues and facilitate the improvement of the system and markets:

  - The Roadmap for New England identifies many of the Strategic Planning Initiative risks and suggests a process for developing potential solutions through the open stakeholder process.

  - Design documents will propose how to incorporate identified local and system reliability requirements into resource adequacy markets and to meet operational needs. The reliability items are scheduled for completion during the second half of 2012, and the operational needs will be addressed during the first quarter of 2013.

  - A discussion paper, Aligning Markets and Planning, identifies potential improvements to the markets that will help address reliability issues caused by the region’s dependency on natural gas. In this paper, the ISO proposes pricing capacity resources to meet both resource adequacy and selected transmission security needs and modifying the planning process, to better coordinate the timing of developing transmission solution “backstops” when competitive wholesale markets cannot solve the identified needs or can do so only at high cost.

  - The white paper, Using the Forward Capacity Market to Meet Strategic Challenges, suggests improvements to the Forward Capacity Market. The long-term vision for the FCM includes the efficient procurement of resources in specific locations and performance characteristics to address both resource adequacy and transmission security needs. A FERC filing is targeted for December 2012.

### Strategic Transmission Analysis (Risks 3 and 4)

The Strategic Transmission Analysis is assessing potential transmission issues associated with generator retirements and examining “broad” transmission system requirements to integrate renewable resources for the 2020 study year. Some portions of the study will be complete in 2012, including interim reports, and the remainder of the study is scheduled for 2013.

The initial study system conditions are based on those used in the 2010 economic study for the 2030 study year and resource assumptions, such as the integration of demand resources and the retirement of oil and coal generating units more than 50 years old. The repowering of existing old coal- and oil-fired generators with natural gas would not require a major expansion of the transmission system. Therefore, the Strategic Transmission Analysis focuses on the ability of wind, other supplemental capacity, or a combination of all resources to address the reliability needs resulting from the potential removal of generators, both simultaneously and in smaller clusters.

The study consists primarily of steady-state transmission analysis for various scenarios of wind generation expansion and sensitivity analyses conducted for various factors, such as system load levels, the amount of wind blowing, and amounts of power transfers with neighboring systems.

The study also is conducting stability simulations to determine whether the transmission plans developed based on steady-state analyses must be enhanced because of inadequate stability performance. Finally, chronological GridView system simulations showing transmission flow patterns and durations are being used to adjust and refine transmission solutions and provide a cursory examination of production costs and cost-benefit analysis.

The Strategic Transmission Analysis is examining 4 GW, 8 GW, and 12 GW levels of wind generation, the same levels studied in the Governors’ Blueprint study. The New England Wind Integration Study analysis suggested that the 2 GW delivery conceptual transmission plan (2 GW overlay) developed in the Governors’ Blueprint study might be adequate to deliver 4 GW of wind resources. Therefore, the starting point for the Strategic Transmission Analysis is the 2 GW transmission overlay shown in Figure 6-2 but with 4 GW of wind resources on the system. The study also is examining larger transmission overlays for larger amounts of wind resource development on the system.

Figure 6-2: Conceptual transmission plan for the delivery of 2 GW of wind resources.

## Summary

In its Strategic Planning Initiative, the ISO has identified risks to the regional electric power system; the likelihood, timing, and potential consequences of these risks; and possible mitigating actions. The initiative has identified that preserving the reliable operation of the system will become increasingly challenging with the uncertain performance of both aging supply resources and active demand resources. Additionally, the possible retirement of coal-fired and oil-fired generating units as a result of economic factors, coupled with the likely integration of variable energy resources, would further increase the need for new resources, especially those able to provide operating reserves and ramping capabilities. Generating units burning natural gas will provide much of the needed electrical flexibility. This in turn will likely affect natural gas system operations and increase the possible need for pipeline companies to improve natural gas system infrastructure. The ISO is conducting studies that quantify locational needs and desired performance characteristics of the electric power system and the exposure to shortages of natural gas system supply.

To address the five challenges, the region can build on the existing tools it has developed to ensure reliability. These tools include market rules that retain resources that seek to leave the capacity market, out-of-merit commitment and dispatch of capacity retained for system security, emergency capacity procurement, special operating procedures, and backstop regulated transmission investments. Given the magnitude and pace of the expected challenges, the region is considering whether these tools should be further improved or replaced to enhance system operations and planning. The ISO currently is working toward updating the requirements of the FCM. It also is monitoring resource performance and verifying detailed resource information on performance characteristics, such as ramp rates and fuel availability. Other efforts involve analyzing additional natural gas issues affecting planning and operations and integrating into the energy markets advancements in demand-resource dispatch.

The Strategic Planning Initiative, as well as other stakeholder efforts, will address these issues over the long term. Analysis and further adjustments of markets may be required to refine the reliable amounts and locations of needed new resources and operating reserves, including the appropriate levels of spinning and nonspinning reserves. Enhancements to the FCM and the locational FRM to better meet operational needs also may be considered, which could include a reexamination of capacity and reserve zones.

RSP studies continually inform stakeholders of the risks identified under the Strategic Planning Initiative and quantify the amounts, locations, and types of resources and transmission improvements the region will require to remain reliable and economically efficient.

Plans call for continuing to discuss these issues with the region’s stakeholders, provide regular updates to the PAC, and develop an approach for addressing the issues through the open stakeholder process. The ISO recognizes that these changes will require a significant amount of stakeholder time and effort but believes they are necessary to ensure the reliability of the power system and the competitiveness of the market structure the region has adopted. As needed, the ISO will work with stakeholder groups, as well as NEPOOL members and other interested parties, to support regional and federal market and policy initiatives.

# Fuel Supply and Diversity

In New England, different types of generators provide capacity and generate electric energy using a variety of fuels, including natural gas, nuclear, coal, oil, hydroelectric, and several types of renewable resources. As discussed in Section 6, one of the main risks to system reliability is that the region has become highly dependent on natural gas to generate electricity and provide reserves, yet enhancing dual-fuel capability, securing the supply of natural gas, and developing renewable resources face several economic and operational hurdles. Implementing measures to ensure a sufficient fuel supply and fuel diversity in the region is of critical importance for addressing these issues.

This section presents information and data about the various fuels used by the region’s generators to provide capacity and generate electric energy. It shows how the region’s use of fuels has changed since 2000 and how this use compares with the nationwide use of fuels. Data are included on the age of the region’s generators to indicate the potential need for capital investment or the replacement of old units. The section also provides an overview of the major events for system operations that occurred in 2011 and 2012 and how the ISO operated the system reliably through each event.

Updates on the main developments and use of natural gas, nuclear, coal, oil, hydroelectric, and renewable resources, including wind and solar energy, are provided. A study of the natural gas sector’s ability to meet the regional demand for natural-gas-fired generation is summarized. Additionally, the section compares potential regional development and energy production by renewable resources with projected state goals for Renewable Portfolio Standards and similar targets.

## Capacity Mix and Electric Energy Production by Fuel Type

Figure 7-1 shows New England’s generation capacity mix by primary fuel type and percentage. Based on the ISO’s 2012 CELT Report, the forecast for the total 2012 installed summer capacity is 31,969 MW with the following fuel mix:

- Fossil-fuel-based generators—natural gas, oil, and coal plants—total 23,143 MW, accounting for 72.4% of the installed capacity within the region.

- Natural-gas-fired generation represents the largest component of total installed capacity at 43.0% (13,764 MW).

- Oil-fired generation is second at 21.6% (6,895 MW).

- Coal-fired generation is fourth at 7.8% (2,484 MW).

- Nuclear generation is third at 14.5% (4,628 MW).

- Hydroelectric capacity (1,483 MW) and pumped-storage capacity (1,698 MW) are at 4.6% and 5.3%, respectively.

- Other renewable resources (i.e., landfill gas, biomass, refuse, photovoltaics, and fuel cells) are at 2.9% (920 MW).

- Wind resources total 0.3% (97 MW).

Figure 7-1: New England’s 2012 summer generation capacity mix by primary fuel type (MW and %).

Table 7-1 compares New England’s generation capacity mix by fuel type for 2012 with that of the nation for 2010, the latest information available. As shown in Table 7-1, fossil fuels represent 74% of the nation’s installed capacity, which is approximately the same as in New England, and the nation has 10% nuclear capacity, which is 4% lower than in New England.

Table 7-1
 New England’s 2012 Summer Generation Capacity Mix by Fuel Type
Compared with the 2010 Nationwide Summer Capacity Mix (%)(a)

| Fuel(b) | New England | United States(C) |
| --- | --- | --- |
| Coal | 8 | 30 |
| Natural gas and other gases | 43 | 39 |
| Petroleum and other fuels | 22 | 5 |
| Nuclear | 14 | 10 |
| Hydroelectric, pumped-storage, and other renewables | 13 | 15 |

- Percentages may not add to 100 because of rounding.

- The “coal” category includes anthracite, bituminous coal, subbituminous coal, lignite, and waste coal. The “natural gas” category includes a small number of generators for which waste heat is the primary energy source. The “other gases” category includes blast furnace gas, propane gas, and other manufactured and waste gases derived from fossil fuels. The “petroleum” category includes distillate fuel oil (all diesel and no. 1, no. 2, and no. 4 fuel oils), residual fuel oil (no. 5 and no. 6 fuel oils and bunker C fuel oil), jet fuel, kerosene, petroleum coke (converted to liquid petroleum), and waste oil. The “other fuels” category includes nonbiogenic municipal solid waste, batteries, chemicals, hydrogen, pitch, purchased steam, sulfur, tire-derived fuel, and miscellaneous technologies. “Other renewables” includes landfill gas, biomass, refuse, photovoltaics, and fuel cells.

- National figures are from the US Energy Information Administration (EIA) 2010 data, available at http://www.eia.gov/energyexplained/index.cfm?page=electricity_in_the_united_states#tab2.

Table 7-2 compares New England’s energy generation mix by fuel type with that of the nation. As shown in Table 7-2, fossil fuels produced 58% of the electric energy used in New England in 2011 compared with 68% of the electric energy used in the United States. Coal produced 6% in New England compared with 42% nationwide, and natural gas produced 51% in New England compared with 25% in the United States. Additionally, nuclear fuel produced 28% of the region’s electric energy in 2011 compared with 19% of the nation’s energy. Renewable and hydroelectric resources provided 14% of New England’s electric energy in 2011, while it produced 13% of the country’s energy. Production from petroleum fuels was less than 1% both in New England and nationwide.

Table 7-2
 New England’s 2011 Electric Energy Generation Mix by Fuel Type
Compared with the 2011 Nationwide Energy Mix (%)(a)

| Fuel(b) | New England | United States(c) |
| --- | --- | --- |
| Coal | 6 | 42 |
| Natural gas and other gases | 51 | 25 |
| Petroleum and other fuels | < 1 | < 1 |
| Nuclear | 28 | 19 |
| Hydroelectric, pumped-storage, and other renewables | 14 | 13 |

- Percentages may not add to 100 because of rounding.

- The “coal” category includes anthracite, bituminous coal, subbituminous coal, lignite, and waste coal. The “natural gas” category includes a small number of generators for which waste heat is the primary energy source. The “other gases” category includes blast furnace gas, propane gas, and other manufactured and waste gases derived from fossil fuels. The “petroleum” category includes distillate fuel oil (all diesel and No. 1, No. 2, and No. 4 fuel oils), residual fuel oil (No. 5 and No. 6 fuel oils and bunker C fuel oil), jet fuel, kerosene, petroleum coke (converted to liquid petroleum) and waste oil. The “other fuels” category includes nonbiogenic municipal solid waste, batteries, chemicals, hydrogen, pitch, purchased steam, sulfur, tire-derived fuel, and miscellaneous technologies. “Other renewable” includes landfill gas, biomass, refuse, photovoltaics, and fuel cells.

- National figures are from EIA 2011 data, available at http://www.eia.gov/energyexplained/index.cfm?page=electricity_in_the_united_states.

Figure 7-2 shows the production of electric energy by fuel type in New England for 2011, not including energy imports. From 2006 to 2011, imports supplied an average of 6% of New England’s net energy for load (i.e., the sum of generation and net interchange minus the energy consumption by the pumping load). Figure 7-3 shows the 2011 annual imports, exports, and net interchange of electric energy by balancing authority area. In 2011, New England imported 15,859 GWh of electric energy and exported 5,737 GWh of electric energy, which resulted in net imports of approximately 10,123 GWh. The 2011 regional net energy for load was 129,146 GWh, which equals the sum of generation (120,612 GWh) and net interchange (+10,123 GWh) minus the region’s pumping load (1,589 GWh). The net imports for 2011 were 7.8% of the net energy for load.

Figure 7-2: New England electric energy production in 2011 by fuel type (GWh and %).

Notes: The figure excludes 10,123 GWh of net imports.

Figure 7-3: New England energy imports and exports by balancing authority area in 2011 (GWh).

Note: Imports are shown as negative values, and exports are shown as positive values. Refer to monthly and annual summaries of net energy and peak load by source at http://www.iso-ne.com/markets/hstdata/rpts/net_eng_peak_load_sorc/index.html.

Figure 7-4 shows New England’s generating capacity and electric energy by fuel type for 2000 and 2011. The figure shows the decrease in coal- and oil-fired capacity and energy from 2000 to 2011 and the increase in natural gas capacity and energy during the same timeframe.

Figure 7-4: New England’s generating capacity and electric energy by fuel type, 2000 and 2011.

Table 7-3 shows New England’s 2012 summer generation capacity mix categorized by fuel type and in-service dates. As shown in the table, most of the oldest units on the system are hydroelectric units, and most of the 40- to 60-year-old stations are either coal- or oil-fired, steam-based units. The majority of the 20- to 40-year-old units are nuclear and pumped-storage stations. Natural-gas-fired generation is predominantly new (within the last 20 years); most of these stations were constructed after electric utility deregulation in the late 1990s or early 2000s.

Table 7-3
New England’s 2012 Summer Generation Capacity Mix
by Fuel Type and In-Service Dates (MW, %)(a, b, c)

|  | In-Service Date |  | In-Service Date |  | In-Service Date |  | In-Service Date |  | In-Service Date |  | Total |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Fuel Type | Before 1950 |  | 1951 to 1970 |  | 1971 to 1990 |  | 1991 to 2000 |  | 2001 and after |  |  |  |
|  | # of Assets | MW | # of Assets | MW | # of Assets | MW | # of Assets | MW | # of Assets | MW | MW | % |
| Gas | 5 | 53 | 1 | 94 | 12 | 1,599 | 20 | 3,538 | 38 | 8,479 | 13,764 | 43.0 |
| Oil | 3 | 9 | 59 | 2,240 | 21 | 3,934 | 11 | 140 | 25 | 571 | 6,895 | 21.6 |
| Nuclear | 0 | 0 | 0 | 0 | 5 | 4,628 | 0 | 0 | 0 | 0 | 4,628 | 14.5 |
| Coal | 0 | 0 | 12 | 2,480 | 2 | 4 | 0 | 0 | 0 | 0 | 2,484 | 7.8 |
| Pumped storage | 1 | 29 | 0 | 0 | 6 | 1,669 | 0 | 0 | 0 | 0 | 1,698 | 5.3 |
| Hydro | 78 | 823 | 8 | 324 | 156 | 275 | 34 | 14 | 27 | 48 | 1,483 | 4.6 |
| Other renewables | 0 | 0 | 1 | 43 | 32 | 613 | 26 | 199 | 91 | 65 | 920 | 2.9 |
| Wind | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 35 | 97 | 97 | 0.3 |
| Totals | 87 | 915 | 81 | 5,181 | 234 | 12,722 | 92 | 3,892 | 216 | 9,260 | 31,969 | 100.0 |
| % of total MW |  | 2.9% |  | 16.1% |  | 39.8% |  | 12.2% |  | 29.0% |  |  |

(a)   Generator assets in this table may be power plants or individual units that make up power plants. Values do not include HQICCs, demand resources, or external purchases and sales.

(b)  	A total of 10,888 MW of new generation has been installed since the start of the markets in May 1999. This total is based on the claimed capability of these assets as of April 1, 2012, and projected capabilities of assets expected to be in service by summer 2012.

(c) 	Totals may not equal the sum because of rounding.

## 2011/2012 Overview of System Operations Events

While the ISO complies with all NERC and NPCC reliability requirements, including those requiring the reliability of the fuel supply, the ISO continues to learn from operating experience to improve ISO operations, planning, and markets. The following summarizes notable operating events since the issuance of RSP11:

- In August 2011, Hurricane Irene caused the loss of over 2.1 million electric customers on the distribution system, which resulted in a severe loss of electrical load throughout New England. Communications among regional gas pipelines, local gas distribution companies, generating units, and the ISO were timely to address electric reliability concerns. The ISO was able to maintain all contingency coverage requirements throughout the system.

- On Saturday, October 29, 2011, and continuing into Sunday, October 30, New England experienced a rare and historic October “nor’easter.” Significant portions of the utility system were damaged by heavy wet snow on trees that had an unusual amount of foliage for this time of year. At all times during the event, the ISO and local control center system operators ran the regional electric power system to meet reliability criteria. The implementation of an Abnormal Conditions Alert started on Saturday, October 29 and continued until Monday, November 7, and Minimum Generation (Min Gen) Emergencies occurred two times during the event. The hardest-hit areas were in the lower Connecticut River Valley where most of the transmission outages occurred during the event.

- On December 19, 2011, the ISO implemented OP 4 actions that provided approximately 1,100 MW of load and capacity relief, including the commitment of additional oil-fired units and approximately 500 MW of real-time demand resources (RTDRs).

- In spring 2012, the ISO determined that reduced and uncertain supplies of liquefied natural gas to power generating resources in New England, attributable to a shortage of LNG, could create reliability challenges to the power grid. Extreme weather conditions, combined with significant unexpected generator outages, could further stress this situation. To mitigate the reliability impact of LNG supply shortfalls and manage system reliability during these shortages, ISO System Operations developed operational contingency plans.

Although the system has experienced fuel supply issues resulting from several natural gas units not having sufficient fuel, possibly because of a lack of firm natural gas contracts, the ISO system has remained secure over the last year. The ISO seeks opportunities to improve the coordination of natural gas and electric power system operations as well as to minimize the adverse impacts of other fuel supply risks, as discussed in Section 6 for the Strategic Planning Initiative and in the following sections.

## Natural Gas Supply and Infrastructure Update

As identified for the Strategic Planning Initiative, risk #2 (see Section 6.1.2), the region has increased its reliance on natural gas to generate electric energy and provide operating reserves, and system reliability concerns can be addressed through more secure natural gas delivery over the 10-year planning horizon. As a result of the forecasted need for new, regional gas supplies, the natural gas industry has invested heavily in infrastructure expansion and enhancements in the northeastern United States and eastern Canada. While past enhancements, such as the Canaport LNG project in Saint John, New Brunswick, were driven by the need to deliver LNG supplies to regional markets, more recently planned improvements are accessing gas supplies from new sources, such as Marcellus Shale, which is geographically close to New England.

### Natural Gas Development and Infrastructure

Updates of New England’s natural gas sector infrastructure and supply involve LNG import terminals, pipeline and storage facilities, and the development of Marcellus Shale and other finds.

#### LNG Import Terminals in New England

Four LNG import terminals serve the New England markets:

- Land-based LNG import/storage terminals:

- Distrigas Import/Storage Terminal—located on the Mystic River in Everett, MA; delivers regasified LNG into the Tennessee and Algonquin pipelines and Boston LDCs

- Canaport Import/Storage Terminal—located in Saint John, New Brunswick; delivers regasified LNG through the Brunswick pipeline for delivery into the Canadian and US gas markets via the Maritimes and Northeast (M&N) pipeline

- Both the Northeast Gateway Deepwater Port and the Neptune Deepwater Port are ocean-based LNG facilities that import LNG and provide regasification facilities. Both are located offshore of Gloucester, MA, and both connect to the Hubline pipeline in Massachusetts Bay.

With lower natural gas prices in the United States compared with global LNG supplies, no new LNG import terminals are scheduled for commercial operation in the Northeast.

#### Marcellus Shale and Other Gas Development

In the Marcellus Shale, a geographic formation in the Appalachian Basin that extends from West Virginia into Ohio, Pennsylvania, and New York, unconventional gas production has been underway using a new drilling method known as “hydraulic fracturing.” Estimates are that this formation holds between 84 and 141 trillion cubic feet (Tcf) of natural gas, but how much of that supply is economically recoverable is yet to be determined. Developing the infrastructure for this fuel, providing land and water access, and ensuring water quality are some of the challenges associated with this fuel source.

The interstate pipeline companies that serve the Appalachian region are adding numerous interconnects from the area’s large and small producers. Natural gas from the Marcellus Shale currently is flowing out of the region at almost 8 billion cubic feet per day (Bcf/d), and analysts project greater production volumes over the near term.

The region continues to receive natural gas produced from offshore Nova Scotia in eastern Canada by the deepwater Sable Offshore Energy Project (SOEP). Construction is nearing completion on the development of another nearby offshore field, Deep Panuke, which is expected to begin exporting gas in 2012. A small gas production field in New Brunswick, Canada, the McCully field of Corridor Resources, began production in 2007 and provides about 35 thousand cubic feet per day (Mcf/d) into the M&N pipeline.

Exploration for new finds continues elsewhere in the Canadian Maritime provinces and in Québec, where shale resources are estimated to be significant. Additionally, offshore Newfoundland is estimated to have considerable natural gas reserves, which also could be developed. Portions of the Northeast region, traditionally a major net consumer of natural gas, are becoming significant sources of natural gas production.

#### New Pipelines and Storage

With over 30 new pipeline and expansion projects targeted to enhance gas flows out of the Marcellus Shale, only one project, Spectra Energy’s Algonquin Incremental Market (AIM) Project, is under consideration to bring incremental gas capacity into New England. If constructed, the AIM project would enable shippers to design transportation services from multiple receipt and delivery points along the Algonquin pipeline system. Increasing Marcellus gas supplies could enable the AIM project ultimately to increase New England pipeline capacity by 350 thousand dekatherms per day (MDtd/d). Spectra’s AIM project has a possible in-service date of 2016.

El Paso Corporation recently proposed the Northeast Exchange project to add a 115-mile pipeline to the Tennessee Gas pipeline and link Tennessee Marcellus receipts with the Iroquois Gas Transmission System (IGTS). The Northeast Exchange project has a proposed capacity of 600 MDth/d and a 2016/2017 in-service date.

### The ISO’s 2011 Natural Gas Study

In support of the Strategic Planning Initiative, the ISO contracted with ICF to perform a high-level, deterministic assessment of the ability of the regional gas supply and delivery systems to serve seasonal electric power sector demands based on the economic dispatch of all generation. The main aspects of the study were as follows:

- The study assessed the gas supply available for New England’s gas-fired power generation through 2020 on peak winter and peak summer days.

- The analysis considered the gas demands of existing generators (the “reference” case scenario) and a separate scenario assuming the retirement of a portion of the non-gas-fired capacity in the region and its replacement with new natural-gas-fired capacity (the “repowering” case scenario). The study did not account for the energy-efficiency forecast (see Section 3.2), which could have reduced the simulated demand for natural gas by generating units.

- Calculations estimated the natural gas available for power generation after LDC and firm industrial load is served, assuming all natural gas infrastructure is available. Scenarios also were run assuming various natural gas infrastructure contingency scenarios (e.g., the loss of a regional natural gas pipeline or LNG infrastructure).

- The quantity of natural-gas-fired generating capacity that existing gas infrastructure can serve under each scenario was compared with the projected level of demand for natural-gas-fired generation in the region.

The analysis did not assess localized constraints that may evolve over time within New England, nor did it investigate mismatches between gas supply and demand that could result from the lack of coordination between the natural gas and electric power markets. The study also did not assess other periods of potential operational limits, such as during high maintenance periods for the pipeline system that could constrain delivery to nonfirm customers.

#### 2011 Natural Gas Study Results

The 2011 Natural Gas Study concluded that the natural gas pipeline capacity is insufficient for satisfying the economical gas needs for New England’s power plants during the next decade. Figure 7-5 shows the results for a winter peak day for gas, with all natural gas infrastructure in place and available. In this scenario, only the demand associated with existing assets is assumed (i.e., no retirements are replaced with new natural-gas-fired capacity). The results are shown for several estimates of electric power system demand.

Figure 7-5: ICF Natural Gas Study Reference Case scenario run for the existing generation fleet, winter peak-day gas supply surplus and deficits.

Note: The Reference case scenario shown was run for four cases: (1) the “Nominal” (50/50 electricity demand) gas demand forecast; (2) the “Reference” (90/10 electricity demand) gas demand forecast; (3) a “Higher” gas demand forecast (90/10 electricity demand) with a disruption to non-gas-fired capacity, such as a large nuclear or coal plant outage but high natural gas prices; and (4) a “Maximum” gas demand forecast (90/10 electricity demand) with a disruption to non-gas-fired capacity, such as a large nuclear or coal plant outage but low gas prices.

For the Reference Case scenario, existing natural gas infrastructure is insufficient to meet electric power system demand (for natural gas) for all winter study years (i.e., the winter of 2011/2012 through the winter of 2019/2020) for all electric system demand scenarios. Deficiencies reach approximately 625,000 dekatherms per day (Dth/d) in some years for the reference gas demand forecast, to as much as 1,375,000 Dth/d in the maximum gas demand forecast. A deficit of 240,000 Dth/d is estimated to be equivalent to a shortage of 1,000 MW/d, with an assumed full-load heat rate of 10,000 Btu/kWh. No shortages are expected under normal system conditions during the summer peak because gas LDC demand in the summer is minimal, opening up substantial capacity on the natural gas system in quantities that mostly exceed increased summertime power generation demand.

The ICF study also considered natural gas system contingencies for the same assumptions of natural gas and power system demand. The results showed that the complete loss of a single major interstate pipeline or liquefied natural gas facility would dramatically increase the winter-peak gas-supply deficit to power generation capacity. Under contingency conditions for the nominal winter-peak gas-demand forecast case, power system deficits range up to almost 2,000,000 Dth/d, or 8,333 MW/d of equivalent generating capacity. Under contingency conditions for the maximum winter-peak gas-demand forecast case, power system deficits range to over 2,800,000 Dth/d, or 11,666 MW/d of equivalent generating capacity.

While the study shows economic gas-fired electric generators would have shortfalls in fuel supply, power system reliability can be preserved in a number of ways. Alternate sources of electric energy from resources that do not burn natural gas would be used when shortage events are projected. These alternate sources include oil-fired generators, dual-fuel generating units using fuels other than natural gas, and imports from neighboring systems, such as New York and Canada. In addition, the region is showing growth in energy efficiency (see Section 3.2), and increased renewable sources of energy will likely develop in the region, as well (Section 7.6).

#### 2011 Natural Gas Study—Next Steps

In 2012, the ISO plans to develop another scope of work that would build on the 2011 Natural Gas Study. The 2012 Natural Gas Study will address specific comments and perform incremental analyses, as suggested by ISO Operations and regional stakeholders. Analyses may gauge the duration that gas sector deliveries to the electric power sector would be deficient under several scenarios.

In addition, ICF is developing an operational tool in 2012 that will assist ISO forecasters in populating the ISO’s seven-day forecast with projected gas unit (un)availability resulting from regional weather and known gas-sector maintenance. ISO New England also is providing input and technical assistance to NYISO as they undertake a multiregional gas study with additional assistance from PJM and the Independent Electric System Operator (IESO) of Ontario.

## Nuclear Supply Update

New England has five nuclear generating units: two in Waterford, Connecticut (Millstone), and one each in Seabrook, New Hampshire; Vernon, Vermont (Vermont Yankee); and Plymouth, Massachusetts (Pilgrim). All generating units require an operating license, which is subject to renewals or extensions, as summarized in Table 7-4.

Table 7-4
New England Operating Nuclear Power Plants

| Unit Name | Operating (OP)/ Renewed License Date | License Expiration Date | Reactor Type | Electrical Output (MWe)(a) | Reactor Vendor/Type |
| --- | --- | --- | --- | --- | --- |
| Millstone 2 | September 26, 1975/ November 28, 2005 | July 31, 2035 | Pressurized water | 884 | Combustion Engineering (vendor) |
| Millstone 3 | January 31, 1986/ November 28,2005 | November 25, 2045 | Pressurized water | 1,227 | Westinghouse/ four-loop |
| Pilgrim | June 8, 1972/ May 29, 2012 | June 8, 2032 | Boiling water | 685 | General Electric/ type 3 |
| Seabrook | OP: March 15, 1990 | March 15, 2030 | Pressurized water | 1,295 | Westinghouse/ four-loop |
| Vermont Yankee | March 21, 1972/ March 21, 2012 | March 21, 2032 | Boiling water | 510 | General Electric/ type 4 |

        - MWe stands for electrical megawatts. Nameplate electrical output was obtained from the Nuclear Regulatory Commission’s (NRC) website, http://www.nrc.gov/info-finder/reactor/.

Regarding the operation of Vermont Yankee, on January 27, 2006, Entergy, the plant’s owner and operator, applied to the Nuclear Regulatory Commission for a license extension of 20 years, and the relicensing of the facility continues to be a significant focus in the state. In early 2010, the Vermont State Senate voted 26–4 to block the Vermont Public Service Board from considering continued operation of Vermont Yankee. On April 18, 2011, Entergy filed a law suit in federal district court against the State of Vermont challenging the validity of several provisions of the state’s statutes concerning the continued operation of the plant after the expiration of its initial operating license (March 21, 2012). In a decision issued January 19, 2012, the judge ruled that provisions of Vermont state law that required approval of the legislature for issuance of a Certificate of Public Good (CPG) and permission to store spent nuclear fuel were preempted by the federal Atomic Energy Act. In these rulings, the court permanently enjoined the state from taking actions to shut down VY pursuant to these invalid state laws. The court also held that Vermont cannot condition the issuance of a CPG on an agreement to provide below-wholesale market rates to Vermont utilities.

This litigation has sparked the following ongoing actions:

Vermont appealed the district court decision, and Entergy filed a cross appeal.

Entergy petitioned the VT Public Service Board to issue a ruling on its request for a renewed CPG.

On March, 10, 2011, the NRC voted to conclude proceedings regarding the renewal of the facility’s operating license, and on March 21, 2011, the NRC issued their renewal of the license for an additional 20 years (i.e., to 2032).

- The US District Court for the District of Vermont issued an order on March 19, 2012, that prevents Vermont from attempting to shut down VY while the appeal of that court’s decision is pending.

These legal proceedings are expected to be resolved later in 2012. Vermont challenged the NRC’s decision to relicense VY claiming that the NRC could not renew the plant’s license because it lacked a necessary state water-quality certification. The D.C. Court of Appeals rejected this challenge. Refer to Section 9.5.6 for information about other Vermont’s legislative actions and energy initiatives.

On May 29, 2012, the NRC approved a 20-year license extension for Pilgrim Nuclear Power Station, authorizing its continued operation until 2032. Entergy, the plant’s owner, had submitted this relicensing application on January 27, 2006.

On June 8, 2012, the US Court of Appeals for the District of Columbia vacated NRC’s rule on temporary storage of spent nuclear fuel on site at operating nuclear power plants (Temporary Storage Rule), determining that it (and a related rule on a final geologic storage repository, the Waste Confidence Decision Update) lacked a sufficiently detailed environmental review, as required under the National Environmental Policy Act. While the NRC considers options for resolving the court decision, operating licensing and renewal proceedings, including those for Seabrook unit #1, may proceed, but the NRC has suspended the issuance of final licenses.

## Hydroelectric Update

According to DOE, approximately 2,500 dams provide 78 GW of conventional and 22 GW of pumped-storage hydro power nationwide. A recent DOE study shows that up to 12 GW of new hydro capacity could be developed at nonpowered dams, which currently do not produce electricity but provide a variety of services, such as water supply and inland navigation. This total includes 247 MW of hydro generation in New England, which has a long history of using hydroelectric resources, including the application of the first large-scale pumped storage unit in the United States. Based on the 2012 CELT Report, the forecast for 2012 installed summer capacity includes 1,483 MW of conventional hydro and 1,698 MW of pumped-storage hydro units. Over 80% of the conventional hydro dams in New England have some water storage capability that allows for peaking and ponding hydro plant operation.

Hydro resources are subject to drought and flow restrictions on water use. Many hydro projects also are subject to relicensing efforts that may limit operating flexibility because of the need to restrict water flows to address environmental or fish-passage concerns. Some of the relicensing proceedings for New England hydro projects have involved negotiations with regulators and other stakeholders regarding the retirement of some projects in exchange for increased energy production at other hydro units.

Hydro generation is a renewable resource, and units with flexible electrical and hydraulic operating characteristics can facilitate the integration of intermittent resources, such as wind power and solar photovoltaics, by providing fast-start generation, regulation, and operating reserves. Hydroelectric power also can provide black-start services, which is used for system restoration.

## Renewable Portfolio Standards and Renewable Project Development

Renewable resources can enhance the diversity of the region’s fuel supply and reduce the regional dependence on natural gas resources. Five New England states have Renewable Portfolio Standards (RPSs), and Vermont has a goal for increasing total generation from renewable resources. These RPSs represent state policy targets that load-serving entities must achieve. As discussed in this section, these LSEs can meet their states’ targets in a variety of ways. Developing renewable resources in the ISO Generation Interconnection Queue will likely be a major source for RPS compliance in the New England states.

This section summarizes the projections for RPSs and related targets through 2021, recognizing the impact of the ISO energy-efficiency forecast (see Section 3.2). The section also projects the renewable energy projects in the queue that typically would be RPS-compliant resources. The section compares the RPS targets with the queue resources, considering the uncertainty of successfully developing all these resources, and discusses other ways LSEs can meet their RPS targets. The information developed in this section does not reflect any ISO assessment of the potential of future projects to qualify for meeting the states’ RPSs.

### Renewable Resources in the ISO Generation Queue

Figure 7-6 shows the megawatts of the renewable resource projects in the April 1, 2012, queue. The 57 projects represent 3,052 MW, with wind projects making up the largest share at 84.5%. Biomass projects account for 10.4% of the total renewable capacity; hydroelectric is 3.4%; and landfill gas, solar PV, and fuel cell projects make up the remaining 1.7%. Onshore wind makes up 69.0% of the total renewable project capacity.

Figure 7-6: Proposed New England capacity from renewable resources in the ISO Generation Interconnection Queue, including non-FERC jurisdictional projects, as of April 1, 2012 (MW and %)

Note: Totals include all queue wind projects located in New England, including non-FERC-jurisdictional wind projects located outside the area administered by the ISO.

To estimate the outlook for RPS compliance from these queue projects, the ISO estimated the electric energy they typically could generate, as shown in Table 7-5. Using assumptions for typical capacity factors for the various types of renewable projects, as shown in the table, and assuming all the projects are developed and fully operating by 2021 without transmission constraints, these resources could provide approximately 10,636 GWh annually.

Table 7-5
Estimated Energy from New England Renewable Energy Projects in the ISO Queue,
as of April 1, 2012

| Type (#) of Projects | Size (MW)(a) | Capacity Factor (%)(b) | Estimated Annual Energy Production (GWh) |
| --- | --- | --- | --- |
| Hydro (9) | 104 | 25% | 228 |
| Landfill gas (1) | 28 | 90% | 221 |
| Biomass (9) | 316 | 90% | 2,491 |
| Wind—onshore (32) | 2,105 | 32% | 5,901 |
| Wind—offshore (2) | 474 | 41% | 1,702 |
| Fuel cells (1) | 9 | 95% | 75 |
| Solar PV (3) | 16 | 13% | 18 |
| Total (57) | 3,052 |  | 10,636 |

- A facility’s size is its megawatt value listed in the ISO queue.

- Capacity factors are based on the ISO’s 2007 Scenario Analysis and ISO’s NEWIS study. See http://www.iso-ne.com/committees/comm_wkgrps/othr/sas/mtrls/elec_report/scenario_analysis_final.pdf and http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/reports/2010/newis_report.pdf.

Figure 7-7 shows the percentage of electric energy from proposed New England renewable resources in the queue, including non-FERC-jurisdictional projects, as of April 1, 2012.

Figure 7-7: Estimated annual electric energy from proposed New England renewable resources in the ISO’s Generator Interconnection Queue, including non-FERC-jurisdictional projects, as of April 1, 2012 (GWh).

Note: Totals include all queue wind projects located in New England, including non-FERC-jurisdictional wind projects located outside the area administered by the ISO.

### Project Development Uncertainty

Previous RSP reports noted that many of the projects in the queue are not built for a variety of reasons, and the ISO has quantified the historical attrition of projects in the queue. Table 7-6 summarizes all projects in the ISO queue as of April 1, 2012, showing this attrition. The table shows that 55% of all projects that have entered the queue since it began have been withdrawn, including 46% of wind projects. The amounts of capacity withdrawn is 74% for wind projects compared with 70% for projects withdrawn from the queue overall.

Table 7-6
Summary of All Projects and Wind Projects in the ISO Queue as of April 1, 2012(a)

| Project Category | All Projects |  |  |  | Wind Projects(b) |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | No. | % | MW | % | No. | % | MW | % |
| Commercial | 87 | 25 | 14,432 | 20 | 10 | 12 | 524 | 4 |
| Active | 72 | 21 | 6,974 | 10 | 34 | 42 | 2,579 | 22 |
| Withdrawn | 193 | 55 | 50,821 | 70 | 37 | 46 | 8,767 | 74 |
| Total(c) | 352 | 100 | 72,227 | 100 | 81 | 100 | 11,870 | 100 |

(a) 	Because these queue values include non-FERC jurisdictional projects located outside of the area administered by ISO, they are not consistent with those presented in Section 4.

(b) 	This category includes projects in New England (including external non-FERC-jurisdictional queue projects) and ignores duplicate listings for projects with more than one potential interconnection point.

(c) 	Percentages may not sum to 100 because of rounding.

### Update of Renewable Projects Indicated by NESCOE

A NESCOE request for information (RFI) issued at the end of 2010 confirmed New England’s sufficient potential for developing and importing renewable resources for meeting the region’s renewable energy goals. The RFI identified strong interest from potential transmission and renewable resources that could be operational by 2016 to help the states cost effectively satisfy their RPSs and similar goals.

In 2011, the New England governors passed a resolution at the New England Governors Conference (NECG) confirming the governors’ continued interest in the coordinated and competitive procurement of renewable resources as a way to identify resources able to serve customers at the lowest overall delivered cost. The resolution directed NESCOE to continue to investigate the potential for the joint or separate, but coordinated and competitive, procurement of renewable resources that satisfy the New England states’ RPSs or goals. In response to this resolution, NESCOE contracted for the development of renewable resource supply curves for two study years (2016 and 2020). The study provided cost estimates for both onshore and offshore wind development and, on a high level, estimates of the transmission required to facilitate the delivery of the electricity from these resources to New England loads. This work was conducted to help signal to the states the potential ranges of “all-in” costs associated with meeting regional RPSs with new renewable projects and not ACPs.

In July 2012, the New England governors adopted another resolution directing NESCOE to take steps to implement the work plan NESCOE developed in 2012 for this coordinated procurement and directing regulatory and policy officials and the governors’ energy policy staffs to implement regulatory proceedings, procedures, or policies as necessary for executing the procurement. NESCOE plans to issue a request for proposals by December 2013 for competitive coordinated procurement of a significant amount of renewable energy. NESCOE will convene a procurement team made up of energy officials and other representatives from each state that will finalize the details of this regional procurement over the course of the next year.

### Update on Meeting State RPSs and Other Targets

The Renewable Portfolio Standards reflected in RSP12 were the standards in effect in New England through April 2012 and had not changed since being summarized in previous RSP reports. Basically, the standards set targets for LSEs to meet the future demand for electric energy using new or existing renewable energy resources. The LSEs can satisfy their RPS obligations by obtaining generation from a variety of renewable technologies, located either within New England or within adjacent balancing authority areas. They can accomplish this by acquiring Renewable Energy Certificates (RECs) from eligible renewable resources qualified by each state. REC transactions are managed using NEPOOL Generation Information System (GIS) reporting on emissions and RECs for generators in the region. LSEs that obtain insufficient RECs can make alternative compliance payments (ACPs), which also serve as a cap on the price of the RECs.

The New England states’ RPSs include technology classes for new and existing resources, and LSEs must provide their customers a specified percentage of electric energy generated by each class each year. Renewables designated as “new” resources (typically Class I RPS resources) are state specific but typically include wind, solar, hydro, biomass, landfill gas, and ocean thermal. Although the required percentage for “new” renewable resources varies by state, it increases each year and accounts for most of the growth of RPS targets in New England. Figure 7-8 shows the RPS percentage targets for “new” resources in 2021 for the five New England states with RPSs. Vermont’s Sustainably Priced Energy Development Program (SPEED), while not an RPS, includes a state goal of satisfying 20% of the state’s load with renewable energy by 2017. Technologies classified in the RPSs as “existing” technologies (typically Class II) often include hydro, biomass, and municipal solid waste plants built before a specified year. The required percentage of electric energy that LSEs must provide from this technology class is fixed. The basic RPS structure for the individual New England states has not changed significantly since RSP11 was published.

Figure 7-8: RPS state targets for "new" renewable resources in 2021.

Table 7-7 summarizes the technologies designated in the various RPSs in New England. Table 7-8 shows the annual percentages of electric energy that affected LSEs are required to provide their customers to satisfy each statewide RPS class through 2021.

Table 7-7
Technologies Designated in Renewable Portfolio Standards in New England, as of April 1, 2012

| Technology | CT Classes |  |  | MA Classes(a) |  |  | ME Classes |  | RI | NH Classes |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | I | II | III | I | IIa | IIb | I | II |  | I | II | III | IV |
| Solar thermal |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Photovoltaic (PV) |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Ocean thermal |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Wave |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Tidal |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Marine or hydrokinetic |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Hydro | <5 MW | <5 MW |  | <25 MW(a) | <5 MW(a) |  | (b) |  | <30 MW | incremental |  |  | <5 MW |
| Wind |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Biomass, biofuels | Sustainable, advanced conversion, low NOX emissions(c) |  |  | Low-emission, advanced technology(d) | (d) |  |  | (e) | Includes cofiring with fossil fuels | Low NOX, and PM emissions |  | <25 MW, low NOX, and PM emissions |  |
| Landfill gas |  |  |  |  |  |  |  |  |  | (f) |  | (f) |  |
| Anaerobic digester |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Fuel cells(g) |  |  |  | w/ renewable fuels |  |  |  |  | w/ renewable resources |  |  |  |  |
| Geothermal |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Municipal solid waste |  |  |  |  |  |  |  | w/ recycling |  |  |  |  |  |
| Cogeneration, combined heat and power (CHP) |  |  | Customer sites, minimum 50% fuel efficiency |  |  |  |  | (e) |  |  |  |  |  |
| Energy efficiency |  |  |  |  |  |  |  |  |  |  |  |  |  |

(a) The Massachusetts Green Communities Act (http://www.mass.gov/legis/laws/seslaw08/sl080169.htm) divides the state’s RPS into Class I and Class II resources, each of which allows primarily the same renewable technologies. Resources that began operating after December 31, 1997, are Class 1 renewables, and those in operation on or before that date are Class II renewables. The act also provided for an Alternative Energy Portfolio Standard (APS) for which the currently active technologies are (1) natural gas and renewably fueled CHP located in state and (2) flywheel storage. Hydropower must be certified by the Low-Impact Hydropower Institute. APS-eligible technologies are not included in the ISO’s RPS projections. On August 3, 2012, Massachusetts enacted legislation that increased the eligibility of individual hydroelectric power facilities for Class I from 25 MW to 30 MW, and for Class II facilities from 5 MW to 7.5 MW. See An Act Relative to Competitively Priced Electricity in the Commonwealth, http://www.malegislature.gov/Bills/187/Senate/S02395, (b) These resources can be pumped hydro units, and they must meet all federal and state fish-passage requirements. (c) These terms are explained in the state’s RPS legislation and regulations: Gen. Stat. of Conn. Ch. 277, §16-1. (a) 45 (Revised January 1, 2011). NOX refers to nitrogen oxides. (d) Renewable Energy Portfolio Standard-Class I, CMR, Ch. 225, Sec. 14.05.7 and 225 CMR 14.00. Massachusetts adopted more stringent eligibility requirements for new and existing woody biomass projects, including overall project efficiency and requirements to reduce GHGs  (see Section 9.5.3), http://www.mass.gov/eea/energy-utilities-clean-tech/renewable-energy/biomass/renewable-portfolio-standard-biomass-policy.html. (e) These can be high-efficiency units built through December 31, 1997. (f) This category also includes biologically derived methane gas from sources such as biodiesel, yard waste, food waste, animal waste, sewage sludge, and septage. (g) Fuel cells are a relatively new “renewable” energy technology. These units emit negligible amounts of sulfur dioxide (SO2), NOX, and particulates such that Connecticut does not require fuel cell installations to obtain air permits. For Massachusetts, an RPS fuel cell using an "eligible biomass fuel" includes landfill or anaerobic digester methane gas, hydrogen derived from such fuels, or hydrogen derived using the electrical output of a qualified renewable generation unit. As shown in the table, RPS fuel cells in Rhode Island must use eligible renewable resources.

Table 7-8
Annual Percentages of Electric Energy Provided by Affected Load-Serving Entities for Meeting the State’s RPS Classes, 2012–2021, as of April 1, 2012

| Year | CT Classes(a) |  |  | MA Classes(b) |  |  | ME Classes(c) |  | RI Classes(d) |  | NH RPS Classes(e) |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | I | I or II | III | I | IIa | IIb | I | II | Existing | New | I | Ii | III |  | IV |
| 2011 | 8.0 | 3.0 | 4.0 | 6.0 | 3.6 | 3.5 | 4.0 | 30 | 2.0 | 3.5 | 2.0 | 0.08 | 6.5 | 1.0 |  |
| 2012 | 9.0 |  |  | 7.0 |  |  | 5.0 |  |  | 4.5 | 3.0 | 0.15 |  |  |  |
| 2013 | 10.0 |  |  | 8.0 |  |  | 6.0 |  |  | 5.5 | 4.0 | 0.2 |  |  |  |
| 2014 | 11.0 |  |  | 9.0 |  |  | 7.0 |  |  | 6.5 | 5.0 | 0.3 |  |  |  |
| 2015 | 12.5 |  |  | 10.0 |  |  | 8.0 |  |  | 8.0 | 6.0 |  |  |  |  |
| 2016 | 14.0 |  |  | 11.0 |  |  | 9.0 |  |  | 9.5 | 7.0 |  |  |  |  |
| 2017 | 15.5 |  |  | 12.0 |  |  | 10.0 |  |  | 11.0 | 8.0 |  |  |  |  |
| 2018 | 17.0 |  |  | 13.0 |  |  |  |  |  | 12.5 | 9.0 |  |  |  |  |
| 2019 | 19.5 |  |  | 14.0 |  |  |  |  |  | 14.0 | 10.0 |  |  |  |  |
| 2020 | 20.0 |  |  | 15.0 |  |  |  |  |  |  | 11.0 |  |  |  |  |
| 2021 | 20.0 |  |  | 16.0 |  |  |  |  |  |  | 12.0 |  |  |  |  |
| Use GIS to track RECs? | Connecticut, Massachusetts, Maine, Rhode Island, and New Hampshire all use the Generator Information System to track Renewable Energy Certificates. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Purchase of RECs from outside ISO New England allowed? | Yes, from adjacent areas, with confirmation of delivery of energy from the renewable energy source and reciprocal RPSs for NY, NJ, PA, MD, and DE |  |  | Yes, from adjacent areas, with confirmation of delivery of energy |  |  | Yes, from adjacent areas |  | Yes, from adjacent areas |  | Yes, from adjacent areas, with confirmation of delivery of energy from the renewable energy source |  |  |  |  |

(a)	All Connecticut Class I technologies except LFG and fuel cells can be used to meet Class II requirements. For Class III, CHP facilities can be used to offset generation on the grid with the more efficient on-site use of fuel.

(b)	Class I includes a “carve-out” that must be satisfied by Solar RECs (SRECs) from post-2007, behind-the-meter PV resources, limited to no more than 6 MW (using the nameplate capacity—the megawatt capability designated by the manufacture per parcel of land. Class IIa is a minimum percentage for existing pre-1998 vintage resources using the same technologies as Class I but with hydro limited to no more than 5 MW (nameplate capacity) per facility. Class IIb is a minimum percentage for pre-1998 vintage waste-to-energy plants that meet certain Massachusetts-specified recycling and other regulations.

(c)	The 30% requirement refers to electric energy delivered to affected LSEs.

(d)	Existing resources can make up no more than 2.0% of the RPS percentage.

(e)	As of April 1, 2012, the NH RPS policy increases Class I resources an additional 1% per year from 2015 through 2025. Classes II to IV remain at the same percentages from 2015 through 2025. Legislation enacted in June 2012 designates a portion of the Class I requirement that must be met with “thermal energy resources,” reduces the incremental increase in annual Class I requirements between 2015 and 2025, adds an incremental increase to the Class III requirements for 2014 and 2015, and adds an incremental increase to the Class IV requirements for 2013 through 2015. See Section 9.5.4.

#### RPS Projection Method Overview

Using the ISO’s 2012 state forecasts for energy use (see Section 3), the ISO has developed projections of the state RPS targets for the 10-year period, 2012 to 2021. The ISO generated the projections using an updated spreadsheet based on one first developed with stakeholder input in 2010, which details the New England regional RPS projections for the five states and Vermont’s renewable goal. This section describes the assumptions used, explains how the 2012 projections were calculated, and summarizes the results.

The RPS projections for 2012 used the ISO’s 2012 CELT forecast for states’ growth in electric energy use and include assumptions for the total municipal suppliers’ share of each statewide energy forecast, passive demand resource levels (through FCA #6), and statewide energy targets applicable to the RPS for each state. For 2015 to 2021, the 2012 energy-efficiency forecast (see Section 3.2) was used to project state energy-efficiency reductions beyond the FCA #6 timeframe. Figure 7-9 illustrates the amount of passive demand resources in gigawatt-hours forecast for each New England state in the 2012 CELT, which total 17,409 GWh of energy reductions in 2021.

Figure 7-9: Passive demand resources in the 2012 CELT, 2012 to 2021 (includes energy-efficiency forecast, 2015 to 2021) (GWh).

#### Projection Results for Meeting State RPSs and Other Targets

Assuming the energy reductions from the passive demand resources in the 2012 CELT forecast, which for 2021 account for an 11.6% reduction in total energy use, LSEs would provide 30,420 GWh of supply-side renewable energy to meet the RPS targets and Vermont’s renewable goals by 2021. This would represent 20.2% of the region’s projected electric energy use. Thus by 2021, 31.8% of the region’s projected electric energy consumption (11.6% plus 20.2%) would be met by energy efficiency, RPS targets, and related goals for renewable energy.

Figure 7-10 illustrates the ISO’s total projected RPS electric energy targets for all RPS classes plus Vermont’s goal for renewable resources. The figure shows that by 2021 the RPS classes for “new” resources represent approximately two-thirds of all the RPS energy targets in the region.

Figure 7-10: Total projected RPS targets (all classes) and goals for New England, 2012 to 2021 (GWh).

Figure 7-11 shows the incremental growth in the “new” RPS state targets in gigawatt-hours beyond 2011. Because the 2011 RPS targets are assumed to be met by “existing” renewable projects, the incremental growth in the “new” RPS targets indicates the amount of renewable projects that must be developed in the future. The results project that by 2021, the RPS targets for “new” resources will grow to 12,147 GWh.

Figure 7-11: Incremental growth in the RPS class targets for the "new" renewable resources for the New England states, net of 2011 RPS targets, 2012 to 2021 (GWh).

While the ISO recognizes that generation from renewable resource projects outside the queue can meet the region’s RPSs, this section focuses on New England’s renewable projects in the ISO queue. These resources could provide the principal supply of projects for meeting the RPS growth over the next 10 years. However, given the historical attrition rate for projects in the queue (refer to Table 7-6), the number of these projects that ultimately will be built is uncertain.

Figure 7-12 shows ranges of uncertainty in the amounts of electric energy that projects in the queue could provide for meeting the RPS targets over the planning period, assuming that projects may not be successful and are withdrawn from the queue. Although historical queue statistics indicate that a higher-percentage buildout of total queue renewable energy is unlikely, 80% and 100% values also are shown for comparison. The figure shows that 40% of the electric energy from queue projects would meet the increase in the RPS targets for renewable resources through 2014. Similarly, roughly 80% of the renewable energy in the queue would meet the RPSs through 2017, and a buildout of the entire queue would satisfy the RPSs and related targets for 2018. Note that because most renewable projects have a short lead time of a few years, they do not need to enter the queue until they are in the later stages of development. The development of renewable projects, such as those in the early stages of development that responded to the NESCOE RFI, would likely occur at a greater rate than the historical development of renewable projects in the queue.

Figure 7-12: Estimated incremental electric energy from meeting new RPS targets (2012 to 2021) compared with estimated electric energy from various percentages of new renewable projects in the ISO queue as of April 1, 2012 (GWh).

In addition to queue resources, other potential contributions to satisfying the RPSs and other policy targets include the development of “behind-the-meter” distributed generation (DG) projects (see Section 7.6.6), the conversion of existing generation to use qualified REC-eligible fuels, and the purchase of RECs from projects in neighboring balancing authority areas. Additionally, energy-efficiency development in excess of the 2012 CELT passive demand resource forecast would further reduce the need for supply-side RPS resources. Alternatively, the affected LSEs can make alternative compliance payments to the states’ clean energy funds, which help finance new renewable projects.

While the development of renewable variable energy resources will help meet the RPS and other policy targets and will enhance fuel diversity, it may also increase the need for flexibility from system resources, especially during stressed operating conditions, as indicated in the ISO’s Strategic Planning Initiative. (Refer to Sections 6.1 and 6.2 for a discussion on how this concern is being addressed.) The ISO continues to analyze renewable resource development through its economic study requests (Section 8.2), resource developer requests for interconnection, and planning studies conducted in support of the Strategic Planning Initiative.

### Wind

As of April 1, 2012, 524 MW of wind power was operating in the region. In terms of public policy, wind energy was the fastest-growing source of RECs in the region from 2005 to 2010, when it became the largest source of the region’s RECs (approximately 39%). While wind generation can provide many system benefits, it also poses unique challenges stemming from the variability of wind resources, the need to accurately forecast wind generation, and the need to develop transmission to access wind resources remote from load centers. This section discusses the ISO’s comprehensive New England Wind Integration Study, conducted in 2010, that provided insights on these issues.

NEWIS highlighted the operational effects of large-scale wind integration in New England, including the effects of wind forecasting and large-scale wind power on the rest of the generation fleet. The study captured the unique characteristics of New England’s electrical power system and wind resources—including historical load and ramping profiles, geography, topology, supply- and demand-side resource characteristics, and wind profiles—and the unique impacts that these characteristics can have on system operations and planning as wind power penetration increases. The study simulated the addition of up to 12,000 MW of wind resources and the conceptual development of a transmission system that can integrate large amounts of these resources. The completed study developed models of various penetrations and geographic layouts of wind generation for hypothesized wind plants suitable for ISO study.

NEWIS results showed that the large-scale integration of wind resources is feasible in the New England region and that transmission will need to be developed to access the locations where onshore wind generation is likely to be built. The study also showed that adding large-scale wind generation, with its characteristic low operating costs, would likely displace energy produced by older oil-fired generating units and reduce generation levels for natural gas generating units. Wholesale electric energy market revenues for all resources would be reduced, but more for some than others. The net energy market revenues for natural-gas-fired resources would decrease, potentially making these units uneconomical and not available to supply system needs if they retired. Thus, these resources could need additional sources of revenue, possibly by modifying the markets, to preserve these units for providing reliability services as required.

According to the study, the system also will need increased operating reserve, regulation, and other ancillary services for integrating large amounts of wind generation, and the market design may need to evolve to provide incentives for resources to add this flexibility, especially if energy revenues decrease. Another finding was that the need for increased regulation and reserves varies as a function of the extent of wind integrated into the system. For example, the conservative estimates contained within NEWIS show that the systemwide regulation requirements could more than triple if wind were to provide up to 20% of the region’s annual energy, while the regulation impacts would be very modest at 2.5% of the annual energy. Similarly, the need for additional systemwide operating reserve may increase from 2,250 MW to 2,758 MW at 20% wind energy penetration, while it may only increase to 2,270 MW at 2.5% wind energy penetration.

NEWIS recommendations and the timing of their implementation are linked to the growth of wind resources in the region. While some NEWIS recommendations currently are being implemented, the modest growth of wind resources in the region to date has deferred the need for implementing others in the near term. The majority of near-term recommended actions were derived from the NEWIS Task 2 report, which outlined technical requirements for wind generation interconnection and integration. The following are some of the recommended actions either underway or being considered as wind penetration grows in the region:

- A centralized, regional wind power forecasting system, which will support the reliable and efficient integration of wind resources, currently is under development and is scheduled to be in service in early 2013.

- Interconnection requirements for wind generators are being updated and implemented.

- As wind penetration grows, existing methods for calculating capacity values will continue to be monitored and may be modified to improve the accuracy of the estimated capacity values for large increases in wind generation.

The balance of the integration efforts will be prioritized and completed through the ISO’s stakeholder process. NEWIS recognized the need for supplemental analyses, such as detailed stability analyses, to integrate large amounts of wind generating units successfully. Ultimately, NEWIS and supplemental results will serve as the basis for regional policies and practices by the ISO, wind project owners, and interconnecting transmission owners and may result in changes to the ISO tariff, operating procedures, and manuals.

### Distributed Generation

Several states throughout New England have specific goals or funding designated for distributed generation projects. Distributed generators are a subset of demand-side resources and consist of relatively small-scale sources of power (i.e., several kilowatts to tens of megawatts in capacity) connected to the grid at the distribution or substation level. DG technologies include both renewable resources (e.g., solar PV, wind turbines, fuel cells, biomass, and small hydro) and conventional resources (e.g., diesel reciprocating engines and gas turbines). Conventional DG resources also may include combined heat and power (CHP) systems that use the waste heat from generating electricity to provide heat for buildings or for industrial purposes. DG resources differ from generating resources connected to the transmission system in that they are neither observable nor able to be dispatched by the regional system operator and, therefore, effectively are a modifier of system load. Where installed, intermittent DG resources (solar and wind) modify the load in response to the weather. DG also affects the load characteristics in response to system deviations in frequency and voltage.

Between 2005 and 2011, more than 2,700 distributed generators were interconnected in Connecticut, totaling 304 MW. Considering the significant funding designated for the long-term procurement of in-state zero- and low-emission distributed generators, these resources seem poised for significant growth in Connecticut over the next decade (see Section 9.5.1). In Massachusetts, more than 1,200 projects, totaling 700 MW of cumulative capacity, have applied to interconnect with the distribution utilities between March 2009 and December 2011. Vermont’s Standard Offer Program had 21 operating distributed generation projects, totaling about 8.6 MW by the end of April 2012, and has a program goal of 127.5 MW over the next decade.

Net metering is a billing arrangement between a distribution utility and an end-use customer that allows the customer to be charged for the net of electricity consumed and energy produced by a DG facility, thereby effectively allowing DG resources to be credited at near retail rates. While all six New England states have net-metering rules (listed in Table 7-9), these rules vary considerably throughout the region and in significant ways, such as in the DG technologies eligible, the limits on system size, and the limits on aggregate in-state net-metered capacity. For example, Connecticut and Maine have no specified limits on aggregate net-metered capacity in their states, whereas New Hampshire has a 50 MW limit. Because net metering is a policy aimed at promoting direct investment in customer-sited generation (especially renewable resources), such capacity limits represent the maximum capacity currently supported by this policy in each state.

Table 7-9
State Net-Metering Rules for Distributed Generation(a)

| State | Eligible Renewables/Other Technologies | Applicable Sectors | Applicable Utilities | Limit on System Capacity | Limit on Aggregate Capacity |
| --- | --- | --- | --- | --- | --- |
| CT | Solar thermal electric; PV; LFG; wind; biomass; hydro and small hydro; fuel cells, including those using renewables; MSW; tidal energy; wave energy; ocean thermal | Commercial; industrial; residential; nonprofits; schools; local, state, and federal. gov’t; multifamily residential; agricultural; institutional | Investor-owned utilities | 2 MW | No limit specified |
| ME | Solar thermal electric; PV; wind; biomass; hydro and small hydro; geothermal electric; fuel cells, including those using renewables; MSW; CHP/cogeneration; tidal energy | Commercial, industrial, residential | All utilities | 660 kW for IOU customers; 100 kW for muni and co-op customers (munis and co-ops may voluntarily offer net-energy billing for systems up to 660 kW) | No limit specified |
| MA | Solar thermal electric; PV; wind; biomass; hydro and small hydro; geothermal electric; fuel cells, including those using renewables; MSW; CHP/cogeneration; anaerobic digestion; other DG technologies | Commercial; industrial; residential; nonprofits; schools; local, state, and federal gov’t; agricultural; institutional | Investor-owned utilities | 10 MW for net metering by a municipality or other governmental entity; 2 MW for all other "Class III" systems; 1 MW for all other "Class II" systems; 60 kW for all other "Class I" systems | 3% of utility's peak load in general; 3% of utility's peak load for net metering by municipalities or governmental entities(b) |
| NH | PV, LFG, wind, biomass, hydro and small hydro, geothermal electric, CHP/cogeneration, tidal energy, wave energy, biodiesel, other DG technologies | Commercial, industrial, residential | All utilities | 1 MW | 50 MW |
| RI | Solar thermal electric, PV, wind, biomass, hydro and small hydro, geothermal electric, anaerobic digestion, ocean thermal, fuel cells using renewables | Commercial; industrial; residential; nonprofits; schools; local, state, and federal gov’t; multifamily residential; agricultural; institutional | Investor-owned utilities | 5 MW (systems must be "reasonably designed" to generate only up to 100% of annual electricity consumption) | 3% of peak load (2 MW reserved for systems under 50 kW) |
| VT | Solar thermal electric, PV, LFG, wind, biomass, hydro and small hydro, CHP/cogeneration, anaerobic digestion, fuel cells using renewables | Commercial; residential; nonprofits; schools; local, state, and federal gov’t; agricultural, institutional | All utilities | 2.2 MW for military systems; 20 kW for micro-CHP; 500 kW for all other systems | 4% of utility's 1996 peak demand or peak demand during most recent calendar year (whichever is greater). |

(a) 	Interstate Renewable Energy Council; updated state net-metering rules are available at http://www.irecusa.org/irec-programs/connecting-to-the-grid/net-metering/ (accessed May 2012).

(b) 	Massachusetts’ net metering rules have been updated to reflect the August 3, 2012, legislative changes affecting the limits on aggregate capacity for utilities, municipalities, and governmental entities.

#### Solar

Solar photovoltaics directly convert sunlight to direct-current power and use an inverter to convert the DC power to nominal power system frequency to be either used by the owner or injected into the grid. Advances in PV technology, PV manufacturing practices, and growing PV installation experience have significantly reduced the installed costs for PV over the last decade. The US Department of Energy’s (DOE’s) SunShot Initiative aims to reduce the total installed cost of solar energy systems by 75% by 2020.

In recent years, the region’s solar photovoltaic resources have grown, and their continued growth is anticipated. As the New England states reach hundreds of megawatts of installed solar capacity, solar PV will begin to have a measurable impact on the power system load and operation. The number of solar PV projects seeking interconnection has increased, especially in states with solar-specific goals or funding for distributed energy technologies. Massachusetts’ Green Communities Act allows electric utilities to own up to 50 MW of solar PV installations and establishes a “solar carve-out” target of 400 MW PV installed capacity by 2020. Eligible projects can earn solar RECs (SRECs). By April 2012, approximately 100 MW of solar PV was operating in Massachusetts, and more than 400 MW of additional PV was seeking interconnection.

In Connecticut, Public Act 11-80 is anticipated to stimulate significant growth of in-state PV over the next decade (see Section 9.5.1). This growth could include 30 MW of residential PV, two 5 MW projects currently under development, and up to an additional 250 MW that could be spurred by the long-term contracts for RECs from “zero emission” Class I renewable energy sources (a.k.a. “ZRECs”).

New Hampshire’s Class II RPS requires PV to meet 0.3% of the state’s load by 2015. This requirement creates a solar REC market that can be satisfied by any regional PV resource. Approximately 8 MW of regional PV currently is registered as eligible Class II generators, and meeting this RPS in 2015 will require an estimated total of 25 MW PV.

Currently, more than 11 MW of PV are installed in Vermont. Of the 127.5 MW goal of Vermont’s Standard Offer program, approximately 40 to 50 MW are anticipated to be PV. However, PV projects developed under the SPEED program are not required to retire their RECS to comply and therefore are allowed to sell the associated RECs to satisfy another state’s RPS program. This means that Standard Offer PV projects can sell their RECs to satisfy New Hampshire’s solar-specific Class II RPS or another Class I RPS in the region, effectively enabling their generation to be counted twice.

As part of legislation passed in 2011, Rhode Island’s “Distributed Generation Standards Contracts” will spur the growth of 40 MW of in-state DG over the next few years, including PV development. While how much of the 40 MW will be PV is unclear, approximately 25 MW of PV may be developed under this program over the next few years, owing to technology ceilings established for the first two contract-procurement enrollment periods.

While some PV development has occurred in Maine, unlike other New England states, Maine currently has no existing solar-related goals or state funding that will support significant growth of PV.

Table 7-10 summarizes the estimates for potential future PV development by state in the region using the results of a survey of existing state policies, funding in the region, and trends in PV development. As indicated, aggregate PV capacity could reach 800 MW by 2021.

Table 7-10
Summary of Estimates for Potential PV Development in 2021 by State(a)

| State | Capacity Installed by End of 2010 (MW)(b) | Total Estimated Potential PV Development by end of 2021 (MW) | Assumptions/Notes |
| --- | --- | --- | --- |
| Connecticut | 24.6 | 280 | Based on estimated growth of in-state PV resources summarized in CT's 2012 Integrated Resource Plan, June 2012 (Appendix D) |
| Massachusetts | 38.2 | 430 | Assumes solar carve-out is achieved; 30 MW of installed PV is not counted toward carve-out |
| Maine | 0.3 | 5 | Assumes statewide average annual growth rate of <0.5 MW/yr |
| New Hampshire | 2 | 10 | NH Class II RPS drives growth of approximately 25 MW in region; some is built in VT as part of VT SPEED, and some may be sold as RECs as part of NH Class II. Assumes statewide average annual growth is <1 MW/yr. |
| Rhode Island | 0.6 | 25 | Assumes approximately 25 MW of distributed generation contracts will be solar and PV will not grow after 2014 contracts are satisfied. |
| Vermont | 2.9 | 50 | Assumes approximately 45 MW PV are developed as part of the Standard Offer program. |
| Regional total | 68.6 | 800 |  |

- Estimated solar capacities represent nameplate direct-current capacities.

- Larry Sherwood, U.S. Solar Market Trends 2010 (Interstate Renewable Energy Council, June 2011), http://irecusa.org/wp-content/uploads/2011/07/IREC-Solar-Market-Trends-Report-revised070811.pdf.

Based on information from the NEPOOL GIS, Figure 7-13 illustrates the electric energy generated by solar PV installations in New England by quarter from 2005 to 2011 and depicts a more than 125% annual growth in PV output since 2008. Of the more than 65 GWh of PV generation registered within the NEPOOL GIS for 2011, only 10 GWh of PV are listed in ISO energy settlements for the same period, suggesting that approximately 15% of the operational PV in the region was registered in the ISO’s wholesale energy market in 2011. Although the region currently has only a small amount of PV relative to the size of the regional electric system, the ISO will continue its proactive tracking of this resource and the potential operational issues that may emerge as this resource continues to grow.

Figure 7-13: Solar PV energy generated in New England by quarter, 2005 to 2011, based on NEPOOL GIS data.

Note: According to NEPOOL GIS, all solar PV listed is located within the ISO New England Balancing Authority Area; see https://www.nepoolgis.com/.

#### NERC Integrated Variable Generation Task Force, Task 1-8

As part of its Task 1-8 activities, NERC’s Integrated Variable Generation Task Force (IVGTF) (see Section 9.2.2.2) is evaluating potential reliability concerns regarding the bulk system arising from the integration of large amounts of distributed resources, such as distributed solar PV, plug-in electric vehicles, distributed electric storage, and demand-response programs. Using the results of its work thus far, the IVGTF has identified a number of ways that high levels of distributed resources potentially can affect the reliability and operations of the bulk system, including the following:

- General lack of observability and controllability of DG

- Nondispatchable ramping and variability issues

- Response to faults: the lack of low-voltage ride through, lack of frequency ride through, and coordination with IEEE 1547 interconnection standards for DG

- Forecast of apparent net load seen by the transmission system

While the current amount of distributed resources is relatively small, the ISO will continue to track the regional growth of DG and other distributed resources and their potential impacts on its operation of the region’s transmission system, market administration, and its long-term planning of the system.

## Conclusions

Electric energy production in New England in 2011 shows the continued prevalence of natural gas, which produces 51.3% of the energy, and nuclear, which produces 28.4%. Hydroelectric is at 6.8%; coal, 5.9%; other renewables, 5.4%; pumped storage, 1.0%; and petroleum, <1%. Coal- and oil-fired generators over 40 years represent almost 6 GW of existing regional capacity, and many units are expected to retire by 2021. The ISO has initiated a study to quantify the impact of this transition.

Improved coordination between natural gas pipeline operators and the ISO is expected to minimize the adverse reliability consequences of fuel-shortage events, and the ISO continues to leverage experience from operating events in the past year, including adverse weather and decreased availability of LNG. Natural-gas-related operational and economic risks have been identified, and the ISO is working with stakeholders through the Strategic Planning Initiative to address fuel diversity needs.

With the growing reliance on natural gas for electric power generation, the ISO commissioned a gas study to assess both the adequacy of projected natural gas supply and the delivery system (pipeline and liquefied natural gas). The 2011 Natural Gas Study considered a variety of scenarios on winter peak and summer peak days through 2020, concluding that existing natural gas pipeline capacity into the region is insufficient for satisfying economical gas supply needs of electric power generators over the next decade. The study did not account for the energy-efficiency forecast, which could have reduced demand, but it did consider scenarios that replaced retired coal- and oil-fired generation with new natural-gas-fired capacity.

While the 2011 Natural Gas Study indicates supply shortfalls over the next decade, various options exist for preserving power system reliability. These options include diversifying the fuel supply and securing greater access to imports of electric power from neighboring systems. The development of Marcellus Shale is a promising new supply of natural gas, but additional development of pipelines would be required for New England to take greater advantage of this supply source.

The addition of intermittent renewable resources can provide additional fuel supply diversity; however, reliably integrating variable energy resources into the system requires additional planning and coordination with the operation of the natural gas system. The New England states have targets for the proportion of electric energy that renewable resources, such as wind and solar, and demand resources, such as energy efficiency, must provide. Assuming the energy reductions from the passive demand resources in the 2012 CELT forecast, energy efficiency and renewable energy would serve to meet 31.8% of the region’s projected electric energy consumption by 2021. This percentage includes an 11.6% reduction in the region’s projected electric energy consumption in 2021 because of passive demand resources, as reported in the CELT, and 20.2% of RPSs and policies addressing renewable supply targets and goals. To facilitate the integration of variable wind resources into the generation mix, the ISO is scheduled to implement a centralized, regional wind power forecasting system by early 2013, which was identified as a priority in the New England Wind Integration Study.

Several New England states also have specific goals, policies, or funding designated for distributed generation, especially renewable resources, and the number of DG projects seeking interconnection to the distribution system has dramatically grown over the last few years, particularly solar PV projects. DG resources are neither observable nor able to be dispatched by the bulk system operator and, therefore, effectively are modifiers of system load. Where installed, distributed solar PV and wind power are intermittent resources that modify the load in response to the weather. The ISO will continue to evaluate the growth of the region’s solar and other DG resources and the potential operational and planning issues that may emerge as this growth occurs.

# Environmental and Economic Performance of the System

Existing and planned federal, regional, and state environmental regulations and policies have an impact on generator operations, which in turn affect the wholesale electricity markets. This section summarizes major environmental initiatives expected to affect the environmental and economic performance of the system, altering generator availability and leading to fuel switching or the replacement of capacity. This section also discusses the economic studies requested by stakeholders to evaluate future scenarios of resource development, retirements, and transmission system constraints.

## Environmental Performance of the System

Federal, regional, and state environmental regulations have always had an impact on the operations and costs for New England generator owners, who must adjust their compliance plans and permits as these regulations evolve. As part of its system planning process, the ISO provides annual updates to its stakeholders of upcoming changes to environmental regulations that could or will likely affect generator operations in the region and system reliability. The ISO also updates its stakeholders about total generator air emissions in the region and regional emission rates.

This section summarizes the emission trends of the New England generators, showing historical progress in reducing regional air emissions resulting from the use of cleaner fuels to generate electricity, improvements in end-use energy efficiency, and the implementation of emission control technologies. The section also provides an update of upcoming air, water, and waste disposal regulations and developments with the potential to affect electric power generators in New England and neighboring areas over the next 10 years. The section summarizes the developments of major US Environmental Protection Agency (EPA) proposed and final regulations. It also summarizes selected state regulations and provides a status of climate change programs, including the Regional Greenhouse Gas Initiative (RGGI). For some generators, these regulations could require the addition of control technologies; for others, the regulatory impacts could lead to retirement or repowering. Refer to Section 7.6 for a discussion of the development of renewable resources in the region, and Section 3.2 for a discussion of the energy-efficiency forecast.

### Potential Regional Impacts of EPA Regulations

EPA has finalized or is in the process of finalizing a suite of environmental regulations under the Clean Air Act, the Clean Water Act, and the Resource Conservation and Recovery Act (RCRA) that will affect existing coal-, oil-, and gas-fired steam generators across the region. Between 2012 and 2021, these regulations could require generators to incur significant capital costs for environmental-compliance retrofits, which could restrict operation and result in the retirement or repowering of certain generators. Regulatory obligations also may change in response to litigation, such as with the overturning of the Cross-State Air Pollution Rule (CSAPR), which could affect certain generators in the region. If the CASPR vacator is sustained, larger fossil-fired generators in Connecticut and Massachusetts will remain subject to the predecessor transport rule, the Clean Air Interstate Rule (CAIR), while EPA determines how to proceed, which ultimately could result in additional emissions reduction requirements for generators. In total, future compliance retrofits could include adding post-combustion control devices, modifying cooling water intakes, switching to closed-cycle cooling systems, or switching fuels. The ISO estimates that, in total, these regulations would affect over 12.1 GW of installed capacity across New England.

Various court orders have required EPA to finalize these rules and implement them between January 2012 and January 2016. The Mercury and Air Toxics Standards Rule (MATS) went into effect on February 16, 2012, and most generators must comply by April 17, 2015. The Cooling Water Intake § 316(b) Rule was scheduled to be finalized by July 27, 2012; however, EPA negotiated a deadline extension of until June 27, 2013, for issuance of the final rule. Generators must comply within eight years after the effective date of this final rule.

The Clean Air Act and Clean Water Act require states to ensure that regulated entities comply with various standards and, potentially, to take regulatory actions to require additional controls of air pollution and water discharges from generators. Table 8-1 summarizes the new and upcoming environmental regulations, their targeted pollutants, and the likely control technologies considered most suitable.

Table 8-1
New and Upcoming EPA Environmental Regulations,
Targeted Pollutants or Actions, and Control Options

| Proposed EPA Regulation | Targeted Pollutant or Impact | Control Options |
| --- | --- | --- |
| Clean Air Act § 112 Mercury and Air Toxics Standards Rule | Hazardous air pollutants: - Mercury (Hg) - Hydrogen chloride (HCI) - Hydrogen fluoride (HF) - Metals - Organics | - Hg removal: - Fabric-filter baghouse (FF)(a) - Activated carbon Injection (ACI), 80-90%(b) - Scrubber—selective catalytic reduction (SCR) cobenefit, >90%(c) - Wet or dry flue-gas desulphurization (FGD)(d) - Dry sorbent injection (DSI)(e) - Fuel switching |
| Clean Air Interstate Rule | Reduction of ozone and fine particulate matter (PM2.5) in nonattainment areas and in areas downwind from nonattainment areas | - NOX removal: - SCR, 70–95% - Selective noncatalytic reduction (SNCR), 30–50%(f) |
| Clean Air Act § 110 Transport Rule (to be proposed) |  | - SO2 removal: - Scrubber ≥95% - Dry sorbent injection, <70% |
| Resource Conservation and Recovery Act (RCRA) Coal Combustion Residue Rule (Coal Ash)(g) | Disposal of coal combustion waste | - Phase out of wet-surface impoundments (ash ponds) - Composite liners - Other design requirements for disposal sites or unit retirements |
| Clean Water Act § 316(b) Cooling Water Intake Rule | Cooling water intake | - Intake design upgrades - Cooling water intake structure retrofits - Closed-cycle cooling towers |
| Clean Water Act § 304(b) Wastewater Rule | Waste water toxic metals | Treatment or zero discharge |

(a) 	Fabric-filter collection system (FF), or baghouse, is a post-combustion particulate control system that traps particles in cylindrical or square filter elements, which are cleaned periodically to remove trapped particles.

(b) 	Activated carbon injection (ACI) is a post-combustion Hg control system that injects specially treated activated carbon into the flue gas where it absorbs Hg that is then removed by a downstream particulate-control device. This technology can remove 80 to 90% of mercury emissions.

(c) 	Selective catalytic reduction (SCR) is a post-combustion NOX control technology that treats flue gas with ammonia (NH3) as it enters a catalyst reactor. The NH3 reacts with NOX, removing greater than 90% under optimal conditions.

(d) 	Flue-gas desulfurization (FGD) (i.e., wet or dry scrubbing) is a post-combustion control system for SO2 and other acid gases that injects a type of lime, using wet or dry means, into the flue gas, where it reacts with the SO2 and other gases. The reaction products are then removed, either in the scrubber or in conjunction with a downstream particulate control device. This process can remove over 90% of acid gas emissions and over 95% of the SO2 emissions. Wet scrubbers, in conjunction with upstream SCR, have achieved 90% Hg emission removal for systems firing bituminous coal.

(e) 	Dry sorbent injection (DSI) is a post-combustion SO2 control system that injects dry sorbent reagents containing either sodium bicarbonate or sodium carbonate into the flue gas where it reacts with SO2 and other acid gases. Systems equipped with DSI and a suitable downstream particulate-control device can remove 30 to 90% of SO2 flue gas along with 90% of other acid gases.

(f) 	Selective noncatalytic reduction (SNCR) is a post-combustion NOX control technology that treats flue gas with ammonia or urea and can remove greater than 30% of NOX in the flue gas under optimal conditions in a temperature range between 1,800 and 2,000°F.

(g) 	The proposed Coal Ash Rule affects waste disposal sites receiving combustion wastes from coal-fired units nationwide, but New England has no active ash storage sites.

#### Potential Impacts in New England of the Proposed Cooling Water Intake Rule

Cooling water intake structures (CWISs) can cause significant adverse environmental impacts by drawing juvenile and adult fish, shellfish, and other aquatic organisms into facility cooling systems and causing them thermal, mechanical, or chemical harm. EPA has concluded that existing measures are inadequate to protect aquatic life as required under the Clean Water Act.

The potential Cooling Water Intake § 316(b) Rule could affect CWISs at thermal generating stations (using fossil or nuclear fuels) with a cooling water design intake over 2 million gallons per day (MGD). EPA estimates that 30 existing fossil and nuclear electric power generating facilities in New England are subject to the proposed rule. Table 8-2 shows statistics for all water-cooled capacity by New England state and identifies the amount that use once-through cooling. These facilities are the most likely to require upgrades, as shown on Table 8-1.

Table 8-2
New England Capacity Potentially Affected by EPA’s Proposed Cooling Water Intake Rule and the Amount of Once-Through Water Cooling Technology Used, 2010 (MW, %)(a)

| State | Total Water Cooled Capacity (MW) | Total Once-Through Water-Cooled Capacity (MW) | % of Water Cooled Capacity Using Once-Through Technology |
| --- | --- | --- | --- |
| CT | 5,578 | 4,558 | 82% |
| MA | 5,850 | 4,877 | 83% |
| ME | 2,068 | 821 | 40% |
| NH | 3,939 | 2,236 | 57% |
| RI | 447 | 447 | 100% |
| VT | 604 | 604 | 100% |

Sources: Cooling technology identified using EIA’s Form EIA-860 detailed data, “EnviroEquipY2010,” (2010), http://205.254.135.7/electricity/data/eia860/index.html. Capacity is summer claimed capability, CELT 2012.

Under the proposed rule, 12.1 GW of installed capacity in New England potentially would be required to collect and submit performance data to regulators to determine needed upgrades to impingement mortality control technologies. Generators that did not already have impingement-mitigation technology or designs already installed, including barriers or operational changes, would need to submit these data. Depending on the performance data collected, facilities would be required to adopt measures for reducing the entrapment of aquatic life against the outside surfaces of CWISs or screening devices.

EPA’s preferred entrainment-mitigation option requires electric power generating facilities with 125 MGD or higher once-through cooling water systems to prepare and submit an entrainment-characterization study for determining whether they would need to retrofit to closed-cycle cooling systems. These facilities would need to follow an expedited schedule for submitting CWIS performance data to regulators.

In New England, approximately 5.6 GW of installed capacity are equipped with CWISs in with a design intake greater than 125 MGD. The need for the region’s larger thermal electric generating facilities to convert once-through cooling to closed-cycle systems most likely would be known within five years or less. The ISO estimates that approximately 1 GW to 3 GW of the 5.6 GW subject to the additional requirements of EPA’s preferred option may retire between 2018 and 2020, rather than retrofit to closed-cycle cooling systems. In June 2012, EPA proposed additional impingement mitigation options that may offer some affected facilities greater flexibility in complying with the § 316(b) requirements for reducing impingement mortality.

In New England, National Pollutant Discharge Elimination System (NPDES) permit renewals already have required electric generating facilities to retrofit existing cooling water intake structures with closed-cycle cooling. One facility with a once-through CWIS with a 1,345 MGD design capacity completed a retrofit to a closed-cycle system with two natural draft cooling towers. The capital cost of this project is $570 million, or $370/KW, and is expected to reduce cooling water intake flow and thermal discharges by roughly 95%. Another generator in New England served by a once-through CWIS received a draft NPDES permit proposing a retrofit of a closed-cycle cooling system using a mechanical draft cooling tower. The latter draft NPDES permit is not expected to be finalized until late 2012.

#### Potential Impacts of MATS in New England

The Mercury and Air Toxics Standard affects coal- and oil-fired steam units over 25 MW. In New England, MATS affects 7.9 GW of existing installed capacity, either coal-steam or oil-and-gas-steam units. Of this affected capacity, many coal-steam generators already have installed or have planned the retrofit of needed air pollution control devices.

As shown in Figure 8-1, 1.9 GW of the affected capacity in New England report the retrofit of activated carbon injection for mercury control, 1.8 GW of affected capacity report some installed flue-gas desulfurization control devices for SO2 control, and 871 MW report installed fabric filter baghouses for particulate control. New England state environmental regulations for reducing air toxics emissions, including mercury, from larger fossil-fired generators have resulted in many of these retrofit air pollution control devices to be installed and operated well ahead of the MATS April 2015 compliance deadline.

Figure 8-1: Existing or planned advanced pollution control technologies at New England generators, 2011.

Existing liquid oil-fired generators in the region generally lack needed pollution control devices for compliance with the proposed MATS. Many are expected to continue operating beyond April 2015 by relying on a “limited-capacity-factor” exemption for oil-fired generators that EPA finalized in MATS to minimize the impact of the regulation on power system reliability. Eligible oil-fired generators will not need to add any advanced pollution control retrofits and may instead follow work practice standards, such as using cleaner fuels during start up and shut down and conducting tune-ups regularly.

Affected generators in New England with controls already installed or planned (i.e., expected to commence operation before 2015) are deemed to be not at risk. The ISO estimates that less than 1 GW of environmental retirements are expected because of MATS. This estimation is based on a review of publicly reported information on existing and planned pollution control devices at affected generators, the likely needed additional pollution control devices, estimated capital costs, and average construction schedules for such retrofit projects.

### Generator Emissions

For more than 10 years, the region’s average and marginal emission rates for SO2, NOX, and carbon dioxide (CO2) have been declining. This is a result of natural-gas-fired generators in the region emitting less than the generating units they displaced in economic dispatch—including older, less efficient oil units—and of oil- and coal-fired units adding emission controls. Compared with 2001, the 2010 average emission rate for SO2 has declined by 64%; the rate for NOX, by 54%; and the rate for CO2, by 11%. While the total system generation has increased by 11% from 2001 to 2010, the total emissions for SO2 and NOX have decreased from the 2001 levels, by 60% and 52%, respectively.

As shown in Table 8-3, the calculated system emission rates for 2010 have changed minimally from the 2009 values; the NOX rate had no change, and the SO2 and CO2 both changed less than 1%. However, the 2010 total energy generation was higher than the 2009 total energy generation by 5.8%, or 6,954 GWh. Total system emissions of NOX, SO2, and CO2, which increased by 4.5%, 5.2%, and 6.0%, respectively, reflected this higher generation. The calculated marginal heat rate has increased from 7.774 to 7.926 MMBtu/MWh, which is approximately 2.0%.

Table 8-3
System Emissions Rates, 2009 and 2010 (lb/MWh)

| Emission | System Emissions |  |  |
| --- | --- | --- | --- |
|  | 2009 Annual Rate (lb/MWh) | 2010 Annual Rate (lb/MWh) | % Change 2009 to 2010 |
| NOX | 0.46 | 0.46 | 0.0 |
| SO2 | 1.29 | 1.28 | −0.8 |
| CO2 | 828 | 829 | 0.1 |

As shown in Table 8-4, the NOX and CO2 marginal emissions rates have increased slightly between 2009 and 2010, by 5.9% and 1.4%, while the SO2 marginal emission rate decreased by 59.1%. This large decrease was observed because of a decrease in oil-fired generation of about 182 GWh and a 13.6% (about 6,794 GWh) increase in natural gas generation, which has low SO2 emissions.

Table 8-4
Marginal Emissions Rates, 2009 and 2010 (lb/MWh)

| Emission | Marginal Emissions |  |  |
| --- | --- | --- | --- |
|  | 2009 Annual Rate (lb/MWh) | 2010 Annual Rate (lb/MWh) | % Change 2009 to 2010 |
| NOX | 0.17 | 0.18 | 5.9 |
| SO2 | 0.22 | 0.09 | −59.1 |
| CO2 | 930 | 943 | 1.4 |

The results show that the 2010 SO2 and NOX system emissions rates are higher than the marginal rates for these pollutants, while the CO2 system emission rates are lower than the marginal rates.

### Greenhouse Gas Reduction Programs

This section summarizes the Regional Greenhouse Gas Initiative and discusses other regional and state initiatives to reduce greenhouse gases (GHGs).

#### Regional Greenhouse Gas Initiative Update

On January 1, 2009, RGGI took effect in 10 participating states in the Northeast. The aim of RGGI is to reduce the carbon dioxide emissions from fossil power plants 25 MW and larger in these states. The annual 10-state cap was 188 million (short) tons through 2014. Each state is allocated a share of the allowances, as shown in Figure 8-2, on the basis of historical emissions and negotiations. Under the existing RGGI Memorandum of Understanding (MOU), between 2015 and 2018, the cap will decrease 2.5% per year, or a total of 10% by 2018. Figure 8-2 shows the historical CO2 emissions data (2000 to 2008) from RGGI-regulated fossil power plants in Connecticut, Maine, Massachusetts, New Hampshire, Rhode Island, and Vermont compared with annual emissions during the initial RGGI compliance period (2009 to 2011). The figure also shows RGGI’s corresponding CO2 cap for New England of 55.8 Mtons for 2009 to 2011. CO2 emissions for New England totaled 42.2 Mtons for 2010, which was 24.4% below the regionwide cap. The CO2 emissions for 2011 were 35.7 Mtons, 36.0% below the cap.

Figure 8-2: Annual CO2 emissions—New England historical (2000 to 2011) and RGGI compliance period (2009 to 2011)—by state (million short tons).

Note: The blue line above 2009 through 2011 indicates RGGI’s 55.8 Mton CO2 cap for that compliance period.

The second RGGI compliance period began on January 1, 2012, and runs through 2014. Nine states are participating in the second compliance period; New Jersey withdrew from RGGI at the end of the first compliance period. The regional cap for the nine states participating in the second compliance period is 165 Mtons/year. The share of the regional cap for the six New England states is 55.8 Mtons/year.

The generators affected by RGGI are responsible for acquiring the allowances they need to cover their actual CO2 emissions over the three-year period. Generators have been the major purchasers of the allowances offered for sale in the quarterly RGGI auctions but also may acquire allowances in the secondary market. The fifteenth RGGI compliance auction, conducted on March 14, 2012, cleared at the reserve price of $1.93/ton of CO2 and raised $14.4 million for participating RGGI states in New England. The sixteenth RGGI compliance auction, conducted on June 6, 2012, cleared at the same reserve price for CO2 and also raised $14.4 million for participating RGGI states in New England.

Under RGGI’s Memorandum of Understanding, a comprehensive program review is required in 2012. The program review will evaluate all aspects of the program, including program impacts, additional reductions, imports and emissions leakage, and offsets. The participating states currently are engaged in electric power system and macroeconomic modeling to inform decision making regarding potential program refinements in late 2012, as necessary and appropriate. Stakeholder engagements and comment will be part of the state review process.

#### State Greenhouse Gas Policy Updates

In addition to participation in RGGI, Massachusetts is pursuing initiatives encouraging the development of clean energy, fostering investment in energy efficiency and reducing greenhouse gases pursuant to the Green Communities Act and the Global Warming Solutions Act, both enacted in 2008, and the Massachusetts Clean Energy and Climate Plan for 2020, released in December 2010.The Global Warming Solutions Act required Massachusetts to establish greenhouse gas emissions limits for 2020 and 2050. The state set an overall target for 2020 of reducing GHG emissions 25% below 1990 emissions levels, the maximum percentage reduction permitted under the Global Warming Solutions Act. This target is an interim target toward reducing GHG emissions 80% below 1990 levels by 2050. The Massachusetts Clean Energy and Climate Plan lays out a set of existing and new policies for meeting the 25% GHG reduction target for 2020. In July 2012, the Massachusetts Legislature enacted amendments to the Green Communities Act to enhance several of the initiatives launched to help meet its 2020 and 2050 GHG reduction goals (refer to Section 9.5.3).

In its fiscal year 2012 state budget, Massachusetts approved diverting some RGGI proceeds from energy-efficiency investments to a tax-abatement program to mitigate property tax losses for the City of Salem for 2012 to 2016. The tax losses will result from unit retirements at Salem Harbor Station from 2011 through 2015. The RGGI proceeds will replace up to $4.75 million annually for five years (2011 to 2016). An energy bill Massachusetts enacted on August 3, 2012, includes an extension of the Salem Harbor tax abatement for an additional three years until 2019 (see Section 9.5.3).

Other states in the region are relying on a mix of executive actions, including regulations, in addition to changes to statutes.

### Environmental Summary

Air emissions from New England’s generators remain low because of the region’s large dependence on natural-gas-fired generation and the continued growth of energy efficiency. EPA regulations most likely will require some older oil- and coal-fired generators in New England to make large capital investments to stay in compliance with air and water regulations.

The final Mercury and Air Toxics Standards Rule will have a relatively modest impact on New England generators. Although 7.9 GW will be affected, less than 1 GW of environmental retirements are anticipated by 2015. Most oil-fired generators are expected to continue operating after 2015, and limited additional pollution control retrofits are required for the remaining coal-fired generators, which have mostly completed or are implementing retrofits.

A total of 12.1 GW of fossil and nuclear capacity are subject to the proposed Cooling Water Intake Rule, which is expected to be finalized in June 2013. This rule directly affects a total of 5.6 GW of fossil-fueled and nuclear facilities with higher water-withdrawal design rates, which likely will be obligated to convert to closed-cycle cooling systems between 2018 and 2024.

Compliance with environmental requirements also will require the coordination of construction schedules and maintenance outages at affected generators to avoid diminishing system reliability. The ISO has quantified the effects of the existing EPA regulations and the potential effects of upcoming regulations. It will continue to monitor and evaluate regulatory developments and communicate with stakeholders about these developments as they emerge and potentially affect the region.

## Economic Performance Studies

The ISO conducts economic planning studies each year, as specified in Attachment K of the OATT. The economic studies provide information on system performance, such as estimated production costs, load-serving-entity energy expenses, transmission congestion, and environmental metrics. This information can assist market participants and other stakeholders in evaluating various resource and transmission options. The studies also may assist policymakers who formulate strategic visions of the future power system and how this system and regional policy objectives are interrelated. The studies are not intended to be an introduction to any specific “Attachment N” Market Efficiency Transmission Upgrade (METU) (refer to Section 5.3.2).

The annual economic study process is consistent with the ISO’s open stakeholder planning process. Stakeholders submit economic study requests to the ISO by April 1 of each year. Study proponents may request scenarios suggesting, for example, general locations and resource types for resource expansion, resource retirements, and possible changes to transmission interface limits. By May 1 of each year, the ISO provides these proponents an opportunity to present the PAC with the justifications for their suggested studies. The ISO and the PAC discuss the draft scopes of work by June 1 and review the study assumptions at later meetings. The ISO then performs up to three economic studies and reviews the draft and final results with the PAC.

The economic studies use assumptions for fuel prices, unit availability, load shape, load growth, resource mix, and many other factors, all of which could affect system performance metrics. Because these study assumptions are uncertain, the modeling results indicate relative values and trends and are not planning projections of future congestion, customer economics, and environmental impacts. These broad and generalized studies also do not address issues associated with specific resources, and the studies do not include detailed transmission analysis. For example, transfer limits are not reevaluated for unit commitment, new unit characteristics, and changes in other system parameters.

This section provides an overview of the status of economic studies conducted in response to stakeholder requests in 2011 and provides an overview of study requests received in 2012. Details and discussion of the assumptions and results are documented in various presentations made to the PAC and in other reports.

### Update of the 2011 Economic Study

As part of the 2011 economic study request process, three participants proposed studies and presented their requests to the PAC on April 14, 2011. In general, these study requests focused on the economics of expanded renewable resources within New England with an emphasis on the economic impact of transmission limitations. Study proponents noted that significant transmission congestion is an impediment to near-term wind energy development. Therefore, the requests were to analyze the impact of relieving constraints from potential wind project development areas (WPDAs), as determined by the interconnection queue and the customer load centers in southern New England. One request envisioned overarching comprehensive analysis with a wide geographic scope. The two other requests focused on the integration of renewable resources in western Maine.

The PAC reviewed these economic study requests, after which the ISO developed a final study plan that merged all three requests into one study. Although the tariff does not specify any deadlines for the completion of economic studies, the ISO made its last presentation on the study using the Interregional Electric Market Model (IREMM) in May 2012. A second phase is expected to be completed by the end of 2012 that will use a more granular approach for estimating production costs and simulating the interaction of generating resources and transmission constraints.

#### Study Framework, Assumptions, Methodology, and Metrics

The 2011 economic study was structured to address the issues of transmission constraints with various amounts of wind installed in various locations. The study had a high-level regional scope rather than analyzing specific transmission infrastructure needed for interconnecting specific wind resources (see Section 5.3.3). For example, the study did not consider the large-scale expansion of remote wind units, which presents integration challenges such as maintaining reliable stability performance of the system. It also did not analyze the design and cost of transmission interconnections in northern Maine and elsewhere, nor did it investigate small resource clusters, which could constitute a study of specific resources and is outside the scope of Attachment K investigations.

Areas Studied. To satisfy the intent of the study requests over the broad geographic range shown in Figure 8-3, the study assessed a large number of combinations and permutations of the wind resources and transmission constraints.

Figure 8-3: Renewable energy clusters evaluated in the 2011 economic study.

Five areas containing relatively large concentrations of wind were selected for detailed review as follows:

- Northern Maine: includes areas labeled as “Aroostook” and “Northern Maine.” This area is limited by Orrington South and, to a lesser extent, by the Surowiec South interface.

- Wyman/Bigelow: includes areas labeled as “Bigelow” and “Upper Kennebec Hydro.” These areas are limited by the Wyman/Bigelow interface and, to a lesser extent, by the Surowiec South interface.

- Rumford: includes the area labeled “Rumford Area.” This area is limited by the Rumford area export interface and, to a lesser extent, by the Surowiec South interface.

- Northern New Hampshire: includes the area labeled “Coos.” This area is limited by the Northern New Hampshire export interface.

- Offshore Massachusetts and Rhode Island: includes areas labeled as “Offshore MA” and “Offshore RI.” These areas are limited by the SEMA/RI export limit.

Figure 8-4 shows the New England transmission system as modeled in this study.

Figure 8-4: The New England transmission system “pipes and bubbles” as modeled in this study.

Transmission System Assumptions. The study used the transmission system interface limits anticipated for 2016. While the Maine Power Reliability Program enhancements are expected by early 2015 (see Section 5.5.1), the impacts of these reinforcements on the interface limits were not determined for this study. Table 8-5  shows the interface limits used throughout the New England region.

Table 8-5 
Single-Value Summer-Peak Transmission Interface Limits for 2016 Used in the IREMM Model

| Interface | 2016 Limit (MW) | Notes(a) |
| --- | --- | --- |
| New Brunswick–New England | 700 |  |
| Orrington South Export | 1,200 | No change assumed with MPRP |
| Surowiec South | 1,150 | No change assumed with MPRP |
| Maine–New Hampshire | 1,550 | No change assumed with MPRP |
| North–South | 2,700 |  |
| Boston Import (N-1) | 4,900 |  |
| SEMA Export | No limit |  |
| SEMA/RI Export | 3,300 | Assumes NEEWS is in place |
| East–West | 3,500 | Assumes NEEWS is in place |
| Connecticut Import (N-1) | 3,400 | Assumes NEEWS is in place |
| Southwestern Connecticut Import (N-1) | 3,200 |  |
| Norwalk/Stamford Import | 1,650 |  |
| Cross-Sound Cable (CSC) (Out) | 346 |  |
| Wyman/Bigelow Export | 350 |  |
| Rumford Area Export | 519 |  |
| Northern New Hampshire Export | 140 |  |

- Refer to Section 5.5.1 for more information on MPRP and Section 5.5.2 for more information about NEEWS.

To better quantify the magnitude of the congestion and cost impacts of transmission constraints, a completely unconstrained system also was evaluated. In this case, all the interface limits were increased to levels where they would not be constraining and where they would provide information on the magnitude of the lowest production cost possible. Comparing the results of the unconstrained case with the cases with the transmission interface limits quantified the amount of energy that could not be delivered because of transmission constraints. A number of additional sensitivity cases were considered to specifically investigate the relaxation of specific interfaces.

Wind Penetration Assumptions. The ISO, with the input of PAC members, agreed to investigate three levels of wind penetration. These levels were meant to capture the range of wind resources likely to develop in the short term, wind projects under mid-term active development, and wind projects that have the potential to develop long term. The levels were determined using data from the June 1, 2011, Generator Interconnection Queue (see Section 4.4.2):

- Commercial wind projects in the queue plus wind resources with FCA #5 capacity obligations (see Section 4.1.3) (Commercial plus FCA #5)—short-term development

- Active wind resources in the queue (Active Wind Queue)—mid-term development

- Wind resources active and withdrawn from the queue (Active Queue plus Withdrawn)—long-term development

Table 8-6 shows the amounts of wind development for the three scenarios and an estimate of the energy production for each area.

Table 8-6
Capacity and Energy Assumed for the Three Primary Wind-Penetration Scenarios

| Area | Capacity Factor (per unit) | Scenario |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Commercial plus FCA #5 |  | Active Wind Queue |  | Active Queue plus Withdrawn |  |
|  |  | Capacity (MW) | Energy (GWh) | Capacity (MW) | Energy (GWh) | Capacity (MW) | Energy (GWh) |
| Northern Maine | 0.315 | 109 | 300 | 1,258 | 3,470 | 2,885 | 7,962 |
| Wyman/Bigelow | 0.340 | 281 | 835 | 597 | 1,777 | 990 | 2,949 |
| Rumford Area | 0.340 | 139 | 413 | 191 | 569 | 230 | 686 |
| Northern New Hampshire | 0.344 | 100 | 301 | 134 | 404 | 460 | 1,385 |
| SEMA/RI Offshore | 0.419 | 0 | 0 | 1,051 | 3,858 | 7,256 | 26,633 |
| Other | 0.342 | 264 | 791 | 697 | 2,087 | 1,244 | 3,727 |
| Totals |  | 892 | 2,641 | 3,927 | 12,164 | 13,066 | 43,342 |
| Energy percentage(a) |  |  | 1.9% |  | 8.9% |  | 31.8% |

- The energy percentage was based on the 2011 net energy for load forecasted for 2016, 136,392 GWh (see Section 3.1).

2011 Economic Study Metrics. As with other economic studies, a number of metrics were used to determine and compare the attributes of the various cases. The metrics provide descriptors for comparing the merits of one case or scenario with another. The typical metrics are as follows:

- Production cost

- Load-serving entity energy expense

- Contributions to a resource’s fixed costs

- Congestion as measured by approximating the Financial Transmission Rights (FTRs) (i.e., the difference in the LMPs on each side of an interface multiplied by the megawatt flow across the interface)  (see Section 2.3)

- Bottled-in wind energy—potential wind energy not producing electrical energy because of one or more transmission constraints

- Fuel consumption used and energy produced by fuel type

- Environmental emissions of CO2, SO2, and NOX

Each defined interface has the potential to become constrained with some level of “upstream” wind resource development. For this study, bottled-in wind energy was selected as a primary metric for evaluation. Stakeholder discussion determined that near-zero bottled-in wind energy (i.e., the point where the system constraint just binds the ability of the wind plants to produce electric energy) was the preferred metric for showing adequate export capability from the WPDAs.

This focus on not having bottled-in wind energy was referred to as “wind producibility” (i.e., the ability of wind resources to generate electric energy; deliver it to customers near New England’s load centers; and displace any, and all, types of resources). Initial indicators of the impacts of wind producibility constraints appear as locally depressed clearing prices. In export-constrained areas, the wind energy may drive the local clearing prices to zero, and the LSE energy expense for this load becomes zero. This reduction in the LSE energy expense metric is magnified when relatively large amounts of load are served at “zero” prices. For example, depressed prices in the Wyman/Bigelow wind development area will have a small effect because the LMP in that area affects only 15 MW. Depressed prices north of Orrington South (which encompasses the RSP subarea, BHE; see Section 2.4) will have a much bigger effect because a lower price in this area affects a larger amount of load.

The metric for the contributions to fixed cost is a high-level metric for summarizing the net energy market revenues for a specific resource type in a certain location. For high wind penetration, the energy prices are depressed, and both wind resources and other resources would realize lower energy market revenues. This reduces the contribution to their fixed costs and may mean other revenue streams would need to be increasingly significant to economically support some resources.

Assumptions about Wind Dispatch. The study includes a number of assumptions about how wind will be dispatched on the grid. A key simplification is that all wind is dispatched at zero variable cost. Consequently, wind may displace any resource with a nonzero dispatch cost, such as coal, oil, nuclear, biomass, and other types of resources. Wind was modeled to be competitive with other zero-cost energy sources, such as other wind, hydro, and price-taking imports. Thus, it would be able to displace other wind, or hydro, only after all other dispatchable fuel-consuming resources were displaced.

Because of model limitations, resources behind a constraint could not be co-optimized with the wind. This means that the study did not model the coordination of hydro schedules with wind and did not capture the benefit of using stored water at a later time when the wind output would be lower. The structure of market rules and how wind resources will affect actual operations are difficult to represent and were not modeled. Unit commitment, ramp rates, minimum run times, and other generator characteristics all contribute to the complexities of coordinating wind dispatch with other resources. Consequently, there may be more “bottled-in” wind energy than observed in these simulations. The simulation results, however, are indicative of the overall system performance for each of the various scenarios.

#### 2011 Study Results

The economic studies addressed several of the region’s strategic issues. For example, accessing the renewable wind energy located in northern New England remote from the load centers in southern New England will require transmission expansion. The study showed how transmission expansion could relieve the concerns about bottled-in wind in various locations in northern New England.

The addition of resources with low energy costs decreases electric energy expenses for LSEs. The lower electric energy market contributions available to offset fixed costs suggest that additional or augmented revenue streams may be necessary to support the remaining resources. For high wind penetration, the lowest energy prices are depressed, and both wind resources and other resources would realize lower energy market revenues. This reduces the contribution to their fixed costs and may mean that other revenue streams would need to be available to economically support some resources.

Highlights of the results are as follows:

- Transmission system limitations would not bottle in significant amounts of wind energy if up to 600 MW of wind resources were added in the Rumford area of Maine. The Wyman/Bigelow area, also in Maine, likely would be export constrained with 600 MW of wind development.

- The Surowiec South interface likely could limit wind production in north–central Maine, but the interaction of wind generation with the existing resources requires further investigation.

- Northern New Hampshire would be able to accommodate approximately 150 MW of wind without major transmission upgrades.

- SEMA/RI would be able to accommodate much more wind energy than the wind resources currently in the interconnection queue likely would produce.

Additionally, the results show decreased systemwide emissions and natural gas consumption because wind resources displace generating units burning coal, oil, and natural gas.

#### Follow-up Analysis for the 2011 Economic Study Request using GridView

The first phase of the 2011 economic studies used the high-level IREMM model that does not include detailed models of both the transmission system and generating units. A second phase of this study that would use a more granular model, GridView, is expected to be completed by the end of 2012. The GridView analysis will be able to include additional effects of the transmission system and resource operating constraints, such as minimum run time, minimum down time, ramp rates, and unit commitment. Additionally, GridView can consider transmission and resource outages explicitly. This phase of the 2011 study using GridView is a key step to analyzing the New England system in greater detail.

### Economic Study Requests, 2012

The ISO received three economic study requests for 2012, but one was withdrawn. These requests, the preliminary scope of work for a combined study, and the assumptions were discussed with the PAC.

#### Overview of 2012 Study Requests

The first economic study request focused on an electricity future consisting of many renewable and low-carbon alternatives promoted by state and federal public policies. One of the assumptions for this study was the retirement of all coal and oil resources. These resources would be replaced by a mix that would include energy efficiency and other resources, such as solar, geothermal, wind, and biomass. These latter resources are intended to qualify as components of the Renewable Portfolio Standards (see Section 7.6). Generation would be assumed to be included at levels to meet the 2015 RPSs and include resources behind the meter to reflect state net-metering goals for renewable resources, such as PV installations (see Section 7.6.6). Because the study focuses on the New England system 10 years into the future, these RPS requirements would be, at the request of the study proponents, assumed to double by the year 2021. Combined heat and power plus geothermal (i.e., ground water heating and cooling) would be assumed to increase to levels envisioned under state goals. Smart grid enhancements to the system (e.g., smart meters) would be assumed, which would facilitate price-responsive demand (see Section 9.3.5) to help manage demand response in the energy market. Metrics would be developed for these studies to describe the results: production costs, average LMPs, LSE energy expenses, fuel consumption, and emissions.

The second economic study request under the Attachment K protocol was for the ISO to analyze the impacts of the loss of one or more of New England’s nuclear power plants. This request was for the ISO to investigate the impacts of these capacity reductions on various metrics. In particular, the request was for the study to quantify energy pricing, possible congestion, tie-line usage, changes in fuel use, and environmental emissions for SO2, NOX, and CO2.

#### 2012 Study Scope

The 2012 economic study will mimic the addition and removal of various types and amounts of load or resources in different locations throughout New England. The study will compare these various additions and removal of resources to a “business-as-usual” scenario of currently known system-expansion plans using information from the ISO Interconnection Queue.

These scenarios will create the framework to interpolate and extrapolate the effects on the metrics for each type of resource addition and removal for each of the RSP “bubbles.” For example, increasing the baseload (which implies increasing the load by a certain megawatt amount in all 8,760 hours of the year) could be used as a surrogate for the retirement of baseload units. Likewise, decreasing the load shapes characteristic of “baseload” can be used as a surrogate for adding generating units with low dispatch costs. Load-shape adjustments that reflect the various types of resources can be used to reflect the characteristics of energy efficiency, demand response, wind, or photovoltaics. The simulation results of these load-shape changes can then be used to estimate the effects on the various metrics developed during economic studies. This information also can show the locational effects on the metrics of adding and retiring resources.

In addition to the typical metrics estimated for past ISO economic studies, for each type of resource, the 2012 study will compare the technology’s capital costs ($/kW-year) with the energy revenues from the energy market. The simulation results also will show where the system may have potential transmission bottlenecks and the effects of relieving these transmission constraints. The study is scheduled for completion by the end of 2012. Follow-up analyses will show the results of combinations of resource additions and retirements, as requested by the original study requests and subject to input from the PAC and Information Policy constraints on the ISO.

### Generic Capital Costs of New Supply-Side Resources

The comparison of the energy market revenues with the annual revenue requirements (also called annual carrying charges) provides some relative measures of the economic viability of different resource types and how these measures change under various scenarios. Each resource type’s annual fixed costs include its capital, operations, and maintenance costs. These fixed costs can be calculated from estimates of annual carrying charges derived from representative capital costs for each resource type. These typically are 15% to 25% of the capital costs.

In support of the economic studies, a 2012 update of generic capital costs for new resources was developed, as shown in Table 8-7. The focus of this capital cost update was on the resource technologies in the ISO Generator Interconnection Queue and those participating in the FCM. The updated plant costs are from both the EIA and the Electric Power Research Institute (EPRI) for technologies that likely will dominate the future generation mix in the United States.

Table 8-7 
Generic Capital Costs of New Supply-Side Resources

| Generation Type | Nominal Plant Capacity (MW) | Plant Costs ($/kW)(a) |
| --- | --- | --- |
| NGCC | 550 | 1,060–1,150 |
| Conventional CT | 85 | 975 |
| Advanced CT | 210 | 665 |
| Wind onshore | 100 | 2,025–2,700 |
| Wind offshore | 200 | 3,100–4,000 |
| Biomass | 100 | 3,500–4,400 |
| Solar PV | 10 | 3,400–4,600 |

- Advanced CT costs are from EIA’s Updated Capital Costs Estimates for Electricity Generating Plants (November 2010). All other costs are from EPRI’s Program on Technology Innovation: Integrated Generation Technology Options (June 2011).

The actual capital costs of new resources may be different from these generic estimates because of the following factors:

- State of technology development

- Changes in material, labor, and overhead costs

- Supply-chain backlogs or oversupply

- Specific site requirements

- Regional cost differences

- Difficulties in obtaining site and technology approvals

In addition, experience suggests that many construction projects encounter unforeseen design and construction problems that tend to increase costs.

## Conclusions

The development and implementation of several major EPA and regional environmental regulations, including those addressing ambient air quality, greenhouse gases (such as carbon dioxide), air toxics, and cooling water, are raising various issues that the ISO is evaluating and addressing through studies and planning processes pursuant to its tariff and in consultation with stakeholders.

Environmental regulations could materially affect various electric power generators beginning in 2012 and continuing through 2020, when many affected facilities are required to come into compliance. EPA estimates show that, when finalized, these regulations could affect a significant amount of installed fossil-fueled capacity and, in the case of cooling water, nuclear capacity across the region. Compliance with upcoming environmental regulations, in some cases, will entail significant capital investment for retrofitting facilities with post-combustion control devices, closed-cycle cooling systems, or fuel-switching equipment or for retiring electric generators.

The aggregate impact of these regulations for many of the affected generators will be greater operations, maintenance, and capital costs. These increased costs will result from new emissions allowances, new pollutant controls, increased waste disposal, and unit conversions to allow the use of cleaner fuels, such as natural gas. These environmental regulations also may affect system reliability by limiting generator energy production, reducing capacity output, or hastening generator retirements. However, these regulations are anticipated to have a greater effect on neighboring systems than New England. Many generators in New England either have retrofits in place or are planning retrofits to comply with environmental rules. Less than 1 GW of generating units are anticipated to retire because of MATS, and 5.6 GW will likely be obligated to convert to closed-cycle cooling systems between 2018 and 2024. The ISO continues to monitor the evolving environmental regulations and evaluate both the likelihood of future compliance activities and the potential retirements of generating units.

Total emissions of NOX, SO2, and CO2 from electric generating plants within New England decreased from 2001 to 2010 at the same time the total system production increased 11%. The NOX, SO2, and CO2 average emission rates decreased by 54%, 64%, and 11%, respectively. The decrease in emissions is attributable to the region’s decreased production of oil-fired and coal-fired generation and the increased use of natural-gas-fired generating units.

The 2011 economic study results show various system metrics for three different levels of wind development in 2016. Transmission constraints are less likely to bottle in wind developed in SEMA/RI than wind developed in northern Maine, which could be limited by Surowiec South. Up to 600 MW of wind could be accommodated in the Rumford area, but this same amount would be restricted if developed in the Wyman/Bigleow area without transmission improvements. Transmission planning analyses are addressing concerns about the effects of high levels of wind penetration on interface limits.

Requests for economic studies were presented to the PAC on April 18, 2012. One of these study requests focused on expanded energy efficiency and renewable resources to replace resources assumed to be retiring. The other focused on the possibility of baseload generator retirements across New England. After holding discussions with the PAC, the ISO developed a final study plan to address both of the requests. The studies will provide system metrics for various amounts of baseload retirements with differing amounts of wind generation, photovoltaics, and energy efficiency. The studies are scheduled for completion by the end of 2012.

# Planning Coordination, Studies, and Initiatives

ISO planning activities are coordinated with governmental representatives of the six New England states, with neighboring systems, across the Eastern Interconnection, and nationally. Federal, regional, and state initiatives and policies have a significant impact on the wholesale electricity markets and transmission developed to meet system needs, specifically influencing the timing, type, and location of resources and transmission infrastructure.

## Federal Initiatives

Federal initiatives have a significant impact on the wholesale electricity markets and transmission developed to meet system needs. The Energy Policy Act of 2005 (EPAct) requires the US Department of Energy and Federal Energy Regulatory Commission to implement several reliability provisions. The requirements include ensuring the reliability of the transmission infrastructure and implementing enforceable reliability standards administered by the North American Electric Reliability Corporation.

### FERC Order 1000 and Order 764

FERC Order 1000, issued on July 21, 2011, sets forth additional requirements that build on Order 890, including regional and interregional planning procedures and cost allocation and the incorporation of “public policy considerations” into the planning process. Compliance filings on the regional requirements are due to FERC on October 11, 2012, and the interregional requirements are due on April 11, 2013. The ISO will continue to work with stakeholders to comply with the order.

On June 22, 2012, FERC issued Order 764, which adopts provisions to facilitate the integration of variable energy resources. Among other things, these provisions provide transmission customers the option of using more frequent transmission scheduling intervals (i.e., 15-minute intervals) within each operating hour. The order also requires new interconnection customers with VER generating facilities to provide meteorological and forced-outage data to transmission providers to facilitate power production forecasting. Compliance filings on these provisions are due 12 months from the effective date of the rule (i.e., 60 days after publication in the Federal Register).

### Metrics Report

As fulfillment of a US Government Accountability Office (GAO) recommendation, FERC submitted a report to Congress in April 2011 outlining 57 performance metrics intended to serve as standardized measures to track performance of ISOs/RTOs. The specific metrics are divided among broader measurements of power system reliability, efficient and effective market operations, and organizational effectiveness. The report is the result of a comprehensive, multiyear effort to measure the performance and benefits of ISOs/RTOs, for which six ISOs/RTOs had compiled a joint report. The report provides an empirical analysis of the benefits of organized power markets; identifies best industry practices; and while respecting key differences between the ISOs/RTOs, directly compares the varying successes of regional grid operators where possible.

The ISOs/RTOs submitted an updated metrics report to FERC in August 2011. In the future, FERC may broaden the report to include non-ISO/RTO regions and comparisons between metrics in regulated and deregulated markets. The ISO anticipates that FERC will request the ISOs/RTOs to submit the next metrics report in 2013.

### US Department of Energy Congestion Studies

DOE is required to conduct a study every three years on electric transmission congestion and constraints within the Eastern and Western Interconnections. Using the results of these studies and comments provided by the states and other stakeholders, the Secretary of Energy may then designate any geographic area experiencing electric transmission capacity constraints or congestion as a national interest electric transmission corridor (National Corridor). Designation as a National Corridor merits federal concern and may enable FERC to exercise “backstop” authority to site transmission facilities. This would occur only under limited circumstances, such as when a state agency has failed to act on a siting application within a National Corridor for more than one year.

The 2009 Congestion Study recognized the regional investment in new supply- and demand-side resources, as well as planning and development of extensive transmission upgrades, and it removed New England as “an area of concern” for the identification of National Corridors. The 2012 National Electric Transmission Congestion Study is scheduled for completion by the end of 2012.

## Interregional Coordination and Initiatives

The ISO is participating in numerous national and interregional planning activities with the US Department of Energy, the Northeast Power Coordinating Council (NPCC), and other balancing authority areas in the United States and Canada. The aim of these projects, as described in this section, is to ensure the coordination of planning efforts for enhancing the widespread reliability of the interregional electric power system. The ISO also conducts studies with other entities within and outside the region and with neighboring areas to, for example, improve production cost models and share simulation results, investigate the challenges to and possibilities for integrating renewable resources, and address other common issues affecting the planning of the overall system.

The ISO must identify and resolve interregional planning issues, as identified in needs assessments and solutions studies, consistent with the mandatory reliability requirements of the North American Electric Reliability Corporation.

### EIPC Studies of the Eastern Interconnection

In 2009, the electric power planning authorities of the Eastern Interconnection, including ISO New England, formed the Eastern Interconnection Planning Collaborative (EIPC). The planning authorities formally agreed to manage the process for combining the existing regional transmission expansion plans and analyzing the interconnection-wide system. Conducted under a DOE Funding Opportunity Announcement (FOA) awarded to EIPC in 2010, the EIPC study process is based on “bottom-up” planning and is committed to interactive dialogue and open, transparent proceedings. The EIPC has contracted with Charles River Associates to support the analysis work and with The Keystone Center to manage the stakeholder process.

In December 2011, EIPC issued a Phase I report, which describes the regional plan integration and the macroeconomic analysis of eight energy futures and 72 related sensitivities representing various potential public policy views. The results of the Phase I work were used to develop resource-expansion options for the three final scenarios selected for more detailed analysis during Phase II work.

Phase II started in January 2012 with the development of transmission buildout options to accommodate each of the three final scenarios:

- “Nationally Implemented Federal Carbon Constraint with Energy Efficiency/Demand Response,” which simulates a national price for CO2 emissions and the large-scale penetration of EE and active demand response (see Section 2.3)

- “Regionally Implemented National Renewable Portfolio Standard,” which simulates 30% of each region’s load supplied by renewable resources

- “Business as Usual,” which is characterized by no new federal, state, or regional energy and environmental policies and programs

Phase II work will include a series of power flow and contingency analyses for 2030 that will focus on bulk power system facilities above 230 kV and result in a transmission buildout for each scenario consistent with NERC’s reliability standards. The production costs for each scenario will be analyzed using the transmission buildouts developed. The EIPC and its consultants also will develop high-level cost estimates for the resource and transmission facilities identified in each scenario. A final report documenting Phase II work is scheduled to be filed with DOE in December 2012.

### NERC Activities

In early 2012, NPCC audited the ISO on nearly three dozen standards that govern ISO operations as reliability coordinator, balancing authority, and transmission operator. The NPCC audit examined the ISO’s practices in carrying out its real-time operations and short-term operations planning responsibilities, as well as its black-start and system restoration capabilities. NPCC found the ISO fully compliant with all the standards and requirements and did not identify any areas of concern. In concluding the audit, NPCC reiterated its favorable assessment of the ISO’s culture of compliance.

#### Electric Reliability Projects

As the RTO for New England, the ISO is charged with making sure its operations comply with applicable NERC standards. In addition, the ISO has participated in regional and interregional studies required for compliance.

Through its committee structure, NERC, which is the FERC-designated Electric Reliability Organization (ERO), regularly publishes reports that assess the reliability of the North American electric power system. Annual long-term reliability assessments evaluate the future adequacy of the power system in the United States and Canada for a 10-year period. The reports project electricity supply and demand, evaluate resource and transmission system adequacy, and discuss key issues and trends that could affect reliability. Summer and winter assessments evaluate the adequacy of electricity supplies in the United States and Canada for the upcoming summer and winter peak-demand periods. Special regional, interregional, or interconnection-wide assessments are conducted as needed.

In November 2011, NERC issued its annual Long-Term Reliability Assessment (LTRA), analyzing reliability conditions across the North American continent. This report describes transmission additions, generation projections, and reserve capability by reliability council area. Results for NPCC over a 10-year planning horizon show that reserves are expected to be sufficient to meet reliability needs. Projected sluggish load growth within the NPCC region over the assessment period is attributed to a combination of energy conservation initiatives and a slow economic recovery. Challenges noted for NPCC include aging infrastructure issues, the integration of variable energy resources, and the retirement of fossil-fueled generation.

#### Integrating Variable Generation Task Force

The NERC Planning Committee and the NERC Operating Committee created the Integrating Variable Generation Task Force to identify and address a number of operating and planning issues surrounding the variability and uncertainty of intermittent resources. The IVGTF is working toward implementing updated interconnection requirements, improving the modeling of capacity values and outputs in resource adequacy and transmission planning studies, and identifying needed operating tools, such as the forecasting of wind power output. The ISO is actively participating as a member of the IVGTF (refer to Section 7.6.6.2).

### IRC Activities

Created in April 2003, the ISO/RTO Council (IRC) is an industry group consisting of the 10 functioning ISOs and RTOs in North America. These ISOs and RTOs serve two-thirds of the electricity customers in the United States and more than 50% of Canada‘s population. The IRC works collaboratively to develop effective processes, tools, and standard methods for improving competitive electricity markets across much of North America. In fulfilling this mission, the IRC balances reliability considerations with market practices that provide competitive and reliable service to electricity users. As a result, each ISO/RTO manages efficient, robust markets that provide competitive and reliable electricity service, consistent with its individual market and reliability criteria.

While the IRC members have different authorities, they have many planning responsibilities in common because of their similar missions consistent with established FERC policy. As part of the ISO/RTO authorization to operate, each ISO/RTO independently and fairly administers an open, transparent planning process among its participants that provides for coordination, information exchange, comparability, dispute resolution, regional coordination, economic planning studies, and cost allocation. This ensures a level playing field for infrastructure development driven efficiently by competition and meeting all reliability requirements.

The IRC has coordinated filings with FERC on many issues, such as those concerning the administration of the ISO‘s Generator Interconnection Queue and other technical issues. The IRC also is acting to address the challenges of integrating demand resources and wind generation and, through its representatives, is leveraging the efforts of NERC‘s Integrating Variable Generation Task Force (see Section 9.2.2.2). The IRC has representation on other NERC task forces and committees.

### Northeast Power Coordinating Council Studies and Activities

The Northeast Power Coordinating Council, Inc. is one of eight regional entities located throughout the United States, Canada, and portions of Mexico responsible for enhancing and promoting the reliable and efficient operation of the interconnected bulk power system. As a member of NPCC, the ISO fully participates in NPCC-coordinated interregional studies with its neighboring areas.

NPCC conducts seasonal reliability assessments, an annual long-range resource adequacy evaluation, and a periodic assessment of the reliability of the planned NPCC bulk power system. All studies are well-coordinated across neighboring area boundaries and include the development of common databases that can serve as the basis for internal studies by the ISO.

### Northeastern ISO/RTO Planning Coordination Protocol

ISO New England, NYISO, and PJM follow a planning protocol to enhance the coordination of planning activities and address planning seams issues among the interregional balancing authority areas. Hydro-Québec TransÉnergie, the Independent Electric System Operator (IESO) of Ontario, the New Brunswick System Operator (NBSO), and New Brunswick Power participate on a limited basis to share data and information. The key elements of the protocol are to establish procedures that accomplish the following tasks:

- Exchange data and information to ensure the proper coordination of databases and planning models for both individual and joint planning activities conducted by all parties

- Coordinate interconnection requests likely to have cross-border impacts

- Analyze firm transmission service requests likely to have cross-border impacts

- Develop the Northeast Coordinated System Plan

- Allocate the costs associated with projects having cross-border impacts consistent with each party’s tariff and applicable federal or provincial regulatory policy

To implement the protocol, the group formed the Joint ISO/RTO Planning Committee (JIPC) and the Inter-Area Planning Stakeholder Advisory Committee (IPSAC) open stakeholder group. Through the open stakeholder process, the JIPC has addressed several interregional, balancing authority area issues. The 2011 Northeast Coordinated System Plan (NCSP11) summarized the following completed and ongoing work activities the JIPC conducted:

- Coordination and sharing of databases, critical contingency lists, and short-circuit equivalents

- Identification of improved planning techniques, modeling, and software tools

- Coordination of interconnection queue studies and transmission improvements

- Completion of market efficiency studies and the initiation of new studies using IREMM (see Section 8.2.1) and PROMOD reflecting coordinated system models

- Evaluations of environmental regulations and their potential effects on the power systems

- Identification of issues and solutions facilitating the integration of intermittent resources

- Assessment of fuel diversity issues, including coordinated studies of the natural gas system

- Determination of the effect of demand-side resources on interregional planning

- Coordination on compliance with FERC Order 1000, particularly on interregional planning and cost-allocation issues

The JIPC recognizes the need for further work based on input from the IPSAC. Planned JIPC activities include conducting additional interregional economic analyses that may identify potential transmission bottlenecks and trigger the need for transmission planning analyses. Another planned activity is the ongoing tracking of environmental regulations.

## Regional Initiatives

State, regional, and federal initiatives and policies have a significant impact on the wholesale electricity markets and transmission developed to meet system needs, specifically influencing the timing, type, and location of resources and transmission infrastructure. While not an all-inclusive list of regional initiatives, activities, and policies, this section discusses several policies, laws, and activities affecting the regional power system.

### Coordination among the New England States

The New England states have worked together continually to identify, discuss, and address energy issues of common interest. Even with this history of cooperation, each state has a unique set of energy policy objectives and goals.

Each of the New England states is actively involved in the ISO’s regional planning process, individually and through the New England States Committee on Electricity (NESCOE). NESCOE serves as a forum for representatives from the states to participate in the ISO's decision-making processes, including those dealing with resource adequacy and system planning and expansion issues.

In addition to NESCOE, the ISO works collaboratively with the state consumer advocates, the New England Conference of Public Utilities Commissioners (NECPUC), and the New England Governors’ Conference and their representatives.

The New England states are active participants in the interconnection-wide planning for the Eastern Interconnection. The Eastern Interconnection States Planning Council (EISPC) is an organization of 39 states and eight Canadian provinces in the Eastern Interconnection electric transmission grid, including representatives from New England, responsible for participating with the planning authorities that are part of the EIPC. Funded by a DOE Funding Opportunity Announcement, the EISPC comprises public utilities commissions, governors' offices, energy offices, and other key government representatives and provides input to the EIPC study effort. As a planning authority, the ISO has provided technical support to the EISPC. ISO New England, NESCOE, and NEPOOL work closely to coordinate New England’s participation in all EISPC and EIPC activities.

### NESCOE Updates

In addition to NESCOE’s efforts in implementing the coordinated competitive procurement of renewable resources in the region (see Section 7.6.3), the committee conducted a number of other activities in 2011, as summarized in its 2011 annual report. The report noted that NESCOE prepared the white paper, Survey of Smart Grid Implementation; formed the New England Interstate Transmission Siting Collaborative to enhance the coordination of the states’ siting processes required for interstate transmission facilities; participated in numerous ISO meetings, including the Forward Capacity Market redesign process; and submitted comments on a range of topics in response to the ISO, DOE, NPCC, NERC, and FERC.

### New England Governors Eastern Canadian Premiers/Northeast International Committee on Energy

Continuing on prior discussions and efforts of the New England governors, eastern Canadian premiers, and NESCOE, on May 17, 2012, the Conference of New England Governors and Eastern Canadian Premiers’ (NEG/ECP) Northeast International Committee on Energy (NICE) met in Montpelier, Vermont. The goal of these meetings was to develop a set of issues and policy recommendations for consideration by the 36th Conference of the NEG/ECP.

Participants at the NICE meeting discussed the mixture of existing renewable resources deployed in the region, as well as new renewable resources expected in the near future. The group agreed that the two main challenges facing renewable projects—the low cost of natural gas and the need for a cost-allocation methodology for necessary transmission upgrades—should be the focus of future policy development. Specifically, participants were largely in agreement that the growing role of low-cost natural gas poses problems regarding fuel diversity in the region as well as a competitive hurdle for renewable projects.

The states are involved in ongoing discussions regarding investments in grid-scale renewable projects and how the costs of these investments may be allocated.

At the conference, the NEG/ECP passed a resolution (No. 36-1) directing NICE to undertake the following actions:

- With other appropriate entities, begin to create a new regional process to identify longer-term opportunities in electricity markets, increase the flow of clean energy and associated infrastructure development to help reach environmental objectives, and ensure long-term security of supply through diversification and regional participation.

- Continue to support the regional coordinated procurement process underway through NESCOE (see Section 7.6.3) and other innovative mechanisms to support longer-term planning to meet the energy, economic, and climate goals of the region.

- Create a natural gas working group consisting of policymakers, industry officials, and other appropriate entities to better coordinate natural gas resource, transmission, and infrastructure planning.

- With its energy-efficiency working group, develop a regional cooperative process to maximize the potential for and accelerate the development of energy-efficiency opportunities regionally. NICE must report on its progress and recommendations to the 37th NEC/ECP in 2013.

The resolution also includes a provision in which the northeastern states and eastern Canadian provinces commit to working together to identify and develop guidance on critical biomass issues of regional significance and report these findings to the governors and premiers.

### Forward Capacity Market Updates

Consistent with an April 13, 2011, FERC Order, after significant stakeholder discussions in 2011, the ISO proposed reforms to the Forward Capacity Market for the seventh auction. The seventh auction is scheduled for February 2013 for a 2016/2017 capacity commitment period. The ISO’s proposal included the elimination of the auction floor price, the elimination of the use of the cost of new entry (CONE) calculation, and the implementation of a new market power mitigation process.

Before the ISO submitted this proposal to FERC, NEPOOL and the states reached a consensus position on an alternative to the ISO’s proposal. This consensus position, which the ISO supported and FERC subsequently approved, allows for the continuation of the rules in place for the sixth auction for the seventh auction, with a modified capacity clearing price floor of $3.15/kW-month and enhanced capacity zone modeling (such that Connecticut, NEMA/Boston, Maine, and Rest of Pool will be modeled).

### Price-Responsive Demand

In March 2011, FERC released Order No. 745, Demand-Response Compensation in Organized Wholesale Energy Markets. This order effectively requires all regional transmission organizations and independent system operators, including ISO New England, to allow demand response to participate in their energy market by reducing their consumption of electric energy from their expected levels in response to price signals.

Order 745 states that demand-response resources can participate in the energy market and receive the market price for energy for reductions when these demand-response resources have the capability to balance supply and demand and when payment of the market price for energy to these resources is cost-effective.

The costs associated with demand-response compensation will be allocated proportionally to all entities that purchase from the relevant energy market where the demand response reduces the market price for energy at the time the demand-response resource is committed or dispatched.

In 2011, the ISO and regional stakeholders developed rules to better integrate demand response into the regional energy market. Once fully implemented, the rules will allow demand-response providers to express a price at which they are willing and able to reduce demand, which effectively allows the ISO to commit and dispatch demand resources as an alternative to committing and dispatching generation resources in balancing energy supply and demand. This better ensures that the most cost-effective resources available at each moment are committed and dispatched to serve regional energy consumption.

### Consumer Liaison Group

ISO New England and regional electricity market stakeholders created the Consumer Liaison Group (CLG) in 2009 to facilitate the consideration of consumer interests in determining the needs and solutions for the region’s power system. With representatives from state offices of consumer advocates and attorneys general, large industrial and commercial consumers, chambers of commerce, and others, the CLG meets quarterly to address various consumer issues. CLG meeting agendas and ideas for special guest speakers and discussion topics are guided by a Coordinating Committee with the input of CLG members.

In 2011, the CLG discussed various topics of interest to electricity consumers, including electricity costs, the ISO’s framework for evaluating the impacts of major initiatives, regional smart grid projects and opportunities, and the Forward Capacity Market.

In 2012, the CLG has continued to address important topics, such as the region’s dependence on natural gas and the most effective ways for consumers to use state programs to achieve energy cost savings. In May 2012, the CLG Coordinating Committee and the ISO issued the 2011 Report of the Consumer Liaison Group, which summarizes the activities of the Consumer Liaison Group and other ISO activities in 2011.

## ISO Initiatives

In addition to the Strategic Planning Initiative discussed in Section 6, the ISO is involved in a number of other initiatives aimed at developing and integrating new technologies, improving the cost estimates for transmission projects, and improving emergency operating procedures to enhance system reliability.

### Updates on Developing and Integrating Smart Grid and Other New Technologies

The ISO strives to keep up to date with new technologies that can have an impact on the region’s electric power grid. As policymakers set targets and allocate public funds for developing smart grid initiatives and renewable generation, the ISO analyzes the effects of these technologies on system operations and reliability. This section discusses several of the technology developments affecting the planning of the New England region. It summarizes some of the challenges of integrating smart grid equipment and discusses advanced technologies, including phasor measurement units (PMUs), high-voltage direct-current (HVDC) facilities, and flexible alternating-current transmission system (FACTS) devices.

#### Participation in Developing Industry Standards and other Professional Activities

The ISO also is actively participating in the development of the national smart grid interoperability standards, led by the National Institute of Standards and Technology (NIST), to establish protocols that provide common interfaces for smart grid equipment. Additionally, as a part of an ISO/RTO Council project with other ISOs/RTOs, ISO New England is providing technical and other support for the development of demand-response-related standards by NIST and the North American Energy Standards Board (NAESB). ISO staff and stakeholders remain professionally active in the Institute of Electrical and Electronics Engineers (IEEE), a society that serves to educate its members and the public at large, as well as develop standards for the interconnection and operation of smart grid technologies.

#### Synchrophasor Infrastructure and Data Utilization Project

The American Recovery and Reinvestment Act (ARRA) of 2009 provided the US Department of Energy with funding to facilitate the development and implementation of smart grid technologies. In close partnership with New England’s transmission owners, the ISO received DOE funding to implement a synchrophasor infrastructure and data utilization (SIDU) smart grid project in New England. Synchrophasors are power system measurements created in devices known as phasor measurement units (PMUs). The units use global positioning satellite technology to monitor the performance of the region’s electric power grid accurately and provide specific data for use in operating the grid and enhancing grid design.

The goals of this project include the installation of PMUs at 40 substations in New England, eight phasor data concentrators (PDCs) at the ISO and seven TOs, communication infrastructure to support streaming PMU data from substations to TOs then to the ISO, and the Region of Stability Existence (ROSE) application to compute operational stability boundaries and margins. ROSE calculates system stability limits and compares these limits to actual operating conditions, showing operators the amount of operating margin. To date, PMUs have been installed at 17 substations in New England and currently are streaming data to the transmission owners and then to the ISO. PDCs receive and store data the ISO uses to compute operational stability limits and the margin from these limits. This project is on schedule to be fully implemented by June 2013.

Entities in the region, including municipal electric utilities and transmission owners, received almost a quarter of a billion dollars in ARRA smart grid grants. Projects include advanced metering infrastructure (AMI) and technology. Grant recipients are in various phases of development.

#### HVDC and FACTS

The application of power electronics to the power system through high-voltage direct-current and flexible alternating-current transmission system technologies can enhance the performance of the transmission system. HVDC and FACTS use a combination of solid-state switches and computerized automation that enables nearly instantaneous customized control of real or reactive power flows—far faster than traditional electromechanical switches. HVDC has been applied to the New England system interconnections with Québec and to New York under the Long Island Sound. FACTS applications have provided a much-needed boost to the transmission system and offer some other technical advantages, especially when dynamic voltage support is needed.

Both HVDC and FACTS are regularly considered as part of transmission planning studies when their application economically meets system or generator interconnection needs. For example, the HVDC controls for Highgate (see Section 5.5.1.3) are being replaced. Future merchant and elective HVDC projects are under consideration as part of additional interconnections with Québec, New Brunswick, and New York, and as part of interconnections within New England between areas with a large potential for wind power development and regional load centers. Changes to the Chester static VAR compensator (SVC) control settings were completed in 2010, and dynamic voltage ampere reactive systems (DVARs) have been applied to stabilize wind farms, such as Kibby (see Section 5.3.3).

Figure 9-1: Existing and planned FACTS devices in New England

Note: The acronyms and abbreviations in the key refer to the following terms: HVDC = high voltage, direct current. VSC = voltage source converter. SVC = static voltage ampere reactive (V) compensator. STATCOM = static synchronous compensator. DVAR = dynamic voltage ampere reactive. TBD = to be determined.

#### Advances in Hydro Power

The United States has the potential to produce 1,420 TWh/yr—more than a third of the nation’s annual electricity usage—using marine and hydrokinetic power (MHK). MHK is a relatively new technology that utilizes waves, currents, and ocean thermal resources to generate electricity. FERC has issued an eight-year hydrokinetic pilot license for a 0.3 MW cross-flow tidal MHK project in Cobscook Bay, Maine, and preliminary permits to several other tidal MHK projects in Maine and one in Massachusetts. Other technological advances in hydro generation technologies include using water flows more efficiently and mitigating the adverse environmental impacts of dams and variations in water flows.

### Improvements to Transmission Cost Estimate Tracking

Since RSP11, the ISO has augmented its RSP Transmission Project List to enable costs to be more easily tracked. This improvement was aimed at assisting stakeholders in recognizing cost changes and facilitating a more comprehensive review of transmission project costs through time.

### Improvements to System Restoration and Black Start

System reliability is maintained by system operators who observe and control the system to withstand normal criteria contingencies. However, extreme contingencies, human errors, and other unexpected events can lead to partial or total blackout conditions necessitating the use of restoration procedures. These procedures must meet established reliability criteria and be implemented by operators at a central control center or local control center (LCC), sometimes both.

As the coordinator and director of restoration activities for New England, the ISO periodically verifies the adequacy and efficiency of system restoration plans and other regulatory, economic, and technical restoration issues. For example, through tests and system simulations, it identifies opportunities for improving plan procedures and training for system operators. For many years, the system restoration plans started with numerous small black-start units that restored individual local load pockets. These bottom-up plans then called for synchronizing the many load pockets and restoring the remaining high-voltage (HV) system before energizing the extra-high-voltage transmission (EHV) facilities. While this bottom-up approach to system restoration has served the region well, the ISO identified opportunities for potentially improving the restoration plans using a top-down approach.

A critical first step toward transitioning from a bottom-up to a top-down restoration plan required a thorough technical evaluation that included simulations of power flow, system dynamic performance, and switching transient overvoltages. The technical studies validated the concept, and the ISO has begun reaching out to selected generators to participate in the top-down program. The project will include the black-start conversion of generators, the modification of many operator procedures, and training before the process can be implemented into system restoration plans.

The standard rate for system restoration service was modified in Schedule 16 of the Open Access Transmission Tariff to account for the size of the unit that could provide black-start restoration services and the need for new investment based on expected costs.

## State Initiatives, Activities, and Policies

The New England states have worked together continually to identify, discuss, and address energy issues of common interest. Over the past few years, the New England states have implemented numerous and varied energy policies and initiatives that have consistently focused on advancing energy efficiency, mitigating costs through long-term contracting, increasing the development of renewable resources, and reducing pollutants from certain generating facilities.

Even with this history of cooperation, each state has a unique set of energy policy objectives and goals. This section presents recently implemented laws, policies, and initiatives that affect regional system planning. While not an all-inclusive list of state initiatives, activities, and policies, this section discusses several policies recently considered and laws enacted in the six New England states.

### Connecticut

By legislation passed in 2011, Connecticut has created a new Department of Energy and Environmental Protection (DEEP). DEEP is responsible for meeting several energy-related goals: reducing electricity rates and costs for Connecticut ratepayers, ensuring the reliability and safety of the state's energy supply, increasing the use of clean energy, and developing the state's energy-related economy. The act that created DEEP provides financial incentives for the development of solar and other clean energy technologies and requires DEEP to study options for reducing ratepayer costs for procuring renewable energy resources and the feasibility of increasing the renewable energy portfolio standard.

A part of DEEP is a new Bureau of Energy and Technology, which is a consolidation of several state agencies responsible for energy policy. The bureau is responsible for developing an integrated resource plan every two years and a comprehensive energy plan every three years and issued its first integrated resource plan in 2012. Another part of DEEP is the Public Utilities Regulatory Authority (PURA), which reviews electricity rates and performs other regulatory functions previously performed by the Department of Public Utility Control.

In 2011, the state procured 10 MW of Class I renewable energy through a competitive solicitation (refer to Section 7.6.4). DEEP, in consultation with the Clean Energy Finance and Investment Authority (CEFIA) and the state’s consumer advocate, selected two 5 MW solar projects from among 21 projects proposing 70 MW of renewable power. The winning projects will enter into long-term (20-year) purchase power agreements with the state’s two electric utilities, Connecticut Light and Power (CL&P) and United Illuminating (UI). The legislation authorizes the companies to develop up to 20 MW of additional Class I renewable energy resources.

In addition, the companies are required to solicit proposals for long-term (15-year) contracts with developers of customer-side Class I generation projects and with a preference for technologies manufactured or developed in Connecticut. Under the solicitation, the companies are required to procure renewable energy credits from renewable energy resources that produce either low or zero emissions (i.e., LRECs or ZRECs) (see Section 7.6.4 and 7.6.6.1). The solicitation is intended to provide more than $1 billion to qualified renewable energy projects over the next 20 years. Projects eligible for funding include low-emission renewable energy resources up to 2 MW (LREC projects) and zero-emission renewable energy resources up to 1 MW (ZREC projects).

### Maine

Maine has established wind power goals, including the development of 2,000 MW of onshore wind by 2015 and 3,000 MW of onshore wind and 5,000 MW of offshore wind by 2030. At the end of 2011, Maine had approximately 400 MW of operational wind power interconnected to the regional power system.

In its most recent 2012 Maine Wind Energy Development Assessment report, the Maine Governor’s Office of Energy Independence and Security made wind policy recommendations. The office recommends that the state consider eliminating the statutory goal of developing 2,000 MW of onshore wind by 2015 because the state has met less than 20% of this goal, and achieving this level of installed capacity is highly unlikely. The office recommends retaining the wind goals for 2030. Other recommendations in the report are as follows:

- Convening a panel to identify the locations in Maine where expedited permitting could be allowed in a way that provides maximum energy, economic and environmental benefits and minimum harm to local residents and the environment

- Making no changes to the 270-day statutory period for processing a permit application

- Requiring wind projects to use best available control technology

Approximately 75% of homes in Maine—the highest percentage in the nation—rely on oil for home heating. In its spring 2012 legislative session, Maine enacted a law, LD 1864, which allows the state’s utilities to develop and implement, on approval of the Public Utilities Commission, a pilot program to measure the effectiveness of efficient electric heating systems. Under this pilot program, utilities may offer rebates to participating customers to be applied to the total installation cost of electric heat pumps and thermal storage units.

### Massachusetts

In January 2012, the Department of Public Utilities (DPU) issued an order establishing a Distributed Generation Working Group to improve the process for connecting on-site clean energy projects. In the Massachusetts Distributed Generation Interconnection Report, issued August 2011, the Massachusetts Department of Energy Resources (MA DOER) recommended 10 changes to the distributed generation interconnection process, including the following:

- Requiring the Department of Public Utilities to mandate shorter, clearer, and binding timelines for interconnection applications

- Creating a uniform, user-friendly, online application system to track the real-time status of applications and deadlines

- Requiring the DPU to assign an interconnection ombudsperson for hearing and quickly resolving issues that arise during the interconnection process

On August 17, 2012, the DOER adopted final Renewable Portfolio Standard regulations regarding the eligibility of woody biomass (see Section 7.6.4). The revised rule imposes overall project efficiency standards and includes a detailed definition of eligible biomass woody fuel, specifying permissible biomass from forests, nonforest residues, and dedicated energy crops (grown for producing fuel). The final rule includes the following provisions:

- Requires resources using eligible biomass wood fuel to demonstrate to DOER on a quarterly basis an overall efficiency of at least 50%

- Requires eligible units that use technologies that significantly advance biomass energy conversion  to demonstrate to DOER on a quarterly basis an overall efficiency of at least 40%

- Requires all woody biomass units to demonstrate to DOER 50% reductions of GHG emissions over a 20-year lifecycle compared with GHG emissions from a new, advanced, natural-gas-fired combined-cycle generator over the same 20-year period

- Requires additional reporting on project performance and sourcing of biomass consumed to ensure compliance

Existing eligible biomass resources remain qualified until the end 2012. To retain their eligibility through 2015, these units must comply with the annual biomass woody fuel sourcing and reporting requirements. To retain their eligibility beginning in 2016, biomass resources must comply with all sourcing, reporting, and efficiency performance and GHG-reduction requirements of the state’s Renewable Portfolio Standard for Class I resources. The retroactive application of the revised biomass rule is expected to have an adverse impact on existing biomass capacity in Massachusetts.

In another regulatory activity in Massachusetts, on August 3, 2012, the state passed an energy bill that includes the following major provisions:

- Requires the DPU to open a docket investigating the need for additional capacity in NEMA for the next 10 years, with the investigation completed by March 15, 2013. If DPU determines that capacity is needed, it may order distribution companies in that load zone to solicit competitive proposals from developers to meet the reliability shortfall, and if approved by DPU, enter into cost-effective long-term contracts (10 to 20 years). Resources must become commercial on or after June 1, 2014; fulfill capacity needs in NEMA; and provide other economic, environmental, and reliability benefits to the NEMA load zone.

- Implements a plant-revitalization task force for implementing a plan, adopting rules, and conducting other tasks for ensuring the full deconstruction, remediation, and redevelopment or repowering of Salem Harbor by December 31, 2016, and extends the deadline (from 2016 to 2019) for the City of Salem to receive RGGI funds to help offset declining property taxes at the Salem Harbor power plant (refer to Section 8.1.3)

- Increases to 7% (from 3%) the required amount of total energy demand that utilities must meet through 10- to 20-year contracts with renewable energy developers per the Green Communities Act long-term contracting statute (refer to Table 7-7 and Section 8.1.3.2)

- Requires the DOER to investigate the reactivation of preexisting hydropower sites and report on the results by January 1, 2016

- Increases the eligibility of individual Class I hydroelectric power facilities from 25 MW to 30 MW, and for Class II facilities from 5 MW to 7.5 MW and further includes hydroelectric power as one of the “new, renewable and alternative energy” sources to meet the state’s goal of 20% renewable resources by 2020 (refer to Section 7.6)

- Expands a utility’s net-metering capacity from 1% to 3% of its peak load; expands the net-metering capacity of municipalities or governmental entities from 2% to 3% of peak load

In February 2012, the US Department of Interior’s Bureau of Ocean Energy Management, Regulation, and Enforcement (BOEMRE) released a Call for Information, Nominations, and Notice of Intent to Prepare an Environmental Assessment. The assessment is for the potential development of offshore wind energy projects in an area of federal waters on the Outer Continental Shelf of Massachusetts. On May 30, 2012, BOEME announced that it had defined a Wind Energy Area (WEA) that will be considered for leasing.

### New Hampshire

A new law enacted in New Hampshire in 2012, HB 648, restricts electric utilities from using eminent domain for nonreliability transmission projects. HB 648 specifically prohibits public utilities from petitioning for permission to take private land or property rights for constructing or operating an electric generating plant or an electric transmission project not eligible for regional cost allocation.

Also during the 2012 legislative session, the state modified its Renewable Portfolio Standards law (see Section 7.6.4). Specifically, Senate Bill 218 (SB 218) was passed into law, which changes the RPS as follows:

- Adds thermal energy to eligible Class I renewable resources and establishes a requirement for the portion of Class I that thermal resources must meet

- Reduces the incremental increases in annual Class I requirements for 2015 through 2025 from 1% to 0.9% per year

- Increases Class III biomass eligibility for 2014 through 2025

- Adds incremental increases to Class III requirements for 2014 and 2015 and to Class IV resources for 2013 through 2015

- Lowers alternative compliance payments for all four classes of renewable resources

House Bill 1490 (HB 1490) addressing New Hampshire’s participation in the Regional Greenhouse Gas Initiative, also was passed into law. Among other things, HB 1490 accomplishes the following:

- Sets a rebate threshold for RGGI auction allowance proceeds to $1, with all amounts in excess of the $1 to be refunded to all default service ratepayers in the state on a per-kilowatt-hour basis

- Repeals the state’s RGGI participation contingent upon the RGGI withdrawal of two or more New England states or their agreement to withdraw, or the withdrawal of a participating state that has at least 10% of the total load of the New England states or their authorization to withdraw from RGGI participation

### Rhode Island

In 2012, Governor Chafee signed a bill requiring National Grid to support the installation and investment of combined heat and power installations at customer facilities. The program is to be included as part of the company’s annual energy-efficiency program plan. Rhode Island also is drafting an energy assurance plan that will be used to improve the state’s energy preparedness. The plan will recognize and consider the state’s specific energy-assurance needs, critical infrastructure, and vulnerabilities, such as its limitations in electric power transmission, geography, and dependency on natural gas.

### Vermont

The Vermont Department of Public Service issued a final version of the state’s comprehensive energy plan in December 2011. The plan established a goal of meeting 90% of the state’s 2050 energy needs (for all needs, not just electricity) with renewable resources. It also addresses Vermont’s energy future for electricity, thermal energy, transportation, and land use. Strategies for the electricity sector included the following recommendations:

- Adopt a Renewable Portfolio Standard

- Expand the existing standard offer (feed-in tariff) program to include small-scale, “clean” distributed energy

- Encourage utilities to develop or expand existing auction mechanisms for resource procurement, particularly targeted at midsized generation projects that relieve transmission constraints

The plan’s recommendations for transmission and regional wholesale market strategies were to continue the focus on efficiency and peak load reduction to reduce Vermont’s share of regional transmission projects. Another recommendation was for the state to continue to pursue market resource alternatives whenever feasible.

A Vermont Public Service Board study analyzed the effectiveness of the state’s renewable energy program and showed that the existing program (known as the Sustainably Priced Energy Development or SPEED program) may not be effective at developing sufficient new renewable resources in the state. Like the Vermont Department of Public Service, the Vermont Public Service Board recommended that the legislature adopt a Renewable Portfolio Standard for Vermont (the only state in New England without one).

Vermont passed an energy bill that amended its existing renewable energy statutes. Specifically, the bill expanded the original 50 MW cumulative program cap of the state’s standard-offer renewable energy program (feed-in tariff) to 127.5 MW. This increase will occur over time, with a 5 MW increase per year running from 2013 to 2016. Increases of 7.5 MW per year will take place from 2017 to 2019; after 2019, the program will increase by 10 MW per year.

This bill maintains the state’s existing renewable energy goal for 20% of statewide retail sales to come from new renewable resources by 2017. The bill also includes a new target for 55% of total energy sales to come from renewable resources (both new and existing) by 2017. This target increases to 75% of total sales by 2032.

Section 7.4 discusses the status of the Vermont Yankee nuclear station.

## Summary of Initiatives

The ISO’s planning activities are closely coordinated among the six New England states, with neighboring systems, across the Eastern Interconnection, and nationally. The ISO has achieved full compliance with all required planning standards and has successfully implemented the Northeastern ISO/RTO Planning Protocol, which has further improved interregional planning among neighboring areas and will continue to do so as it is expanded to assure compliance with Order 1000. Each New England state has a unique set of energy policy objectives and goals and continues to implement laws, policies, and initiatives that affect the regional system planning in New England.

# Key Findings and Conclusions

In accordance with all requirements in the Open Access Transmission Tariff, ISO New England’s 2012 Regional System Plan discusses the electrical system needs and plans for meeting these needs from 2012 through 2021. The RSP also discusses several regional challenges expected over this same 10-year planning horizon, which are being addressed by the regional Strategic Planning Initiative.

The load forecast for RSP12 is similar to RSP11, and the ISO has developed an energy-efficiency forecast to quantify the energy savings and reductions in peak load achieved as a result of the states’ energy-efficiency investments and mandates across the region. Sufficient resources are being procured through the Forward Capacity Market and the locational Forward Reserve Market to meet the tariff requirements for capacity and reserves. Additional resource retirements are anticipated as a consequence of economics, upcoming environmental compliance obligations, and other factors. Some capacity may be replaced with natural-gas-fired generation and renewable resources. Natural-gas-fired generation is providing over 50% of the region’s electric energy, and with the natural gas sector’s expected gain of additional market share, the ISO (in collaboration with regional stakeholders) and industry are taking actions to improve the reliability of generators and diversify the region’s fuel supply.

Renewable Portfolio Standards and the Regional Greenhouse Gas Initiative are encouraging the development of renewable resources and energy efficiency in the region. The region has the potential for developing significant amounts of wind resources, but because the most favorable onshore siting locations are remote from load centers, major additions to the transmission system would be needed to access these resources. Economic studies have shown the potential effects of scenarios that increase renewable resources and demand resources in the region and the imports of these resources from neighboring regions. These studies have helped provide guidance to policymakers and developers of supply and demand resources and merchant transmission.

Along with the reliability improvements transmission projects bring to the system, transmission upgrades support market efficiency, reflected by the low amounts of congestion and other out-of-merit charges, such as second-contingency and voltage-control payments. Additionally, elective and merchant transmission facilities are in various stages of development in the region and have the potential to provide access to renewable resources in remote areas of New England and neighboring regions, including Atlantic Canada and Québec.

The regional energy landscape is undergoing a dramatic change in terms of the composition of generation, transmission, demand resources, and wholesale markets. This evolution poses a series of challenges the ISO is addressing through the Strategic Planning Initiative. This initiative is a collaborative effort of the New England states and market participants who are developing enhancements to the planning process and wholesale electricity markets to ensure both the reliable and economic development and operation of the system. Over the past year, the ISO and participating stakeholders identified several interrelated issues that need to be addressed in both short-term and long-term planning:

  - Resource Performance and Flexibility— the uncertain amounts, unclear performance, and operational challenges of using demand resources and less responsive and limited supply resources and the need to increase system flexibility

  - Increased Reliance on Natural-Gas-Fired Capacity—the reliance on natural-gas-only resources because the gas supply and infrastructure systems may not be sufficient to meet power system needs when seasonal demand is high, the system is stressed in other ways, or when facing natural gas supply and distribution system contingencies

  - Retirement of Generators— economic and policy factors that could lead to the exit of a substantial portion of older fossil-fuel capacity

  - Integration of a Greater Level of Variable Energy Resources—the need for a steady increase in reserves, regulation, and ramping capabilities as more intermittent resources, primarily renewable energy resources, are added to the system over the next several years

  - Alignment of Markets with Planning—the need to better align the timing and analysis of wholesale market procurements with the transmission planning processes to allow for meeting reliability needs through market resources or backstop transmission solutions

As part of the Strategic Planning Initiative, the ISO is studying the economic and reliability effects of retiring aging, environmentally vulnerable generators and their likely replacement with natural-gas-fired generation, renewable variable energy resources, and imports from the neighboring Canadian provinces. The studies include production cost simulations, analyses of the natural gas system requirements, and transmission planning studies for some of these scenarios. Plans call for continuing discussions of these issues with the region’s stakeholders and providing an update on Strategic Planning Initiative studies in RSP13. Evaluating how to better align the wholesale market design with system planning requirements will be an important aspect of this regional dialogue.

RSP12 draws the following conclusions about the outlook for New England’s electric power system over the next 10 years:

- Forecasts for the Annual and Peak Use of Electric Energy—The RSP12 10-year forecast is for the annual use of electric energy to increase 0.9% per year for 2012 through 2021 and for the average growth in the summer peak demand to be 1.5%. This forecast is slightly lower than the RSP11 forecast. The 50/50 and 90/10 summer peak forecasts both are 660 MW lower in 2012 and both would be about 290 MW lower in 2021 than the RSP11 forecast.

At the request of stakeholders, the ISO developed an energy-efficiency forecast that estimates the energy saved as a result of energy-efficiency investments across the region over the 10-year planning horizon, beyond the quantity of passive demand resources that clears the Forward Capacity Auction. Using data from energy-efficiency program administrators and stakeholder input, the ISO developed an energy-efficiency forecast for 2015 to 2021. The results show a regional annual average energy savings of 1,343 GWh, an average annual reduction in the peak demand by 206 MW, and a total reduction in the peak demand by 1,444 MW from 2015 to 2021.

- Capacity Needs and Resource Development—Resources with capacity supply obligations in the Forward Capacity Market are exceeding the “representative” value of 35,600 MW for capacity resources needed by 2021, with 36,309 MW of resources procuring capacity supply obligations for 2016 in FCA #6. A comparison of the representative ICR with the FCA #6 resources plus the EE forecast shows a surplus of 1,903 MW in 2021. In addition, 6,574 MW of resources are active projects in the ISO Generator Interconnection Queue. Potential generator retirements, however, would need to be evaluated individually to ensure the reliable performance of the transmission system.

- Operating Reserve and Ancillary Services—Resources participating in the locational Forward Reserve Markets are helping to satisfy the operating-reserve requirements of the region overall and in major load pockets to address contingencies. As a result of transmission upgrades and other resource additions, the Greater Southwest Connecticut area is not expected to need any additional local operating reserve from 2013 to 2016. Over the same period, the forecasted need for operating reserve in the Greater Connecticut area is 400 to 1,100 MW during the summer, and similarly, the need for the BOSTON area is between 0 and 200 MW. Unit retirements and the addition of variable energy resources, particularly wind, will likely grow with time and increase the need for flexible resources to provide operating reserves as well as other ancillary services, such as regulation and ramping.

- Transmission Projects—Completed transmission projects are required for providing reliable electric service to load throughout the system and meeting the demand in areas with significant load growth. From 2002 through June 2012, 400 projects have been put into service, totaling approximately $4.8 billion of new infrastructure investment. The RSP Project List summarizes transmission projects under various stages of development to meet regional system needs. It also includes information on project status and cost estimates. The descriptions of transmission projects in RSP12 are based on the June 2012 update, which includes 256 projects at a total cost of approximately $6.0 billion.

The region has made progress on the NEEWS project, which consists of several projects to serve load and improve transfer capability across southern New England. Two components—the Springfield and Rhode Island components—have received siting approval and are under construction. The Interstate component of NEEWS has begun the siting process. The Maine Power Reliability Program also has received siting approval and is under construction.

Transmission planning studies show the system needs and transmission additions required for the ISO’s continued compliance with NERC and NPCC reliability standards and criteria. Beginning in 2012, the ISO began including in needs assessments and resulting solutions studies the impact of future energy-efficiency programs beyond those participating in the Forward Capacity Market. The need for some system improvements is being delayed or the preferred solutions are being reassessed as a result of the energy-efficiency forecast that reduces the summer peak demand from 2015 through 2021.This includes the Interstate Reliability Project, which has been reassessed, and the Central Connecticut Reliability components of NEEWS.

- Fuel Diversity—New England remains heavily dependent on natural gas as a primary fuel for generating electric energy for the foreseeable future; natural gas plants represented 42.6% of the region’s generating capacity and provided 51.3% of the system’s electrical energy in 2011. The region’s dependence on natural gas is expected to increase as additional natural gas capacity replaces older coal, oil, and nuclear units. The Strategic Planning Initiative identifies this increased reliance on natural gas as a major near- and longer-term issue:

  - The addition of renewable resources would provide some diversity of the fuel supply; however, the increased regulation and reserve requirements needed to reliably integrate new variable energy resources could place new stresses on the natural gas delivery system that would need to provide fuel to generators on short notice.

  - Many natural-gas-fired units lack dual-fuel capability or may be unable to switch fuels within the timeframes required to meet system reliability needs.

The 2011 Natural Gas Study quantifies the potential amounts of natural gas shortages for several scenarios. These results show the need for additional natural gas system infrastructure or for the use of non-gas-fired resources, such as generators with dual-fuel capability, renewable resources, and demand resources.

- Environmental Regulations and Initiatives—While New England’s generators have significantly reduced their SO2, NOX, and CO2 emissions over the last decade, new and pending environmental regulations for the region and neighboring areas will add requirements for generators to reduce their emissions even further. These regulations cover ozone precursors, fine particulate matter, and toxic air emissions. Other pending EPA actions would require thermal generating stations to enhance their control measures for mitigating the adverse impacts from cooling water withdrawals and various other generating stations to limit the waste streams from their water discharges. The ISO estimates that up to 12.1 GW of fossil fuel and nuclear capacity could be subject to cooling water mitigation requirements, and a subset of 5.6 GW (those with larger withdrawal capacities) could be required to convert to closed-cycle cooling systems by 2021. Some cooling water retrofits in the region will be required earlier. Approximately 7.9 GW of existing coal steam or oil steam units over 25 MW are subject to the final Mercury and Air Toxics Standards and must come into compliance by early 2015. However, less than 1 GW of generators are anticipated to retire because of the need for compliance with MATS. The Cross-State Air Pollution Rule has been suspended temporarily and its predecessor, the Clean Air Interstate Rule, reinstated, requiring compliance from generators in Connecticut and Massachusetts during the summer ozone NOX control season.

Environmental controls necessary for compliance with these regulations will likely increase the capital investments and operating costs for fossil fuel and nuclear plants. Although the FCM allows resources with a significant investment in environmental upgrades to qualify as new resources, making them eligible for established FCM revenues for up to five years, this provision may not be sufficient to pay for all required remediation measures. By 2021, environmental compliance obligations could result in limitations in energy production and available generation capacity. The Strategic Planning Initiative identified as a near-term issue generating unit retirements resulting from their inability to comply with upcoming environmental obligations. Most of the at-risk capacity faces compliance or retirement decisions later this decade, which is expected to affect positions in upcoming FCA auctions. The ISO continues to identify such generators and study potential impacts.

The RGGI program review is expected to be completed late in 2012. RGGI allowance auction proceeds have provided over $304 million to the six New England states for their energy-efficiency assistance programs and renewable resource development. New England RGGI generators’ CO2 emissions for 2010 were 24.4% below the region’s RGGI budget of 55.8 Mtons. The 2011 emissions were 36% below the budget.

- Meeting State Targets for Renewable Energy—The New England states have targets for the proportion of electric energy to be provided by renewable resources and energy efficiency. The ISO projects that electric energy reductions from passive demand resources, as reported in the 2012 CELT, along with the New England state targets for renewable resources, will meet approximately 31.8% of New England’s total projected electric energy use by 2021. This consists of 11.6% for energy efficiency from the passive demand resources reported in the CELT and 20.2% for Renewable Portfolio Standards and policies addressing renewable supply goals.

Options for meeting, or exceeding, the region’s RPS targets include developing the renewable resources in the ISO queue, importing qualifying renewable resource energy from adjacent balancing authority areas, building new renewable resources in New England not yet in the queue, developing “behind-the-meter” projects, and using eligible renewable fuels in existing generators. Analysis of the renewable resources in the queue indicates that all these resources alone would meet the growth of RPS targets through 2018, assuming all state energy-efficiency targets are met. Even if only 40% of the renewable resources in the queue were developed, they would meet the RPS goals through the year 2014. A NESCOE request for information identified potential amounts and locations of renewable resources the New England region could readily access. The responses to the RFI showed the potential production by renewable resources of approximately 15,000 GWh annually, enough to exceed the regional RPS target for 2021.

- Integrating Intermittent Renewable Resources—The ISO completed the New England Wind Integration Study that analyzed various planning, operating, and market aspects of wind integration based on simulations for scenarios that added up to 12 GW of wind resources. The study developed models of generation output for a hypothesized fleet of wind plants suitable for the ISO’s future planning studies and conceptual transmission systems for each scenario. The study concluded that the large-scale integration of wind resources is feasible in the New England region, but the region will need to address a number of system operating issues associated with wind integration. Many of the recommendations currently are being implemented, such as forecasting wind production. Solar photovoltaic resources have grown in the region in recent years, and continued growth is anticipated. The ISO will continue to track this growth as well and any potential operational issues that emerge as a result. New England is a leader in applying advanced technologies, including FACTS and HVDC, phasor measurement units, and smart meters, which may be used to provide the regulation and reserve services required to reliably integrate intermittent renewable resources.

- Economic and Interregional Planning Studies—The ISO is conducting a transmission system study of replacing aging coal- and oil-fired generating units with wind resources within New England and renewable resource imports from Canada. This Strategic Transmission Analysis is developing conceptual transmission buildouts to inform stakeholders and government officials as they establish policies that affect the future planning and development of the system.

The 2011 economic study examined several scenarios of wind development in northern New England and identified potential transmission bottlenecks in the Wyman/Bigelow area and interfaces in northern New England, such as Surowiec South. The ISO also is conducting economic studies in response to stakeholder requests received in 2012. These studies will examine a number of resource development and retirement scenarios that will evaluate various economic study metrics, including production costs, environmental emission performance, and congestion. These metrics will be used to show the locational effects of adding or retiring resources and the need for transmission development. The study also will show various economic and environmental metrics for renewable and demand-resource scenarios.

The economic studies reinforce several of the strategic issues the region is assessing: connecting renewable wind energy remote from the load centers; replacing older, higher-emitting coal- and oil-fired generators with cleaner-burning natural-gas-fired generators; and decreasing load-serving entity electric energy expenses while maintaining sufficient market revenues for resources. In addition to the New England economic studies, interregional production cost studies have been coordinated successfully through considerable effort by ISO/RTO personnel and stakeholders.

In addition to coordinating planning activities with the New England states, ISO New England proactively coordinates activities with neighboring ISO/RTO systems in the NPCC, across the Eastern Interconnection through the Eastern Interconnection Planning Collaborative, and nationally through NERC. The ISO has jointly issued the Northeast Coordinated System Plan 2011 with NYISO and PJM, which summarizes interregional planning issues. Sharing more supply and demand resources with other systems will likely become necessary, particularly to meet environmental compliance obligations and successfully integrate variable energy resources. Identifying interregional system needs and the potential impacts that proposed generating units and transmission projects could have on neighboring systems is beneficial for supporting interregional reliability and economic performance.

- Federal, Regional, and State Initiatives—The ISO continuously works with a wide variety of state policymakers and other regional stakeholders through its planning process. Regional initiatives have improved the transparency of transmission cost estimates, provided critical load levels and other information on market resources in needs assessments, and demonstrated progress in improving a forecast of energy efficiency. The ISO has continued to provide technical support to a number of state agencies and groups, such as NECPUC, the New England Governors’ Conference, the Consumer Liaison Group, NESCOE, and others. The planning process will continue to evolve in response to FERC and other policy developments.

Active involvement and participation by all stakeholders, including public officials, state agencies, NESCOE, market participants, and other PAC members, are key elements of an open, transparent, and successful planning process. As needed, the ISO will work with these groups, as well as NEPOOL members and other interested parties, to support regional and federal policy initiatives, one of which is compliance with FERC Order No. 1000 on transmission planning and cost allocation. The ISO will continue to provide required technical support to the New England states and the federal government as they formulate policies for the region.

Appendix A
Glossary

The RSP12 Glossary defines a number of terms appearing in the RSP for facilitating reader understanding of the electric power system and markets. It is not a comprehensive list of definitions or the precise definitions included in the OATT and market rules.

| Term | Definition |
| --- | --- |
| 10-minute nonspinning reserve (TMNSR) | Operating reserve provided by off-line generation that can be electrically synchronized to the system and increase output within 10 minutes in response to a contingency; also called 10-minute nonsynchronized reserve. |
| 10-minute spinning reserve (TMSR) | Operating reserve provided by on-line operating generation that can increase output within 10 minutes in response to a contingency. |
| 30-minute operating reserve (TMOR) | Operating reserve provided by on-line or off-line operating-reserve generation that can either increase output within 30 minutes or be electrically synchronized to the system and increase output within 30 minutes in response to a contingency. (Also see spinning and nonspinning.) |
| 50/50 peak load | A peak load with a 50% chance of being exceeded because of weather conditions, expected to occur in the summer in New England at a weighted New England-wide temperature of 90.2°F, and in the winter, at 7.0°F. |
| 90/10 peak load | A peak load with a 10% chance of being exceeded because of weather conditions, expected to occur in the summer in New England at a weighted New England-wide temperature of 94.2°F, and in the winter, 1.6°F. |
| abnormal condition | When the reliability of the New England power system is degraded. |
| Abnormal Conditions Alert | An ISO notice to applicable power system operations, maintenance, construction, and test personnel, and applicable market participants, about an existing abnormal condition affecting the reliability of the electric power system or about an anticipated abnormal condition. |
| activated carbon injection | A post-combustion mercury control system for a coal-fired electric power plant, which injects specially treated activated carbon into the flue gas where it absorbs mercury that is then removed by a downstream particulate-control device. |
| active demand resource | A resource that reduces load in response to a request from the ISO for system reliability reasons or in response to a price signal. |
| administrative export delist bid | A type of delist bid submitted during a Forward Capacity Auction for capacity exports associated with multiyear contracts but wanting to opt out of a capacity supply obligation, initiated using the same requirements as for export delist bids. (See delist bid and export delist bid.) |
| ambient-air delist bid | A type of delist bid submitted for a thermal generator for opting out of a Forward Capacity Auction capacity supply obligation to reflect that the generator’s summer capability is less than its winter capability because high ambient air temperatures can reduce the generator’s capacity ratings. (See delist bid.) |
| ancillary service | A service provided to the system other than power, including regulation, reserve, and voltage support. |
| assumed marginal unit | An electric generating unit assumed to increase or decrease generation to economically meet a unit change in load, usually calculated for 1 MW. (See marginal emissions rate.) |
| balancing authority area | For compliance with North American Electric Reliability Corporation reliability standards, an area comprising the generation, transmission, and loads within metered boundaries for which a responsible entity (defined by NERC to be a balancing authority) integrates the resource plans for that area, maintains the area's load-resource balance, and supports the area's interconnection frequency in real time. Balancing authority areas were formerly known as control areas. |
| baseload generating unit | A generator that satisfies all or part or the minimum load of the system, producing electric energy continuously—typically more than 70% of the year—at a constant rate, and close to maximum output. These units usually are economical to operate day to day. |
| best technology available (BTA) | A technology-based standard established under the US Clean Water Act that requires power plants and other industrial facilities to use the most effective technology, process, or operational method available, as set by a local permitting authority, for minimizing the adverse environmental impacts of cooling water intake structures. |
| bilateral trading | The purchase and sale of electric energy or regulation obligations between two market participants. The energy (megawatts) is traded through the ISO from one market participant to another. |
| blackout | The unplanned and emergency loss of electric service to load because of a failure of the generation, transmission, or distribution system. |
| black start | When a generating unit goes from a shutdown condition to an operating condition without electrical support from the grid after a system blackout. |
| bottled-in generation | When electricity cannot be produced in one area because one or more transmission constraints prevents it from being transmitted to other areas |
| bottled-in wind energy | Potential wind energy not producing electrical energy to respect binding transmission constraints. |
| bus | An electrical node or point of interconnection to the system where power is available for transmission. Also, an electrical conductor that serves as a common connection for two or more electrical circuits. |
| capability year | See capacity commitment period. |
| Capacity Capability Interconnection Standard | An ISO capacity and energy requirement to ensure intrazonal deliverability by avoiding the redispatch of other capacity network resources; includes the same criteria as the Network Capability Interconnection Standard and criteria. |
| capacity commitment period | The one-year period from June 1 to May 31 of the following year for which Forward Capacity Market obligations are assumed and payments are made. Also called capability year. |
| capacity factor | The ratio of the electrical energy a generating unit produced for a certain period to the electrical energy it could have produced at full operation during the same period. |
| capacity supply obligation (CSO) | A requirement for a resource to provide capacity, or a portion of capacity, to satisfy a portion of the ISO’s Installed Capacity Requirement. CSOs are acquired through a Forward Capacity Auction, a reconfiguration auction, or a CSO bilateral contract through which a market participant may transfer all or part of its CSO to another entity. |
| capacity zone | Determined before each Forward Capacity Auction, a geographic subregion of the New England Balancing Authority Area that may represent a load zone that is export constrained (having a maximum capacity limit), import constrained (having a local sourcing requirement), or contiguous—neither export nor import constrained. These limits and requirements are based on network models using lines that will be in service no later than the first day of the relevant capacity commitment period. |
| carbon dioxide leakage | Increased CO2 emissions from lower-cost electric energy generated outside the Regional Greenhouse Gas Initiative region and imported into the region, offsetting, in part, the CO2 emissions by generators within the RGGI states. |
| claimed capability | A generator's maximum production or output. |
| compound annual growth rate (CAGR) | A calculation of the rate at which electric energy use or peak load would have grown if it grew at a steady rate. The CAGR equals the nth root of the total percentage growth rate, where n equals the number of years in the period under consideration. |
| congestion | A condition that arises on the transmission system when one or more restrictions prevents the economic dispatch of electric energy resources from serving load. Also, a condition that occurs when the transfer capability is insufficient for simultaneously implementing all the preferred schedules for the transmission of electric energy. |
| constraint | The maximum level a transmission system facility (or facilities) can operate to respect the most restrictive of its thermal, stability, and voltage limits. |
| contingency | The unplanned disconnection from the electricity grid of one or more power system elements, such as a generation or transmission facility. (See first contingency and second contingency.) |
| cost of new entry (CONE) | A pricing threshold derived from the capacity clearing prices established in the Forward Capacity Auctions, except for FCA #1, where it was administratively set. CONEs are used to (1) establish the starting price for each FCA, (2) set thresholds for reviewing delist bids to deter the exercise of market power, (3) set initial pricing for some reconfiguration auctions, and (4) determine pricing when the supply is inadequate and competition is insufficient. |
| critical load level | The load level at which transmission constraints are respected but where system problems could occur for small incremental changes in load levels. |
| Day-Ahead Energy Market | A market that produces financially binding schedules for the production and consumption of electric energy one day before the operating day. |
| delist | The temporary removal of a facility from service for various reasons, usually associated with maintenance; the removal of a facility from the Forward Capacity Market. A classification for facilities that can be brought back on line relatively easily. |
| delist bid | A submission in a Forward Capacity Auction for an existing Forward Capacity Market resource indicating that the resource wants to opt out of the auction before the deadline for qualifying its existing capacity and does not want a capacity obligation below a certain price. (See administrative export delist bid, ambient-air delist bid, dynamic delist bid, export delist bid, permanent delist bid, static delist bid, and nonprice retirement request.) |
| demand | Load; the amount of electrical power used; the level of electricity consumption, measured in megawatts, at a particular time. |
| demand resource | A capacity product, type of equipment, system, service, practice, or strategy that verifiably reduces end-use demand for electricity from the power system. Demand-resource measures include the use of energy-efficient appliances and lighting, advanced cooling and heating technologies, electronic devices to cycle air conditioners on and off, and equipment to shift load to off-peak hours of demand. See active demand resource and passive demand resource. |
| demand-resource dispatch zone | Any one of 19 groups of nodes used to dispatch real-time demand-response resources or real-time emergency generation resources. |
| demand response | When market participants reduce their consumption of electric energy from the network when instructed in exchange for compensation based on wholesale market prices. The ISO operates three types of demand-response programs: those activated by price, those activated for reliability, and those that reduce on-peak consumption. |
| deterministic analysis | A type of analysis based on a snapshot of assumed specific conditions for a specific scenario. This type of analysis does not quantify the likelihood that these conditions will actually materialize. (See probabilistic analysis.) |
| distributed generation (DG) | Generation provided by relatively small, on-site installations directly connected to distribution facilities or retail customer facilities and not the regional power system, which can alleviate or prevent regional power system transmission or distribution constraints or reduce or eliminate the need to install new transmission or distribution facilities. A small (24 kilowatt) solar photovoltaic system installed by a retail customer is an example of distributed generation. |
| dual-fuel capability | When a generator has the flexibility and storage capacity to use two types of fuel, typically oil as well as natural gas. |
| dynamic delist bid | A type of delist bid submitted during a Forward Capacity Auction to indicate that a resource wants to opt out of a capacity supply obligation below a certain price in the auction and, unlike other types of delist bids, that can be offered below 0.8 times the Forward Capacity Market’s cost of new entry (CONE) threshold price. (See delist bid.) |
| Eastern Interconnection | One of two major AC power grids in North America spanning from central Canada eastward to the Atlantic coast (excluding Québec), south to Florida, and west to the foot of the Rocky Mountains (excluding most of Texas—the portion in the Electric Reliability Corporation of Texas) that, during normal system conditions, interconnects transmission and distribution infrastructure and operates at a synchronized frequency of 60 Hz average. The Eastern Interconnection is tied to the Western Interconnection, the Texas Interconnection, and the Québec Interconnection through numerous high-voltage DC transmission lines. |
| economic dispatch | The selection of resources available to satisfy system load as inexpensively as possible, which is run every five minutes to reoptimize the generation to meet load at minimum cost. |
| economic-merit order | When the generators with the lowest-price offers are committed and dispatched first, and increasingly higher-priced generators are brought on line as demand increases. |
| Elective Transmission Upgrade (ETU) | An upgrade to the New England transmission system voluntarily funded by one or more participants that have agreed to pay for all the costs of the upgrade. |
| emergency outage | A type of unplanned outage when a piece of transmission equipment fails and comes out of service on its own or requires immediate operator intervention to remove it from service. |
| emissions allowance | Under an emissions trading program the authorization for a source of a pollutant to emit one ton of the pollutant during a specific compliance period. At the end of a compliance period, the source must hold an amount of allowances at least equal to its annual emissions. |
| energy efficiency | A type of demand resource that reduces the total amount of electrical energy and capacity at an end-use customer’s facility that otherwise would have been needed to deliver an equivalent level of end-use service. Such measures or systems include the use of more efficient lighting, motors, refrigeration, HVAC equipment, control systems, and industrial process equipment. See passive demand resource. |
| energy-efficiency forecast (EEF) | A predictive tool to calculate anticipated load reductions in response to state energy-efficiency programs. |
| established Installed Capacity Requirement | An Installed Capacity Requirement value approved by FERC or that the ISO has filed with FERC for subsequent approval. |
| existing Forward Capacity Market resource | An FCM-qualified generating or import capacity resource or demand resource that has a Forward Capacity Auction capacity supply obligation that counts toward meeting the ISO’s Installed Capacity Requirement. |
| export delist bid | A type of Forward Capacity Auction delist bid for a resource that wants to opt out of a capacity supply obligation, similar to a static delist bid but that may have an opportunity-cost component as part of the supporting cost data. (See delist bid.) |
| export-constrained load zone | An area where the available resources, after serving local load, exceed the area’s transmission capability to export the excess electric energy. |
| fast-start resource | A resource that can be electrically synchronized to the system and reach its maximum production or output within 10 to 30 minutes to respond to a contingency and serve demand. Also a demand resource that helps with recovery from a contingency and assists in serving peak demand. Same as quick-start resources; fast-start resources is preferred. |
| feed-in tariff (FIT) | A part of a long-term electricity purchasing agreement that guarantees a specified price, usually above the market level, for the electric power produced under the agreement. |
| Financial Transmission Right (FTR) | A financial instrument—equal to the amount of electric energy flowing in one direction between two specific locations on the regional power system—that a market participant can buy to help hedge against the economic impacts associated with transmission congestion and to arbitrage differences between expected and actual day-ahead congestion caused by constraints on the transmission system. The FTR holder might incur an obligation to pay a charge or the right to receive revenues. |
| firm supply | Fuels under a delivery contract that includes priority transportation service and that cannot be interrupted or restricted. |
| first contingency (N-1) | The loss of the power element (facility) with the largest impact on system reliability. See contingency and second contingency.) |
| flexible alternating-current transmission system (FACTS) | A system that incorporates power electronic controllers and other static equipment to enhance the controllability of transmission system parameters and increase power-transfer capability. |
| floor price | An administratively set price, which currently is used in the ISO’s Forward Capacity Auctions. |
| flue-gas desulfurization (FGD) | A post-combustion control system for sulfur dioxide (SO2) and other acid flue gases produced by a coal- or oil-fired electricity generating unit, which injects a type of lime, using wet or dry means, into a ”scrubber” where it reacts with the SO2 and other gases. The reaction products are then removed either in the scrubber or in conjunction with a downstream particulate-control device. Also called wet or dry scrubbing. |
| forced outage | A type of unplanned outage that involves the unexpected removal from service of a generating unit, transmission facility, or other facility or portion of a facility because of an emergency failure or the discovery of a problem. These problems must be repaired as soon as crews, equipment, corrective dispatch actions, or a combination of all measures can be activated to allow the work to be performed. |
| Forward Capacity Auction (FCA) | The annual auction of the Forward Capacity Market during which capacity resources compete to obtain a commitment to supply capacity in exchange for a market-priced capacity payment. In the "descending-clock” format of the FCAs, the price for capacity is decreased until the quantity of capacity remaining in the auction equals the quantity of capacity needed. This auction allows new capacity to set the market-clearing price while accounting for locational capacity requirements and providing a market-based measure of the cost of new entry. |
| Forward Capacity Market (FCM) | A locational capacity market in the New England Balancing Authority Area whereby the ISO projects the needs of the power system three years in advance and then holds an annual auction to purchase power resources to satisfy the region's future needs. The aim of the FCM is to send appropriate price signals to attract new investment and maintain existing resources where and when needed to help ensure the reliability of the New England electricity grid. |
| Forward Reserve Market (FRM) | A market of the New England Balancing Authority Area for acquiring forward commitments for the delivery of 10-minute nonspinning or 30-minute operating reserves in real time. The market provides incentives (competitive price signals) for investing in new reserve resources, particularly fast-start generation, in areas where operating reserves are needed to support system reliability. |
| frequency | The rate of oscillation (cycles/second) of the alternating current in an electric power system, measured in hertz (Hz). In the United States, the rate is 60 Hz. |
| frequency ride through | The capability of a generator to remain connected to the power system during frequency excursions defined (in IEEE Standard 1547) as tolerable and caused by events external to the generating plant. (The Institute of Electrical and Electronics Engineers [IEEE] 1547 Standard provides uniform criteria for interconnecting distributed resources with electric power systems.) |
| generating resource, generating unit, generator | A facility that produces electric energy. (See resource.) |
| generation | The production of electric energy from other sources of energy (i.e., fuel), expressed in megawatts; supply. |
| Generator Interconnection-Related Upgrade | A transmission addition or upgrade to support the connection of a new or uprated generating facility in ISO New England. |
| greenhouse gas (GHG) | Any gas that absorbs infrared radiation in the atmosphere. Greenhouse gases include carbon dioxide, methane, nitrous oxide, ozone, chlorofluorocarbons, hydrochlorofluorocarbons, hydrofluorocarbons, perfluorocarbons, and sulfur hexafluoride. |
| grid | The network of the transmission lines, substations, and associated equipment of an electric power system. |
| GridView | A production cost program that provides detailed representations of the transmission network. |
| hazardous air pollutant (HAP) | A US Clean Air Act category of air pollutants known or suspected of causing cancer and other serious health effects, such as reproductive effects or birth defects, or adverse environmental effects. HAPs emitted by fossil-fired generators include acid gases, such as hydrogen chloride (HCl) and hydrogen fluoride (HF); organic pollutants, such as dioxins and furans; mercury; and other metallic HAPs, such as arsenic, chromium, nickel, and selenium. HAPs also are known as toxic air pollutants or air toxics. |
| heat rate | A measure of a thermal power plant’s efficiency of converting fuel to (Btu) to electricity (kWh); the amount of heat, measured in British thermal units (Btus), required to produce a kilowatt-hour of electrical output. The lower the heat rate, the more efficient the facility. |
| high-voltage direct current (HVDC) | Typically, when the direct-current voltage is above 100 kilovolts. |
| high-voltage transmission line | A line that transmits electric power from a generator to a local distribution line. In New England, these lines include 115 kV and higher voltage lines. (See low-voltage lines.) For purposes of the RSP, extra-high-voltage lines, 345 kV and above, are included in this definition. |
| historical energy-efficiency savings | Reductions in past power system loads resulting from energy-efficiency measures. |
| Hub | A specific set of predefined pricing nodes on the power system for which the ISO calculates locational marginal prices are which are used to establish reference prices for electric energy purchases, the transfer of day-ahead and real-time adjusted load obligations, and the designation of Financial Transmission Rights. |
| Hydro-Québec Interconnection Capability Credits (HQICCs) | A monthly value defined in the ISO New England Transmission, Markets, and Services Tariff that reflects the annual installed capacity benefits of the HQ Interconnection, as determined by the ISO using a standard methodology on file with FERC. HQICCs are used to modify the Installed Capacity Requirement. |
| import-constrained load zone | An area that does not have enough local generating resources and transmission-import capability to serve local demand reliably or economically. |
| Independent System Operator (ISO). | An independent, federally regulated organization formed at the recommendation of FERC to impartially coordinate, control, and monitor the operation of a regional electric power system, including the dispatch of electric energy over the system and the monitoring of the electricity markets, for ensuring the safety and reliability of the system. |
| in-merit generation | See economic merit order. |
| in service | When a unit or transmission line is available for use. |
| installed capacity | The megawatt capability of a generating unit, dispatchable load, external transaction or resource, or demand resource that qualifies as a participant in the ISO’s Forward Capacity Market. |
| Installed Capacity Requirement (ICR) | The minimum amount of resources (level of capacity) a balancing authority area needs in a particular year to meet its resource adequacy planning criterion, according to the Northeast Power Coordinating Council resource adequacy criterion, A-2, Basic Criteria for Design and Operation of Interconnected Power Systems. This criterion states that the probability of disconnecting any firm load because of resource deficiencies must be, on average, less than once in 10 years. |
| intermediate-load generating unit | A generator that ramps up and down to follow the system load as it transitions between baseload levels (during the middle of the night) and peak-load levels (during the day), operating from 10 to 70% of the year. |
| Interregional Electric Market Model (IREMM) | A “pipe and bubble” production cost program that models the region’s subareas (bubbles) and the transmission lines that connect them (pipes) for developing hourly, chronological, system-production costs and other metrics. |
| ISO Generator Interconnection Queue (the queue) | The listing of generators that have submitted requests to interconnect to the ISO New England transmission system. |
| landfill gas (LFG) | The gas resulting from landfill decomposition that either is collected, cleaned, and used for generation or is vented or flared |
| large generator interconnection procedure (LGIP) | Standard procedures for the interconnection of generating units larger than 20 MW, per the ISO’s Transmission, Markets, and Services Tariff, Section II, Schedule 22. |
| load | The demand for electricity measured in megawatts; electricity consumption; the amount of electric power delivered to any specified point on a system, accounting for the requirements of the customer's electrical equipment. |
| load factor | The ratio of the average hourly load during a year to peak hourly load. |
| load forecast | An estimation of the future demand for electricity. |
| load pockets | Areas of the system that require local generation to meet demand because the transfer capability of the transmission system is insufficient to serve the load in the area. |
| load-serving entity (LSE) | An entity that secures and sells electric energy, transmission service, and related services to serve the demand of its end-use customers at the distribution level. |
| load shedding | Controlled or scheduled power outages (controlled blackouts) to balance the demand for electricity with limited supply. |
| load zone | An aggregation of pricing nodes within a specific area. |
| local gas distribution companies (LDCs) | Entities that transfer natural gas from pipelines to consumers; equivalent to load-serving entities. |
| local sourcing requirement (LSR) | The minimum amount of capacity that must be electrically located within an import-constrained load zone to meet its share of the Installed Capacity Requirement. |
| locational marginal price (LMP) | The calculated price of electric energy at a pricing node, load zone, reliability region, or the Hub based on the patterns of load, generation, and the physical limits of the transmission system. |
| loss-of-load-expectation (LOLE) analysis | A probabilistic analysis used to identify the amount of installed capacity (in MW) the system needs to meet the NPCC and ISO resource adequacy planning criterion to not disconnect firm load more than once in 10 years. |
| low-capacity-factor generating unit | A generating unit with an annual capacity factor of less than 10%. |
| low-voltage transmission line | A transmission line, usually with a voltage of less than 66 kV, which delivers electric power from local distribution company facilities to homes and businesses. (See high-voltage transmission line.) |
| marginal emissions rate | A measure (lb/MWh) of the energy-weighted average emissions from a unit that would typically increase its output if the regional energy demand were higher during the period of interest In New England. “Assumed marginal units” typically are natural-gas-fired generators and oil-fired generators, including those burning residual, distillate, diesel, kerosene, and jet fuel. The marginal emissions rate is calculated by dividing the emissions from the assumed marginal units during the desired period in pounds (lb) by the generation from the assumed marginal units (MWh). Assumed marginal units also may be expressed as lb/MMBtu by applying a systemwide conversion factor. |
| marginal heat rate | A measure (MMBtu/MWh) of how efficiently assumed marginal units (i.e., in New England, units fueled with natural gas or oil, including residual, distillate, diesel, kerosene, and jet fuel) convert fuel to electricity. This rate is equal to the amount of fuel consumed by the assumed marginal units divided by the actual generation of the assumed marginal units. |
| marine and hydrokinetic energy (MHK) | Technologies that use waves, currents, and ocean thermal resources to generate electricity. |
| Market Efficiency Transmission Upgrade (METU) | A type of transmission upgrade in ISO New England primarily designed to reduce the total net production cost to supply the system load, including the costs for electric energy, capacity, reserves, and losses and those associated with bilateral prices for electricity. |
| market participant | An entity in the New England wholesale electricity markets that has executed a Market Participant Service Agreement or on whose behalf an unexecuted agreement has been filed with the Federal Energy Regulatory Commission. |
| market resource alternative | Supply or demand resources at one or multiple locations in an area that can meet a transmission system reliability need in that area. |
| maximum capacity limit (MCL) | The maximum amount of capacity that can be procured in an export-constrained load zone for meeting the Installed Capacity Requirement. |
| mechanical draft cooling tower | A device of a power plant (or other industrial facility) that cools heated process water or other fluid using mechanical fans that draw air through the tower and into contact with the heated fluid. |
| merchant transmission facility | An independently developed and funded facility in the region subject to the operational control of the ISO, pursuant to an operating agreement specific to each of these facilities. |
| Minimum Generation Emergency | A type of abnormal system condition declared by the ISO for which it anticipates requesting one or more generating resources to operate at or below its economic minimum limit. A widespread power outage that greatly reduces the demand for electricity compared with the forecasted demand is one type of situation for which the ISO will declare a Minimum Generation Emergency to reduce the excess amount of electric power available. |
| N-1 | See first contingency. |
| N-1-1, N-2 | See second contingency. |
| nameplate capacity, nameplate | The rating of a generator and a measure of its ability to produce electricity. |
| National Corridor | Geographic regions identified by the US Department of Energy as locations where transmission congestion or constraints adversely affect consumers; also called National Interest Electric Transmission Corridors. |
| natural draft cooling tower | A device of a power plant (or other industrial facility) that cools heated process water or other fluid using exhaust air rising in a hyperbolic shape of sufficient elevation (reaching 500 ft), which creates a temperature differential between the top and bottom of the tower and cools the heated fluid as it contacts the rising air. |
| net commitment-period compensation (NCPC) | A “make-whole” payment to a supply resource that responded to the ISO’s dispatch instructions but did not fully recover its start-up and operating costs in either the Day-Ahead or Real-Time Energy Markets. |
| net energy for load (NEL) | The net generation output within a balancing authority area, accounting for electric energy imports from other areas and subtracting energy exports to others. It includes system losses but excludes the electric energy required to operate pumped storage plants. |
| Network Capability Interconnection Standard (NCIS) | An energy-only standard that includes the minimum criteria the ISO requires to permit a generator to connect to the transmission system so that it has no adverse impacts on reliability, stability, or the operation of the system. |
| New England Power Pool (NEPOOL) | A group formed in 1971 by the region's private and municipal utilities to foster cooperation and coordination among the utilities in the six-state region for ensuring a dependable supply of electricity. Today, NEPOOL members are ISO stakeholders and market participants. |
| new Forward Capacity Market resource | (1) A resource that has never previously been counted as a capacity resource or (2) a resource or portions of a resource that previously has been counted as capacity but now meets certain criteria governing an increase of output or financial investment. |
| no. 1 diesel fuel | A light distillate fuel oil used in high-speed diesel engines generally operated under frequent speed and load changes, such as those in city buses and similar vehicles. |
| no. 1 fuel oil | A light distillate fuel oil used primarily for portable outdoor stoves and portable outdoor heaters. |
| no. 2 fuel oil | A high-grade distillate fuel oil used for residential heating and moderate-capacity commercial and industrial burner units and as a backup fuel for peaking power plants. Also referred to as no. 2 distillate, no. 2 diesel fuel oil, heating oil, light fuel oil, or diesel fuel oil. |
| no. 4 fuel oil | Typically, a blend of distillate and residual fuel oils, such as no. 2 and no. 6 fuel oils, classified as diesel, distillate, or residual fuel oil. |
| no. 5 fuel oil | Part of the remaining component of crude oil after gasoline and other distillate fuel oils are extracted. Typically a mixture of no. 6 (75 to 80%) and no. 2 fuel oils; also referred to residual fuel oil or heavy fuel oil. |
| no. 6 fuel oil | Remaining component of crude oil after gasoline and distillate fuel oils are extracted; used by oil-burning power plants. No. 6 oil (1%) refers to the percentage of sulfur in the oil. referred to as residual fuel oil or heavy fuel oil. |
| nonfirm gas | Natural gas delivered under a contract that allows the transportation service to be interrupted to avoid interfering with or restricting gas deliveries having a higher priority. |
| nonprice retirement request | An irrevocable request in a Forward Capacity Auction to retire the entire capacity of a resource, subject to an ISO review for reliability impacts and that supersedes any other delist bids submitted. If the ISO determines the resource is needed for reliability, the resource owner can either retire the resource as requested or continue to operate it until the reliability need has been met and then retire the resource. (See delist bid.) |
| nonspinning | Off-line generation not synchronized to the system. |
| nonsynchronized reserves; nonspinning reserves | Off-line fast-start resources that can be electrically synchronized to the system quickly and reach rated capacity to respond to a contingency and serve demand. |
| off-peak hours | In New England, weekday hours between 11:00 p.m. and 7:00 a.m. and all day Saturdays, Sundays, and holidays. (See peak hours.) |
| operable capacity analysis | An estimate of the availability of a power system's net capacity under specific scenarios and load conditions. The results are in the form of operable capacity margins, which show either an expected system surplus or a deficiency in meeting the conditions. |
| operable capacity margins | The amount of resources that must be operational to meet peak demand plus operating-reserve requirements of the electric power system. |
| operating day | A calendar day, beginning at midnight, during which market transactions are scheduled. |
| operating reserve | The megawatt capability of a power system greater than system demand, which is required for providing frequency regulation, correcting load forecasting errors, and handling forced outages and is drawn from spinning and nonspinning sources of power. Also, the synchronized (spinning) or nonsynchronized (nonspinning) reserves that may be used to recover from a contingency. |
| out of economic-merit order (out of merit) | Capacity (in megawatts) that is more expensive than the marginal, price-setting, supply offer. |
| out-of-merit dispatch | When higher-priced generators are committed and dispatched before lower-priced resources to respect system reliability requirements, which results in increased cost to load. |
| overlapping interconnection impact analysis | A study for each new supply-side resource that assesses whether the resource can provide useful capacity and electric energy without negatively affecting the ability of other capacity resources to provide these services also. |
| participating transmission owner (PTO) | An entity that owns and maintains transmission facilities. |
| particulate matter (PM); PM10; PM2.5 | A mixture of solid particles and liquid droplets suspended in the air, originating from a variety of sources, such as power plants, industrial processes, and diesel trucks; also formed in the atmosphere by transformation of gaseous emissions. PMs are composed of both coarse and fine particles, although their chemical and physical compositions vary depending on location, time of year, and weather. PM10 refers to inhalable coarse particles larger than 2.5 micrometers in diameter but smaller than 10 micrometers. PM2.5 refers to fine particles with diameters less than 2.5 micrometers. |
| passive demand resource | A demand resource principally designed to save electric energy use, which is in place at all times without requiring direction from the ISO. Passive demand resources include energy-efficiency measures, such as the use of energy-efficient appliances and lighting, advanced cooling and heating technologies, electronic devices to cycle air conditioners on and off, and equipment to shift load to off-peak hours of demand. |
| peak hours | In New England, the hours between 7:00 a.m. and 11:00 p.m. on nonholiday weekdays. (See off-peak hours.) |
| peaking unit | Units usually on line during very high, peak-day load periods that may be used in response to system contingencies because they can start quickly on demand and operate for only a few hours; typically operates less than 10% of the year (i.e., a few hundred hours per year). |
| permanent delist bid | A delist bid that prohibits a resource from participating in any future Forward Capacity Auction (FCA) or assuming any capacity obligation unless it qualifies for and clears as a new resource in a subsequent FCA. (See delist bid.) |
| phasor measurement unit (PMU) | A device that measures the electrical waves on a power grid at many remote sites using synchronized real-time measurements (i.e., synchrophasors) and global positioning satellite (GPS) technology to monitor the performance of the grid accurately and provide specific data for operating the system and enhancing its design. |
| pool transmission facility (PTF) | A facility rated 69 KV or above owned by a participating transmission owner over which the ISO has operating authority. |
| price response | The reduction of electricity consumption in response to a price signal from the ISO in exchange for compensation based on wholesale electricity prices. (Also see demand response.) |
| pricing point (pnode) | Any one of approximately 900 locations on the transmission system (external interface, load node, individual unit node, load zone, and the Hub, which are collections of pnodes) for which the ISO calculates and publishes prices. |
| probabilistic analysis | A type of analysis that statistically estimates the likelihood of an event taking place and recognizes that the inputs are uncertain. (See deterministic analysis.) |
| PROMOD | A production cost program that provides detailed representations of the transmission network. |
| pumped storage facility | A generating facility that pumps water up to a storage pond, often during periods of low electric energy demand and lower costs, to produce electricity at a later time, particularly when demand and prices are higher. |
| pumping load | Off-peak load required to pump water into a pumped-storage unit’s storage pond. |
| ramp rate | The rate at which a generating resource can increase its output, usually expressed in megawatts per minute (MW/min.) |
| Real-Time Demand-Response Program | An ISO New England program whereby participants curtail the consumption of electric energy by responding within 30 minutes or two hours after receiving notice from the ISO to do so, for which they are paid the greater of either the real-time locational marginal price applicable to their resource's load zone or the applicable floor price. |
| real-time emergency generation (RTEG) | Distributed generation the ISO calls on to operate during certain voltage-reduction or more severe actions; limited to 600 MW per the ISO market rules. |
| Real-Time Energy Market | In the New England Balancing Authority Area, a market that balances differences between the day-ahead scheduled amounts of electric energy needed and the actual real-time load requirements. (See Day-Ahead Energy Market.) |
| real-time reserve pricing | A way to co-optimize the use of resources for providing real-time reserves and electric energy by optimizing the use of local transmission capabilities and generating resources to provide the electric energy and reserves. |
| reconfiguration auction | An auction of the Forward Capacity Market whereby capacity supply obligations are traded monthly and annually to clear supply offers and demand bids for each capacity zone in New England. |
| Regional Transmission Organization (RTO) | An independent regional transmission operator and service provider established by FERC and that meets FERC's RTO criteria, including those addressing independence and market size. The RTO controls and manages the high-voltage flow of electricity over an area generally larger than the typical power company's service territory for its distribution system. |
| regional network service | The transmission service over the pool transmission facilities (PTFs), including services used for network resources or regional network load not physically interconnected with a PTF. |
| regulation | The capability of specially equipped generators to increase or decrease their generation output every four seconds in response to signals they receive from the ISO to balance supply levels with the second-to-second variations in demand. Also see voltage regulation. |
| Regulation Market | In the New England Balancing Authority Area, a market in which load-serving entities pay for regulation service on the basis of real-time load obligations and market participants satisfy regulation requirements with their own resources, through internal bilateral transactions, or by market purchases. |
| reliability | The assurance that electric power is available even under adverse conditions, such as storms or outages of generation or transmission lines. |
| reliability region | A defined region that reflects the operating characteristics of, and the major constraints on, the region’s transmission system. These regions contain the load zones. |
| Reliability Transmission Upgrade (RTU) | A transmission addition or upgrade necessary to ensure the system’s continued reliability and not necessary to support a generator interconnection. |
| renewable energy | Sources of fuel continually and naturally replenished and never exhausted, such as solar, hydro, wind, selected biomass, geothermal, ocean thermal, and tidal sources of power. Landfill gas also is regarded as a renewable resource, and some states consider fuel cells to be renewable. Pumped hydro is not considered a renewable resource because the electricity for pumping mostly comes from fossil fuel and nuclear (i.e., nonrenewable) generators. |
| Renewable Energy Certificate (REC) or Renewable Energy Credit | A tradable, nontangible commodity representing the eligible renewable generation attributes of 1 MWh of actual generation from a grid-connected renewable resource. |
| representative net ICR | An illustrative future Installed Capacity Requirement for the region, minus a monthly value that reflects the annual installed capacity benefits of the Hydro Québec Phase II Interconnection. The ISO calculates representative net ICR values solely to inform New England stakeholders; these values have not and will not be filed with the Federal Energy Regulatory Commission for approval. |
| reserve zone | An area for which the ISO has established 30-minute operating reserve requirements, which are met by the reserve markets. The New England region has four reserve zones—Connecticut, Southwest Connecticut, Northeast Massachusetts/Boston, and Rest-of-System. |
| resource | Any source of electric energy that increases the availability of capacity (in megawatts), such as a generator, a demand-response resource, or an electricity import or external transaction. |
| resource adequacy | The ability of a regional electric power system to supply the aggregate electrical demand and energy requirements (i.e., the electrical loads of all the customers at all times plus external transaction sales to other balancing authority areas), taking into account scheduled and reasonably expected unscheduled outages of system devices (e.g., generators, transformers, circuits, circuit breakers, or bus sections). Annual expected system resource adequacy is calculated in terms of system loss-of-load expectation, accounting for uncertainty in the load forecast caused by weather and resource availability and reflecting assumed forced and scheduled outages. |
| resulting reserves | The amount of capacity in excess of the forecast 50/50 peak load (i.e., one with a 50% chance of being exceeded because of weather conditions). Percentage resulting reserves = [{(Net ICR − 50/50 peak load) ÷ 50/50 peak load} × 100]. |
| retirement | The permanent removal from service of a facility, which cannot return to service without major refurbishment or relicensing. |
| seasonal claimed capability (SCC) | A generator's maximum production or output during a particular season, adjusted for physical and regulatory limitations. |
| second contingency (N-1-1) | After the occurrence of a first contingency, the loss of the facility that at that time has the largest impact on the system. Also, a constraint met by maintaining operating reserve that can increase output when the first contingency occurs. |
| selective catalytic reduction (SCR) | A post-combustion nitrogen oxide (NOX) control technology for fossil-fired generators, which chemically reduces NOX into molecular nitrogen (N2) and water vapor using a nitrogen-based reducing reagent, such as ammonia or urea, and a catalyst to allow the process to occur at lower temperatures. |
| selective noncatalytic reduction (SNCR) | A post-combustion nitrogen oxide (NOX) control technology for fossil-fired generators that chemically reduces NOX with a nitrogen-based reducing reagent, such as ammonia or urea, into molecular nitrogen (N2) and water vapor |
| self-supply | When a market participant provides itself with a market product from its own resources rather than purchasing it from the market. |
| shortage event | A designated period (hours) of stressed system conditions during which capacity resources are most needed. |
| Small Generator Interconnection Procedure (SGIP) | Standard procedures for interconnection of generating units smaller than 20 MW per the ISO’s Transmission, Markets, and Services Tariff, Section II, Schedule 23. |
| smart grid | According to the Institute of Electrical and Electronics Engineers (IEEE), a “next-generation” electrical power system that typically employs the increased use of communications and information technology for generating, delivering, and consuming electrical energy. |
| Solar Renewable Energy Credit (SREC) | In states that have Renewable Portfolio Standards, a form of the tradable, nontangible renewable energy credits for eligible grid-connected solar energy facilities that represents the environmental attributes of the facility for every 1,000 kilowatt-hours of electricity it produces. The income from selling SRECs increases the value of a solar investment. |
| special protection system (SPS) | Power system equipment designed to detect abnormal system conditions and take corrective action other than the isolation of faulted elements. |
| spinning | On-line capacity electrically synchronized to the system. |
| spinning reserve | On-line operating reserve capability in excess of load and synchronized to the system, which a generator can fully convert into electric energy within 10 minutes after receiving a request from the ISO to do so. |
| spot market | A market that typically involves short-term, often interruptible contracting and immediate delivery of specified volumes of electric energy, as opposed to bilateral trading. In New England, the Real-Time Energy Market is a spot market. |
| Standard Market Design (SMD) | New England's wholesale electricity market structure that incorporates locational marginal pricing, day-ahead and real-time energy markets, and risk-management tools to hedge against congestion expenses. |
| static delist bid | A delist bid submitted for a resource before a Forward Capacity Auction—and that cannot be changed during the auction—requesting for the resource to opt out of a capacity supply obligation and reflecting either the cost of the resource or a reduction in ratings as a result of ambient air conditions. The ISO may be required to submit a static delist bid on behalf of a resource that would not be able to supply its awarded capacity during the winter because its summer-qualified capacity is greater than its winter-qualified capacity. (See delist bid and ambient-air delist bid.) |
| subarea | One of 13 zones into which the system is divided for conducting several types of RSP analyses, such as production cost simulations. |
| supply resources | Generating units that use nuclear energy, fossil fuels (such as gas, oil, or coal), or renewable fuels (such as water, wind, or the sun) to produce electricity. |
| synchronized reserves, or spinning reserves | On-line reserves that can increase output. |
| synchrophasor | Power system measurement created in phasor measurement units. |
| synchrophasor infrastructure and data utilization (SIDU) | A phasor measurement unit that uses global positioning satellite technology to accurately conduct wide-area monitoring of a power grid performance; provide specific data for operating the grid to increase response time to real-time system events and reduce congestion; and enhance grid design. |
| system emissions rate | A measure (lb/MWh) of the annual emissions produced by all generators in the region divided by the annual generation in the region. The emissions data are obtained from the US EPA Clean Air Markets database and the generation data are obtained from ISO New England Settlements. |
| tie line | A transmission line that connects two balancing authority areas; an interconnection. |
| tie-reliability benefits | Receipts of emergency electric energy from neighboring regions that account for both the transmission-transfer capability of the tie lines and the emergency capacity assistance that may be available from neighboring systems when and if New England would need it; also referred to as tie-line benefits. |
| transfer capability | The amount of megawatts that interconnected electricity systems under specified conditions can reliably transfer from one system to the other over all transmission lines that connect the systems. |
| transmission line | Any line with a voltage greater than 50 kV that carries bulk power over long distances. Typical industry voltages are 69 kV, 115 kV, 138 kV, 230 KV, and 345 kV. |
| unloaded operating capacity | Operational capacity not generating energy but able to convert to generating energy. |
| unplanned outage | When equipment is forced out of operation as a result of a discovered problem, but the request for the outage did not meet the timing requirements for it to be considered a planned outage. Unplanned outages are categorized as emergency outages or forced outages. |
| voltage ampere reactive (VAR) | Unit of measurement for reactive power in an AC electric power system, which maintains transmission voltages within acceptable ranges. |
| voltage regulation | When an electric power system provides constant voltage over a range of load conditions. |
| voltage support | An ancillary service of the New England wholesale electricity markets provided by a resource for maintaining voltage-control capability, which allows system operators to maintain transmission voltages within acceptable limits. |
| weather-normalized load factor | The ratio of the average hourly demand during a year to the peak hourly demand, both adjusted to normal weather conditions. |
| weather-normalized results | Analytical results that would have been observed if weather were the same as the long-term average. |

Appendix B
Acronyms and Abbreviations

| Acronym/Abbreviation | Description |
| --- | --- |
| AC | Administrative Committee |
| ACI | advanced carbon injection |
| ACP | alternative compliance payment |
| AEO | Annual Energy Outlook |
| AGT | Algonquin Gas Transmission |
| AIM | Algonquin Incremental Market (Spectra Energy project) |
| AMI | advanced metering infrastructure |
| AMRXY | 20XY Annual Markets Report |
| APS | Alternative Energy Portfolio Standard |
| ARA | annual reconfiguration auction |
| ARRA | American Recovery and Reinvestment Act of 2009 |
| Attn. Gen. | attorney general |
| Bcf; Bcf/d | billion cubic feet; billion cubic feet per day |
| BHE | 1) RSP subarea of northeastern Maine 2) Bangor Hydro Electric (Company) |
| BOEMRE | Bureau of Ocean Energy Management, Regulation, and Enforcement (US Department of Interior) |
| BOSTON | RSP subarea of Greater Boston, including the North Shore |
| BTA | best technology available |
| Btu | British thermal unit |
| CAA | Clean Air Act (US) |
| CAGR | compound annual growth rate |
| CAIR | Clean Air Interstate Rule |
| CATR | Comprehensive Area Transmission Review of the New England Transmission System |
| CC | combined cycle |
| CCP | capacity commitment period |
| CCRP | Central Connecticut Reliability Project |
| CCRR | Coal Combustion Residue Rule (US) |
| CEFIA | Clean Energy Finance and Investment Authority (CT) |
| CEII | critical energy infrastructure information |
| CELT | capacity, energy, loads, and transmission |
| 2010 CELT Report | 2010–2019 Forecast Report of Capacity, Energy, Loads, and Transmission |
| 2011 CELT Report | 2011–2020 Forecast Report of Capacity, Energy, Loads, and Transmission |
| 2012 CELT Report | 2012–2021 Forecast Report of Capacity, Energy, Loads, and Transmission |
| CEP | comprehensive energy plan (CT and VT) |
| CFR | Code of Federal Regulations |
| CHP | combined heat and power |
| Civ. | civil court |
| CL&P | Connecticut Light and Power |
| CLG | Consumer Liaison Group |
| CMA/NEMA | RSP subarea comprising central Massachusetts and northeastern Massachusetts |
| CMP | Central Maine Power (Company) |
| CMR | Code of Massachusetts Regulations |
| CO2 | carbon dioxide |
| CONE | cost of new entry (capacity) |
| Conn | Connecticut |
| CPCN | Certificate of Public Convenience and Necessity |
| CPG | Certificate of Public Good (VT) |
| CRS | Congressional Research Service |
| CSAPR | Cross State Air Pollution Rule (US) |
| CSC | Cross-Sound Cable |
| CSO | capacity supply obligation |
| CT | 1) State of Connecticut 2) RSP subarea that includes northern and eastern Connecticut 3) Connecticut load zone |
| CT DPUC | Connecticut Department of Public Utility Control |
| CWA | Clean Water Act (US) |
| CWIR | Cooling Water Intake Rule (US) |
| CWIS | cooling water intake structures |
| DC | direct current |
| D.C. | District of Columbia |
| D.C. Cir. | District of Columbia Circuit (US Court of Appeals) |
| DCT | double-circuit tower |
| D.D.C. | US District Court for the District of Columbia |
| DE | Delaware |
| DEEP | Department of Energy and Environmental Protection (CT) |
| DG | distributed generation |
| DLR | dynamic line rating |
| DOE | Department of Energy (US) |
| DOER | Department of Energy Resources (MA) |
| DPS | Department of Public Service (VT) |
| DPU | Department of Public Utilities (MA) |
| DPUC | Department of Public Utility Control (CT) |
| DSI | dry sorbent injection |
| Dth/d | dekatherms per day |
| DVAR | dynamic voltage ampere reactive system |
| DZ | dispatch zone |
| ecomin | economic minimum |
| EE | energy efficiency |
| EEF | energy-efficiency forecast |
| EEFWG | Energy-Efficiency Forecast Working Group |
| EGEAS | Electric Generation Expansion Analysis System |
| EHV | extra-high voltage |
| EIA | Energy Information Administration (US DOT) |
| EIPC | Eastern Interconnection Planning Collaborative |
| EISPC | Eastern Interconnection States Planning Council |
| EMS | Energy Management System |
| EPA | US Environmental Protection Agency (US) |
| EPAct | Energy Policy Act of 2005 |
| EPRI | Electric Power Research Institute |
| ERCOT | Electric Reliability Council of Texas |
| ERO | Electric Reliability Organization |
| ETU | Elective Transmission Upgrade |
| EV | Efficiency Vermont |
| F.3d | Federal Reporter, third series |
| FACTS | Flexible Alternating-Current Transmission System |
| FAQ | frequently asked question |
| FCA | Forward Capacity Auction |
| FCA #N | nth Forward Capacity Auction |
| FCM | Forward Capacity Market |
| Fed. Reg. | Federal Register |
| FERC | Federal Energy Regulatory Commission |
| FF | fabric filter |
| FGD | flue-gas desulfurization |
| FIT | feed-in tariff |
| FOA | Funding Opportunity Announcement |
| FRM | Forward Reserve Market |
| FTR | financial transmission rights |
| GAO | Government Accountability Office (US) |
| GCA | Green Communities Act (MA) |
| GDP | gross domestic product |
| GHCC | Greater Hartford Central Connecticut (part of NEEWS) |
| GHG | greenhouse gas |
| GIS | Generation Interconnection System (NEPOOL) |
| G.L. | general law |
| GOEIS | Governor’s Office of Energy Independence and Security (ME) |
| GPM | gallons per minute |
| GPS | global positioning satellite |
| Greater Connecticut | RSP study area that includes the RSP subareas of NOR, SWCT, and CT |
| Greater Southwest Connecticut | RSP study area that includes the southwestern and western portions of Connecticut and comprises the SWCT and NOR subareas |
| GRI | Greater Rhode Island |
| GSRP | Greater Springfield Reliability Project |
| GW | gigawatt |
| GWh | gigawatt-hour(s) |
| HAP | hazardous air pollutant |
| HB | House Bill |
| HCL | hydrogen chloride |
| HF | hydrogen fluoride |
| Hg | mercury |
| HQ | Hydro-Québec Balancing Authority Area |
| HQICC | Hydro-Québec Installed Capability Credit |
| H.R. | House of Representatives |
| HV | high voltage |
| HVDC | high-voltage direct current |
| ICR | Installed Capacity Requirement |
| IEEE | Institute of Electrical and Electronics Engineers |
| IESO | Independent Electric System Operator (Ontario, Canada) |
| IGTS | Iroquois Gas Transmission System |
| IPSAC | Inter-Area Planning Stakeholder Advisory Committee |
| IRC | ISO/RTO Council |
| IREMM | Interregional Electric Market Model |
| ISO | Independent System Operator of New England; ISO New England |
| ISO/RTO | Independent System Operator/Regional Transmission Organization |
| ISOs | Independent System Operators |
| ISO tariff | ISO New England’s Transmission, Markets, and Services Tariff |
| IVGTF | Integrating Variable Generation Task Force (NERC) |
| JIPC | Joint ISO/RTO Planning Committee |
| kton | kiloton |
| kV | kilovolt(s) |
| kW | kilowatt |
| kWh | kilowatt-hour |
| lb | pound |
| LCC | local control center |
| LDC | local distribution company |
| LFG | landfill gas |
| LGIP | large generator interconnection procedure |
| LLC | limited liability company |
| LMP | locational marginal price |
| LNG | liquefied natural gas |
| LOLE | loss-of-load expectation |
| LOS | loss of source |
| Lower SEMA; LSM | lower southeastern Massachusetts |
| LREC | Low-Emissions Renewable Energy Certificate |
| LSE | load-serving entity |
| LSR | local sourcing requirement |
| LTRA | Long-Term Reliability Assessment (NERC) |
| M&NE | Maritimes and Northeast (Pipeline) |
| MA | Massachusetts |
| MA DOER | Massachusetts Department of Energy Resources |
| MA DPU | Massachusetts Department of Public Utilities |
| Mass. Gen. Laws | General Laws of Massachusetts |
| MATS | Mercury and Air Toxics Standard (US EPA) |
| max | maximum |
| Mcf/d | thousand cubic feet per day |
| MCL | maximum capacity limit |
| MD | Maryland |
| MDth/d | thousand dekatherms per day |
| ME | 1) State of Maine 2) RSP subarea that includes western and central Maine and Saco Valley, New Hampshire 3) Maine load zone |
| MEPCO | Maine Electric Power Company, Inc. |
| METU | Market Efficiency Transmission Upgrade |
| MHK | marine and hydrokinetic power |
| min gen | minimum generation |
| MISO | Midwest Independent System Operator |
| mils | one thousandth of a dollar |
| MMBtu | million British thermal units |
| mo. | month |
| MOU | Memorandum of Understanding |
| MPRP | Maine Power Reliability Program |
| MPUC | Maine Public Utilities Commission |
| MRA | market resource alternative |
| MSW | municipal solid waste |
| mtons | million tons |
| MVAR | megavolt-ampere reactive |
| MW | megawatt(s) |
| MWh | megawatt-hour(s) |
| N-1 | first-contingency loss |
| N-1-1 | second-contingency loss |
| na | not applicable |
| NAESB | North American Energy Standards Board |
| NB | New Brunswick |
| n.d. | no date |
| NBSO | New Brunswick System Operator |
| NCIS | Network Capability Interconnection Standard |
| NCPC | Net Commitment-Period Compensation |
| NCSPXY | Northeast Coordinated System Plan 20XY |
| NECPUC | New England Conference of Public Utilities Commissioners |
| NEEWS | New England East–West Solution |
| NEGC | New England Governors' Conference |
| NEG/ECP | New England Governors/Eastern Canadian Premiers |
| NEL | net energy for load |
| NEMA | 1) RSP subarea for northeast Massachusetts 2) Northeast Massachusetts load zone |
| NEMA/Boston | combined load zone that includes northeast Massachusetts and the Boston area |
| NEPOOL | New England Power Pool |
| NERC | North American Electric Reliability Corporation |
| NESCOE | New England States Committee on Electricity |
| NESHAP | National Emission Standard for Hazardous Air Pollutant |
| NEWIS | New England Wind Integration Study |
| NG | natural gas |
| NGA | Northeast Gas Association |
| NGCC | natural gas combined cycle |
| NH | 1) State of New Hampshire 2) RSP subarea comprising northern, eastern, and central New Hampshire; eastern Vermont; and southwestern Maine 3) New Hampshire load zone |
| NIETC | National Interest Electric Transmission Corridors |
| NIST | National Institute of Standards and Technology |
| NJ | New Jersey |
| NNE | northern New England |
| No. | number |
| NO2 | nitrogen dioxide |
| NOPR | Notice of Proposed Rulemaking |
| NOR | RSP subarea that includes Norwalk and Stamford, Connecticut |
| NOX | nitrogen oxide(s) |
| NPCC | Northeast Power Coordinating Council, Inc. |
| NPDES | National Pollution Discharge Elimination System |
| NRC | Nuclear Regulatory Commission (US) |
| NRI | Northeast Reliability Interconnection |
| Nuc | nuclear |
| NWVT | Northwest Vermont |
| NY | New York Balancing Authority Area |
| NYISO | New York Independent System Operator |
| O3 | ozone |
| OATT | Open Access Transmission Tariff |
| OP 4 | ISO Operating Procedure No. 4, Action during a Capacity Deficiency |
| OP 7 | ISO Operating Procedure No. 7, Action in an Emergency |
| OP 8 | ISO Operating Procedure No. 8, Operating Reserve and Regulation |
| OP 19 | ISO Operating Procedure No. 19, Transmission Operations |
| PA | 1) Pennsylvania 2) program administrator |
| PAC | Planning Advisory Committee |
| PDC | phasor data concentrator |
| PDR | passive demand resource |
| PER | peak energy rent |
| PEV | plug-in electric vehicle |
| PJM | PJM Interconnection LLC; the RTO for all or parts of Delaware, Illinois, Indiana, Kentucky, Maryland, Michigan, New Jersey, North Carolina, Ohio, Pennsylvania, Tennessee, Virginia, and the District of Columbia |
| PM | particulate matter |
| PM2.5 | fine particulate matter |
| PMU | phasor measurement unit |
| pnode | pricing node |
| PP 10 | ISO Planning Procedure No. 10, Planning Procedure to Support the Forward Capacity Market |
| PPA | Proposed Plan Application |
| PSPC | Power Supply Planning Committee |
| PTF | pool transmission facility |
| PTO | participating transmission owner |
| Pub. L. | public law |
| PUC | Public Utilities Commission |
| PURA | Public Utility Regulatory Authority (CT) |
| PV | photovoltaic |
| queue (the) | ISO Generator Interconnection Queue |
| RC | Reliability Committee |
| RCRA | Resource Conservation and Recovery Act (US) |
| REC | Renewable Energy Certificate |
| REMVEC | Rhode Island-Eastern Massachusetts-Vermont Energy Control |
| RFI | request for information |
| RFP | request for proposals |
| RGGI | Regional Greenhouse Gas Initiative |
| RGSP | real gross state product |
| RI | 1) State of Rhode Island 2) RSP subarea that includes the part of Rhode Island bordering Massachusetts 3) Rhode Island load zone |
| RIRP | Rhode Island Reliability Project |
| RNS | Regional Network Service |
| ROS | rest of system |
| ROSE | Region of Stability Existence |
| RPS | Renewable Portfolio Standard |
| RSP | Regional System Plan |
| RSPXY | 20XY Regional System Plan |
| RTDR | real-time demand resource |
| RTEG | real-time emergency generation |
| RTO | Regional Transmission Organization |
| S. | Senate (US) |
| SB | Senate Bill |
| SCC | seasonal claimed capability |
| SCR | selective catalytic reduction |
| SDNY | US District Court Southern District of New York |
| SEMA | 1) RSP subarea comprising southeastern Massachusetts and Newport, Rhode Island 2) Southeastern Massachusetts load zone |
| Sess. | Session (Congress) |
| SGIP | small generator interconnection procedure |
| SIDU | synchrophasor infrastructure and data utilization |
| SLOD | severe line-outage detection |
| SMD | Standard Market Design |
| SME | RSP subarea for southeastern Maine |
| SNCR | selective noncatalytic reduction |
| SO2 | sulfur dioxide |
| SOEP | Sable Offshore Energy Project |
| SPEED | Sustainably Priced Energy Development Program |
| SPS | special protection system |
| sq. | square |
| SREC | Solar Renewable Energy Certificate or Credit |
| STATCOM | static synchronous compensator |
| SVC | static voltage ampere reactive (VAR; V) compensator |
| SWCT | RSP subarea for southwestern Connecticut |
| tbd | to be determined |
| Tcf | trillion cubic feet |
| TGP | Tennessee Gas Pipeline |
| TMNSR | 10-minute nonspinning reserve |
| TMOR | 30-minute operating reserve |
| TMSR | 10-minute spinning reserve |
| TO | transmission owner |
| TWh | terawatt-hour |
| UI | United Illuminating |
| US | United States |
| VAR | voltage ampere reactive |
| VER | variable energy resource |
| USC | United States Code |
| VELCO | Vermont Electric Power Company |
| VSC | voltage source converter |
| VT | 1) State of Vermont 2) RSP subarea that includes Vermont and southwestern New Hampshire 3) Vermont load zone |
| 20XY VT LRP | 20XY Vermont Long-Range Plan |
| WCMA | Western/Central Massachusetts load zone |
| WEA | wind energy area |
| WMA | RSP subarea for western Massachusetts |
| WMECO | Western Massachusetts Electric Company |
| WPDA | wind project development areas |
| yr | year |
| ZREC | Zero-Emission Renewable Energy Certificate |

The requirements of the OATT include Attachment K, the ISO Information Policy, and interconnection procedures and address generator and elective upgrades. ISO New England Open Access Transmission Tariff, Section II, Attachment K, “Regional System Planning Process” (March 1, 2012), http://www.iso-ne.com/regulatory/tariff/sect_2/oatt/sect_ii.pdf . ISO New England Inc. Transmission, Markets, and Services Tariff (ISO tariff), Part II, Section 48 (2010), http://www.iso-ne.com/regulatory/tariff/index.html. ISO tariff, Attachment D, “ISO New England Information Policy” (March 12, 2012), http://www.iso-ne.com/regulatory/tariff/attach_d/index.html. OATT, Schedules 22 and 23, “Standard Large Generator Interconnection Procedures” (January 31, 2011) and “Standard Small Generator Interconnection Procedures” (January 31, 2011), http://www.iso-ne.com/regulatory/tariff/sect_2/index.html.

RSP12 is based on the June 2012 RSP Project List, http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/projects/index.html.

NEPOOL was formed by the region’s private and municipal utilities to foster cooperation and coordination among the utilities in the six-state region and ensure a dependable supply of electricity. Today, NEPOOL members serve as ISO stakeholders and market participants. More information is available at http://www.iso-ne.com/committees/nepool_part/index.html.

Past RSPs are archived at http://www.iso-ne.com/trans/rsp/index.html. For access to supporting reports, contact ISO Customer Service at 413-540-4220.

PAC materials and meeting minutes are available at http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/index.html. For access to PAC critical energy infrastructure information (CEII), complete the PAC Access Request Form at http://www.iso-ne.com/support/custsvc/forms/index.html and mail to ISO New England Inc., Attn: Customer Support, One Sullivan Road, Holyoke, MA 01040-2841, or email the PDF file to custserv@iso-ne.com.

ISO New England Inc. Transmission, Markets, and Services Tariff (ISO tariff), Part II (2011), http://www.iso-ne.com/regulatory/tariff/index.html. Information on NERC requirements is available at http://www.nerc.com. Information on NPCC is available at http://www.npcc.org/. An NPCC compliance audit conducted from March 12 through March 15, 2012, showed no ISO violations of any standards and requirements.

Meeting materials and notes and meeting dates for discussing the Strategic Planning Initiative are available at http://www.iso-ne.com/committees/comm_wkgrps/strategic_planning_discussion/index.html.

The ISO Generator Interconnection Queue includes those generators that have submitted requests to interconnect to the ISO New England transmission system.

ICF International, Assessment of New England’s Natural Gas Pipeline Capacity to Satisfy Short and Near-Term Electric Generation Needs, draft report (June 15, 2012) (ICF Natural Gas Study), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/reports/2012/gas_study_ceii.pdf. Also see the ISO’s memo to the PAC regarding this study (June 15, 2012), http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/reports/2012/gas_study_ltr.pdf.

In-merit generation is when the generators with the lowest-price offers are committed and dispatched first, and increasingly higher-priced generators are brought on line as demand increases. Out-of-merit dispatch is when higher-priced generators are committed and dispatched before lower-priced resources to respect system reliability requirements, which results in increased costs to load.

GE Applications and Systems Engineering, New England Wind Integration Study (December 5, 2010), http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/reports/2010/newis_report.pdf.

PJM Interconnection LLC, is the RTO for all or parts of Delaware, Illinois, Indiana, Kentucky, Maryland, Michigan, New Jersey, North Carolina, Ohio, Pennsylvania, Tennessee, Virginia, and the District of Columbia.

FERC, Transmission Planning and Cost Allocation by Transmission Owning and Operating Public Utilities, 18 CFR Part 35, Docket No. RM10-23-000, Order 1000, 136 FERC ¶ 61,051 (July 21, 2011), http://www.ferc.gov/industries/electric/indus-act/trans-plan.asp and http://www.ferc.gov/whats-new/comm-meet/2011/072111/E-6.pdf.

National Interest Electric Transmission Corridors and Congestion Study documents are available at http://nietc.anl.gov/documents/index.cfm. DOE’s 2012 congestion study is scheduled to be released by the end of 2012. See the DOE website, “2012 National Electric Transmission Congestion Study,” http://energy.gov/oe/services/electricity-policy-coordination-and-implementation/transmission-planning/2012-national.

The 50/50 “reference-case” peak loads have a 50% chance of being exceeded because of weather conditions. For the reference case, the summer peak load is expected to occur at a weighted New England-wide temperature of 90.2°F, and the winter peak load is expected to occur at 7.0°F. The 90/10 “extreme-case” peak loads have a 10% chance of being exceeded because of weather. For the extreme case, the summer peak is expected to occur at a temperature of 94.2°F, and the winter peak is expected to occur at a temperature of 1.6°F.

Passive demand resources principally are designed to save electric energy use and are in place at all times without requiring direction from the ISO. Active demand resources reduce load in response to a request from the ISO to do so for system reliability reasons or in response to a price signal. The total gross load forecast is the load forecast in the ISO’s 2012–2021 Forecast Report of Capacity, Energy, Loads, and Transmission (2012 CELT Report) before applying the reductions attributable to federal energy-efficiency standards. See http://www.iso-ne.com/trans/celt/report/index.html. Copies of all CELT reports are located at http://www.iso-ne.com/trans/celt/index.html (May 2012).

The ISO’s Forecast Data 2012 (May 4, 2012), sheet 9 (http://www.iso-ne.com/trans/celt/fsct_detail/index.html) shows that the gross consumption of electric energy for 2021 is 152,770 gigawatt-hours (GWh). The savings attributable to federal appliance standards is 2,395 GWh for 2021. In addition, passive demand resources are projected to save 17,409 GWh for 2021.

The open stakeholder process included communications with the newly formed Energy-Efficiency Forecast Working Group (EEFWG), the PAC, and other committees, such as the Load Forecast Committee, the Reliability Committee, and the Interarea Planning Stakeholder Advisory Committee (IPSAC).

The ISO analyzed approximately 130 unique EE programs.

The net ICR values for 2012/2013 to 2015/2016 are the latest values approved by FERC and are available at http://www.iso-ne.com/markets/othrmkts_data/fcm/doc/summary_of_icr_values.pdf. Representative net ICR values are illustrative future ICRs for the region, minus a monthly value that reflects the annual installed capacity benefits of the Hydro Québec Phase II Interconnection.

A capacity commitment period runs from June 1 through May 31 of the following year. FCA #6 covers June 1, 2015, through May 31, 2016. Existing capacity resources are required to participate in the FCA and automatically are entered into the capacity auction. However, these resources may indicate a desire to be removed from the FCA by submitting a delist bid before the existing-capacity qualification deadline.

A nonprice retirement request is a binding request to retire the entire capacity of a generating resource.

A local sourcing requirement is the minimum amount of capacity that must be electrically located within an import-constrained capacity zone to meet the ICR.

FERC, Order on Paper Hearing and Order on Rehearing, Docket Nos. ER10-787-000, EL10-50-000, EL10-57-000, ER10-787-004, EL10-50-002, and EL10-57-002, 135 FERC ¶ 61,029 (April 13, 2011), http://www.iso-ne.com/regulatory/ferc/orders/2011/apr/err10-787-000_4-13-11_fcm_redesign_order.pdf. FERC, Order on Rehearing and Clarification and Order Accepting Compliance Filings, Docket Nos. Er10-787-005, EL10-50-003, EL10-57-003,ER10-787-006, EL10-50-004, EL10-57-004, ER10-787-007, EL10-50-005, EL10-57-005, 138 FERC ¶ 61,027 (January 19, 2012), http://www.iso-ne.com/regulatory/ferc/orders/2012/jan/er10-787_1-19-12_order_fcm_redesign.pdf. FERC, Order on Tariff Revisions to the Forward Capacity Market, Docket Nos. ER12-953-000, 138 FERC ¶ 61,238 (March 30, 2012), http://www.iso-ne.com/regulatory/ferc/orders/2012/mar/er12-953-000_3-30-12_order_fcm_redesign_ext.pdf.

According to NERC, NPCC, and ISO criteria, a contingency is the loss of one or more generation, transmission, or both types of facilities or power system elements. A system’s first contingency (N-1) is when the power element (facility) with the largest impact on system reliability is lost. A second contingency (N-1-1) takes place after a first contingency has occurred and is the loss of the facility that at that time has the largest impact on the system.

To conduct some RSP studies, the region is divided into various areas associated with their electrical system characteristics. Greater Connecticut is an area that has boundaries similar to the State of Connecticut but is slightly smaller because of electrical system limitations near Connecticut’s borders with western Massachusetts and Rhode Island. Greater Southwest Connecticut includes southwestern and western portions of Connecticut. The BOSTON area (all capitalized) includes the city of Boston and northeast Massachusetts. (See Section 2.4.)

The ISO develops the representative operating-reserve requirements of these major import areas as ranges to account for future uncertainties about the availability of resources, load variations due to weather, and other factors.

See the materials presented at the May 26, 2011, PAC meeting at https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2011/may262011/nta_analysis.pdf.

Regional network service is the transmission service over the pool transmission facilities (PTFs), including services used for network resources or regional network load not physically interconnected with a PTF.

The current update of the RSP Project List is available at http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/projects/index.html. ISO New England Open Access Transmission Tariff (August 1, 2012), http://www.iso-ne.com/regulatory/tariff/sect_2/index.html.

Cost estimates without transmission cost allocation approval are subject to established variations as projects progress through various stages of implementation. The $6.0 billion cost estimate has a range of $4.9 to $7.1 billion based on projects proposed, planned, and under construction. See the Regional System Plan Transmission Projects June 2012 Update, PAC presentation (June 19, 2012), slide 16, at. http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/mtrls/2012/jun192012/june2012_project_list.pdf.

The ISO is studying the amount of export-transfer capability from Maine to New Hampshire.

An Elective Transmission Upgrade (ETU) is an upgrade to the New England transmission system voluntarily funded by one or more participants that have agreed to pay for all the costs of the upgrade. Merchant transmission facilities are independently developed and funded and subject to the operational control of the ISO, pursuant to an operating agreement specific to each of these facilities.

ICF Natural Gas Study, https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/reports/2012/gas_study_ceii.pdf.

2010 ISO New England Electric Generator Air Emissions Report (April 2012), http://www.iso-ne.com/genrtion_resrcs/reports/emission/final_2010_emissions_report_v2.pdf.

Air emission regulations cover nitrogen oxides, particulates, sulfur dioxide, mercury, other air toxics, and greenhouse gases, such as carbon dioxide.

The 11.6% is the reduction from the CELT forecast after accounting for the energy savings attributable to federal appliance standards. 2012 CELT Report, http://www.iso-ne.com/trans/celt/report/index.html.

RPSs apply only to competitive retail suppliers, which excludes municipal utilities.

Renewable Energy Certificates are tradable, nontangible commodities, each representing the eligible renewable generation attributes of 1 MWh of actual generation from a grid-connected renewable resource.

PAC archives of NEWIS materials are available at http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/reports/2010/index.html.

The metrics include production costs, LSE energy expenses, congestion, environmental emissions, average LMPs, fuel consumption and energy production by fuel type, revenues from the energy market, and the capital investment supported by simulated energy revenues.

Additional information on the EIPC is available at http://www.eipconline.com/.

The 2011 Northeast Coordinated System Plan (NCSP11) (ISO New England, NYISO, and PJM; May 31, 2012) and supplemental materials and reports are available at http://www.iso-ne.com/committees/comm_wkgrps/othr/ipsac/ncsp/index.html and http://www.iso-ne.com/committees/comm_wkgrps/othr/ipsac/index.html.

EIPC, Phase I Report: Formation of Stakeholder Process, Regional Plan Integration, and Macroeconomic Analysis (December 2011), http://www.eipconline.com/Phase_I.html.

Any stakeholder can designate a representative to the PAC by providing written notice to the ISO. PAC materials (2001–2012) are available at http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/index.html.

NEPOOL was formed by the region’s private and municipal utilities to foster cooperation and coordination among the utilities in the six-state region and ensure a dependable supply of electricity. Today, NEPOOL members serve as ISO stakeholders and market participants. More information on NEPOOL participants is available at http://www.iso-ne.com/committees/nepool_part/index.html.

ISO New England Inc. Transmission, Markets, and Services Tariff (ISO tariff) (2012), http://www.iso-ne.com/regulatory/tariff/index.html, including Section II. ISO New England Open Access Transmission Tariff, http://www.iso-ne.com/regulatory/tariff/sect_2/index.html.

Supply resources are generating units that use nuclear energy, fossil fuels (such as gas, oil, or coal), or renewable fuels (such as water, wind, or the sun) to produce electricity. In general, demand resources are measures that reduce consumer demand for electricity from the power system.

Renewable sources of energy are naturally replenished resources, such as solar, hydro, wind, selected biomass (e.g., wood and wood-waste solids and gas), geothermal, ocean thermal, and tidal sources of power. Other fuel sources that can be regarded as renewable resources include landfill gas (LFG) (i.e., the gas that results from decomposition in landfills and either is collected, cleaned, and used for generation or is vented or flared) and refuse (municipal solid waste). Some states consider fuel cells to be renewable.

Changes to markets may help meet future system needs by providing incentives for the development of market resources. These changes are subject to a different stakeholder process and are described in the ISO’s Annual Markets Report (http://www.iso-ne.com/markets/mkt_anlys_rpts/annl_mkt_rpts/index.html) and Wholesale Markets Project Plan (http://www.iso-ne.com/pubs/whlsle_mkt_pln/index.html).

For a list of PAC agendas, see http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/mins/2011/2011_pac_agenda_summary.pdf and http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/mins/2012/2012_agenda_summary.pdf.

Conference calls to discuss economic studies were held March 8, March 12, and April 5, 2012. Materials are available at http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/mtrls/2012/index.html. The Environmental Advisory Group (EAG) met six times during 2012 to discuss environmental regulatory issues and studies. EAG materials are available at http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/eag/mtrls/2012/index.html. The Energy-Efficiency Forecast Working Group (EEFWG) met four times in 2012 to discuss the ISO’s energy-efficiency forecast. EEFWG materials are available at http://www.iso-ne.com/committees/comm_wkgrps/othr/enrgy_effncy_frcst/mtrls/index.html.

PAC materials and meeting minutes are available at http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/index.html.

Market Rule 1 (ISO tariff, Section III) (2012), http://www.iso-ne.com/regulatory/tariff/sect_3/index.html.

A merchant transmission facility is an independently developed and funded facility subject to the operational control of the ISO, pursuant to an operating agreement specific to each facility (refer to Section 5.3.4).

Refer to the OATT, Attachment K, Section 4.1 and 4.2 for complete definitions for needs assessments and solutions studies;  http://www.iso-ne.com/regulatory/tariff/sect_2/oatt/sect_ii.pdf.

The current list is available at http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/projects/index.html. The June 2012 update lists information for 48 projects and 41 projects expected to be placed in service in New England by the end of 2012 and a cumulative investment of about $10.3 billion through 2016 for projects proposed, planned, under construction, and placed in service.

Recent and archived RSP materials are available at http://www.iso-ne.com/trans/rsp/index.html. The latest and archived editions of the AMR are available at http://www.iso-ne.com/markets/mkt_anlys_rpts/annl_mkt_rpts/. The latest and archived WMPPs are available at http://www.iso-ne.com/pubs/whlsle_mkt_pln/index.html. The needs assessments and solutions studies that have been presented to the PAC and posted on the ISO website can be obtained by contacting ISO Customer Service at 413-540-4220.

Stakeholders also can obtain publicly available network models of the transmission system through the FERC 715 process, which requires transmitting utilities that operate facilities rated at or above 100 kilovolts (kV) to submit information to FERC annually; see http://www.ferc.gov/docs-filing/forms/form-715/overview.asp. ISO New England Information Policy (ISO tariff, Attachment D) (2012) contains the requirements for controlling the disclosure of CEII and confidential information; see http://www.iso-ne.com/regulatory/tariff/attach_d/index.html. On May 11, 2011, the ISO filed with FERC a revision to the Information Policy to provide additional stability and short-circuit data to stakeholders; see http://www.iso-ne.com/regulatory/ferc/filings/2011/may/er11-3530-000_5-6-11_fap_revisions.pdf.

A balancing authority area is a group of generation, transmission, and loads within the metered boundaries of the entity (balancing authority) that maintains the load-resource balance within the area. Balancing authority areas were formerly referred to as control areas. Further information is available in the NERC glossary at http://www.nerc.com/files/Glossary_12Feb08.pdf.

The Eastern Interconnection consists of the interconnected transmission and distribution infrastructure that synchronously operates east of the Rocky Mountains, excluding the portion of the system located in the Electric Reliability Council of Texas (ERCOT) and Québec.

FERC, Preventing Undue Discrimination and Preference in Transmission Service, 18 CFR Parts 35 and 37, Docket Nos. RM05-17-000 and RM05-25-000, Order 890 (February 16, 2007), http://www.ferc.gov/whats-new/comm-meet/2007/021507/E-1.pdf. NERC Reliability Standards (2012), http://www.nerc.com/page.php?cid=2|20. NPCC Regional Standards (2012), https://www.npcc.org/Standards/default.aspx. ISO New England Planning Procedures, http://www.iso-ne.com/rules_proceds/isone_plan/index.html. ISO New England Operating Procedures, http://www.iso-ne.com/rules_proceds/operating/index.html.

FERC, Transmission Planning and Cost Allocation by Transmission Owning and Operating Public Utilities, Docket No. RM10-23-000, 136 FERC ¶ 61,051 (July 21, 2011), http://www.ferc.gov/whats-new/comm-meet/2011/072111/E-6.pdf. “Order No. 1000—Transmission Planning and Cost Allocation,” web page FERC, last updated May 18, 2012, http://www.ferc.gov/industries/electric/indus-act/trans-plan.asp.

The ISO is not responsible for portions of northern and eastern Maine. The Northern Maine Independent System Administrator, Inc. (NMISA) is a nonprofit entity responsible for the administration of the northern Maine transmission system and electric power markets in Aroostook and Washington counties, which has a peak load of approximately 131 MW. NMISA, Seven-Year Outlook: An Assessment of the Adequacy of Generation and Transmission Facilities of the Northern Maine Transmission System (June 2012), http://nmisa.com/docs/2012_NMISA_7_Year_Adequacy_Base_Case.pdf.

In exchange for compensation based on wholesale electricity prices, customers in ISO demand-response programs reduce load continuously or quickly, when instructed, to enhance system reliability or in response to price signals. The 2,100 MW of ISO demand resources do not include energy efficiency provided by other customer-based programs outside the ISO markets or are otherwise unknown to the ISO. Section 2.3 provides more information on demand resources.

For more information on New England wholesale electricity markets, see the ISO’s 2011 Annual Markets Report (AMR11) (May 15, 2012), http://www.iso-ne.com/markets/mkt_anlys_rpts/annl_mkt_rpts/index.html, and an Overview of New England’s Wholesale Electricity Markets and Market Oversight (May 15, 2012), http://www.iso-ne.com/pubs/spcl_rpts/2012/markets_overview_final_051512.pdf.

Installed capacity is the megawatt capability of a generating unit, dispatchable load, external resource or transaction, or demand resource that qualifies as a participant in the ISO’s Forward Capacity Market according to the market rules. Additional information is available at http://www.iso-ne.com/markets/othrmkts_data/fcm/index.html.

Regulation is the capability of specially equipped generators to increase or decrease their generation output every four seconds in response to signals they receive from the ISO to control slight changes on the system.

Unloaded operating capacity is operational capacity not generating electric energy but able to convert to generating energy. A contingency is the sudden loss of a generation or transmission resource. A system’s first contingency (N−1) is when the power element (facility) with the largest impact on system reliability is lost. A second contingency (N−1−1) takes place after a first contingency has occurred and is the loss of the facility that at that time has the largest impact on the system.

Load zones can also have the same boundaries as reliability regions, which reflect the operating characteristics of, and the major constraints on, the New England transmission system. See Market Rule 1, Section III.2.7, of the ISO tariff, http://www.iso-ne.com/regulatory/tariff/sect_3/mr1_sec_1-12.pdf.

The ISO tariff allows loads that meet specified requirements to request and receive nodal pricing.

Real-time emergency generation is distributed generation (i.e., the use of electricity generated on site; DG) the ISO calls on to operate during certain voltage-reduction or more severe actions but must limit its operation to 600 MW to comply with the generation’s federal, state, or local air quality permit(s) or combination of permits, as well as the ISO’s market rules. RTEG operations result in curtailing load on the grid, as the distributed energy provided by the emergency generator begins serving demand. Section 7.6.6 contains more information on distributed generation.

Active demand resources reduce load in response to a request from the ISO to do so for system reliability reasons or in response to a price signal. They include installed measures, such as equipment, services, and strategies that reduce end-use demand on the electricity network during specific performance hours. Passive demand resources are designed to save electric energy and include energy-efficiency measures, such as the use of energy-efficient appliances and lighting, advanced cooling and heating technologies, electronic devices to cycle air conditioners on and off, and equipment to shift load to off-peak hours of demand.

The distribution of generation resources by RSP subarea is available in the ISO’s presentation, System Overview, slide 12 (April 18, 2012), http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/mtrls/2012/apr182012/system_overview.pdf.

The ISO’s Capacity, Energy, Load, and Transmission (CELT) Reports and associated documentation contain more detailed information on short- and long-run forecast methodologies, models, and inputs; weather normalization; regional, state, subarea, and load-zone forecasts of annual electric energy use and peak loads; high- and low-forecast bandwidths; and retail electricity prices. They are available at “CELT Forecasting Details 2012,” http://www.iso-ne.com/trans/celt/fsct_detail/index.html. Also see 2012–2021 Forecast Report of Capacity, Energy, Loads, and Transmission (May 2012), http://www.iso-ne.com/trans/celt/report/, and ISO Seasonal Peaks since 1980 (May 4, 2012), http://www.iso-ne.com/markets/hstdata/rpts/ann_seasonal_pks/index.html.

See Moody’s presentation to the PAC (December 14, 2011), http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/mtrls/2011/dec142011/index.html.

The 50/50 “reference” case peak loads have a 50% chance of being exceeded because of weather conditions. For the reference case, the summer peak load is expected to occur at a weighted New England-wide temperature of 90.2°F, and the winter peak load is expected to occur at 7.0°F. The 90/10 “extreme” case peak loads have a 10% chance of being exceeded because of weather. For the extreme case, the summer peak is expected to occur at a temperature of 94.2°F, and the winter peak is expected to occur at a temperature of 1.6°F.

The compound annual growth rate (CAGR) is calculated as follows:

See ISO New England RSP12 Long-Run Forecast of Energy and Seasonal Peaks, PAC presentation, slide 21 (February 15, 2012), http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/mtrls/2012/feb152012/energy_peak_forecast.pdf.

OP 4 actions include allowing the depletion of the 30-minute and partial depletion of the 10-minute reserve (1,000 MW) (See Section 4.3), scheduling market participants’ submitted emergency transactions and arranging emergency purchases between balancing authority areas (1,600 to 2,000 MW), and implementing 5% voltage reductions (400 to 450 MW). The extent of OP 4 actions would be affected by system conditions and the effectiveness of the actions. Operating Procedure No. 4, Action during a Capacity Deficiency (December 15, 2011), http://www.iso-ne.com/rules_proceds/operating/isone/op4/index.html.

Weather conditions during the actual peak summer loads were slightly below the expected 90/10 weather conditions for 1994, 1999, 2001, and 2002, and weather conditions were slightly above the expected 90/10 weather during both the 2006 and 2010 peaks. A spreadsheet containing historical annual peak loads and associated weather conditions since 1980 is available at http://www.iso-ne.com/markets/hstdata/rpts/ann_seasonal_pks/seasonal_peak_data_summary.xls.

Economy.com forecasts of New England gross state product (millions of 2005 $) from November 2011 and October 2010 forecasts.

Refer to the ISO presentation, RSP12 Long-Run Forecast of Energy and Seasonal Peaks (February 15, 2012), http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/mtrls/2012/feb152012/energy_peak_forecast.pdf.

2012 CELT Report (May 2012), http://www.iso-ne.com/trans/celt/report/index.html. Copies of all CELT reports are available at http://www.iso-ne.com/trans/celt/index.html. The ICR is the amount of capacity the New England region will need in a particular year to meet its NPCC resource adequacy planning criteria; see Section 4.1.1 for additional information.

Other demand resources, an asset category that was retired on May 31, 2010, at the end of the transition period leading to the FCM, consisted of energy-efficiency measures, load management, and distributed generation—typically nondispatchable resources that tend to reduce end-use demand on the electricity network across many hours but usually not in direct response to changing hourly wholesale prices. For additional information on ODRs, refer to AMR10, Section 2.7, http://www.iso-ne.com/markets/mkt_anlys_rpts/annl_mkt_rpts/index.html.

Forecasts of net energy for load and peak loads are “gross loads.” Additional details of the loads are available at “CELT Forecasting Details 2012,” http://www.iso-ne.com/trans/celt/fsct_detail/index.html. Also see the full 2012 CELT report, 2012–2021 Forecast Report of Capacity, Energy, Loads, and Transmission (May  2012), http://www.iso-ne.com/trans/celt/report/.

For additional information, refer to the pricing node tables available at “Settlement Model Information,” http://www.iso-ne.com/stlmnts/stlmnt_mod_info/index.html.

State-sponsored EE programs consist of various efforts designed to reduce energy consumption. These efforts generally are funded by multiple sources, the largest of which is a system benefits charge (SBC) applied to customer bills.

The ISO’s 2010 Regional System Plan (http://www.iso-ne.com/trans/rsp/2010/index.html) provides an overview of the states’ legislative authority for EE programs.

The Maine Legislature approves the budget for Maine’s energy-efficiency program, administered by the Efficiency Maine Trust.

Most of the energy efficiency implemented in Maine and Vermont is by energy-efficiency utilities, Efficiency Maine Trust and Efficiency Vermont, respectively.

In response to a stakeholder PAC presentation, the ISO worked with the PAs, analyzed FCM data, and found that the FCM captures nearly all the state-sponsored EE programs. See http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/mtrls/2011/apr142011/energy_efficiency.pdf.

A description of the ISO’s efforts to understand the role of EE is reported in past RSPs. See RSP10, Section 8.4, http://www.iso-ne.com/trans/rsp/2010/index.html and RSP11, Section 4, http://www.iso-ne.com/trans/rsp/2011/index.html.

“Final ISO-NE Forecast of EE 2105-2012,”http://www.iso-ne.com/committees/comm_wkgrps/othr/enrgy_effncy_frcst/index.html.

Information about the Energy-Efficiency Working Group is available at http://www.iso-ne.com/committees/comm_wkgrps/othr/enrgy_effncy_frcst/index.html. The chairs of the relevant committees expressed concern that the EEFWG did not fit into their committee structure and that the expertise needed for the EEFWG did not reside in the Reliability Committee.

For more information on these data, see ISO-NE Proof-of-Concept Forecast of New State Sponsored Energy Efficiency, PAC presentation (November 8, 2011), http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/mtrls/2011/nov162011/index.html.

EE data submitted to the ISO by the PAs is available at http://www.iso-ne.com/committees/comm_wkgrps/othr/enrgy_effncy_frcst/frcst/index.html.

The ISO did not request data from municipal electric entities and merchant energy-efficiency providers.

Mixed lighting refers to programs that include lighting and other measures, such as mechanical systems, building envelope, process improvements, and appliances. See Energy Efficiency Forecast 2015-2020, EEFWG presentation, slide 28 (February 24, 2012), http://www.iso-ne.com/committees/comm_wkgrps/othr/enrgy_effncy_frcst/mtrls/2012/ee_forecast_work_group_2_24_12_final.pdf.

Energy Efficiency Forecast  2015-2012. EEFWG presentation (February 24, 2012), http://www.iso-ne.com/committees/comm_wkgrps/othr/enrgy_effncy_frcst/mtrls/2012/ee_forecast_work_group_2_24_12_final.pdf.

ISO New England’s Draft Final Energy-Efficiency Forecast 2015–2021 (March 19, 2012), http://www.iso-ne.com/committees/comm_wkgrps/othr/enrgy_effncy_frcst/frcst/2012/draft_final_ee_forecast_3_16_12.pdf.

The year 2012 was used for all states, except Rhode Island and Vermont, for which 2012 to 2014 was used. A 10% uncertainty was applied to the Massachusetts and Rhode Island budgets. See http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/mtrls/2012/apr182012/final_ee_forecast.pdf.

The final EE forecast for 2015 to 2021 is available at http://www.iso-ne.com/committees/comm_wkgrps/othr/enrgy_effncy_frcst/frcst/2012/iso_ne_ee_forecast_2015_2021.pdf.

In future EE forecasts, a longer EE data record may allow for the refinement of the uncertainty factors.

The EE forecast will not have an impact on FCM auctions, FCM reliability studies, ICR calculations, or system operations analysis across the four-year FCM window.

The ISO’s Generator Interconnection Queue includes the requests submitted by generators to interconnect to the ISO New England electric power system.

Deterministic analyses are snapshots of assumed specific conditions that do not quantify the likelihood that these conditions will actually materialize. The results are based on analyzing the assumed set of conditions representing a specific scenario.

Probabilistic analyses use statistical estimates of the likelihood of an event taking place and explicitly recognize that the inputs are uncertain.

NPCC, Regional Reliability Reference Directory # 1—Design and Operation of the Bulk Power System (December 1, 2009), https://www.npcc.org/Standards/Directories/Directory%201%20-%20Design%20and%20Operation%20of%20the%20Bulk%20Power%20System%20%20Clean%20April%2020%202012%20GJD.pdf and  ISO New England Planning Procedure No. 3—Reliability Standards for the New England Area Bulk Power Supply System, http://www.iso-ne.com/rules_proceds/isone_plan/pp03/pp3_r5.pdf.

Refer to the Glossary (Appendix A) for the definitions of new and existing FCM resources.

For the 2012/2013 ICR calculations, the purchases and sales data are based on the values published in the ISO’s 2012 CELT Report available at http://www.iso-ne.com/trans/celt/index.html. Tie-reliability benefits account for both the transmission-transfer capability of the tie lines and the emergency capacity assistance that may be available from neighboring systems when and if New England would need it.

A bus is a point of interconnection to the system. Internal transmission constraints are addressed through the modeling of local sourcing requirements (LSRs) and maximum capacity limits (MCLs); see Section 4.1.2.

Established ICR values refer to the values that either FERC has approved or the ISO has filed with FERC for approval. Representative net ICR values are the representative ICRs for the region, minus the tie-reliability benefits associated with the Hydro-Québec Interconnection Capability Credits (HQICCs). As defined in the ISO’s tariff, the HQICC is a monthly value that reflects the annual installed capacity benefits of the HQ Interconnection, as determined by the ISO using a standard methodology on file with FERC. The ISO calculates representative net ICR values solely to inform New England stakeholders; these values have not and will not be filed with FERC for approval. The values for FCA #7 for the 2016/2017 CCP are scheduled to be filed with FERC in November 2012. Capacity commitment periods, also referred to as capability years, run from June 1 through May 31 of the following year.

The most recent version of this presentation, Net Installed Capacity Requirements, Indicative Future Net ICR, and Operable Capacity Analysis for 2012 Regional System Plan (June 19, 2012), is available at http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/mtrls/2012/jun192012/net_icr.pdf.

Resulting reserves are the amount of capacity in excess of the forecast 50/50 peak load. Percentage resulting reserves =
[{(Net ICR − 50/50 peak load) ÷ 50/50 peak load} × 100].

2011-2020 Forecast Report of Capacity, Energy, Loads, and Transmission (April 2011), http://www.iso-ne.com/trans/celt/report/2011/index.html and 2010-2019 Forecast Report of Capacity, Energy, Loads, and Transmission (April 2010), http://www.iso-ne.com/trans/celt/report/2010/index.html.

MCLs and LSRs are based on network models using transmission facilities that will be in service no later than the first day of the relevant capacity commitment period.

FERC, Order on Tariff Revisions to the Forward Capacity Market, Docket No. ER12-953-000, 138 FERC ¶ 61,238 (March 30, 2012), http://www.iso-ne.com/regulatory/ferc/orders/2012/mar/er12-953-000_3-30-12_order_fcm_redesign_ext.pdf.

FERC, Order on Paper Hearing and Order on Rehearing, Docket Nos. ER10-787-000, EL10-50-000, EL10-57-000, ER10-787-004, EL10-50-002, and EL10-57-002, 135 FERC ¶ 61,029 (April 13, 2011), http://www.iso-ne.com/regulatory/ferc/orders/2011/apr/err10-787-000_4-13-11_fcm_redesign_order.pdf.

The ICR requirements for 2010/2011 to 2015/2016 are available in the FERC filings at http://www.iso-ne.com/regulatory/ferc/filings/2009/dec/er10-___-000_12-15-09_icr_2010-2011_ara3.pdf, http://www.iso-ne.com/regulatory/ferc/filings/2010/dec/er11-2281-000_12-01-10_icr_2011-12_2012-13_ara.pdf, http://www.iso-ne.com/regulatory/ferc/filings/2011/nov/er12-496-000_11-30-11_icr_2012-2013.pdf, http://www.iso-ne.com/regulatory/ferc/filings/2011/mar/er11-3048-000_03-08-11_icr_2014-2015.pdf, and http://www.iso-ne.com/regulatory/ferc/filings/2012/jan/er12-756-000_01-03-12_icr_2015-2016_filing.pdf. The ISO filed with FERC the results of FCA #6, which was held on April 2-3, 2012, for the 2015/2016 capacity commitment period. ISO New England Inc., Forward Capacity Auction Results Filing, Docket NO. ER12-___000 (April 30, 2012), http://www.iso-ne.com/regulatory/ferc/filings/2012/apr/index.html.

The ISO’s 2011 Annual Markets Report, Section 3.5 (May 15, 2011), describes the FCM in more detail. The report is available at http://www.iso-ne.com/markets/mkt_anlys_rpts/annl_mkt_rpts/index.html. Also see the ISO’s Overview of New England’s Wholesale Electricity Markets and Market Oversight (Market Overview Report) (May 15, 2012), http://www.iso-ne.com/pubs/spcl_rpts/index.html.

Various types of delist bids exist, including static, dynamic, permanent, export, nonprice and several others. Refer to the Glossary (Appendix A) and the Market Overview Report, 7–8, for more information on delist bids.

ISO New England Inc. Informational Filing of the Internal Market Monitoring Unit’s Report Analyzing the Operations and Effectiveness of the Forward Capacity Market, 15, Table 3-1, Quantity Rule, FERC filing (June 5, 2009), http://www.iso-ne.com/regulatory/ferc/filings/2009/jun/er09-1282-000_06-05-09_market_monitor_report_for_fcm.pdf.

Annual reconfiguration auctions, which acquire one-year commitments, are held approximately two years, one year, and just before the FCA commitment period begins. Monthly reconfiguration auctions, held beginning the first month of the first commitment period, adjust the annual commitments during the commitment period.

Shortage events seldom occur in New England. Refer to AMR10, Sections 1, 2, 4, and 7, and AMR11, Section 3.5.5.3, both available at http://www.iso-ne.com/markets/mkt_anlys_rpts/annl_mkt_rpts/.

The 2012 CELT Report, Section 3 and Appendix D (May 2011) (http://www.iso-ne.com/trans/celt/report/2011/index.html) contains the FCM capacity supply obligations for all capacity resources by load zone.

ISO New England Status of Nonprice Retirement Requests (January 20, 2012), http://www.iso-ne.com/genrtion_resrcs/reports/sts_non_retrmnt_rqst/npr_tracking_external_01202012.pdf.

Operating Procedure No. 4, Action during a Capacity Deficiency (December 15, 2011), http://www.iso-ne.com/rules_proceds/operating/isone/op4/index.html. Operating Procedure No.7, Action in an Emergency (June 26, 2011), http://www.iso-ne.com/rules_proceds/operating/isone/op7/index.html.

Net Installed Capacity Requirements (ICRs), Indicative Future Net ICR and Operable Capacity Analysis for 2012 Regional System Plan, PAC presentation (June 19, 2012), http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/mtrls/2012/jun192012/net_icr.pdf.

ISO Operating Procedure No. 8, Operating Reserve and Regulation (January 7, 2011), http://www.iso-ne.com/rules_proceds/operating/isone/op8/op8_rto_final.pdf.

ISO Operating Procedure No. 19, Transmission Operations (June 1, 2010), http://www.iso-ne.com/rules_proceds/operating/isone/op19/op19_rto_final.pdf.

Also see New England Regional System Plan (RSP12) Representative Locational Forward Reserve Requirements, PAC presentation (June 19, 2012), http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/mtrls/2012/jun192012/operating_reserve.pdf.

Market Rule 1, Standard Market Design (ISO tariff, Section III) (2011), defines the types of reserves that can meet these requirements; http://www.iso-ne.com/regulatory/tariff/sect_3/index.html.

Economic-merit order (i.e., in merit or in merit order) is when the generators with the lowest-price offers are committed and dispatched first, and increasingly higher-priced generators are brought on line as demand increases. Out-of-merit dispatch is when generators are run less economically to respect system reliability requirements.

See Section 4.4 for an explanation about the characteristics of baseload, intermediate, and peaking units.

In some circumstances, when transmission contingencies are more severe than generation contingencies, shedding some load may be acceptable.

See the NEPOOL Participant Committee COO Report for Monthly Updates at http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/prtcpnts/mtrls/index.html. Further information on the queue is available at http://www.iso-ne.com/genrtion_resrcs/nwgen_inter/index.html.

The projects that were proposed but discontinued faced problems associated with financing, licensing, insufficient market incentives, or other issues. More information on interconnection projects is available at “Interconnection Status” (April 1, 2012), http://www.iso-ne.com/genrtion_resrcs/nwgen_inter/status/index.html.

Introduction to Nontransmission Alternatives, PAC presentation (October 21, 2010), http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/mtrls/2010/oct212010/nta.pdf.

Nontransmission Alternatives Analysis: Preliminary Results of the NH/VT Pilot Study, PAC presentation (April 13, 2011), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2011/apr132011/nta.pdf. Nontransmission Alternatives Analysis: Results of the NH/VT Pilot Study, PAC presentation (May 26, 2011), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2011/may262011/nta_analysis.pdf.

The nine subareas are Northwestern Vermont, Central Vermont, Connecticut River Corridor, Southeastern Vermont and Western New Hampshire, Northern New Hampshire and Northern Vermont, Seacoast New Hampshire, Southern Vermont, Central New Hampshire, and Southern New Hampshire.

VT/NH Critical Load Level Results and Preliminary Transmission Alternatives, PAC presentation (February 17, 2011), http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/mtrls/2011/feb172011/index.html.

Nineteen demand-response dispatch zones became effective on June 1, 2011, for the New England system (see Section 2.3).

A sensitivity analysis of smaller block sizes of 50 MW and 10 MW was discussed in the April 13, 2011, PAC presentation of the NH/VT nontransmission alternatives pilot study, http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/mtrls/2011/apr132011/index.html.

The ISO conducts an overlapping interconnection impact analysis for each new supply-side resource to assess whether the resource can provide useful capacity and electric energy without negatively affecting the ability of other capacity resources to provide these services also.

The Greater Hartford and Central Connecticut (GHCC) area comprises the following four subareas: Greater Hartford, Northwest Connecticut, Middletown, and Manchester/Barbour Hill.

Market Resource Alternative Analysis—Preliminary Results: Greater Hartford and Central Connecticut Area (August 9, 2012), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2012/aug92012/ghcc_mra_results.pdf.

Higher tie-reliability benefits and reductions in the net ICR would increase the frequency and depth of OP 4 actions.

Past RSPs are available at http://www.iso-ne.com/trans/rsp/index.html. PAC materials and reports are available at http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/index.html.

ISO practices and procedures are available at http://www.iso-ne.com/trans/services/types_apps/.

A special protection system comprises equipment installed on a power system designed to detect abnormal system conditions and take corrective action other than the isolation of faulted elements.

For access to PAC critical energy infrastructure information, complete the PAC Access Request Form at http://www.iso-ne.com/support/custsvc/forms/index.html and mail to ISO New England Inc., Attn: Customer Support, One Sullivan Road, Holyoke, MA 01040-2841, or email PDF file to custserv@iso-ne.com.

See the OATT, Section II.B, Attachment N, “Procedures for Regional System Plan Upgrades,”
http://www.iso-ne.com/regulatory/tariff/sect_2/oatt/index.html.

The Network Capability Interconnection Standard is an energy-only standard that includes the minimum criteria required to permit a generator to connect to the transmission system so that it has no adverse impacts on the reliability, stability, or operation of the system, including the degradation of transfer capability for interfaces affected by the generating facility. The Capacity Capability Interconnection Standard is a capacity and energy standard that includes the same criteria as the Network Capability Interconnection Standard but also includes criteria to ensure intrazonal deliverability by avoiding the redispatch of other capacity network resources. Before October 29, 1998, Generator Interconnection-Related Upgrades included cost responsibility for additional upgrades beyond those required to satisfy the minimum interconnection standard. The OATT, Section 22, defines the standards; http://www.iso-ne.com/regulatory/tariff/sect_2/sch22/index.html.

The filing for the addition or modification to the transmission upgrade must be in accordance with the OATT, Section II.47.2, on a date after the RSP Project List (as of the date of that application) already has documented the addition or modification, other than as an Elective Transmission Upgrade.

Pool transmission facilities are the facilities rated 69 kV or above owned by the participating transmission owners, over which the ISO has operating authority in accordance with the terms set forth in the Transmission Operating Agreements. Refer to the OATT, Section II.49, 109, for additional specifications, http://www.iso-ne.com/regulatory/tariff/sect_2/oatt/sect_ii.pdf.

Section I.3.9 of the ISO tariff, 98, covers the review of participants’ proposed plans. Section I.3.9 project approval recognizes that the proposed project can be implemented without significantly degrading the performance of the system; it is not an endorsement of the need for or associated costs of the project. See http://www.iso-ne.com/regulatory/tariff/sect_1/sect_i.pdf.

PAC materials and meeting minutes are available at http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/index.html. The RSP Project List is available at http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/projects/index.html.

The range for the $6.0 billion cost estimate is $4.9 to $7.1 billion.

Regional network service is the transmission service over the PTFs, including services used for network resources or regional network load not physically interconnected with a PTF.

One exception is that Aroostook and Washington Counties in Maine are served radially from New Brunswick.

Further details about individual transmission projects can be obtained by contacting ISO Customer Service at (413) 540-4220. As part of the PAC materials, the ISO includes study schedules of system performance needs assessments and solutions studies.

The flows vary with system conditions, as shown by the 2011 historical market data, which include the occurrence of northbound flows. See RSP12 2011 Historical Market Data: Locational Marginal Prices, Interface MW Flows, PAC presentation (January 18, 2012), http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/mtrls/2012/jan182012/lmp_and_interface.pdf.

Maine Power Reliability Program (MPRP) Steady State Needs Assessment, PAC presentation (May 14, 2007), https://smd.iso-ne.com/trans/sys_studies/rsp_docs/pres/2007/maine_power_reliability_program_steady_state_needs_assessment.pdf. Final Report Maine Power Reliability Program Needs Assessment of the Maine Transmission System (June 19, 2007), https://smd.iso-ne.com/trans/sys_studies/rsp_docs/pres/2007/maine_power_reliability_program_needs_assessment_final_report.pdf.

Northern Maine System Performance, PAC presentation (September 21, 2010), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2010/sep212010/northern_maine.pdf.

Maine Power Reliability Program (MPRP): Transfer Capability Study Update, PAC presentation (March 15, 2012), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2012/mar152012/mprp_transfer_limits.pdf.

The Vermont Long-Range Transmission Plan identifies reliability concerns and the transmission alternatives to address these concerns. The plan serves as the basis for considering whether alternatives, including new generation and energy efficiency, can meet Vermont's reliability needs. It also provides information about transmission projects that may be needed to maintain grid reliability.

2006 Vermont Transmission System Long-Range Plan (June 30, 2006), http://www.velco.com/LongRange/Documents/abridged_2006_plan%5B1%5D.pdf. 2009 Vermont Long-Range Transmission Plan (July 1, 2009), http://www.velco.com/LongRange/Documents/2009planlinked.pdf. Vermont Transmission System Needs Assessment, PAC presentation (February 25, 2009), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2009/feb252009/vermont_needs.pdf. A 2012 plan will be completed by the end of 2012.

New Hampshire/Vermont Transmission System 2011 Needs Assessment (November 2011), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/reports/2011/nhvt_2011_needs.pdf.

Follow-Up Analysis to the New Hampshire/Vermont Solutions Study (NH/VT Solutions Study Follow Up) (April 2012), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/reports/2012/final_nhvt_solutions_followup.pdf. Final NH/VT Transmission Follow-Up Appendices (April 13, 2012), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/reports/2012/nhvt_sol_followup_apps.pdf. Also see the ISO’s web page, “Study Area: Vermont and New Hampshire” (2012), http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/key_study_areas/vt_nh/index.html.

Vermont Shunt Reactor Needs and Alternatives, PAC presentation (February 16, 2011), http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/mtrls/2011/feb162011/vt_reactors.pdf.

Vermont Substation Rebuilds and Reactive Device Additions, PAC presentation (July 15, 2010), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2010/jul152010/vt_sub_rebuilds.pdf.

Vermont Substation Rebuilds and Reactive Device Additions Update, PAC presentation (September 21, 2010), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2010/sep212010/vermont_substation.pdf.

VELCO, Highgate Converter Station Cooling and Control System Refurbishment (February 16, 2011), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2011/feb162011/highgate.pdf.

Overview—New Hampshire Second Deerfield Autotransformer, PAC presentation (June 4, 2008), http://www.iso-ne.com/trans/sys_studies/rsp_docs/pres/2008/deerfield_area.pdf. New Hampshire Second Deerfield Autotransformer—Update to June 2008, PAC presentation (December 16, 2008), http://www.iso-ne.com/trans/sys_studies/rsp_docs/pres/2008/deerfield.pdf. Second 345/115-kV Deerfield Autotransformer Proposed Plan Application Analysis Report (June 16, 2009), http://www.iso-ne.com/committees/comm_wkgrps/relblty_comm/relblty/ceii/ceii_mtrls/2009/jun162009/2nd_deerfield_txfmr_rev1_ppa.zip.

MPRP Steady State Needs Assessment, PAC presentation (May 14, 2007), https://smd.iso-ne.com/trans/sys_studies/rsp_docs/pres/2007/maine_power_reliability_program_steady_state_needs_assessment.pdf. MPRP Needs Assessment of the Maine Transmission System, final report (June 19, 2007), https://smd.iso-ne.com/trans/sys_studies/rsp_docs/pres/2007/maine_power_reliability_program_needs_assessment_final_report.pdf.

Maine Power Reliability Program (MPRP) Transmission Alternatives—Revised, PAC presentation (January 24, 2008), https://smd.iso-ne.com/trans/sys_studies/rsp_docs/pres/2008/amprprevised.pdf. Final Report Maine Power Reliability Program Transmission Alternatives Assessment for the Maine Transmission System (June 10, 2008), https://smd.iso-ne.com/trans/sys_studies/rsp_docs/pres/2008/mprp_final_report.pdf. The Maine Power Reliability Program Transmission Alternatives Assessment for the Maine Transmission System (May 30, 2008) describes the original version of this project in more detail. The CMP Maine Power Reliability Program Proposed Plan Application Analyses Addendum Report (February 6, 2009) updates the project descriptions.

Central Maine Power Company and Public Service of New Hampshire, Request for Certificate of Public Convenience and Necessity for the Maine Power Reliability Program Consisting of the Construction of Approximately 350 miles of 345 kV and 115 kV Transmission Lines, Maine PUC Docket No. 2008-255 (July 31, 2008), http://www.cmpco.com/OurCompany/MPRP_CPCN_APPLCTN.html, see MPRP CPCN Volume I, Petition.

PSNH and CMP Joint Supplemental Filing with Respect to Termination of Section 3022 Adjacent to Existing Three Rivers Substation, Maine PUC Docket No. 2008-255 (July 26, 2010).

Dave Conroy, Maine Power Reliability Program Update, PAC presentation (CMP, September 21, 2010), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2010/sep212010/cmp_mprp.pdf.

Bangor Hydro’s Northern System Review, PAC presentation (June 4, 2008),
https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2008/bhe.pdf.

The need to reassess these upgrades was driven by a lower load forecast, new supply and demand resources, and sensitivities to the unavailability of the Vermont Yankee generating facility. An area where the load is growing constantly and no new resources are being added would not need to be reassessed.

GHCC Needs Assessment— Scope of Work, final (July 2012); GHCC Needs Assessment Scope of Work Appendices, final (July 2012); ISO Response to Stakeholder Comments on GHCC Scope of Work (June 10, 2011), http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/reports/index.html.

New England East–West Solution (NEEWS) Rhode Island and Springfield Current Needs Assessments (June 17, 2009), http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2009/jun172009/neews.pdf.

New England East-West Solution (NEEWS): Interstate Reliability Project Component Updated Needs Assessment (April 2011), 
https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/reports/2011/neews_interstate_final.pdf.

New England East-West Solution (NEEWS): Interstate Reliability Project Component Updated Solutions Study Report (Feb 2012),
https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/reports/2012/neews_interstate_solution.pdf.

The original Interstate Project included the following major components: a new Millbury–West Farnum–Lake Road–Card Street 345 kV line and associated substation upgrades; four 345 kV, 120 MVAR capacitor banks at Montville; and the looping in of the Millstone–Manchester 345 kV line into the Card Street substation.

Follow-Up Analysis to the 2011 New England East-West Solution: Interstate Reliability Project Component Updated Needs Assessment (July 20120, https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/reports/2012/draft_neews_interstate_rlblty_comp_needs_addendum.pdf.

Pittsfield-Greenfield, MA Area Transmission Solutions Study Report (March 30, 2012), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/reports/2012/pitt-green_solution_report.pdf.

Greater Boston Area Transmission Needs Assessment (July 8, 2010), http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/reports/2011/index.html.

Pittsfield–Greenfield MA Area Transmission: Preferred Solution and Alternatives Study, PAC presentation (October 21, 2010), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2010/oct212010/pittsfield-greenfield.pdf.

Power system equipment must be able to withstand and interrupt short circuits. The highest level of expected short-circuit currents is called fault-duty availability.

SWCT Area Transmission Needs Assessment (July 13, 2011), http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/reports/index.html.

SWCT Update on Continuing Alternatives Analyses (November, 16, 2011), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2011/nov162011/swct_solution_study.pdf.

Southwest Connecticut Advanced Solutions Introduction (April 13, 2011), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2011/apr132011/swct_adv_sol_intro.pdf. SWCT Advanced Solutions Mill River to Quinnipiac 8300 Line Reconfiguration Project (April 13, 2011), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2011/apr132011/8300_line.pdf. SWCT Advanced Solutions Stamford Reliability Project (April 13, 2011), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2011/apr132011/stamford.pdf.

Greater Hartford and Central Connecticut Area Needs Assessment Scope of Work (March 16, 2011), http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2011/mar162011/ghcc.pdf.

Western Massachusetts Transmission Reinforcements 2007 to 2017 (September 2007), http://www.iso-ne.com/committees/comm_wkgrps/relblty_comm/relblty/mtrls/2007/oct102007/zip2_western_ma_ppa.zip.

Merrimack/North Shore Area Transmission Reliability Study Steady State Analysis to Support Proposed Plan Application (April 2006), http://www.iso-ne.com/committees/comm_wkgrps/relblty_comm/relblty/mtrls/2008/feb142008/zip3_wakefield.zip.

National Grid, Auburn St. Substation Upgrades System Impact Study (November 2007) and Auburn St. Substation and Area Transmission System Reliability Study (July 2007), http://www.iso-ne.com/committees/comm_wkgrps/relblty_comm/relblty/mtrls/2007/dec192007/Zip%203%20auburn%20area.zip.

Lower SEMA Short-Term Upgrades System Impact Study Steady-State Analysis (May 3, 2007), http://www.iso-ne.com/committees/comm_wkgrps/relblty_comm/relblty/mtrls/2007/aug82007/zip1b_study-reports.zip.

This circuit’s designated line number is “115,” coincidentally the same as the voltage class.

Greater Rhode Island Transmission Reinforcements (March 2008), http://www.iso-ne.com/committees/comm_wkgrps/relblty_comm/relblty/mtrls/2008/apr152008/zip1_gri-study-reports.zip.

Steady-State and Short-Circuit Analysis for the System Impact Study of the Grand Avenue Project (November 21, 2008), http://www.iso-ne.com/committees/comm_wkgrps/relblty_comm/relblty/ceii/2008/dec/grand_avenue_project_steady_state_report.pdf.

Northeast Utilities, Millstone 345 kV Circuit Separation Project and SLOD Special Protection System Retirement, PAC presentation (January 19, 2011), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2011/jan192011/millstone.pdf.

SWCT Advanced Solutions–Mill River to Quinnipiac 8300 Line Reconfiguration (April 13, 2011), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2011/apr132011/8300_line.pdf.

SWCT Advanced Solutions–Stamford Reliability Project (April 13, 2011), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2011/apr132011/stamford.pdf.

NH/VT Solutions Study Follow Up (April 2012), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/reports/2012/final_nhvt_solutions_followup.pdf.

Greater Boston Needs Assessment/Solutions Study Status Update, PAC presentation (June 2011), http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/mtrls/2011/jun302011/index.html.

Load Pockets—2012, PAC presentation (July 18, 2012), http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/mtrls/2012/jul182012/load_pockets_2012.pdf.

NCPC is a “make-whole” payment to a supply resource that responded to the ISO’s dispatch instructions but did not fully recover its start-up and operating costs in either the Day-Ahead or Real-Time Energy Markets.

ISO New England Inc., Forward Capacity Auction Results, FERC filing, Docket No. ER10-___-000 (August 30, 2010), http://www.iso-ne.com/regulatory/ferc/filings/2010/aug/er10-2477-000_08-30-10_fca_4_results.pdf. FERC, Order on Forward Capacity Auction Results Filing, Docket No. ER10-2477-000 (December 16, 2010), http://www.iso-ne.com/regulatory/ferc/orders/2010/dec/er10-2744-000_12-16-10_order_fca_results.pdf.

The ISO’s website for the nonprice retirement determination letters and resource responses in 2011 is http://www.iso-ne.com/genrtion_resrcs/reports/non_prc_retremnt_lttrs/2011/index.html.

ISO New England Inc., Forward Capacity Auction Results FERC filing, Docket No. ER11-___-000 (June 27, 2011), http://www.iso-ne.com/regulatory/ferc/filings/2011/jun/er11-3891-000_06-27-11_fca_5_results_filing.pdf.

ISO New England Inc., Forward Capacity Auction Results, FERC filing, Docket No. ER12-___-000 (April 30, 2012), http://www.iso-ne.com/regulatory/ferc/filings/2012/apr/index.html.

This total includes seven projects in 2002, 26 projects in 2003, 30 projects in 2004, 51 projects in 2005, 55 projects in 2006, 36 projects in 2007, 64 projects in 2008, 38 projects in 2009, 36 projects in 2010, 39 projects in 2011, and 18 additional projects through June 2012. The June 2012 RSP Project List shows that 30 more projects are due in service by the end of 2012.

Strategic Planning Initiative materials are available at http://www.iso-ne.com/committees/comm_wkgrps/strategic_planning_discussion/index.html.

The ISO assesses fuel diversity issues as part of NPCC and NERC study requirements for assessing the system. With few exceptions, the loss of gas infrastructure could result in the loss of multiple generators over a long period, during which gas system operators and electric system operators would be able to take actions as needed to prevent cascading electric system outages.

The heat rate (MMBtu/MWh) for a power plant, or its efficiency in converting fuel input to electricity, is equal to its fuel consumption divided by its generation. A unit’s heat rate depends on the individual plant design, its operating conditions, and its level of electrical power output. Plants with lower heat rates are more efficient than plants with higher rates.

Aligning Planning and Markets (October 27, 2011), http://www.iso-ne.com/committees/comm_wkgrps/strategic_planning_discussion/materials/alignment_of_markets_and_planning_white_paper.pdfAlso see ISO on Background: Strategic Planning Initiative (October 6, 2011), http://www.iso-ne.com/nwsiss/pr/2011/final_2011_on_background_presentation.pdf.

Compared with generating units with more inertia, generators with lighter inertia, such as lightweight fast-start units, tend to have greater angular displacements in response to system disturbances, which degrades stability performance. Fast-start units, when off line,  can reduce the total inertia of all generating units connected to the system, reducing total system inertia and further degrading stability performance.

GE Applications and Systems Engineering. New England Wind Integration Study (December 5, 2010), http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/reports/2010/newis_report.pdf. PAC archives of NEWIS materials are available at http://iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/reports/2010/index.html.

A load-serving entity secures and sells electric energy, transmission service, and related services to serve the demand of its end-use customers at the distribution level.

2012 Economic Study—ISO New England Summary of Requests (May 15, 2012), http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/mtrls/2012/may162012/2012_eco_study.pdf.

ICF International, Assessment of New England’s Natural Gas Pipeline Capacity to Satisfy Short and Near-Term Electric Generation Needs, draft report (June 15, 2012), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/reports/2012/gas_study_ceii.pdf. Also see the ISO’s memo to the PAC regarding this study (June 15, 2012), http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/reports/2012/gas_study_ltr.pdf.

Addressing Gas Dependence, white paper (July 2012), http://www.iso-ne.com/committees/comm_wkgrps/strategic_planning_discussion/materials/natural-gas-white-paper-draft-july-2012.pdf.

PJM Interconnection is the RTO for all or parts of Delaware, Illinois, Indiana, Kentucky, Maryland, Michigan, New Jersey, North Carolina, Ohio, Pennsylvania, Tennessee, Virginia, and the District of Columbia.

Nontransmission Alternatives Analysis: Results of the NH/VT Pilot Study, PAC presentation (May 26, 2011), https://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2011/may262011/nta_analysis.pdf.

Roadmap for New England: A Proposal for Meeting the Challenges Identified in the Strategic Planning Initiative (March 27, 2012), http://www.iso-ne.com/committees/comm_wkgrps/strategic_planning_discussion/materials/strategic_plan_initiative_roadmap_march_2012.pdf.

Aligning Markets and Planning, discussion paper (June 13, 2012), http://www.iso-ne.com/committees/comm_wkgrps/strategic_planning_discussion/materials/mra_discussion_paper_06132012_vtransmit.pdf. The integration of new market resources can require the development of new or updated transmission system equipment as part of the overall solution.

The 2010 economic study was a follow-up to the 2009 New England Governors’ Renewable Energy Blueprint, also referred to as the Governors’ Blueprint study (see RSP11, Section 13.1, http://www.iso-ne.com/trans/rsp/2011/index.html and http://www.nescoe.com/uploads/September_Blueprint_9.14.09_for_release.pdf). New England 2030 Power System Study: Scenario Analysis of Renewable Resource Development, report to the New England governors (February 2010), http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/reports/2010/economicstudyreportfinal_022610.pdf.

The steady-state analysis is considering summer peak, winter peak, shoulder peak (fall and spring), and light load conditions. For each level of wind generation expansion, different wind conditions, including maximum wind, high wind, typical wind, and low wind, are being simulated. Transfers with neighboring systems are being varied with load levels. See Strategic Transmission Analysis Update, PAC presentation (March 14, 2012), http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/mtrls/2012/mar142012/strat_trans_analysis.pdf.

The 2012 CELT Report (May 1, 2012) is available at http://www.iso-ne.com/trans/celt/report/index.html. The summer installed capacity total includes existing generation and expected generation capacity additions but not HQICCs, demand-response resources, or external purchases and sales. The 2012 CELT Report, Section 2.1, “Generator List with Existing and Expected Seasonal Claimed Capability (SCC),” contains details on 2012 summer installed capacity.

Pumping load is the off-peak load required to pump water into the pumped-storage units’ storage ponds.

An Abnormal Conditions Alert is a notice from the ISO to applicable power system operations, maintenance, construction, and test personnel, as well as each applicable market participant, to alert them about an existing abnormal condition affecting the reliability of the power system or about an anticipated abnormal condition. Master/Local Control Center Procedure No. 2 (M/LCC 2), Abnormal Conditions Alert (April 19, 2012), http://www.iso-ne.com/rules_proceds/operating/mast_satllte/mlcc2.pdf. A Minimum Generation Emergency is a type of abnormal system condition defined by the real-time market rules and declared by the ISO for which it anticipates requesting one or more generating resources to operate at or below its economic minimum (ecomin) limit. A widespread power outage that greatly reduces the demand for electricity compared with the forecasted demand is one type of situation for which the ISO would declare a Min Gen Emergency so that it could reduce the excess amount of electric power available. Implement Minimum Generation Emergency Remedial Action, SOP—RTMKTS.0120.0015 (March 26, 2012), http://www.iso-ne.com/rules_proceds/operating/sysop/rt_mkts/sop_rtmkts_0120_0015.pdf.

The Northeast Gas Association’s (NGA) 2011 Statistical Guide (December 2011) shows the lack of LNG project development in the greater Northeast United States; see http://www.northeastgas.org/pdf/statguide11.pdf.

Technically recoverable undiscovered resources in the Marcellus total 84 Tcf, according to the US Geological Survey (USGS). USGS, “Fact Sheet 2011–3092” (August 2011), http://pubs.usgs.gov/fs/2011/3092/. The US Department of Energy (DOE), Energy Information Administration (EIA) estimates that the  unproved technically recoverable resource of Marcellus Shale is 141 Tcf. EIA, Annual Energy Outlook 2012, DOE/EIA-0383(2012) (June 2012), http://www.eia.gov/forecasts/aeo/pdf/0383(2012).pdf.

Water is one of the key ingredients in the hydraulic fracturing process used to dislodge the gas from the shale rock formations.

Jennifer Robinson, Bentek Energy, Northeast Natural Gas Market Outlook, NGA Regional Market Forum presentation, Hartford, CT (April 2012), http://www.northeastgas.org/pdf/j_robinson_dynamics.pdf.

Encana Corporation, “Deep Panuke,” web page (2012), http://www.encana.com/operations/canada/deep-panuke.html.

Corridor Resources Inc., “McCully Field,” web page (2008), http://www.corridor.ca/operations/mccully-field.html.

The site of another deep shale gas deposit, Utica Shale, is located between Montréal and Quebec City near the Appalachian Mountain front. The potential for extracting shale gas from this deposit, which has an increased potential for natural fractures, is still in the early evaluation stages.

NGA, 2011 Statistical Guide.

One dekatherm (1 Dth) is approximately equivalent to one million Btu (1 MMBtu) and one thousand cubic feet (1 Mcf). The approximate take-away capacity from Mahwah/Ramapo, NY, is 500 MDth/d, with approximately 350 MDth/d entering the New England markets.

Michael Dirrane, Spectra Energy, Project Updates, NGA Regional Market Forum presentation, Hartford, CT (April 25, 2012), http://www.northeastgas.org/pdf/m_dirrane_update.pdf.

In June 2012, Kinder Morgan Inc. bought the El Paso Corporation.

2011 NGA Statistical Guide.

ICF International, Assessment of New England’s Natural Gas Pipeline Capacity to Satisfy Short and Near-Term Electric Generation Needs, draft report (June 15, 2012), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/reports/2012/gas_study_ceii.pdf. Also see the ISO’s memo to the PAC regarding this study (June 15, 2012), http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/reports/2012/gas_study_ltr.pdf.

The natural gas available for power generation (and the associated megawatts of power generation that amount of gas represents) after serving LDC and firm industrial load was estimated, assuming the availability of all natural gas infrastructure. Other scenarios were run assuming various natural gas infrastructure contingencies. The quantity of natural-gas-fired generating capacity that existing gas infrastructure could serve under each scenario (base case, retirement, contingencies) was compared with the projected level of demand for natural-gas-fired generation in the region.

More specifically, the study did not investigate intraday balancing of gas supply with load. Additional analysis could focus at a more granular geographic level within New England and on intraday balancing issues to further assess the adequacy of natural gas pipeline capacity.

The 2012 CELT Report shows that 62 generating stations, totaling 7,358 MW, claimed dual-fuel capability, with a combination of oil or oil and natural gas as their primary fuel source.

Nuclear Regulatory Commission, “Vermont Yankee Nuclear Power Station—License Renewal Application." (February 27, 2007), http://www.nrc.gov/reactors/operating/licensing/renewal/applications/vermont-yankee.html.

“Senate votes to close Vermont Yankee nuclear plant in 2012," Burlington Free Press (February 24, 2010), http://www.burlingtonfreepress.com/article/20100224/NEWS02/100224050/Senate-votes-to-close-Vermont-Yankee-nuclear-plant-in-2012.

New electric power installations in the State of Vermont are required to have a Certificate of Public Good. Vermont, Title 30: Public Service, Chapter 5, 30 V.S.A. § 248, “New gas and electric purchases, investments, and facilities; certificate of public good,” http://www.leg.state.vt.us/statutes/fullsection.cfm?Title=30&Chapter=005&Section=00248.

NRC, "NRC Will Renew Vermont Yankee Operating License for an Additional 20 Years" (March 10, 2011), http://pbadupws.nrc.gov/docs/ML1106/ML110691224.pdf (retrieved March 21, 2011); NRC license renewal letter (March 22, 2011); and NRC, Entergy Nuclear Operations, Inc.; Vermont Yankee Nuclear Power Station; Notice of Issuance of Renewed Facility Operation License No. DPR-28 for an Additional 20-Year Period, Record of Decision, Docket No. 50-271, NRC-2011-0067, 76 Fed. Reg. No. 17162 (March 28, 2011), http://www.gpo.gov/fdsys/pkg/FR-2011-03-28/pdf/2011-7218.pdf.

US District Court for the District of Vermont, Memorandum and Order on Plaintiffs’ Expedited Motion for an Injunction Pending Appeal (Doc. 190). Entergy Nuclear Vermont Yankee, LLC and Entergy Nuclear Operations, Inc., Plaintiffs, v. Gov. Peter Shumlin, Attn. Gen. William Sorrell, et al, defendants, Docket No. 1:11-cv-99 (jgm) (March 19, 2012), http://www.atg.state.vt.us/assets/files/District%20Courts%20Ruling%20on%20Entergys%20Motion%20for%20Injunction%20Pending%20Appeal.pdf.

State of Vermont, Dept. of Pub. Serv. v. Nuclear Regulatory Commission (D.C. Circuit, 09-1322, June 26, 2012), http://www.cadc.uscourts.gov/internet/opinions.nsf/9A5D42515EB8E24785257A290052AD0F/$file/11-1168-1380703.pdf.

NRC, “Pilgrim Nuclear Power Station—License Renewal Affirmation Session" (June 7, 2012), http://pbadupws.nrc.gov/docs/ML1215/ML121590225.pdf.

State of New York, et al., v. Nuclear Regulatory Commission, No. 11-1045 (D.C. Cir. June 8, 2012). The environmental review lacked detail on the availability of a final geologic repository “when necessary” and on the interim on-site storage of spent nuclear fuel for at least 60 years. National Environmental Policy Act, 42 USC §§ 4321 et seq. (1970), http://www.epa.gov/oecaerth/basics/nepa.html.

NRC, Waste Confidence Order, CLI-12-16, memorandum and order (August 7, 2012), http://www.nrc.gov/reading-rm/doc-collections/commission/orders/2012/2012-16cli.pdf.

US DOE, “Water Power Program,” web page (July 3, 2012), http://www1.eere.energy.gov/water/index.html and National Hydropower Association, “US Hydropower Supply Chain,” web page (2012), http://hydro.org/.

Boualem Hadjerioua, Yaxing Wei, et al., An Assessment of Energy Potential at Nonpowered Dams in the United States (US DOE, Oak Ridge National Laboratory, April 2012), http://www1.eere.energy.gov/water/pdfs/npd_report.pdf.

DOE’s assessment of potential development of nonpowered dams by state included 68 MW in Connecticut, 19 MW in Maine, 67 MW in Massachusetts, 63 MW in New Hampshire, 13 MW in Rhode Island, and 17 MW in Vermont. American Society of Mechanical Engineers, Rocky River Pumped-Storage Hydroelectric Station (September 13, 1980), http://files.asme.org/asmeorg/Communities/History/Landmarks/3137.pdf.

Peaking operation stores water daily during off-peak load periods for use when needed, typically during peak load periods. Similarly, ponding stores water over longer periods, such as weekends, when the load is low.

Municipally owned utilities that sell basic electric energy service to end-use customers are exempt from compliance with RPSs.

Non-FERC-jurisdictional projects, including wind projects located in northern Maine and therefore outside the area administered by the ISO, are included in the renewable queue resources summarized in this section.

NESCOE, “Coordinated Procurement,” website (2011), http://www.nescoe.com/Coordinated_Procurement.html.

New England Governor’s Conference, Inc., A Resolution Endorsing the Continued Investigation into the Potential for Coordinated Regional Renewable Power Procurement, Resolution No. 204 (July 11, 2011), rhttp://www.nescoe.com/uploads/NEGC_Coord_Procure_Res._.pdf.

NESCOE, Renewable Resource Supply Curve Report (January 2012), http://www.nescoe.com/Renewable_Supply_Curve.html.

NEGC, “Resolution No. 205—A Resolution Directing the New England State Committee on Electricity (NESCOE) to Implement a Work Plan for the Competitive Coordinated Procurement of Regional Renewable Power,” NESCOE web page (July 30, 2012), http://nescoe.com/uploads/CP_Resolution_July_2012.pdf. Information about the draft work plan is available at http://nescoe.com/2013_Solicitation.html.

Previous RSPs are available at http://www.iso-ne.com/trans/rsp/index.html. Changes to New Hampshire’s RPS for Class I and Class III resources, implemented in June 2012, are not included in the RPS discussion herein. Refer to Section 9.5.4 for more information about these changes.

Renewable energy certificates are tradable, nontangible commodities, each representing the eligible renewable generation attributes of 1 MWh of actual generation from a grid-connected renewable resource.

Additional information about NEPOOL GIS reporting is available at NEPOOL Generation Information System Operating Rules (July 1, 2011), http://www.iso-ne.com/committees/comm_wkgrps/mrkts_comm/geninfo_sys/operating/.

The states have occasionally modified the definitions of eligible Class I renewable resources qualifying for individual state RPSs. One example is Massachusetts’s reassessment of new biomass eligibility as a Class I renewable resource.

More information about the SPEED program is available at http://vermontspeed.com/.

See Section 11 of RSP11, available at http://www.iso-ne.com/trans/rsp/2011/rsp11_final_102111.doc.

This spreadsheet enables ISO New England stakeholders to calculate the annual energy goals of the New England states’ RPSs. It also includes Vermont's goals for growth in renewable resources. Users can review the ISO's calculations and make their own assumptions based on how load growth or state policies might affect the future RPS share of total energy demand. This spreadsheet provides all the assumptions and the results, by state and by class of renewables, extrapolated to 2031.

The existing Montville #5 unit, an 80 MW gas- and oil-fired thermal unit in southeastern Connecticut, has qualified for CT Class I RECs under a project to convert the unit to produce up to 40 MW using biomass fuel. Once converted, the Montville #5 biomass unit could contribute up to 300 GWh per year toward meeting the state’s and region’s RPS goals.

This value represents aggregate megawatts in the April 1, 2012, queue, including all non-FERC-jurisdictional projects.

Wind energy’s share of the region’s total RECs has grown from 7% in 2006, to 27% in 2008, to almost 39% in 2010. These wind resources include projects both within New England and in adjacent balancing authority areas. Massachusetts Department of Energy Resources, Renewable and Alternative Energy Portfolio Standards (RPS & APS) Annual Compliance Report for 2010 (January 11, 2012), http://www.mass.gov/eea/docs/doer/rps/rps-aps-2010-annual-compliance-rpt-jan11-2012.pdf.

NEWIS materials are available at http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/reports/2010/newis_report.pdf and http:/www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/reports/2010/index.html.

The NEWIS methodology is discussed in more detail in RSP09, http://www.iso-ne.com/trans/rsp/2009/rsp09_final.pdf.

GE Energy Application and Systems Engineering, et al., Technical Requirements for Wind Generation Interconnection and Integration (November 3, 2009), http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/reports/2009/newis_report.pdf.

Distributed generators installed in Connecticut included 239 MW of CHP, 33 MW of solar PV, and 10 MW of fuel cells. See the CL&P and UI presentation materials for the 2012 Installer Conference (March 30, 2012), http://www.cl-p.com/downloads/2012%20Installer%20Conference.pdf?id=4294987815&dl=t.

These projects seeking interconnection include more than 524 MW of solar PV, 134 MW wind, and more than 45 MW of natural-gas-fired generators and CHP. Massachusetts Department of Energy Resources (MA DOER), Status and Challenges of RPS Solar Carve-Out and DG Interconnection presentation at the Solar Energy Business Association of New England (SEBANE) Annual Membership Meeting (March 2012), https://docs.google.com/open?id=0B836U49Yrh_QVFNmTFRYQVRUa08waUd2bmZRMTZfdw.

The list of project “Applications Being Processed” under Vermont’s Standard Offer Program is available at http://vermontspeed.com/standard-offer-program/.

The initiative’s targets for 2020 installed costs include $1/W for utility-scale PV, $1.25/W for commercial rooftop PV, and $1.50/W for residential PV. According to DOE, bringing PV costs down to these levels “will require a combination of evolutionary and revolutionary technological improvements, in conjunction with, and in support of, substantial market and manufacturing scale-up.” More information on the SunShot Initiative is available at http://www1.eere.energy.gov/solar/sunshot/index.html.

Solar capacity is defined as nameplate direct-current capacity.

MA’s Green Communities Act established the solar carve-out as a very small solar-specific portion of the state’s Class I RPS goal. For example, the solar carve-out percentage obligation for each retail load supplier in 2010 was 0.0679%, and the remaining Class I obligation was 4.9321%. More information about the solar carve-out is available at http://www.mass.gov/eea/energy-utilities-clean-tech/renewable-energy/solar/rps-solar-carve-out/. Massachusetts, An Act Relative to Green Communities, Mass Gen. Laws, Ch. 169 (enacted April 2, 2008), http://www.mass.gov/legis/laws/seslaw08/sl080169.htm.

An SREC is a market-priced product (in addition to the produced electricity) representing the positive environmental attributes associated with the solar energy production. To be eligible for the  RPS Solar Carve-Out program, projects must have a capacity of 6 MW (DC) or less per parcel of land, be located in Massachusetts (including municipal light district territories), use some of its generation on site and be interconnected to the utility grid, and have a commercial operation date of January 1, 2008, or later. More information is available at http://www.mass.gov/eea/energy-utilities-clean-tech/renewable-energy/solar/rps-solar-carve-out/about-the-rps-solar-carve-out-program.html.

The estimate of anticipated PV development stimulated by ZREC funding is based on information contained in Connecticut’s  2012 Integrated Resource Plan, Appendix D, available at http://www.dpuc.state.ct.us/DEEPEnergy.nsf/c6c6d525f7cdd1168525797d0047c5bf/cb827b1ffa58b2fd85257a1d0060c374/$FILE/CTIRP%202012_Appendix%20D%20(Renewables).pdf. Based on the plan, the ZREC contracts are anticipated to stimulate the development of approximately 250 MW of solar PV. The actual amount of PV development resulting from ZREC contracts will depend on a number of factors, including the prices of ZRECs and future installed costs of PV.

See the 2011 Renewable Energy Portfolio Standard Review, 2011 report to the NH PUC (November 2011), http://www.puc.nh.gov/Sustainable%20Energy/RPS/RPS%20Review%202011.pdf.

The amount of current PV is based on installed PV listed within the Vermont Energy Atlas (accessed March 18, 2012), http://www.vtenergyatlas.com/.

Eligible technologies include solar PV, biomass, hydro, wind, farm methane, and landfill methane projects with a maximum capacity of 2.2 MW. As of April 2012, more than 30 MW were accepted into the Standard Offer program, and 133 MW of the 140 MW of project applications not yet processed are solar PV, suggesting that accepted projects that withdraw from the program will likely be replaced by additional solar PV projects. See http://vermontspeed.com/standard-offer-program/.

Vermont Public Service Board, Study on Renewable Electricity Requirements, 4 (October 3, 2011), http://psb.vermont.gov/sites/psb/files/publications/Reports%20to%20legislature/RPSreport2011/Study%20on%20Renewable%20Electricity%20Requirements%20-%20Final.pdf.

For more information concerning Vermont PSB’s recommendations for future state programs, see Vermont’s 2011 Comprehensive Energy Plan—Facts, Analysis, and Recommendations (Volume 2) (December 2011), http://www.vtenergyplan.vermont.gov/sites/cep/files/Vol%202%20Public%20Review%20Draft%202011%20CEP.pdf.

RI General Assembly S. 0723 requires National Grid to enter into 15-year contracts with small-scale energy producers, <5 MW, for an aggregate capacity of at least 40 MW by 2014. See An Act Relating to Public Utilities and Carriers—Distributed Renewable Energy (January 2011 session), http://www.rilin.state.ri.us/BillText/BillText11/SenateText11/S0723Aaa.pdf.

Two enrollment periods, for a total of 10 MW, were conducted in December 2011 and April 2012, which resulted in 7 MW of PV contracts and 3 MW of wind contracts. See National Grid’s Rhode Island Renewable Distributed Generation Standard Contract Enrollment Application, available at http://www.nationalgridus.com/energysupply/current/20090508/2012%20RI%20DG%20Application%20_Final_%20rev2.pdf.

The sole purpose of this estimate of potential PV development in the region by 2021 is for preliminary characterization of the potential growth of this resource over the RSP planning horizon. Actual growth of PV in the region will depend on many factors, including, but not limited to, realized state funding, future state policies, and future installed costs.

For the electric energy generated by solar PV installations listed as settlement-only generators, see http://www.iso-ne.com/markets/hstdata/rpts/net_eng_peak_load_sorc/energy_peak_source.xls.

IVGTF, Potential Bulk Reliability Impacts of Distributed Resources, Task 1-8 report (August 2011), http://www.nerc.com/docs/pc/ivgtf/IVGTF_TF-1-8_Reliability-Impact-Distributed-Resources_Final-Draft_2011.pdf.

Frequency ride through is the capability of a generator to remain connected to the power system during frequency excursions defined [in IEEE Standard 1547) as tolerable and caused by events external to the generating plant. The Institute of Electrical and Electronics Engineers (IEEE) 1547 Standard provides uniform standards for interconnecting distributed resources with electric power systems. IEEE adopted the standard in June 2003, and it was approved as an American National Standard in October 2003. See http://grouper.ieee.org/groups/scc21/1547/1547_index.html.

Clean Air Act, 42 USC. §§ 7401 et seq. (1970). Clean Water Act, 33 USC § 1251 et seq. (1972). Resource Conservation and Recovery Act, 42 USC § 6901 et seq. (1976).

EME Homer City Generation, L.P. v. EPA, No. 11-1302 (D.C. Cir. August 21, 2012).

Various court orders require several upcoming EPA rulemakings: Clean Air Transport Rule (North Carolina v. EPA, 531 F3.d 896 (D.C. Cir. 2008) (revoking CAIR), North Carolina v. EPA, 550 F.3d 1176 (D.C. Cir. 2008) (remanding CAIR, ordering development of the Clean Air Transport Rule, CATR)); Mercury and Air Toxics Standards (New Jersey v. EPA, 517 F.3d 574 (D.C. Cir. 2008) (revoking Clean Air Mercury Rule (CAMR), American Nurses Association v. Jackson, No. 08-2198 (D.D.C. 2010) (setting rulemaking schedule)); Cooling Water Intake Rule (Riverkeeper, Inc. v. Jackson, 93 Civ. 0314 (SDNY 2010) (setting rulemaking schedule).

EPA, National Emission Standards for Hazardous Air Pollutants From Coal- and Oil-Fired Electric Utility Steam Generating Units and Standards of Performance for Fossil-Fuel-Fired Electric Utility, Industrial-Commercial-Institutional, and Small Industrial-Commercial-Institutional Steam Generating Units, final rule, 77 Fed. Reg. 9304 (February 16, 2012).

Second Amendment to Settlement Agreement between EPA, Plaintiffs in Cronin, et al v. Reilly, 93 Civ. 314 (SDNY) and Riverkeeper, Inc. v. Jackson, 93 Civ. 0314 (SDNY 2010) (setting rulemaking schedule). See http://water.epa.gov/lawsregs/lawsguidance/cwa/316b/index.cfm.

National Pollutant Discharge Elimination System-Cooling Water Intake Structures at Existing Facilities and Phase I Facilities, proposed rule, 76 Fed. Reg. 22174 (April 20, 2011). Also see the EPA’s “Cooling Water Intake Structures—CWA §316(b)” web page (2012), http://water.epa.gov/lawsregs/lawsguidance/cwa/316b/index.cfm, and the Modified Settlement Agreement for Proposed Regulations and Plaintiffs in Riverkeeper, et at. v. EPA, 06 Civ. 12987 (PKC) (SDNY July 17, 2012), http://water.epa.gov/lawsregs/lawsguidance/cwa/316b/loader.cfm?csModule=security/getfile&PageID=627843.

Section 316(b) of the Clean Water Act requires that the location, design, construction, and operation of cooling water intake structures withdrawing waters of the United States reflect the best technology available (BTA) for minimizing adverse environmental impacts, which EPA defines as the impingement, entrainment, or thermal stressing of aquatic life.

US EPA, National Pollutant Discharge Elimination System—Cooling Water Intake Structures at Existing Facilities and Phase I Facilities, proposed rule, 76 Fed. Reg. 24976, 22174, 22214 (April 20, 2011).

EPA notes in the proposed Cooling Water Intake Rule (76 Fed. Reg., 22210) that in a number of areas of the country (i.e., California, Delaware, New York, and New England), permitting authorities already have required or are considering requiring existing facilities to install closed-cycle cooling operations.

US EPA, National Pollutant Discharge Elimination System—Proposed Regulations to Establish Requirements for Cooling Water Intake Structures at Existing Facilities; Notice of Data Availability Related to Impingement Mortality Control Requirements, 77 Fed. Reg. 34315 (June 11, 2012).

In New England, Connecticut, Maine (except for facilities located in sovereign Indian nations), Rhode Island, and Vermont have delegated authority to issue NPDES permits under the federal Clean Water Act. Massachusetts and New Hampshire are nondelegated states and issue joint NPDES permits to affected facilities in collaboration with EPA Region 1.

EPA indicates that the most appropriate basis for determining compliance costs for impingement-mortality control technologies is to estimate the minimum modifications or reconstruction of existing physical barriers for fish and shellfish that would be required in accordance with the targets specified in the final rule. This does not preclude using other technologies or reducing the maximum intake velocity to less than 0.5 feet per second.

See EPA’s “NPDES Water Permit Program in New England” web page (March 27, 2012), http://www.epa.gov/region1/npdes/index.html.

EPA, “Cleaner Power Plants,” web page (April 10, 2012), http://epa.gov/mats/powerplants.html#time.

The marginal emissions rate (lb/MWh) a measure (lb/MWh) of the energy-weighted average emissions from a unit that would typically increase its output if the regional energy demand were higher during the period of interest In New England. “assumed marginal units” typically are natural-gas--fired generators and oil-fired generators, including those burning residual, distillate, diesel, kerosene, and jet fuel. The marginal emissions rate is calculated by dividing the emissions from the assumed marginal units during the desired period in pounds (lb) by the generation from the assumed marginal units (MWh). Assumed marginal units also may be expressed as lb/MMBtu by applying a systemwide conversion factor.

2010 ISO New England Electric Generator Air Emissions Report (April 2012), http://www.iso-ne.com/genrtion_resrcs/reports/emission/final_2010_emissions_report_v2.pdf.

The system emission rate (lb/MWh) is a measure of the annual emissions produced by all generators in the region divided by the annual generation in the region. The emissions data are obtained from the US EPA Clean Air Markets database (http://ampd.epa.gov/ampd/), and the generation data are obtained from ISO New England Settlements.

The marginal heat rate (MMBtu/MWh) is a measure of how efficiently assumed marginal units (i.e., in New England, units fueled with natural gas or oil, including residual, distillate, diesel, kerosene, and jet fuel)  convert fuel to electricity. This rate is equal to the amount of fuel consumed by the assumed marginal units divided by the actual generation of the assumed marginal units.

The calculated marginal emissions rate excludes coal, refuse, biomass, and wood-burning generating units. The ISO is benchmarking a new methodology for calculating the marginal emissions rate for use in the 2011 emissions study.

Under RGGI, one allowance equals the limited right to emit one ton of CO2.

Regional Greenhouse Gas Initiative, Memorandum of Understanding (December 20, 2005) signed by Connecticut, Delaware, Maine, New Jersey, New York, and Vermont. Amended with additional participants on August 31, 2006, and revised by a second amendment to the RGGI MOU on April 20, 2007. See http://www.rggi.org/design/history/mou.

Regional Greenhouse Gas Initiative, Auction 15 results (conducted March 14, 2012), http://www.rggi.org/docs/Auction_15_State_Proceeds_and_Allowances.pdf. RGGI compliance auction proceeds through Auction #15 total $304.1 million for New England RGGI states.

Regional Greenhouse Gas Initiative, Auction 16 results (conducted June 6, 2012), http://www.rggi.org/market/co2_auctions/results/Auction-16. RGGI compliance auction proceeds through Auction #16 total $318.5 million for New England RGGI states.

RGGI, “Program Review,” web page (2012), http://www.rggi.org/design/program_review.

Massachusetts, Green Communities Act, http://www.malegislature.gov/Laws/SessionLaws/Acts/2008/Chapter169; An Act Establishing the Global Warming Solutions Act, Mass Gen. Laws, Ch. 169, http://www.malegislature.gov/Laws/SessionLaws/Acts/2008/Chapter298 (approved August 7, 2008 ); and  Massachusetts Executive Office of Energy and Environmental Affairs, Massachusetts Clean Energy and Climate Plan for 2020 (December 29, 2010), http://www.mass.gov/green/cleanenergyclimateplan.

MassDEP, Overview of Global Solutions Act and Green Communities Acts (n.d.), http://www.mass.gov/dep/air/climate/gwsa.htm.

Massachusetts, FY2012 Final Budget (187th General Court, July 11, 2011), http://www.malegislature.gov/Budget/CurrentBudget.

In general, the ISO has accommodated all past study requests that would not result in a violation of the ISO’s Information Policy (see Section 2.1.5). For example, the ISO has studied general resource-expansion scenarios and retirements but has not conducted studies of individual generating plants or groups of plants by one participant owner.

PAC Presentation materials for the April through July 2011 meetings and supplemental materials are available at http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/mtrls/index.html.

Western Maine Economic Study Request, PAC presentation (April 14, 2011), http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/mtrls/2011/apr142011/cmp_eco_study_request.pdf. Economic Impacts of Relieving Transmission Congestion for Near-Term Wind Development 2011 Economic Study Request (April 14, 2011), http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/mtrls/2011/apr142011/renew_eco_study_request.pdf. LS Power Transmission, LLC 2011 Economic Study Request to ISO-NE PAC (April 14, 2011), http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/mtrls/2011/apr142011/ls_power_eco_study_slides.pdf.

IREMM is a “pipe and bubble” production cost program that models the region’s subareas (bubbles) and the transmission lines that connect them (pipes). 2011 Economic Studies Draft Results (May 17, 2011), http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/mtrls/2012/may172012/2011_eco_study.pdf. 2011 Economic Study Requests, PAC presentation (May 26, 2011), http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/mtrls/2011/may262011/2011_eco_study_requests.pdf. 2011 Economic Study Update, PAC presentations (July 1, July 21, and September 21, 2011), http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/mtrls/2011/jul212011/2011_eco_study_update.pdf, http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/mtrls/2011/jul212011/2011_eco_study_update.pdf, and http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/mtrls/2011/sep212011/2011_eco_study.pdf.

Interconnections are the responsibility of the resource developers in accordance with the Network Capability Interconnection Standard (NCIS) defined in the OATT, Schedule 22, Standard Large Generator Interconnection Procedures (LGIP) (January 31, 2011), http://www.iso-ne.com/regulatory/tariff/sect_2/sch22/index.html, and Schedule 23, Standard Small Generator Interconnection Procedures (SGIP) (January 31, 2011), http://www.iso-ne.com/regulatory/tariff/sect_2/sch23/index.html. The NCIS specifies the minimum criteria required to permit the interconnection customer to interconnect to the New England transmission system in a manner that avoids significant adverse effects on the reliability, stability, and operability of the system, including the degradation of transfer capability for interfaces affected by the generating facility.

A wind integration sensitivity study was withdrawn because the ISO had already addressed this issue as part of the 2011 Economic Study.

2012 Economic Study: Scope of Work (June 19, 2011), http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/mtrls/2012/jun192012/2012_eco_study_sow.pdf.

Update on Generic Supply-Side Resource Capital Costs, PAC presentation (January 18, 2012), http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/mtrls/2012/jan182012/generic_costs_resources.pdf.

EIA, “Updated Capital Cost Estimates for Electricity Generating Plants,” web page (November 2010), http://www.eia.gov/oiaf/beck_plantcosts/index.html. EPRI, Program on Technology Innovation: Integrated Generation Technology Options, 1022782 (June 2011), http://www.energync.net/Portals/14/Documents/EnergyPolicyCouncil/2009_Prism_MERGE_Gen_Options_Report.pdf.

Energy Policy Act of 2005, Pub. L. 109-58, Title XII, Subtitle B, 119 Stat. 594 (2005) (amending the Federal Power Act to add a new § 216).

FERC, Transmission Planning and Cost Allocation by Transmission Owning and Operating Public Utilities, Docket No. RM10-23-000, Order 1000, 18 CFR Part 35, 136 FERC ¶ 61,051 (July 21, 2011), http://www.ferc.gov/industries/electric/indus-act/trans-plan.asp and http://www.ferc.gov/whats-new/comm-meet/2011/072111/E-6.pdf. Preventing Undue Discrimination and Preference in Transmission Service, 18 CFR Parts 35 and 37, Docket Nos. RM05-17-000 and RM05-25-000, Order 890 (February 16, 2007), http://www.ferc.gov/whats-new/comm-meet/2007/021507/E-1.pdf.

FERC, Integration of Variable Energy Resources, 18 CFR Part 35, Docket No. RM10-11-000, Order 764, 139 FERC ¶ 61,246 (June 22, 2012), http://mc.dwt.com/files/Uploads/Documents/Publications/VER%20Rule.pdf.

FERC, Performance Metrics for Independent System Operators and Regional Transmission Organizations (April 2011), http://www.ferc.gov/industries/electric/indus-act/rto/metrics/report-to-congress.pdf.

California ISO, ISO New England, Midwest ISO, New York ISO, PJM Interconnection, and Southwest Power Pool, 2010 ISO/RTO Metrics Report (December 7, 2010), http://www.isorto.org/atf/cf/%7B5B4E85C6-7EAC-40A0-8DC3-003829518EBD%7D/2010%20ISO-RTO%20Metrics%20Report.pdf. The metrics report outlines investment in regional electric power system infrastructure and identifies several future challenges for the New England region, including the efficient integration of greater levels of intermittent resources and demand-response programs and planning for the retirement of traditional fossil-fuel-fired capacity.

Differences between the various ISO/RTOs are the result of differing factors, such as geographic scale or scope of the respective operations (e.g., number/types of markets).

PJM, RTO/ISO Performance Metrics, AD10-5-000, FERC filing of the 2011 ISO/RTO Metrics Report (August 31, 2011), http://www.iso-ne.com/regulatory/ferc/filings/2011/aug/ad10-5-00_8-31-11_joint_iso-rto_metrics_report.pdf.

Piedmont Environmental Council v. FERC, 558 F.3d 304 (4th Cir. 2009).

National Interest Electric Transmission Corridors and Congestion Study documents are available at http://nietc.anl.gov/documents/index.cfm.

DOE, Office of Electricity Delivery and Energy Reliability, “2012 National Electric Transmission Congestion Study: Preliminary Findings,” web page and presentation (August 2012), http://energy.gov/oe/downloads/2012-national-electric-transmission-congestion-study-preliminary-findings.

Additional information on the EIPC is available at http://www.eipconline.com/.

EIPC, Final DOE Statement of Project Objectives (July 14, 2010), http://www.eipconline.com/uploads/SOPO_14Jul10_DE-OE0000343.pdf.

EIPC, Phase I Report: Formation of Stakeholder Process, Regional Plan Integration and Macroeconomic Analysis, DOE Award Project DE-OE0000343 (December 2011), http://eipconline.com/uploads/Phase_1_Report_Final_12-15-2011.pdf.

More information about NERC is available at http://www.nerc.com/.

NERC, 2011 Long-Term Reliability Assessment (November 2011), http://www.nerc.com/files/2011LTRA_Final.pdf.

IVGTF materials are posted at http://www.nerc.com/filez/ivgtf.html.

NERC, Special Report: Accommodating High Levels of Variable Generation (April 2009), http://www.nerc.com/files/IVGTF_Report_041609.pdf.

The NPCC region covers nearly 1.2 million square miles and is populated by more than 55 million people. NPCC in the United States includes the six New England states and the state of New York. NPCC Canada includes the provinces of Ontario, Québec, and the Maritime provinces of New Brunswick and Nova Scotia. As full members, New Brunswick and Nova Scotia also ensure that NPCC reliability issues are addressed for Prince Edward Island.

Additional information about the protocol is available at http://www.interiso.com/public/document/Northeastern%20ISO-RTO%20Planning%20Protocol.pdf.

All IPSAC materials are available at http://www.iso-ne.com/committees/comm_wkgrps/othr/ipsac/index.html.

ISO New England, New York ISO, and PJM, 2011 Northeast Coordinated System Plan, final (May 31, 2012), http://www.iso-ne.com/committees/comm_wkgrps/othr/ipsac/ncsp/index.html.

PROMOD’s production cost program provides a much more detailed simulation of the power system and unit commitment than IREMM’s “pipe and bubble” program. PROMOD’s program includes minimum-cost, security-constrained unit commitment and dispatch (SCUC/ED) algorithms with a more explicit representation of the transmission system.

For more information, see www.nescoe.com.

Eric Runge, “Sector Caucus Representatives for the EIPC,” memorandum (June 23, 2010), http://www.iso-ne.com/committees/comm_wkgrps/othr/eipc/eipc_caucus_reps.doc.

NESCOE, 2011 Report to the New England Governors (n.d.), http://www.nescoe.com/Annual_Report.html.

NESCOE, Survey of Smart Grid Implementation in New England (Spring 2012), http://www.nescoe.com/uploads/Smart_Grid_Final_May_2012.pdf.

See the New England Governors’ Conference website at http://www.negc.org/main/.

NEC/ECP, Resolution 36-1, “Resolution Concerning Energy,” materials from the 36th Annual Conference of New England Governors and Eastern Canadian Premiers, Burlington, Vermont (July 29–30, 2012).

FERC, Order on Paper Hearing and Order on Rehearing Docket Nos. ER10-787-000, EL10-50-000, EL10-57-000, ER10-787-004, EL10-50-002, and EL10-57-002 (issued April 13, 2011), http://www.iso-ne.com/regulatory/ferc/orders/2011/apr/err10-787-000_4-13-11_fcm_redesign_order.pdf.

The cost of new entry is a threshold price used to calculate the starting price for each Forward Capacity Auction. The CONE also is used for controlling market power concerns with delist bids and in determining reserve pricing when supply is inadequate and competition is insufficient.  More information is available in the ISO’s Market Overview Report (May 15, 2012), http://www.iso-ne.com/pubs/spcl_rpts/index.html.

FERC, Demand-Response Compensation in Organized Wholesale Energy Markets, final rule, Docket No. RM10-17-000, Order No. 745, 134 FERC ¶ 61,187 (March 15, 2011), http://www.iso-ne.com/regulatory/ferc/orders/2011/mar/rm10-17-000_3-15-000_demand_resp_order.pdf.

The existing Day-Ahead Load-Response Program (DALRP) expired on June 1, 2012, and the transition rules began for the full integration of demand resources. The transition-period rules are based on the present Day-Ahead Load-Response Program, which is a bid-based program in which a market participant with a real-time demand-response asset can submit demand-reduction offers into the energy market. See the ISO’s Order 745 Compliance Filing (August 19, 2011), http://www.iso-ne.com/regulatory/ferc/filings/2011/aug/er11_4336-001_prd_filing.pdf, and subsequent filing (December 2011), http://www.iso-ne.com/regulatory/ferc/filings/2011/dec/er11-4336-003_12-22-11_req_chg_eff_date_.pdf.

Additional information on the CLG is available at http://www.iso-ne.com/committees/comm_wkgrps/othr/clg/index.html.

For more information on the CLG’s Governance, see http://www.iso-ne.com/committees/comm_wkgrps/othr/clg/consum_lias_grp_gov/index.html.

Consumer Liaison Group Coordinating Committee and ISO New England, 2011 Report of the Consumer Liaison Group (May 2012), http://www.iso-ne.com/committees/comm_wkgrps/othr/clg/annual_rpts/index.html.

The Institute of Electrical and Electronics Engineers (IEEE) describes the smart grid as a “next-generation” electrical power system that typically employs the increased use of communications and information technology for generating, delivering, and consuming electrical energy. See the IEEE’s “What Is the Smart Grid” website (2011) at http://smartgrid.ieee.org/about-smartgrid. A more detailed discussion of smart grid technology is available at http://smartgrid.ieee.org/.

Additional information on NIST is available at http://www.nist.gov/index.html. Also see “2030 Smart Grid Interoperability Series of Standards” website, IEEE Standards Association (2010), http://grouper.ieee.org/groups/scc21/dr_shared/2030/.

“Smart Grid Standards Project” website, ISO/RTO Council (2011), http://www.isorto.org/site/c.jhKQIZPBImE/b.6368657/k.CCDF/Smart_Grid_Project_Standards.htm.

For more information on IEEE, see http://www.ieee.org/index.html.

A map illustrating all the PMUs installed in North America as of March 30, 2012, is available at http://www.eia.gov/todayinenergy/detail.cfm?id=5630.

The IEEE defines FACTS as flexible alternating-current transmission systems that incorporate power-electronics-based controllers and other static controllers to enhance controllability and power-transfer capability. See http://www.ieee-pes.org/nari-hingorani-facts-award.

Michael Henderson and Donald Ramey, Planning Issues for FACTS, presentation at the IEEE Power Engineering Society General Meeting, Tampa (June 2007). Also see “Transmission System Application Requirements for FACTS Controllers Special Publication 06TP178,” produced by the IEEE Power Engineering Society Working Group 15.05.13.

Static VAR compensators and DVARs provide dynamic voltage support.

FERC, “Hydropower Licensing,” web page (June 7, 2012), http://ferc.gov/industries/hydropower/gen-info/licensing.asp. FERC’s list of issued permits and preliminary permits for hydrokinetic projects are available at http://www.ferc.gov/industries/hydropower/gen-info/licensing/licenses.xls and http://www.ferc.gov/industries/hydropower/gen-info/licensing/hydrokinetics/permits-issued.xls.

An example of the improved RSP Transmission Project List is available at http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/projects/2012/march2012_projects.xls.

FERC, letter order accepting Schedule 16 Revisions to the Open Access Transmission Tariff of ISO New England Inc., Docket Nos, ER12-727-000, ER12-729-001, and ER12-729-002 (February 12, 2012),  http://www.iso-ne.com/regulatory/ferc/orders/2012/feb/index.html and ISO New England Inc. and New England Power Pool, Docket No. ER11-   -000; Revisions to Schedule 16 of the OATT (Part 1 of 2) and . . . Part 2 of 2 (both, December 30, 2011), http://www.iso-ne.com/regulatory/ferc/filings/2011/dec/index.html.

An Act Concerning the Establishment of the Department of Energy and Environmental Protection and Planning for Connecticut’s Energy Future, Conn. Public Act No. 11-80 (June 17, 2011), http://www.cga.ct.gov/2011/ACT/Pa/pdf/2011PA-00080-R00SB-01243-PA.pdf.

Connecticut DEEP, 2012 Integrated Resource Plan (June 14, 2012), http://www.ct.gov/deep/cwp/view.asp?a=4120&q=486946.

In Connecticut, one REC is created for each megawatt hour of electricity produced by a Class I renewable energy source. On April 4, 2012, PURA approved, with modifications, the LREC and ZREC solicitation plan filed by CL&P and UI. CT DEEP PURA, Joint Petition by CL&P and UI for Approval of the Solicitation Plan for the Low and Zero Emissions Renewable Energy Credit Program, Docket Number 11-12-06. (April 4, 2012), http://www.ct.gov/deep/lib/deep/press_releases/2012/2012april4lzrecdecision.pdf.

Maine Governor’s Office of Energy Independence and Security, Maine Wind Energy Development Assessment Report and Recommendations (March 2012), http://maine.gov/energy/pdf/Binder1.pdf.

US EIA, “Maine,” web page (2009), http://205.254.135.7/state/state-energy-profiles.cfm?sid=ME.

State of Maine, An Act to Improve Efficiency Maine Trust Programs to Reduce Heating Costs and Provide Energy-Efficient Heating Options for Maine’s Consumers, Pub. L. Chapter 637, LC 1864m (125th Maine State Legislature, April 10, 2012), http://www.mainelegislature.org/legis/bills/bills_125th/chappdfs/PUBLIC637.pdf.

MA DPU, Order Establishing Distributed Generation Working Group, DPU 11-75-A (January 23, 2012), http://www.mass.gov/eea/docs/dpu/electric/dpu-11-75-a-jan23-2012.pdf.

MA DOER, DPU Petition to Address Interconnection (August 18, 2011), http://www.mass.gov/eea/docs/doer/renewables/dg-inter.pdf.

MA DOER, Renewable Energy Portfolio Standard—Class I,  225 CMR 14.00 (August 17, 2012), http://www.mass.gov/eea/energy-utilities-clean-tech/renewable-energy/biomass/renewable-portfolio-standard-biomass-policy.html, and Massachusetts Executive Office of Energy and Environmental Affairs, “Patrick-Murray Administration Announces Enactment of Biomass Regulations,” press release (August 17, 2012), http://www.mass.gov/eea/pr-2012/120817-pr-biomass.html.

Massachusetts, An Act Relative to Competitively Priced Electricity in the Commonwealth, Mass Gen. Laws, Ch. 209 (approved August 3, 2012), http://www.malegislature.gov/Laws/SessionLaws/Acts/2012/Chapter209.

Massachusetts, Green Communities Act, http://www.mass.gov/legis/laws/seslaw08/sl080169.htm.

US Bureau of Ocean Energy Management, “State Activities, Massachusetts,” web page (2012), http://www.boem.gov/Renewable-Energy-Program/State-Activities/Massachusetts.aspx.

BOEM’s May 30, 2012, Announcement of Area Identification is available at http://www.boem.gov/uploadedFiles/BOEM/Renewable_Energy_Program/State_Activities/MA_AreaID_Announcement_052412_Final.pdf.

New Hampshire, An Act Relative to Eminent Domain by Public Utilities and Establishing a Commission to Investigate the Procedural Rights of the Landowner . . ., HB 648 —final version (approved March 5, 2012), http://www.gencourt.state.nh.us/legislation/2012/hb0648.html.

New Hampshire, An Act Relative to Electric Renewable Portfolio Standards, SB 318-FN—final version (Approved June 19, 2012), http://www.gencourt.state.nh.us/legislation/2012/SB0218.html.

New Hampshire, An Act Relative to New Hampshire’s Regional Greenhouse Gas Initiative Cap-and-Trade Program for Controlling Carbon Dioxide Emissions, HB 1490-FN—final version (approved June 23, 2012),   http://www.gencourt.state.nh.us/legislation/2012/hb1490.html.

Rhode Island, An Act Relating to Public Utilities and Carriers—Least-Cost Procurement (RI General Assembly S. 2792-Sub A, signed June 21, 2012), http://www.rilin.state.ri.us/BillText/BillText12/SenateText12/S2792A.pdf.

A feed-in tariff is part of a long-term electricity purchasing agreement that guarantees a specified price, usually above the market level, for the electric power produced under the agreement. The standard-offer program requires utilities to purchase qualifying renewable resources at prices set by the Public Service Board. For more information, see the Vermont Public Service Board’s web page, “Implementation of Standard Offer Program for SPEED,” Docket Nos. 7523 and 7533 (2012), http://psb.vermont.gov/docketsandprojects/electric/7523.

State of Vermont, An Act Relating to the Vermont Energy Act of 2012, S.214 (May 18, 2012), http://www.leg.state.vt.us/docs/2012/Acts/ACT170.pdf.

In Vermont, large-scale hydroelectric generators are considered renewable resources.