## Slide 1: Transmission Line Refurbishment Project K19 Line Reliability Committee Meeting May 15, 2025

## Slide 2: K19 Line
115 kV line from Sandbar to Georgia
8.88 mile line built in 1975 on wooden H-frame Structures

## Slide 3: Example Inspection Results

## Slide 4: K19 Line Structure Replacement Summary
Located in variable lowland terrain with large wetlands and challenging side slopes
Major issues being addressed include significant woodpecker damage, internal pole voids, and rotten pole tops
Additional assessment findings include severely weathered and cracked poles
Replace 41 out of 93 wood H-frame structures. Majority of replacements will be steel H-frames, especially in areas seeing woodpecker damage. Minimal wood H-frames will be installed to reduce current wood pole inventory.
Extensive matted roads are required to reach many of the D and C rated structures. These temporary roads will pass by the B rated structures. Replacement of the B rated, 50 year old structures is occurring to avoid having to re-incur the significant matting costs for the temporary roads.
Total Estimate: $5.8 million PTF
Completion of work projected in 2025

## Slide 5: Cost estimate details