This version of OP-16 and Appendices A, B, C, D, E, G, H, and I were approved at the May 21, 2026, Reliability Committee meeting and will become effective on October 21, 2026, to coincide with deployment of the redesigned NX Application as part of FERC Order No. 881.

Appendix A - Explanation of Terms and Instructions

for Data Preparation of NX-9A

ISO New England Transmission Equipment Rating, Characteristic, and Operational Data

Transmission Line

Effective Date: October 21, 2026

Review By Date: October 21, 2028

Table of Contents

I.	Equipment Requirements	2

II.	General Data Instructions	3

III.	Rating Data Instructions	4

IV.	Characteristic and Operational Data Instructions	5

V.	Explanation Of Data Changes	5

VI.	Equipment Notes	5

Example 1, NX-9A Transmission Line	6

Example 2, NX-9A Transmission Line, Breaker in/out Conditional Ratings	7

Example 3, NX-9A Transmission Line, Companion Cable in/out Conditional Ratings	8

# Equipment Requirements

Data for all transmission line segments designated as part of the Bulk Electric System (BES) or connecting to the New England Transmission System at a voltage of 69 kV or greater shall be provided by the Transmission Owners and Market Participants who own the equipment.

Data for other line segments connecting at voltages that are less than 69 kV may be required when ISO determines that the data is necessary for reliable operation of the New England Transmission System. When required by ISO, the TO or MP shall submit the data within thirty (30) calendar days of ISO’s notification.

NX-9A data form requirements for lines associated with generator connections:

All generators participating in the Real-Time Energy Market and connecting via a line of any voltage level that is dedicated solely to the generation interconnection (i.e., via an express feeder) will be evaluated for impact to the ISO EMS Network Model. Based on this evaluation, NX-9A data forms may be required.

When NX-9A data is determined to be required,

- The TO shall provide NX-9A data for the line(s) from its connecting substation to the point of change of ownership between the generator and the TO.

- The Generator Asset Lead MP shall provide NX-9A data for the line(s) from the generator step-up (GSU) transformer to the point of change of ownership between the generator and the TO.

NX-9A data forms are not required for a line(s) between the transmission system and a generator when customer load is also served from the line.

NX-9A data forms are not required for lines connecting solely to Settlement Only Generators.

Submittal of an NX-9A for a line segment internal to a substation is not required when the following conditions are met and the exemption has been approved by the ISO NX-9 Administrator:

- The total reactance (x) of the segment (all owners) is less than 0.01 (percent on a 100 MVA base)

- The segment is not part of a 3-terminal line tap

- The MW and MVAR of the segment are not metered

- All potentially limiting equipment is included in the rating calculation of the adjacent equipment

A transmission line segment is defined as follows:

As used by the ISO nodal network model, a line segment is a transmission path between two (2) electrical nodes of the same kV level. For multi-terminal lines, a line segment is defined for each electrical node connecting to a common tap. In the example below, the four (4) terminals; A, B, C and D, are connected by three (3) line segments. These segments are: 1) A to B; 2) B to C; and 3) B to D. In this example, B is the common tap. Each of the three segments is treated as a separate segment for which ISO Identification Numbers are assigned and transmission rating and characteristic data is required.

A

C

B

D

A separate NX-9A form shall be provided for each transmission line segment. ISO shall provide ISO Identification Numbers for all line segments. On any jointly owned line, each MP or TO shall report the data for only that portion of the line segment that it owns or is otherwise responsible for providing as described above.

If a series reactive device cannot be switched in or out independently of the associated line, the line and reactive device can be reported together on a single NX-9 form. Combined impedance and rating information shall be submitted. On all new and revised NX-9A forms, if a series reactive device is combined with a line and reported on a single combined NX-9A form, the MP or TO shall update the Participant Equipment Notes field to indicate that the NX-9A form includes the series reactive device information.

Series reactive devices operated independently of the line shall be reported on the NX-9H form using the instructions in Operating Procedure 16, Appendix H.

# General Data Instructions

The NX-9A form provides for entry of both ISO and MP/TO data. ISO fields cannot be modified by the MP or TO. The MP or TO is responsible for providing data for all non-ISO fields via the NX Application.

The circuit number shall initially be entered by the MP or TO for new equipment and thereafter maintained by ISO.

Select the terminals that reflect the connection points of the equipment. Terminals are created and maintained by ISO. The user should contact the ISO NX-9 Administrator (nx9admin@iso-ne.com) if terminal additions or changes are needed.

In the Cable Type field select “Overhead,” “Underground” or “Both.”  Select “Both” if the NX-9A form contains information for both overhead conductor and underground cable.

To remove equipment from service, select the Remove Equipment From Service checkbox. Equipment is removed from service either when the equipment is being retired from service or if new forms are being submitted as a replacement due to a change in configuration.

To assist in completing the NX-9A form, a completed sample NX-9A form is attached (Example 1).

# Rating Data Instructions

All ratings for equipment shall be provided via the Limit Exchange Portal (LEP). Requirements for ratings data provided in LEP are in the ISO New England Operating Procedure No.16, Transmission System Data document section IV. LEP Data Submittal Requirements.

Certain characteristics of equipment ratings must be indicated on the NX-9 form to allow for accurate equipment modeling in LEP. Required characteristic data includes:

- Nominal Ratings

  - For new equipment, the initial nominal ratings shall be provided on the NX-9 form. Any future revisions to these nominal ratings shall be provided only in LEP.

  - Nominal ratings shall be the lowest of the real-time, forecast or seasonal ratings for a network segment that provides for reliable operation of the New England Transmission System.

  - Initial nominal ratings data shall be provided in MVA (rounded down to the nearest whole number) and must meet nesting requirements: Normal <= LTE <= STE <= DAL

  - Nominal ratings are only enterable on the NX-9 form until the form is effective and approved.

- Bi-directional checkbox

  - Selected to indicate ratings are dependent on flow direction.

- Conditional checkbox

  - Selected to indicate conditional rating sets will be provided for breaker(s) in/out or companion cable(s) in/out.

- Conditional Rating Set

  - Add a conditional rating set record with text that identifies the condition the rating applies to.

  - For breaker in/out – each conditional rating set represents a switching device that directly affects the status of the line.

    - Example:

      - STATION1 Line Disconnect A

      - STATION1 Line Terminal Breaker B

      - STATION1 Line Terminal Breaker C

      - STATION2 Line Disconnect D

      - STATION2 Line Terminal Breaker E

      - STATION2 Line Terminal Breaker F

  - A completed sample NX-9A form showing conditional rating sets for breaker in/out conditions is shown in Example 2 of this document.

  - For cable in/out – each condition rating set represents the cable or the combination of cables that are in or out of service

    - Example:

      - LINE1 with LINE2 In AND LINE3 In

      - LINE1 with LINE2 In AND LINE3 Out

      - LINE1 with LINE2 Out AND LINE3 In

      - LINE1 with LINE2 Out AND LINE3 Out

  - A completed sample NX-9A form showing conditional ratings sets for cable(s) in/out conditions is shown in Example 3 of ISO New England Operating Procedure No.16, Appendix A.

- Ratings provided via telemetry checkbox

  - Select for equipment with ratings being determined more frequently than an hourly basis that will be provided via SCADA telemetry as defined by ISO New England Operating Procedure No.18.

# Characteristic and Operational Data Instructions

Provide positive sequence impedance data in percent on a 100 MVA base. Impedance on new or revised NX-9A forms shall be calculated and provided out to at least the 3rd decimal place.

R = resistance

X = reactance

B = susceptance

# Explanation Of Data Changes

Any time an NX-9A form is modified or created, a brief description of the reason(s) for the entry shall be provided in the Revision Comments field. It will provide a written record of the change and clearly identify the equipment changes made in the field and/or other reasons that necessitated the update of the NX-9A form. For example: ABC line was re-conductored in January, 2011.

This data is utilized by ISO in the NX-9A form review and approval process.

# Equipment Notes

The Equipment Notes field is used to provide explanations of data or other pertinent or operational information. For example: Border point is switch 123.

Fields are provided for both ISO and MP/TO notes. An additional private field is available to the MP or TO for internal notes that can be edited and viewed only by the MP or TO owning the record.

Equipment notes are carried forward when an NX-9A form is updated. MPs and TOs should review and modify or delete any MP or TO note that is no longer pertinent. ISO is responsible for maintaining ISO notes.

## Example 1, NX-9A Transmission Line

## Example 2, NX-9A Transmission Line, Breaker in/out Conditional Ratings

## Example 3, NX-9A Transmission Line, Companion Cable in/out Conditional Ratings

# OP-16 Appendix A Revision History

Document History (This Document History documents action taken on the equivalent NEPOOL Procedure prior to the RTO Operations Date as well revisions made to the ISO New England Procedure subsequent to the RTO Operations Date.)

| Rev. No. | Date | Reason |
| --- | --- | --- |
| - - | 10/26/23 | For previous revision history, refer to Rev 10 available through Ask ISO. |
| Rev 11 | 10/26/23 | Periodic review performed by procedure owner; Add a clarifying statement that series reactive devices are reported on the NX-9H form; Add footnote to define “relay loadability limits” as used in this Appendix. |
| Rev 11.1 | 10/23/25 | Biennial review by procedure owner requiring no changes; Made administrative changes required to publish the Minor Revision. |
| Rev 12 | 10/21/26 | Biennial review by procedure owner; Revise language on ratings requirements in NX App, describe new fields for ratings characteristics on NX forms; Replaced example NX form images with redesigned NX forms; Added new example NX forms showing submittal for conditional ratings due to breaker statuses and companion cable statuses. |

Bulk Electric System (BES) is defined in Glossary of Terms Used in NERC Reliability Standards.

New England Transmission System is defined in the ISO Transmission, Markets, and Services Tariff, Section I.2.2.

Generally, under Section I of Operating Procedure No. 16, data shall be provided by Transmission Owners (TOs) and Market Participants, i.e. Market Participants who own the equipment or Lead Market Participants for Generator Assets (collectively MPs).