This version of OP-16 and Appendices A, B, C, D, E, G, H, and I were approved at the May 21, 2026, Reliability Committee meeting and will become effective on October 21, 2026, to coincide with deployment of the redesigned NX Application as part of FERC Order No. 881.

Appendix B - Explanation of Terms and Instructions

for Data Preparation of NX-9B

ISO New England Transmission Equipment Rating, Characteristic and Operational Data

Transformer - FIXED/GSU/TCUL

Effective Date: October 21, 2026

Review By Date: October 21, 2028

Table of Contents

I.	Equipment Requirements	2

II.	General Data Instructions	3

III.	Rating Data Instructions	4

IV.	Characteristic and Operational Data Instructions	5

V.	Explanation Of Data Changes	9

VI.	Equipment Notes	9

Example 1, NX-9B Fixed Tap Transformer	11

Example 1 (continued), NX-9B Fixed Tap Transformer	12

Example 1 (continued), Manufacturer’s Nameplate	13

Example 2, NX-9B Generator Step-Up (GSU) Transformer	14

Example 2 (continued), NX-9B Generator Step-Up (GSU) Transformer	15

Example 2 (continued), Manufacturer’s Nameplate	16

Example 3A, NX-9B TCUL 3-Winding Transformer With Tertiary Loaded	17

Example 3A (continued), NX-9B TCUL 3-Winding Transformer With Tertiary Loaded	18

Example 3B, NX-9B TCUL 2-Winding Transformer With Tertiary Not Loaded	19

Example 3B (continued), NX-9B TCUL 2-Winding Transformer With Tertiary Not Loaded	20

Example 3A+B (continued), Manufacturer’s Nameplate	21

VII.	OP-16 Appendix B Revision History	22

# Equipment Requirements

Data for all transformers designated as part of the Bulk Electric System (BES) or with at least one winding connecting to the New England Transmission System at a voltage of 69 kV or greater shall be provided by the Transmission Owners and Market Participants who own the equipment.

- Data for all generator step-up transformers (GSUs) attached to generators 1 MW or greater that participate in the Real-Time Energy Market, including generators connecting via a line of any voltage level that is dedicated solely to the generation interconnection (i.e., via an express feeder), will be evaluated for impact to the ISO EMS Network Model. Based on this evaluation, NX-9B data forms may be required. When required, the NX-9B data forms shall be provided by the Lead MP for the Generator Assets.

- NX-9B data forms are not required for GSUs that connect a generator to the transmission system via a line(s) that also serves customer load.

- NX-9B data forms are not required for GSUs associated solely with Settlement Only Generators.

NX-9B data forms for transformers or individual wind turbine or solar GSUs connected at voltages that are less than 69 kV may be required when ISO determines that the data is necessary for reliable operation of the New England Transmission System. When required by ISO, the TO or MP shall submit the data within thirty (30) calendar days of ISO’s notification.

A separate NX-9B form shall be provided for each transformer. All data items shall be completed for each winding unless these instructions specifically indicate otherwise.

A copy of the manufacturer’s nameplate, either by document (.pdf format) or digital photograph (.tif or .jpg formats), shall be included as a file attachment to the NX-9B form for new or replaced equipment.

A copy of the manufacturer’s test report document (in .pdf format) shall be included as a file attachment to the NX-9B form for all new or replaced equipment and upon revision of existing NX-9B forms for transformers whose low voltage connection is 69 kV or greater.

# General Data Instructions

The NX-9B form provides for entry of both ISO and MP/TO data. ISO fields cannot be modified by the MP or TO. The MP or TO is responsible for providing data for all non-ISO fields via the NX Application.

The circuit number shall initially be entered by the MP or TO for new equipment and thereafter maintained by ISO.

Select the terminals that reflect the connection points of the equipment. Terminals are created and maintained by ISO. The user should contact the ISO NX-9 Administrator (nx9admin@iso-ne.com) if terminal additions or changes are needed.

To remove equipment from service, select the Remove Equipment From Service checkbox. Equipment is removed from service either when the equipment is retiring from service or if new forms are being submitted as a replacement due to a change in configuration.

All voltage data item responses are to be in kV unless otherwise indicated in these instructions.

To assist in completing the NX-9B form, sample manufacturer's nameplate data and completed NX-9B forms utilizing that data are attached.

Example 1:  Fixed Tap Transformer

Example 2:  Generator Step-Up (GSU) Transformer

Example 3a and 3b:  Tap Change under Load (TCUL) Three Winding Transformer (developed using the same nameplate data)

3a -	TCUL Three Winding Model:  Transformer with tertiary loaded.

Any 3-winding transformer whose tertiary winding connects to a generator, a transmission bus, a sub-transmission bus, a distribution bus or a capacitor/reactor bank should be modeled consistent with Example 3a. This example assumes the tertiary is connected to a capacitor bank.

3b -	TCUL Two Winding Model:  Transformer with tertiary not loaded.

Any 3-winding transformer whose tertiary winding is not loaded should be modeled consistent with Example 3b. If the total station service load served by one or more tertiary windings is less than 1 MW, then the transformer shall be modeled consistent with Example 3b.

If the total station service load served by one or more tertiary windings is greater than 1 MW, then the MP or TO shall confirm with ISO whether the transformer should be modeled consistent with Example 3a or 3b.

All tap position item responses shall indicate tap positions using numbers (1, 2, 3, 4, etc.) as opposed to letters (a, b, c, d, etc.). See examples 3a and 3b where tap positions designated by letter on the nameplate sheet have been designated by number on the sample NX-9B forms.

# Rating Data Instructions

All ratings for equipment shall be provided via the Limit Exchange Portal (LEP). Requirements for ratings data provided in LEP are in ISO New England Operating Procedure No.16, Transmission System Data document Section IV. LEP Data Submittal Requirements.

Certain characteristics of equipment ratings must be indicated on the NX-9 form to allow for accurate equipment modeling in LEP. Required characteristic data includes:

- Nominal Ratings

  - For new equipment, the initial nominal ratings shall be provided on the NX-9B form. Any future revisions to these nominal ratings shall be provided only in LEP.

  - Nominal ratings shall be the lowest of the real-time, forecast or seasonal ratings for a network segment that provides for reliable operation of the New England Transmission System.

  - Initial nominal ratings data shall be provided in MVA (rounded down to the nearest whole number) and must meet nesting requirements: Normal <= LTE <= STE <= DAL

  - Nominal ratings are only enterable on the NX-9B form until the form is effective and approved.

- Bi-directional checkbox

  - Selected to indicate ratings are dependent on flow direction.

- Conditional checkbox

  - Selected to indicate conditional rating sets will be provided for breaker(s) in/out.

- Conditional Rating Set

  - Add a conditional rating set record with text that identifies the condition the rating applies to.

  - For breaker in/out – each conditional rating set represents a switching device that directly affects the status of the transformer.

    - Example:

      - STATION Transformer Disconnect A

      - STATION Transformer Terminal Breaker B

      - STATION Transformer Terminal Breaker C

  - A completed sample NX-9A form showing conditional rating sets for breaker in/out conditions is shown in Example 2 of ISO New England Operating Procedure No.16, Appendix A.

- Ratings provided via telemetry checkbox

  - Select for equipment with ratings being determined more frequently than an hourly basis that will be provided via SCADA telemetry as defined by ISO New England Operating Procedure No.18.

# Characteristic and Operational Data Instructions

Complete the following fields as instructed below:

Nameplate kV – Provide the transformer voltage rating for utilized connections as listed on the nameplate document.

Impedance Data – Provide the positive sequence resistance (R) and reactance (X) calculated at the kV of the no load tap position in use for the fixed tap, and the Nameplate kV on the tap change side, in percent on a 100 MVA base. Do not adjust values to nominal system voltage. Impedance on new or revised NX-9B forms shall be calculated and provided out to at least the 3rd decimal place.

- For transformers with different fixed normal tap settings at Heavy and Light Load, provide the impedance calculated at the Heavy Load fixed tap setting.

- For transformers whose test report does not provide impedance at each tap, provide the impedance at the closest tap for which impedance is provided on all new or revised NX-9B forms. Provide a statement in the Equipment Notes field of the NX-9B form indicating the tap position at which the impedance is calculated.

Impedance data for three (3) winding transformers being modeled consistent with Section I Example 3a should be submitted using a wye configuration. Refer to diagram below.

345

1

115

69

2

3

*

1 = 345/

*

R

X

2 = 115/

*

3 =  69/

*

kV

Impedance data for three (3) winding transformers being modeled consistent with Section I Example 3b should be submitted in two (2) winding format.

Transformer Type – Enter the type of the transformer based upon the descriptions below:

- GSU – Generator Step-Up transformer.

- FIXED – Transformer without a load tap changer (LTC). Tap changes for these transformers typically require the transformer be out of service.

- TCUL-Non Auto – Transformer has an LTC but it is disabled.

- TCUL-Auto – Transformer has an enabled LTC.

Normal Operating Mode – For a TCUL-Auto type transformer, enter the normal operating mode based upon the descriptions below. The normal operating mode selected should reflect the operational state that the transformer is expected to be in the majority of the time.

If the operational mode is dependent upon local generation, load level or other system condition, provide this information in the Equipment Notes field of the 
NX-9B form (example: transformer is operated in automatic mode when generator XYZ is offline or when load level is above xx mw). The Normal Operating Mode field shall still reflect the operational state that the transformer is expected to be in the majority of the time.

- Manual-Local – LTC is operated locally at the substation.

- Manual-Remote –Tap changes are made using the SCADA system and are manually initiated by an LCC System Operator or a TO control room operator remotely.

- Auto – Transformer has enabled controls for automatic operation that allow the equipment to respond to a contingency, typically within 2 minutes, without manual intervention. Tap changes for normal operation occur without LCC System Operator or TO control room operator intervention.

Tap Switching Time Delay – For a TCUL-Auto type transformer with the Normal Operating Mode field set to Auto, enter the tap switching time delay in seconds.

Voltage Schedules – Voltage schedule data is required for all TCUL-Auto transformers with Auto and Manual-Remote control types and is optional for transformers with the Normal Operating Mode field set to Manual-Local. Voltage schedule data is not accepted for GSU, Fixed and TCUL Non-Auto transformers.

- The Controlled Winding and Controlling/LTC Side Winding flags shall be set when entering voltage schedule data.

- Typically a transformer operates to the same schedule in both on peak and off peak hours so the prevalent schedule shall be entered as both on and off peak in the voltage schedule table. If a transformer operates to a different schedule during on-peak and off-peak hours, the different schedules shall be entered in the voltage schedule table and a brief explanation shall be provided in the Equipment Notes field describing how the voltage schedule is modified in the field.

- A transformer with the technology to use SCADA to modify the programmed target voltage shall enter the single most prevalent scheduled voltage and minimum/maximum voltage range for both on and off peak and shall provide all other minimum, scheduled and maximum settings available in either the Equipment Notes field or as a file attachment (referenced in the Equipment Notes field).

TCUL-Auto transformer with the Normal Operating Mode field set to Auto (voltage schedule data is required):

- Schedule data entered in the voltage schedule table shall equal the field programmed target voltage and the minimum and maximum voltages shall equal the control bandwidth settings from the field.

TCUL-Auto transformer with the Normal Operating Mode field set to Manual-Remote (voltage schedule data is required):

- The voltage schedule data entered shall equal the most prevalent target voltage and range used by the operators.

- If there is no typical voltage schedule or range used by the operators:

- Enter a scheduled voltage that matches the overall area voltage profile and/or any nearby regulating devices such as generators, STATCOMs or synchronous condensers.

- Enter a generic 100% and 105% of nominal system voltage for the minimum and maximum voltages.

TCUL-Auto transformer with the Normal Operating Mode field set to Manual-Local (voltage schedule data is optional):

- If the optional voltage schedule data is provided, it shall equal the most prevalent target voltage and range used by the operators.

- If there is no typical voltage schedule or range used by the operators:

- Enter a scheduled voltage that matches the overall area voltage profile and/or any nearby regulating devices such as generators, static synchronous compensators (STATCOMs) or synchronous condensers.

- Enter a generic 100% and 105% of nominal system voltage for the minimum and maximum voltages.

Heavy/Light Load Normal Tap - This is required for all windings with taps. Enter zero (0) for windings without taps.

- For the purposes of this document, heavy load shall mean the summer months of June through August and light load shall mean the remaining calendar months of January through May and September through December.

- For no load windings with fixed tap positions - Enter the seasonal no load tap position (position number) as the normal tap number for each load period.

- For other windings with fixed tap positions - Enter the fixed tap position (position number) as the normal tap number for each load period.

- For LTC windings on TCUL-Auto transformers (the Normal Operating Mode field is set to Manual-Local, Manual-Remote or Auto):

- Enter the typical heavy load tap position as the normal tap number for both load periods.

- If no typical heavy load tap position exists, enter the tap number corresponding with the nameplate voltage of that winding as the normal tap number for both load periods.

Step Size (per unit) – Enter the step size for each winding (per unit). This data can usually be taken from the manufacturer’s nameplate information and should be calculated as follows. Enter zero (0) for windings without taps.

Step Size = (maximum voltage - minimum voltage)

(nameplate voltage)(# of taps - 1)

Nameplate Tap Number – Enter the tap number for each winding at which nameplate voltage is achieved. Enter zero (0) for windings without taps.

Minimum Tap No. – Enter the tap number for each winding at which minimum kV is achieved. Enter zero (0) for windings without taps.

Minimum kV – Indicates the voltage of the windings when at minimum tap position. Value is calculated based on nameplate voltage and associated tap number, minimum tap number and step size.

Maximum Tap No. – Enter the tap number for each winding at which maximum voltage is achieved. Enter zero (0) for windings without taps.

Maximum kV – Indicates the voltage of the windings when at maximum tap position. Value is calculated based on nameplate voltage and associated tap number, maximum tap number and step size.

Controlled and Controlling/LTC Side Winding (TCUL-Auto transformers only):

- These fields are required for all TCUL-Auto transformers with the Normal Operating Mode field set to Auto or Manual-Remote.

- These fields are required for transformers with the Normal Operating Mode field set to Manual-Local when the optional voltage schedule has been entered.

- These fields are not enterable for GSU, Fixed and TCUL Non-Auto transformers.

- Select with a (√) the Controlling/LTC Side Winding (the winding on which the tap changer is located).

- Select with a (√) the Controlled Winding (the winding for which desired voltages/voltage schedules are established).

# Explanation Of Data Changes

Any time an NX-9B form is modified or created, a brief description of the reason(s) for the entry shall be provided in the Revision Comments field. It will provide a written record of the change and clearly identify the equipment changes made in the field and/or other reasons that necessitated the update of the NX-9B form. For example: Tap information corrected to match nameplate.

This data is utilized by ISO in the NX-9B form review and approval process.

# Equipment Notes

The Equipment Notes field is used to provide explanations of data or other pertinent or operational information. For example:  This transformer is operated in automatic mode when generator XYZ is offline or when load level is above xx MW.

For transformers that are part of a dynamic reactive device control scheme, a brief description of the control scheme is required to provide clarity regarding the manner in which the transformer is operated.

Fields are provided for both ISO and MP/TO notes. An additional private field is available to the MP or TO for internal notes that can be edited and viewed only by the MP or TO owning the record.

Equipment notes are carried forward when an NX-9B form is updated. MPs and TOs should review and modify or delete any MP or TO note that is no longer pertinent. ISO is responsible for maintaining ISO notes.

## Example 1, NX-9B Fixed Tap Transformer

## Example 1 (continued), NX-9B Fixed Tap Transformer

## Example 1 (continued), Manufacturer’s Nameplate

## Example 2, NX-9B Generator Step-Up (GSU) Transformer

## Example 2 (continued), NX-9B Generator Step-Up (GSU) Transformer

## Example 2 (continued), Manufacturer’s Nameplate

## Example 3A, NX-9B TCUL 3-Winding Transformer With Tertiary Loaded

## Example 3A (continued), NX-9B TCUL 3-Winding Transformer With Tertiary Loaded

## Example 3B, NX-9B TCUL 2-Winding Transformer With Tertiary Not Loaded

## Example 3B (continued), NX-9B TCUL 2-Winding Transformer With Tertiary Not Loaded

## Example 3A+B (continued), Manufacturer’s Nameplate

# OP-16 Appendix B Revision History

Document History (This Document History documents action taken on the equivalent NEPOOL Procedure prior to the RTO Operations Date as well revisions made to the ISO New England Procedure subsequent to the RTO Operations Date.)

| Rev. No. | Date | Reason |
| --- | --- | --- |
| - - | 10/26/23 | For previous revision history, refer to Rev 10 available through Ask ISO. |
| Rev 11 | 10/26/23 | Periodic review completed by procedure owner; Add footnote to define “relay loadability limits” as used in this Appendix; Update Normal Operating Mode field labels from Manual + SCADA to Manual-Local + Manual-Remote as previously requested by the Reliability Committee; Add requirement for control scheme information to Equipment Notes for transformers connecting dynamic reactive devices. |
| Rev 11.1 | 10/23/25 | Biennial review by procedure owner requiring no changes; Made administrative changes required to publish the Minor Revision. |
| Rev 12 | 10/21/26 | Biennial review by procedure owner; Revise language on ratings requirements in NX App, describe new fields for ratings characteristics on NX forms; Replaced example NX form images with redesigned NX forms. |

Bulk Electric System (BES) is defined in the Glossary of Terms Used in NERC Reliability Standards.

New England Transmission System is defined in the ISO Transmission, Markets, and Services Tariff, Section I.2.2.

Generally, under Section I of Operating Procedure No. 16, data shall be provided by Transmission Owners (TOs) and Market Participants, i.e. Market Participants who own the equipment or Lead Market Participants for Generator Assets (collectively MPs).

The term TCUL-Auto as used in this appendix, represents a transformer with an enabled LTC that may or may not be an autotransformer. An autotransformer has only a single voltage winding which is common to both primary and secondary.

System Operator is defined in the Glossary of Terms Used in NERC Reliability Standards.

On-Peak is from 0700-2300 on weekdays that are not NERC holidays.

Off-Peak is from 2300-0700 on weekdays, all weekends and NERC