This version of OP-16 and Appendices A, B, C, D, E, G, H, and I were approved at the May 21, 2026, Reliability Committee meeting and will become effective on October 21, 2026, to coincide with deployment of the redesigned NX Application as part of FERC Order No. 881.

Appendix G - Explanation of Terms and Instructions

for Data Preparation of NX-9G

ISO New England Transmission Equipment Rating, Characteristic, and Operational Data

Variable Reactor

# Effective Date: October 21, 2026

# Review By Date: October 21, 2028

Table of Contents

I.	Equipment Requirements	2

II.	General Data Instructions	2

III.	Rating Data Instructions	3

IV.	Characteristic And Operational Data Instructions	4

V.	Explanation Of Data Changes	5

VI.	Equipment Notes	5

Example 1, NX-9G Variable Reactor	6

Example 1 (Continued), NX-9G Variable Reactor	7

VII.	OP-16 Appendix G Revision History	8

# Equipment Requirements

Data for all variable reactors designated as part of the Bulk Electric System (BES) or connecting to the New England Transmission System at a voltage of 69 kV or greater shall be provided by the Transmission Owners and Market Participants who own the equipment.

Data for variable reactors connected at voltages that are less than 69 kV may be required when ISO determines that the data is necessary for reliable operation of the New England Transmission System. When required by ISO, the TO or MP shall submit the data within thirty (30) calendar days of ISO’s notification.

A copy of the manufacturer’s nameplate, either by document (.pdf format) or digital photograph (.tif or .jpg formats), shall be included as a file attachment to NX-9G forms for new or replaced equipment.

A copy of the manufacturer’s test report document (in .pdf format) shall be included as a file attachment to NX-9G forms for new or replaced equipment.

# General Data Instructions

The NX-9G form provides for entry of both ISO and MP/TO data. ISO fields cannot be modified by the MP or TO. The MP or TO is responsible for providing data for all non-ISO fields via the NX Application.

The circuit number shall initially be entered by the MP or TO for new equipment and thereafter maintained by ISO.

Select the terminals that reflect the connection points of the equipment. Terminals are created and maintained by ISO. The user should contact the ISO NX-9 Administrator (nx9admin@iso-ne.com) if terminal additions or changes are needed.

To remove equipment from service, select the Remove Equipment From Service checkbox. Equipment is removed from service either when the equipment is retiring from service or if new forms are being submitted as a replacement due to a change in configuration.

All voltage data item responses are to be in kV unless otherwise indicated in these instructions.

To assist in completing the NX-9G form, sample manufacturer's nameplate data and a completed NX-9G form utilizing that data are attached (Example 1).

All tap position item responses shall indicate tap positions using numbers (1, 2, 3, 4, etc.) as opposed to letters (a, b, c, d, etc.).

# Rating Data Instructions

All ratings for equipment shall be provided via the Limit Exchange Portal (LEP). Requirements for ratings data provided in LEP are in ISO New England Operating Procedure No.16, Transmission System Data document Section IV. LEP Data Submittal Requirements.

Certain characteristics of equipment ratings must be indicated on the NX-9 form to allow for accurate equipment modeling in LEP. Required characteristic data includes:

- Nominal Ratings

  - For new equipment, the initial nominal ratings shall be provided on the NX-9 form. Any future revisions to these nominal ratings shall be provided only in LEP.

  - Nominal ratings shall be the lowest of the real-time, forecast or seasonal ratings for a network segment that provides for reliable operation of the New England Transmission System.

  - Initial nominal ratings data shall be provided in MVA (rounded down to the nearest whole number) and must meet nesting requirements: Normal <= LTE <= STE <= DAL

  - Nominal ratings are only enterable on the NX-9 form until the form is effective and approved.

- Bi-directional checkbox

  - Selected to indicate ratings are dependent on flow direction.

- Conditional checkbox

  - Selected to indicate conditional rating sets will be provided.

- Conditional Rating Set

  - Add a conditional rating set record with text that identifies the condition the rating applies to.

- Ratings provided via telemetry checkbox

  - Select for equipment with ratings being determined more frequently than an hourly basis that will be provided via SCADA telemetry as defined by ISO New England Operating Procedure No.18.

# Characteristic And Operational Data Instructions

Complete the following fields as instructed below:

Control Type – Indicate the normal control mode based upon the descriptions below. The Control Type selected should reflect the operational state that the device is expected to be in the majority of the time.

- Manual-Local – Reactor is operated locally at the substation.

- Manual-Remote – Tap changes are typically made using the SCADA system and initiated by an LCC System Operator or a TO control room operator.

- Auto – Reactor has controls which are set up for complete automatic operation. Tap changes typically occur without LCC System Operator or TO control room operator intervention.

Nominal Capability

- Fixed – Provide the fixed capability (MVAR) calculated at nominal system voltage and 60 Hertz.

- Variable – This value is calculated by the NX Application as Maximum – Fixed

- Maximum – Provide the maximum capability (MVAR) calculated at nominal system voltage and 60 Hertz.

Impedance Data Table - For each position listed, Minimum, Midpoint, Nameplate and Maximum, provide the following values:

- Tap # @ MVAR Consumption – Indicate the tap number at the listed position.

- MVAR Consumption – Indicate the MVAR consumption at the listed position.

- Impedance X – Provide the positive sequence reactance (X) calculated in percent on a 100 MVA base at the listed position. Do not adjust values to nominal system voltage. Impedance on NX-9G forms shall be calculated and provided out to at least the 3rd decimal place.

# Explanation Of Data Changes

Any time an NX-9G form is modified or created, a brief description of the reason(s) for the entry shall be provided in the Revision Comments field. It will provide a written record of the change and clearly identify the equipment changes made in the field and/or other reasons that necessitated the update of the NX-9G form.

This data is utilized by ISO in the NX-9G form review and approval process.

# Equipment Notes

The Equipment Notes field is used to provide explanations of data or other pertinent or operational information. For example:  Unit is connected to the bus between breakers CB1 and CB2.

Fields are provided for both ISO and MP/TO notes. An additional private field is available to the MP or TO for internal notes that can be edited and viewed only by the MP or TO owning the record.

Equipment notes are carried forward when an NX-9G form is updated. MPs and TOs should review and modify or delete any MP or TO note that is no longer pertinent. ISO is responsible for maintaining ISO notes.

## Example 1, NX-9G Variable Reactor

## Example 1 (Continued), NX-9G Variable Reactor

# OP-16 Appendix G Revision History

Document History (This Document History documents action taken on the equivalent NEPOOL Procedure prior to the RTO Operations Date as well revisions made to the ISO New England Procedure subsequent to the RTO Operations Date.)

| Rev. No. | Date | Reason |
| --- | --- | --- |
| Rev 0 | 05/04/12 | New appendix defines data required for transmission equipment installed in New England and not covered by Appendices A-D |
| Rev 1 | 12/09/13 | Biennial review by procedure owner. General language changes to accommodate new web-based NX Application for NX-9/NX-12D data. Globally change the term “Participant’ to “Market Participant or Transmission Owner” Define Market Participant as MP and use throughout document. Define Transmission Owner as TO as use throughout document Sections I+II: renamed and reorganized. Some instructions moved from Section I to Section II Section III: Specify that temperature provided in the rating set should be the temp used to obtain the Normal rating. Section V: renamed to match new application and clarified the desired information and purpose of the field. Changed all references to use “Equipment Notes” Replaced example with report from new application. |
| Rev 2 | 11/06/15 | Biennial review by procedure owner; With this set of revisions to OP16 and its appendices, separate NX-9 form types of NX-9G and NX-9H have been created to represent Variable Reactors and Series Devices which were originally included in Appendix G for Other Equipment; As a result, Appendix G has been re-written and re-purposed to reflect the new NX-9G form and Variable Reactor equipment data requirements; A new Appendix H has been created for the new NX-9H form and Series Device equipment data requirements; A new Appendix I has been created for Other Equipment which covers the equipment requirements for the remaining equipment types not represented on a specific NX-9 form; |
| Rev 3 | 08/05/16 | Globally all footers, added the required corporate document identity; Update equipment requirements to include BES equipment; |
| Rev 4 | 11/03/17 | Biennial review by procedure owner; Globally, made editorial changes to be consistent with current practices and management expectations (e.g., grammar changes from “must” to “shall”’ and “which” to “that” as appropriate; and remove capitalization from non-defined terms; Clarify circumstance for ISO to require reporting of equipment connected at voltages less than 69 kV is because it is needed for reliable operation of the New England Transmission System; |
| Rev 4.1 | 06/06/19 | Annual review by procedure owner requiring no changes; Made administrative changes required to publish the Minor Revision |
| Rev 4.2 | 01/25/21 | Annual review by procedure owner requiring no changes; Made administrative changes required to publish the Minor Revision; |
| Rev 5 | 08/22/22 | Biennial review by procedure owner; Clarify ratings requirements to include relay loadability limits and other equipment deemed necessary by Good Utility Practice. |
| Rev 6 | 10/26/23 | Periodic review by performed procedure owner; Add footnote to define “relay loadability limits” as used in this Appendix; Update Control Type field labels from Manual + SCADA to Manual-Local + Manual-Remote as previously requested by the Reliability Committee. |
| Rev 6.1 | 10/23/25 | Biennial review by procedure owner requiring no changes; Made administrative changes required to publish the Minor Revision. |
| Rev 7 | 10/21/26 | Biennial review by procedure owner; Revise language on ratings requirements in NX App, describe new fields for ratings characteristics on NX forms; Replaced example NX form images with redesigned NX forms; |

Bulk Electric System (BES) is defined in the Glossary of Terms Used in NERC Reliability Standards.

New England Transmission System is defined in the ISO Transmission, Markets, and Services Tariff, Section I.2.2.

Generally, under Section I of Operating Procedure No. 16, data shall be provided by Transmission Owners (TOs) and Market Participants, i.e. Market Participants who own the equipment or Lead Market Participants for Generator Assets (collectively MPs).

System Operator is defined in the Glossary of Terms Used in NERC Reliability Standards.