This version of OP-16 and Appendices A, B, C, D, E, G, H, and I were approved at the May 21, 2026, Reliability Committee meeting and will become effective on October 21, 2026, to coincide with deployment of the redesigned NX Application as part of FERC Order No. 881.

ISO New England Operating Procedure No.16
Transmission System Data

Effective Date: October 21, 2026

Review By Date: October 21, 2028

Table of Contents

I.	Overview and Purpose	3

II.	NX-9 Data Submittal Schedule	4

III.	Entry and Maintenance of NX-9 Form Effective Date Fields	8

IV.	LEP Data Submittal Requirements	9

V.	One-Line Schematic Diagram Requirements	12

VI.	Determination and Submittal of NX-9 Data Representing the Physical Characteristics, Ratings, and Operational Data of Transmission System Equipment (NX-9 Forms)	16

VII.	Annual NX-9 Data Certification	17

VIII.	MOD-032 Dynamics And Short Circuit Data for Transmission System Equipment	17

IX.	OP-16 Revision History	17

X.	APPENDICES	19

References:

|  | ISO New England Operating Procedure No. 3 - Transmission Outage Scheduling (OP-3) |
| --- | --- |
|  | ISO New England Operating Procedure No. 14, Appendix B - Generator Reactive Data Explanation of Terms and Instructions for Data Preparation for ISO Form NX-12D (OP-14) |
|  | ISO New England Planning Procedure No. 7 - Procedures for Determining and Implementing Transmission Facility Ratings in New England (PP7) |
|  | NERC Reliability Standard FAC-008 Facility Ratings |
|  | NERC Reliability Standard IRO-010 Reliability Coordinator Data Specification and Collection |
|  | NERC Reliability Standard MOD-032 Data for Power System Modeling and Analysis |
|  | NERC Reliability Standard TOP-003 - Operational Reliability Data |
|  | Glossary of Terms Used in NERC Reliability Standards |
|  | ISO New England Compliance Bulletin - MOD-032 and ISO New England’s Model Data Requirements and Reporting Procedures |
|  | ISO New England Inc. Transmission, Markets, and Services Tariff, Section I.2.2 Definitions |
|  | ISO New England Transmission, Markets, and Services Tariff, Section I.3.9 Review of Market Participant’s Proposed Plans |
|  | ISO New England Operating Procedure No. 18 - Metering and Telemetering Criteria (OP-18) |
|  | ISO New England Inc. Transmission, Markets, and Services Tariff, Attachment Q |
|  | FERC Order No. 881/881-A Managing Transmission Line Ratings |

# Overview and Purpose

|  | Data that defines and represents the physical characteristics, ratings, and operational data of all New England Transmission System equipment, is required to develop accurate system models and maintain the day-to-day reliable operation of the New England bulk power generation and transmission system. The timely submittal of accurate and complete data is critical to the creation of the models used in Real-Time reliability operations, market operations, operations planning and to the applications that operate on those models. |
| --- | --- |
|  | It is the responsibility of Transmission Owners (TOs) and Market Participants, i.e., Market Participants who own the equipment or Lead Market Participants (LMPs) for Generator Assets (collectively MPs) to determine and submit the required data for new, reconductored, and reconfigured facilities for all their transmission equipment in accordance with the submittal schedules in Sections II and IV of this ISO New England Operating Procedure No. 16 - Transmission System Data (OP-16). |

|  | ISO will maintain the NX Application and the Limit Exchange Portal (LEP) applications The NX application hosts the physical characteristics and operational data for all existing transmission equipment, as provided by the MPs and TOs on the appropriate NX-9 form (see Section V). ISO is responsible for acquiring the data for that portion of any transmission facility that is beyond the ISO border. All ratings, except initial nominal provided via NX9 form and real time ratings provided via ICCP, shall be submitted via the LEP. The LEP applications host equipment seasonal ratings, nominal ratings, reasonability limits, Ambient Adjusted Ratings (AARs) or AAR exemption status and historical ratings data. |
| --- | --- |
|  | MPs and TOs shall collaborate with ISO in developing or revising rating procedures, establishing ratings for new transmission facilities and modifying ratings of existing transmission facilities consistent with Planning Procedure No. 7 “Procedures for Determining and Implementing Transmission Facility Ratings in New England” (PP7) and Attachment Q of the Open Access Transmission Tariff (OATT). |
|  | ISO will internally implement NX-9 data that is submitted by the MP or TO after such data has been reviewed and approved in accordance with OP-16 and its appendices and ISO has been notified that it is effective. Notification of data approval or implementation will be sent via email to ISO staff and external stakeholders who have requested such notification in the ISO Customer and Asset Management System (CAMS). |
|  | Questions regarding NX-9 data requirements or use of the NX-9 application should be directed to the ISO Participant Support & Solutions. |
|  | Questions regarding MOD-032 Dynamic data, Dynamic Demand data or short circuit data requirements covered by OP-16 and its appendices should be directed to ISO Participant Support & Solutions and should reference NERC Reliability Standard MOD-032 Data for Power System Modeling and Analysis (MOD-032) and the ISO-NE Compliance Bulletin – MOD-032 and ISO New England’s Model Data Requirements and Reporting Procedures. |

# NX-9 Data Submittal Schedule

|  | MPs and TOs shall submit equipment data for new facilities, planned modifications, planned re-evaluation of existing facilities, correction of detected data errors, unplanned equipment changes, impedance changes, and re-submittal of rejected NX-9s, consistent with the schedules defined in this section. For the purposes of OP-16 and its appendices, In-Service Date shall mean the date upon which the MP or TO reasonably expects the equipment will be ready to be energized or carry power. |
| --- | --- |
|  | New facilities: |
|  | For the purposes of OP-16 and its appendices, new facilities shall include new substations, new lines, new transformers, transformer replacements and additions of equipment to existing substations. |
|  | MPs and TOs shall submit required advanced notice NX-9 data to ISO for new facilities, including planned transformer replacements. Equipment must have an approved NX-9 form to be included in the ISO EMS model. Submittals must be completed at the earliest of one hundred twenty (120) calendar days in advance of the new facility’s expected In-Service Date or in accordance with the dates below. - By March 1st for inclusion in the May EMS model release. - By July 1st for inclusion in the September EMS model release. - By November 1st for inclusion in the February EMS model release. This advanced notice data can be based on preliminary, planned or MP/TO specification data and shall be the most accurate data available at the time of submittal. |
|  | NX-9 data for transformer replacements due to failure shall be submitted by MPs and TOs no later than five (5) Business Days after determining the replacement equipment or one hundred twenty (120) calendar days prior to the expected In-Service Date of the replacement, whichever is later. This advanced notice data can be based on preliminary, planned or MP/TO specification data and shall be the most accurate data available at the time of submittal. Replacement equipment shall be determined by MPs and TOs in accordance with Good Utility Practice. |
|  | MPs and TOs shall update advanced notice NX-9 data at least fifteen (15) Business Days prior to the In-Service Date. Transformer data shall be derived from the transformer test report. Data for all other equipment shall either be based on as-built or derived from the specification for construction and shall be the most accurate data available at the time of submittal. |
|  | Submittal of NX-9 data for a project with an accelerated In-Service Date shall be coordinated with the ISO NX-9 Administrator (nx9admin@iso-ne.com). |
|  | Planned modifications to existing facilities: |
|  | Data associated with substation equipment modifications or retirements and changes to existing lines shall be submitted at least fifteen (15) Business Days prior to the expected In-Service Date and shall either be based on as-built or derived from the specification for construction and shall be the most accurate data available at the time of submittal. For planned modifications to existing facilities for the addition or removal of conditional rating sets, a change to the bi-directional flag or addition of telemetry provided ratings, MPs and TOs shall submit advanced notice NX-9 data to ISO in accordance with the timelines for New Facilities defined above. |
|  | Modifications to transfer Lead Market Participant: Notification to ISO New England of a transfer in Lead Market Participant (LMP) for existing equipment is required at least fifteen (15) Business days prior to the effective date of transfer. ISO will create the initial NX-9 form to transfer the LMP and make the change in LEP. The new LMP must review, update if necessary, and submit the NX-9 form at least five (5) Business Days prior to the effective date of transfer. |
|  | As-built data for new and modified facilities: |
|  | As-built data shall be confirmed or submitted no later than three (3) months after the equipment In-Service Date. If as-built data is not available within this timeframe, the MP or TO shall notify the ISO NX-9 Administrator (nx9admin@iso-ne.com). |
|  | Planned re-evaluation of existing facilities: |
|  | A planned re-evaluation, such as due to a methodology change or a change to impedance or rating calculation formula, shall be coordinated with the ISO NX-9 Administrator (nx9admin@iso-ne.com). |
|  | Correction of detected data error: |
|  | Upon discovery of a data error, MPs and TOs shall determine the correct data in accordance with Good Utility Practice. Corrected NX-9 data shall be submitted no later than ten (10) Business Days after establishing corrected data for a detected error. Corrected data shall be provided to the Local Control Center (LCC). |
|  | Unplanned equipment change: |
|  | NX-9 data pertaining to an unplanned equipment repair or replacement that results in a change to equipment impedance shall be submitted as soon as possible and no later than ten (10) Business Days after the repair. Updated data shall be provided to the LCC. |
|  | Temporary characteristics changes: |
|  | Unplanned temporary adjustments to characteristics such as impedance data, including those due to localized emergency situations shall be provided to the ISO-NE Control Room without delay. Planned temporary adjustments shall be reported during the outage application process. |
|  | Temporary changes expected to be in place forty-five (45) calendar days or longer require an NX-9 submittal to be made by the MP or TO in accordance with normal submittal schedules. Temporary changes that are expected to be in place less than forty-five (45) calendar days do not require an NX-9 submittal. |
|  | Re-submittal of rejected NX-9s: |
|  | NX-9 forms submitted by MPs or TOs that are rejected by the ISO NX-9 Administrator will be returned to the MP or TO for correction. For equipment with a scheduled In-Service Date within fifteen (15) Business Days, corrections shall be submitted no later than five (5) Business Days after ISO notification to the MP or TO. For equipment with a scheduled In-Service Date later than fifteen (15) Business Days, corrections shall be submitted no later than ten (10) Business Days after ISO notification to the MP or TO. |
|  | Widespread outage and major system restoration: |
|  | ISO recognizes that during times of widespread outage and major system restoration, it may not be possible to adhere to the above timelines in all situations. However, all affected NX-9 data shall be updated no later than six (6) months after system restoration. |  |

|  | The table below is a quick reference guide to the submittal schedule above: |  |
| --- | --- | --- |

| Change Type: | NX-9 Submittal Required: |
| --- | --- |
| All data shall be the most accurate data available at the time of submittal |  |
| New facilities including planned transformer replacements - initial submittal of preliminary data | By the earlier of the NX-9 data requirement date associated with the EMS model release that will include the new facility or at least one hundred twenty (120) calendar days in advance of the expected In-Service Date |
| Transformer replacements due to failure - initial submittal of preliminary data | No later than five (5) Business Days after determining the replacement equipment or one hundred twenty (120) calendar days in advance of the expected In-Service Date, whichever is later |
| New facilities including all transformer replacements - update to preliminary data (as tested, as-built or based upon specification) | At least fifteen (15) Business Days prior to the In-Service Date |
| Retirements of existing facilities | At least fifteen (15) Business Days prior to the expected retirement date |
| Planned modifications to existing facilities - data is as-built or based upon specification | At least fifteen (15) Business Days prior to the expected In-Service Date |
| Planned modifications to existing facilities for the addition or removal of conditional rating sets, a change to the bi-directional flag, or the addition of telemetry provided ratings | By the earlier of the NX-9 data requirement date associated with the EMS model release that will include the change or one hundred twenty (120) calendar days in advance of the expected effective date |
| Modification to transfer Lead Market Participant | Notification to ISO-NE at least fifteen (15) Business Days prior to the effective date of transfer NX-9 submittal at least five (5) Business Days prior to the effective date of transfer |
| As-built data for new and modified facilities | No later than three (3) months after equipment In-Service Date |
| Planned re-evaluation of existing facilities | Coordinated with the ISO NX-9 Administrator |
| Correction of detected data error | No later than ten (10) Business Days after establishing correct data |
| Unplanned equipment change | No later than ten (10) Business Days after the repair |
| Temporary characteristics changes of less than forty-five (45) calendar days | NX-9 submittal not required |
| Temporary characteristics changes of forty-five (45) calendar days or longer | In accordance with normal submittal schedules |
| Re-submittal of rejected NX-9s with In-Service Date less than or equal to fifteen (15) Business Days of rejection date | No later than five (5) Business Days after rejection notification |
| Re-submittal of rejected NX-9s with In-Service Date later than fifteen (15) Business Days of rejection date | No later than ten (10) Business Days after notification |

# Entry and Maintenance of NX-9 Form Effective Date Fields

|  | MPs and TOs are required to provide and maintain the Requested and Actual Effective Date fields as defined below for all NX-9 data. As changes to project dates arise, the Requested Effective Date field on NX-9 forms shall be updated by the MP or TO in the ISO NX Application. LEP Implementation Date is an ISO maintained field and is not enterable by MPs and TOs. |
| --- | --- |
|  | Requested Effective Date: |
|  | When submitting changes to NX-9 data for existing equipment, the Requested Effective Date field shall reflect the date the MP or TO reasonably expects the data to be effective. |
|  | When submitting NX-9 data for new equipment, the Requested Effective Date field shall reflect the date the MP or TO reasonably expects the equipment will be In-Service. |
|  | When submitting corrections to NX-9 equipment data that are effective immediately, the Requested Effective Date field shall be the date submitted plus one day. |
|  | Actual Effective Date: |
|  | The Actual Effective Date field shall be populated with the date the NX-9 data went into effect in the field. Entry of the actual effective date will trigger a notice to the ISO NX-9 Administrator that the data can be implemented in ISO applications. |
|  | For both modifications to existing equipment and for new equipment, the MP or TO shall populate the NX-9 form’s Actual Effective Date field as soon as possible upon completion of work. |
|  | For corrections to NX-9 equipment data that are effective immediately, the actual effective date shall be the date that the correct data was determined and shall be entered by the MP or TO at the time of form submittal. |

# LEP Data Submittal Requirements

For the purposes of OP-16, the term “network segment” refers to individual pieces of equipment whose ratings are required to determine the ratings of the parent facility.

ISO is responsible for modeling all equipment that is represented on an NX-9 form in LEP. ISO will provide notification to MPs and TOs of LEP changes prior to implementing them in LEP.

Network segment ratings entered in LEP shall be provided in MVA and determined in accordance with PP7 and Attachment Q of the OATT.

Submittal Schedule:

MPs and TOs shall initially submit, and thereafter maintain, seasonal ratings for new equipment in LEP within five (5) Business Days of equipment becoming available in LEP. New equipment becomes available in LEP with ISO New England’s EMS model releases that occur in the months of February, May, and September.  Additionally, MPs and TOs shall submit forecasted hourly AARs at least 72 hours in advance of energization.

MPs and TOs shall enter, and thereafter maintain the following data, for all network segments into LEP.

Reasonability Limits:

MPs and TOs shall provide low and high reasonability limit values for all network segments in LEP. Reasonability limits are used to validate all other rating data provided in LEP.

Low reasonability limit: must be entered for each network segment before ratings can be entered.

- Must be greater than zero (0) and less than the High Reasonability Limit.

- Represents the lowest rating value that LEP will accept for the network segment.

High reasonability limit: must be entered for a network segment before ratings can be entered.

- Must be greater than the low reasonability limit.

- Represents the highest rating value that LEP will accept for the network segment.

Rating Nesting Requirements:

All real-time, forecasted, seasonal, scenario, temporary and nominal ratings must fall between low and high reasonability limits and must also meet the nesting requirements of: Normal <= LTE <= STE <= DAL

Seasonal Ratings:

MPs and TOs shall determine seasonal ratings for all segments in accordance with PP7, Appendix A and the seasonal information below.

If the equipment has conditional rating sets due to element in/out condition(s), seasonal ratings must be provided for each altering condition.

| Season Name | Start Date (mm-dd) | Start Time |
| --- | --- | --- |
| JAN | 01-01 | 00:00:00 |
| FEB | 02-01 | 00:00:00 |
| MAR | 03-01 | 00:00:00 |
| APR | 04-01 | 00:00:00 |
| MAY | 05-01 | 00:00:00 |
| JUN | 06-01 | 00:00:00 |
| JUL | 07-01 | 00:00:00 |
| AUG | 08-01 | 00:00:00 |
| SEP | 09-01 | 00:00:00 |
| OCT | 10-01 | 00:00:00 |
| NOV | 11-01 | 00:00:00 |
| DEC | 12-01 | 00:00:00 |

Scenario Ratings:

MPs and TOs shall determine scenario ratings in accordance with PP7, Appendix A and are used by ISO-NE Transmission Planning and ISO-NE Operations Support Services.

- If the equipment has conditional rating sets due to element in/out condition(s), scenario ratings must be provided for each altering condition.

Temporary ratings:

MPs and TOs shall provide temporary ratings in LEP when a condition arises that requires the use of ratings other than the real-time, forecast or seasonal ratings for a network segment.

Examples of conditions warranting entry of temporary ratings include:

- Equipment de-rate due to an operational issue

- Cable heat exchanger in service

- Change in gallons per minute flow rate for a cable

- an outage impacting topology that impacts ratings such as a companion cable or terminal breaker opened

Planned outage conditions

- MPs and TOs shall provide temporary ratings in LEP at least 72 hours prior to the start of the Outage.

Unplanned outage conditions

- MPs and TOs shall provide temporary ratings in LEP as soon as possible.

- Temporary ratings due to unplanned outages must be communicated to the LCCs and ISO-NE Control Room as soon as reasonably possible.

- MPs and TOs shall enter the following for each temporary rating:

  - Start date and time

  - End date and time

    - If the end date and time is known based on a planned outage, enter the expected end date and time.

    - If the end data and time is not known, enter a projected end date and time. This can be updated.

- Reason for the temporary rating

Nominal Ratings:

Nominal ratings shall be the lowest of the real-time, forecast or seasonal ratings for a network segment that provides for reliable operation of the New England Transmission System.

MPs and TOs shall update nominal ratings in LEP for any rating change that impacts the nominal ratings for the network segment including any physical equipment or rating methodology changes.

AAR Exemption status:

MPs and TOs shall determine if each segment is exempt from the AAR requirements of FERC Order 881, and if so, shall toggle the default status of non-exempt to exempt in LEP and provide a reason for exemption. See Section IV.D, Exceptions and Alternate Ratings within the FERC Order for more information.

If a network segment is marked as exempt, the MPs and TOs shall re-evaluate the AAR exempt status at least every five (5) years. The segment’s re-evaluation date is automatically generated upon being set as exempt or re-approved.

Forecast Ratings:

Entered and required only for network segments that are not marked as exempt from providing AARs.

MPs and TOs shall provide forecasted AAR data for network segments whose AAR exemption setting is “non-exempt”. Forecast AAR data is not entered for network segments whose AAR exemption setting is “exempt”. Based on ISO’s filing, forecasted data shall cover a 72-hour-ahead period, including when a temporary rating is in effect. The ratings provided for each hour shall be based on the expected ambient temperature and expected system conditions (e.g., equipment status based on approved outages).

Real-Time Ratings:

Entered and required only for network segments that are not marked as exempt from providing AARs.

The ratings provide for the current hour that are based on the ambient temperature and actual system conditions, at a minimum.

When submitted the rating will be used for one (1) hour in the ISO-NE software.

Expected to be submitted if current conditions cause the previously submitted forecast rating to be invalid.

# One-Line Schematic Diagram Requirements

|  | ISO will maintain an application housing all one-line schematic diagrams (one-lines) provided by the MPs and TOs. These one-lines are required to be on file for use by ISO and the LCCs. ISO will use these one-lines to define the substation model. MPs and TOs shall provide their one-lines using the one-line form in the ISO web-based application. |
| --- | --- |
|  | MPs and TOs shall provide documentation that identifies equipment changes, additions or removals and/or nomenclature changes on revised one-lines by providing a description of the changes in the one-line form Revision Comments field. |
|  | When uploading a revised one-line, the one-line being replaced shall be terminated. |
|  | Required facility one-lines: |
|  | MPs and TOs shall provide new or revised individual station one-lines of all substations containing equipment designated as part of the Bulk Electric System (BES) or with equipment operating at voltages of 69 kV or greater. |
|  | Lead MPs for Generator Assets shall provide new or revised individual station one-lines of all substations that include generators participating in the Real-Time Energy Market regardless of voltage level. One-lines shall depict all equipment, including equipment nomenclature, up to the point of interconnection. New Generator Assets will initially provide their one-lines through the ISO’s new generator coordination process. Those required to submit their diagrams to the ISO web-based application will be identified during the coordination meetings. |
|  | One-lines for stations or areas operating at voltages that are less than 69 kV may be required when ISO determines that the one-lines are necessary for reliable operation of the New England Transmission System. When required by ISO, the TO or MP shall submit the one-line no later than thirty (30) calendar days after ISO’s notification. |
|  | Required facility one-lines shall include all equipment that affects the flow of system real or reactive power of equipment at voltages of 69 kV or greater or between a generator and its point of interconnection. This includes switching devices, transformers, phase shifters and reactive devices (shunt, variable or dynamic) and the nomenclature for all such devices. |
|  | When it is necessary to provide a system overview one-line for the purpose of satisfying the criteria for individual station one-lines, the system overview one-line shall be considered a required facility one-line and shall adhere to the rules and submittal schedule for required facility one-lines. |
|  | Optional facility one-lines: |
|  | Optionally, MPs and TOs may provide one-lines of substations with equipment operating at voltages that are less than 69 kV and/or overview one-lines of any kV level. |
|  | MPs and TOs are not expected to provide preliminary versions of optional facility one-lines. |
|  | MPs and TOs are not expected to provide relay or metering specific diagrams or topological diagrams. |
|  | Submittal schedule for required facility one-lines: |
|  | Preliminary one-lines for required facilities and equipment: |
|  | MPs and TOs shall submit preliminary individual substation one-lines with final nomenclature to ISO for new facilities or changes to existing facilities. Equipment must have an approved NX one-line form to be included in the ISO EMS model. Submittals must be completed at the earliest of at least one hundred eighty (180) calendar days in advance of the expected In-Service Date or in accordance with the following schedule: |
|  | - By March 1st for inclusion in the May EMS model release. |
|  | - By July 1st for inclusion in the September EMS model release. |
|  | - By November 1st for inclusion in the February EMS model release. |
|  | Preliminary individual substation one-lines are required when a change meets one or more of the following criteria: |
|  | - New substation with equipment designated as part of the BES or with equipment operating at voltages of 69 kV or greater. |
|  | - New generator participating in the Real-Time Energy Market regardless of voltage level. |
|  | - New line, transformer, phase shifter or reactive device (shunt, variable or dynamic) connecting at voltages of 69 kV or greater. |
|  | - Addition or removal of a switching device that affects connectivity and system real or reactive power flow of equipment at voltages of 69 kV or greater or that affects connectivity between a generator and its point of interconnection. |
|  | - Device type or nomenclature change for a switching device operating at voltages of 69 kV or greater when the device affects connectivity and system real or reactive power flow. |
|  | - ISO groups devices into four main types: breaker, circuit switcher, motor-operated switch and manual switch. Changes such as a breaker type change from gas to oil do not affect the ISO device type and are not required in advance of the change. |
|  | It is acceptable to provide a document with multiple diagrams outlining the various project phases rather than multiple separate documents with various effective dates as long as the diagrams in the document: |
|  | - include all required devices and nomenclature; and |
|  | - provide an estimated effective date for each diagram. |
|  | When such a document is used, the user shall enter the expected effective date of the final configuration as the expected effective date of the entire document. When exercising this option, the diagram is required to be submitted at least one hundred eighty (180) calendar days in advance of the expected In-Service Date of the first phase included in the document. |
|  | Preliminary one-lines are not required for the following changes to required facility one-lines unless specifically requested by ISO: |
|  | - A device type change that does not affect the ISO device type. |
|  | - ISO groups devices into four main types: breaker, circuit switcher, motor-operated switch and manual switch. Changes such as a breaker type change from gas to oil do not affect the ISO device type. |
|  | - Changes (including additions or removals) to devices or equipment operating at any kV level that do not affect the connectivity and system real or reactive power flow at voltages of 69 kV or greater or between a generator and its point of interconnection. This includes changes to grounding devices, relay equipment, metering equipment, wave traps, VTs, CTs, etc. |
|  | Preliminary one-lines can be based on preliminary, planned or MP or TO specification data but shall include device nomenclature. This device nomenclature shall be consistent with the nomenclature that will be used by all station and system operators to identify equipment. |
|  | - When uploading a preliminary one-line, the user shall enter the expected effective date of the changes depicted on the preliminary one-line. |
|  | - Users are not expected to update or maintain the expected effective date of preliminary one-lines. |
|  | MPs and TOs shall provide any updated issued for construction one-line schematic diagrams prior to the In-Service Date of the facility. One-lines shall either be based on as-built or derived from the specification for construction. |
|  | As-built one-lines shall be submitted no later than thirty (30) calendar days after the In-Service Date if not provided prior to the In-Service date. |
|  | Revisions to required facility one-lines not requiring submittal of a preliminary one-line shall be submitted within fifteen (15) Business Days of being revised and re-issued by the participant. |
|  | Submittal schedule for optional facility one-lines: |
|  | System overview one-lines, area one-lines and non-requested one-lines for facilities connected at voltages that are less than 69 kV are not required to be submitted but can be helpful for ISO System Planning engineers and LCC System Operators. To this end, submittal of these one-lines to ISO is desired. |
|  | Once initially provided, MPs and TOs shall submit revisions to one-lines for optional facilities no later than thirty (30) calendar days after being revised and re-issued by the MP or TO. |

# Determination and Submittal of NX-9 Data Representing the Physical Characteristics, Ratings, and Operational Data of Transmission System Equipment (NX-9 Forms)

|  | Revised or new transmission facility data is to be submitted electronically to the ISO NX-9 Administrator in the NX Application. The data required and the appropriate NX-9 forms are identified in the following appendices, which also provide explanations of terms and instructions for data preparation: |
| --- | --- |
|  | - OP-16 Appendix A - Explanation of Terms and Instructions for Data Preparation of NX-9A - ISO New England Transmission Equipment Rating, Characteristic, and Operational Data - Transmission Line |
|  | - OP-16 Appendix B - Explanation of Terms and Instructions for Data Preparation of NX-9B - ISO New England Transmission Equipment Rating, Characteristic, and Operational Data - Transformer - FIXED/GSU/TCUL |
|  | - OP-16 Appendix C - Explanation of Terms and Instructions for Data Preparation of NX-9C - ISO New England Transmission Equipment Rating, Characteristic, and Operational Data - Transformer - Phase Shifting |
|  | - OP-16 Appendix D - Explanation of Terms and Instructions for Data Preparation of NX-9D - ISO New England Transmission Equipment Rating, Characteristic, and Operational Data - Static Capacitor/Reactor |
|  | - OP-16 Appendix G - Explanation of Terms and Instructions for Data Preparation of NX-9G - ISO New England Transmission Equipment Rating, Characteristic, and Operational Data - Variable Reactor |
|  | - OP-16 Appendix H - Explanation of Terms and Instructions for Data Preparation of NX-9H - ISO New England Transmission Equipment Rating, Characteristic, and Operational Data - Series Device |
|  | - OP-16 Appendix I - Explanation of Terms and Instructions for Data Preparation of NX-9 - ISO New England Transmission Equipment Rating, Characteristic, and Operational Data - Other Equipment |
|  | ISO will review all submitted data to verify that it is complete, reasonable and consistent with the related data and with the reason for the revision and to ensure that it conforms to the explanation of terms. ISO will notify the MP or TO of any discrepancies found. The MP or TO will provide corrections to the NX-9 form consistent with the schedule identified in Section II, Re-submittal of Rejected NX-9s. |
|  | If any submitted data is in dispute, ISO Reliability & Operations Compliance and ISO Legal Department will send a formal written notification to the MP or TO seeking resolution. The MP or TO will review the data and provide substantiation of data they find accurate. If the data submittal is then determined to be reasonable by ISO, it will be approved by ISO. If the data is determined to be inaccurate by the MP or TO, it will be modified and re-submitted by the MP or TO after which ISO approval will proceed. |

# Annual NX-9 Data Certification

|  | In January of each year, unless otherwise communicated to the MP and TO NX-9 Contacts as identified in ISO CAMS, ISO will initiate a certification process in the NX application. MPs and TOs shall respond as outlined in OP-16 Appendix E - Annual Data Certification of ISO New England Transmission Equipment Rating Characteristic, and Operational Data by the date specified by ISO which will be at least thirty (30) calendar days from the certification initiation. This process requires that the MP or TO certify that all transmission facilities identified in OP-16 and its appendices are accurately represented in the ISO NX and LEP Applications. |
| --- | --- |
|  | MPs and TOs should not include Planned Re-evaluations of Existing Facilities, or unreported changes due to widespread outage and major system restoration that are within the six-month time allowance, when responding to the annual certification. |

# MOD-032 Dynamics And Short Circuit Data for Transmission System Equipment

|  | It is the responsibility of Transmission Planners (TPs), TOs and MPs to determine and submit the required MOD-032 dynamics and short circuit data for new and reconfigured facilities for all its transmission equipment in accordance with the requirements in the appendices listed below. |
| --- | --- |
|  | - OP-16 Appendix J - Instructions for Submittal of Dynamics Data - ISO New England Transmission Equipment Rating, Characteristic, and Operational Data - Transmission Equipment Dynamics Data |
|  | - OP-16 Appendix K - Instructions for Submittal of Short Circuit Data - ISO New England Transmission Equipment Rating, Characteristic, and Operational Data - Generation and Transmission Equipment Short Circuit Data |
|  | ISO will review all submitted data to verify that it is complete, reasonable and consistent with the related data and with the reason for the revision and to ensure that it conforms to the explanation of terms. ISO will notify the TP, MP or TO of any discrepancies found. The TP, MP or TO will provide corrections to the dynamics or short circuit data as identified in requirement R3 of MOD-032. |

# OP-16 Revision History

Document History (This Document History documents action taken on the equivalent NEPOOL Procedure prior to the RTO Operations Date as well as revisions made to the ISO New England Procedure subsequent to the RTO Operations Date.)

| Rev. No. | Date | Reason |
| --- | --- | --- |
| - - | 11/03/17 | For previous revision history, refer to Rev 10 available through Ask ISO; |
| Rev 11 | 11/03/17 | Biennial review by procedure owner; Add detail to one-line schematic diagram section specifying required versus optional one-lines and the submittal schedule for all one-lines; Specify calendar versus Business Days where not already specified; Made editorial changes to be consistent with current practices and management expectations (e.g., grammar changes from “must” to “shall”’ and “which” to “that” as appropriate; and remove capitalization from non-defined terms; Truncated the Revision History per SOP-RTMKTS.0210.0010 Section 5.6; |
| Rev 11.1 | 06/06/19 | Biennial review by procedure owner requiring no changes; Made administrative changes required to publish the Minor Revision |
| Rev 11.2 | 01/25/21 | Biennial review by procedure owner requiring no changes; Made administrative changes required to publish the Minor Revision |
| Rev 12 | 08/22/22 | Biennial review by procedure owner; Clarify ratings requirements to include relay loadability limits and other equipment deemed necessary by Good Utility Practice; Clarify one-line diagram requirements for Generator Assets; Modify submittal schedule for one-line diagrams. |
| Rev 13 | 10/26/23 | Periodic review by procedure owner; Add reference to OP-14, Appendix B; Add footnote to define “relay loadability limits” as used in this Procedure; Modify lead time for new facility preliminary NX-9 submittals to potentially require earlier submittals for projects required to be in a specific EMS model release. |
| Rev 13.1 | 10/23/25 | Biennial review by procedure owner requiring no changes; Made administrative changes required to publish the Minor Revision. |
| Rev 14 | 10/21/26 | Biennial review by procedure owner; Add references to FERC Order 881, OP-18 and OATT Attachment Q; Globally change the term "Submission" to "Submittal"; Add footnote to Overview section to define term "nominal ratings"; Define Limit Exchange Portal to LEP throughout document; Introduce LEP as new ratings host for NE; Revise language on ratings requirements in NX app, describe new fields for ratings characteristics on NX forms; Add new section for LEP Ratings submittal requirements; Add the timeframe participants have to notify ISO of LMP transfers and to submit LMP transfer revisions; Add the timeframe participants have to submit revisions which include addition or removal of conditional ratings, bi-directional ratings, or the providing of ratings via telemetry. Change submittal dates for new facilities associated with model releases from the 15th to the 1st of March, July and November; Remove submittal schedule for planned modifications to existing facilties with OP3 exception. |

# APPENDICES

|  | Appendix A - Explanation of Terms and Instructions for Data Preparation of NX-9A - ISO New England Transmission Equipment Rating, Characteristic, and Operational Data - Transmission Line |
| --- | --- |
|  | Appendix B - Explanation of Terms and Instructions for Data Preparation of NX-9B - ISO New England Transmission Equipment Rating, Characteristic, and Operational Data - Transformer - FIXED/GSU/TCUL |
|  | Appendix C - Explanation of Terms and Instructions for Data Preparation of NX-9C - ISO New England Transmission Equipment Rating, Characteristic, and Operational Data - Transformer - Phase Shifting |
|  | Appendix D - Explanation of Terms and Instructions for Data Preparation of NX-9D - ISO New England Transmission Equipment Rating, Characteristic, and Operational Data - Static Capacitor/Reactor |
|  | Appendix E - Annual Data Certification of ISO New England Transmission Equipment Rating Characteristic, and Operational Data |
|  | Appendix F - Retired 05/04/2012 |
|  | Appendix G - Explanation of Terms and Instructions for Data Preparation of NX-9 - ISO New England Transmission Equipment Rating, Characteristic, and Operational Data - Variable Reactor |
|  | Appendix H - Explanation of Terms and Instructions for Data Preparation of NX-9 - ISO New England Transmission Equipment Rating, Characteristic, and Operational Data - Series Device |
|  | Appendix I - Explanation of Terms and Instructions for Data Preparation of NX-9 - ISO New England Transmission Equipment Rating, Characteristic, and Operational Data - Other Equipment |
|  | Appendix J - Instructions for Submittal of Dynamics Data - ISO New England Transmission Equipment Rating, Characteristic, and Operational Data - Transmission Equipment Dynamics Data |
|  | Appendix K - Instructions for Submittal of Short Circuit Data - ISO New England Transmission Equipment Rating, Characteristic, and Operational Data - Generation and Transmission Equipment Short Circuit Data |

New England Transmission System is defined in the ISO Transmission, Markets, and Services Tariff, Section I.2.2.

Nominal Rating definition: The lowest of the real-time, forecast or seasonal ratings for a network segment that provides for reliable operation of the New England Transmission System.

Business Day is defined in the ISO Transmission, Markets, and Services Tariff, Section I.2.2.

All changes shall have completed any applicable planning approval requirements, such as Tariff Section I.3.9 approval.

Bulk Electric System (BES) is defined in the Glossary of Terms Used in NERC Reliability Standards.

System Operator is defined in the Glossary of Terms Used in NERC Reliability Standards.