2015 Regional System Plan

© ISO New England Inc.
System Planning
November 5, 2015

ISO-NE PUBLIC

Preface

ISO New England Inc. (ISO) is the not-for-profit corporation responsible for the reliable and economical operation of New England’s electric power system. It also administers the region’s wholesale electricity markets and manages the comprehensive planning of the regional power system. The planning process includes the preparation of an annual Regional System Plan (RSP) in accordance with the ISO’s Open Access Transmission Tariff (OATT) and other parts of the Transmission, Markets, and Services Tariff (the ISO tariff), approved by the Federal Energy Regulatory Commission (FERC). Regional System Plans meet the tariff requirements by including the following:

- Forecasts of annual energy use and peak loads (i.e., the demand for electricity) for a 10-year planning horizon and the need for resources (i.e., capacity)

- Information about the amounts, locations, and characteristics of market responses (e.g., generation or demand resources or elective transmission upgrades) that can meet the defined system needs—systemwide and in specific areas

- Descriptions of transmission projects for the region that could meet the identified needs, as summarized in an RSP Project List, which includes information on project status and cost estimates and is updated several times each year.

RSPs also must summarize the ISO’s coordination of its system plans with those of neighboring systems, the results of economic studies of the New England power system, and information that can be used for improving the design of the regional wholesale electricity markets. In addition to these requirements, RSPs identify other actions taken by the ISO, state officials, regional policymakers, participating transmission owners (PTOs), New England Power Pool (NEPOOL) members, market participants, and other stakeholders to meet or modify the needs of the system.

The regional system planning process in New England is open and transparent and reflects advisory input from regional stakeholders, particularly members of the Planning Advisory Committee (PAC), according to the requirements specified in the OATT. The PAC is open to all entities interested in regional system planning activities in New England.

The 2015 Regional System Plan (RSP15) and the regional system planning process identify the region’s electricity needs and plans for meeting these needs for 2015 through 2024. Study proposals, scopes of work, assumptions, draft and final study results, and other materials appearing in RSP15 were discussed during PAC meetings held from September 2014 to August 2015. The ISO also posted to its website PAC presentations, meeting minutes, reports, databases, and other materials for stakeholder review. On August 6, 2015, the ISO and the PAC discussed stakeholder comments on an earlier draft of RSP15, and the ISO held a public meeting on September 10, 2015, to discuss RSP15 and other planning issues facing the New England region.

As required by the OATT Attachment K, the ISO New England Board of Directors has approved the 2015 Regional System Plan.

Contents

Preface	i

Figures	viii

Tables	x

Section 1
Executive Summary	1

1.1 RSP15 Summary	1

1.2 Introduction to the Regional System Planning Process	2

1.3 Highlights and Key Results of the Regional System Plan	3

1.3.1 Forecasts of the Annual and Peak Use of Electric Energy, Energy Efficiency,
and Photovoltaic Capacity and Energy	3

1.3.2 Projections of the Systemwide Need for Capacity and Operating Reserves	5

1.3.3 Existing and Future Resource Development in Areas of Need	6

1.3.4 Transmission System Needs, Solutions, and Cost Considerations	7

1.3.5 Interregional Planning Coordination and Studies	8

1.3.6 Fuel-Related Risks to System Reliability and Solutions	9

1.3.7 Existing and Pending Environmental Regulations, Emissions Analyses, and Other Studies	11

1.3.8 Integrating Renewable and Other Resources to Meet System Needs	12

1.3.9 Federal, State, and Regional Initiatives that Affect System Planning	13

1.4 Conclusions	14

Section 2
Overview of RSP15, the Power System, and Regional System Planning	16

2.1 Overview of the System Planning Process and RSP15	16

2.1.1 Types of Transmission Upgrades	17

2.1.2 Transmission Planning Guides	20

2.1.3 Planning Studies Conducted for and Summarized in RSP15	20

2.1.4 Accounting for Uncertainty	22

2.1.5 Working with the Planning Advisory Committee and Other Committees	22

2.1.6 Providing Information to Stakeholders	23

2.1.7 FERC Order No. 1000 on Transmission Planning and Cost Allocation	24

2.1.8 Meeting All Requirements	25

2.2 Overview of the New England Electric Power System	25

2.3 Overview of the New England Wholesale Electricity Market Structure	26

2.4 Overview of System Subdivisions Used for Analyzing and Planning the System	28

Section 3
Forecasts of New England’s Peak Demand, Annual Use of Electric Energy, Energy Efficiency,
and Distributed Generation	32

3.1 ISO New England Gross Demand Forecasts	32

3.2 Energy-Efficiency Forecast for New England	35

3.3 Distributed Generation Forecast	37

3.3.1 Development of a PV Forecast Methodology	37

3.3.2 Data Collection and Analysis	38

3.3.3 PV Forecast	39

3.4 The Net Demand Forecast	42

3.5 Summary of Key Findings of the Demand, Energy-Efficiency, and PV Forecasts	45

Section 4
Resource Adequacy—Resources, Capacity, and Reserves	46

4.1 Determining Systemwide and Local-Area Capacity Needs	46

4.1.1 Systemwide Installed Capacity Requirements	46

4.1.2 Local Resource Requirements and Limits	48

4.1.3 Capacity Supply Obligations from the Forward Capacity Auctions	49

4.2 Determining FCM Capacity Zones	58

4.2.1 Identifying Potential Zonal Boundaries and Associated Transfer Limits to Be Tested
for FCM Modeling	58

4.2.2 Transfer-Capability Assessment for FCA #10	61

4.2.3 Capacity Zone Formation in Future Years of the Planning Horizon	64

4.3 Analyzing Operable Capacity	64

4.4 Determining Operating Reserves and Regulation	67

4.4.1 Systemwide Operating-Reserve Requirements	67

4.4.2 Locational Reserve Needs for Major Import Areas	68

4.5 Summary	72

Section 5
Existing and Future Resource Development in Areas of Need	74

5.1 Existing Generating Capacity by Subarea, Load Zone, and State	74

5.2 Summer Seasonal Claimed Capability of New England’s Generating Resources	76

5.3 Generation Retirement and Additions in New England	76

5.4 Generating Units in the ISO Generator Interconnection Queue	78

5.5 Strategic Transmission Analysis—Generator Retirement Analysis	81

5.6 Analysis of Market-Resource Alternatives	81

5.7 Summary	83

Section 6
Transmission System Performance Needs Assessments and Upgrade Approvals	84

6.1 The Need for Transmission Security	84

6.2 Overview of New England’s Transmission System	85

6.3 Northern New England	87

6.3.1 Northern New England Transmission	87

6.3.2 Northern New England Transmission System Studies	88

6.3.3 Northern New England Transmission Projects	90

6.4 Southern New England	93

6.4.1 Southern New England Transmission	93

6.4.2 Southern New England Transmission System Studies	93

6.4.3 Southern New England Transmission System Projects	106

6.5 RSP Project List and Projected Transmission Project Costs	108

6.5.1 Reliability Transmission Upgrades	109

6.5.2 Lack of Need for Market-Efficiency-Related Transmission Upgrades	111

6.5.3 Required Generator-Interconnection-Related Upgrades	114

6.5.4 Elective Transmission Upgrades	114

6.6 Summary	115

Section 7
Interregional Coordination	117

7.1 Eastern Interconnection Planning Collaborative Studies	117

7.2 Electric Reliability Organization Overview	118

7.3 IRC Activities	119

7.4 Northeast Power Coordinating Council Studies and Activities	120

7.5 Northeastern ISO/RTO Planning Coordination Protocol	121

7.6 Interregional Transfers	122

7.7 Summary	124

Section 8
Fuel-Certainty Risks to System Reliability and Solutions	125

8.1 Capacity and Electric Energy Production in the Region by Fuel Type	125

8.2 Natural Gas Infrastructure	127

8.3 Natural Gas and Oil Fuel Certainty and Risks to System Reliability	130

8.3.1 Fuel-Certainty Risks	131

8.3.2 Natural Gas Price Volatility	131

8.4 Addressing Fuel-Certainty and Cost Risks	134

8.4.1 Electric Power System and Natural Gas Sector Coordination	134

8.4.2 Winter Reliability Programs to Address Fuel Certainty	135

8.4.3 Improvements to the Wholesale Electric Markets	137

8.4.4 Pipeline Improvements	139

8.5 EIPC Gas-Electric System Interface Study	141

8.5.1 Target 1	142

8.5.2 Target 2	142

8.5.3 Target 3	142

8.5.4 Target 4	143

8.6 Summary	144

Section 9
Impacts of Environmental Regulations and Siting Requirements on Generators and the Power System	146

9.1 Federal, State, and Regional Environmental Regulations Affecting Generators	146

9.1.1 Emerging Impacts of Clean Water Act Regulations on the Region’s Generators	147

9.1.2 Clean Air Act Requirements and Regional and Federal Greenhouse Gas Regulations	149

9.1.3 Cost of Compliance with Environmental Regulations	154

9.2 Update of Regional Nuclear Generation Licensing Renewals	155

9.3 Update on Hydroelectric Generation Relicensing	155

9.4 Conclusions	156

Section 10
Integration of Variable Energy Resources	157

10.1 Potential System Impacts on Fossil Fuel Generators of Integrating Wind and Solar Resources	157

10.2 Integration of Wind Resources	157

10.2.1 Wind Forecasting and Dispatch	157

10.2.2 Strategic Transmission Analysis—Wind Integration Study	158

10.3 Large-Scale Adoption of Photovoltaic Resources and Other Distributed Generation Resources	161

10.3.1 Operational Solar Forecasting	161

10.3.2 Potential Reliability Impacts of PV	162

10.3.3 Other Challenges of PV Integration	163

10.3.4 Eastern Renewable Generation Integration Study	164

10.4 Economic Performance of the System and Other Studies	164

10.4.1 2011 to 2013 Economic Studies and 2015 Economic Study Request	164

10.4.2 Generic Capital Costs of New Supply Resources	166

10.5 Summary	167

Section 11
Federal, Regional, ISO, and State Initiatives	169

11.1 Federal Initiatives	169

11.1.1 FERC Order No. 1000	169

11.1.2 FERC Actions to Better Align Natural Gas and Wholesale Electricity Markets	169

11.1.3 FERC ISO/RTO Performance Metrics	170

11.1.4 FERC Directive on Physical Security	170

11.1.5 Executive Order on Cybersecurity	171

11.1.6 US Department of Energy Congestion Studies	171

11.1.7 DOE Quadrennial Energy Review	172

11.2 Regional Initiatives	173

11.2.1 Coordination among the New England States	173

11.2.2 Consumer Liaison Group	174

11.2.3 Southern New England States’ RFP	174

11.3 ISO Initiatives	175

11.3.1 Updates on Developing and Integrating Smart Grid and Other New Technologies	175

11.3.2 Transmission Planning Process Guide and Transmission Planning Technical Guide	177

11.4 State Initiatives, Activities, and Policies	177

11.4.1 Connecticut	177

11.4.2 Maine	178

11.4.3 Massachusetts	179

11.4.4 New Hampshire	180

11.4.5 Rhode Island	181

11.4.6 Vermont	182

11.4.7 Summary of Renewable Portfolio Standards	183

11.5 Summary of Initiatives	183

Section 12
Key Findings and Conclusions	184

12.1 Changes in the Planning Process	184

12.2 Forecasts of Peak Load, Energy Use, Energy Efficiency, and PV	184

12.3 Systemwide and Local Area Needs and Meeting These Needs	185

12.4 Transmission Projects	186

12.5 Interregional Coordination	186

12.6 Fuel Flexibility and Certainty	186

12.7 Environmental Regulations and Initiatives	187

12.8 Planning for and Integration of Variable Energy Resources	187

12.8.1 Wind Resources	187

12.8.2 Photovoltaics	188

12.9 Federal, Regional, ISO and State Initiatives	188

12.10 Looking Ahead	189

Acronyms and Abbreviations	190

# Figures

Figure 2-1: 	Key facts about New England’s electric power system and wholesale electricity markets.	26

Figure 2-2: 	Active-demand-resource dispatch zones in the ISO New England system.	30

Figure 2-3: 	RSP15 geographic scope of the New England electric power system.	31

Figure 3-1: 	The ISO’s actual summer peak loads (i.e., reconstituted to include the megawatt reductions
from OP 4 actions and FCM passive demand resources) and the 50/50 and 90/10 forecasts,
1992 to 2013 (MW).	35

Figure 3-2: 	Cumulative New England PV forecast for each classification of PV, 2015 to 2024 (MW).	42

Figure 3-3: 	RSP15 annual energy-use forecast (diamond); energy forecast minus PV BTMNEL (circle);
energy forecast minus PV and FCM #9 PDRs through 2018 (triangle); and energy forecast
minus PV BTMNEL, minus FCM PDRs, minus the energy-efficiency forecast (square)
for 2019 to 2024 (MW).	43

Figure 3-4: 	RSP15 summer peak demand forecast (90/10) (diamond); demand forecast minus PV BTMNEL (circle); demand forecast minus PV and FCM #9 PDRs through 2018 (triangle); and demand
forecast minus PV BTMNEL, minus FCM PDRs, minus the energy-efficiency forecast (square)
for 2019 to 2024 (MW).	43

Figure 4-1: 	Sloped demand curve for FCA #9.	53

Figure 4-2: 	Summary of total capacity of new capacity and delist requests that cleared
FCA #1 to FCA #9 (MW).	56

Figure 4-3: 	Summary of total capacity of nonprice retirement requests, FCA #4 to FCA #9 (MW).	57

Figure 4-4: 	Projected summer operable capacity analysis, 2015 to 2024 (MW).	65

Figure 5-1: 	Actual and Projected Summer SCC generation retirements and additions, 2010 to 2018 (MW).	77

Figure 5-2: 	Capacity of generation-interconnection requests by RSP subarea, November 1997
to April 2015 (MW).	78

Figure 5-3: 	Resources in the ISO Generator Interconnection Queue, by state and fuel type,
as of April 1, 2015 (MW and %).	79

Figure 5-4: 	Resources in the ISO Generator Interconnection Queue, by RSP subarea and fuel type,
as of April 1, 2015 (MW).	80

Figure 5-5: 	Percentage of resources in the ISO Generator Interconnection Queue, by RSP subarea
and fuel type, as of April 1, 2015.	80

Figure 6-1: 	Approximate geographic region of each of the major 345 kV transmission projects
in New England, as of June 1, 2015.	86

Figure 8-1: 	New England’s summer seasonal claimed capability (MW, %) and electric energy
production (GWh, %) by fuel type for 2014.	126

Figure 8-2: 	Generating resource summer capability by fuel type based on the 2015 CELT Report
and the interconnection queue (MW, %).	127

Figure 8-3: 	Overview map of the natural gas infrastructure serving New England.	129

Figure 8-4: 	Sources of natural gas, including Marcellus shale gas, in the Continental United States.	130

Figure 8-5: 	Natural gas pipeline network in the Continental United States.	130

Figure 8-6: 	Monthly average fuel prices and real-time Hub LMPs compared with regional natural gas prices ($/MWh; $/MMbtu).	132

Figure 8-7: 	Natural gas market data, November 2013 to April 2015 ($/MMBtu).	133

Figure 8-8: 	On-site fuel oil inventories (both heavy and light oil) at all New England fossil-fuel stations,
winter 2013/2014 and 2014/2015 (beginning of each month) (million barrels)	136

Figure 8-9: 	Proposed natural gas pipeline expansions benefiting New England, 2015.	139

Figure 9-1: 	Capacity and total water consumption by thermoelectric generators with once-through
cooling in New England, 2010 (MW, MGD).	148

Figure 9-2: 	2004 to 2013 New England system annual emissions of NOX, SO2, and CO2,
2004 to 2013 (ktons).	151

Figure 9-3: 	New England RGGI states’ quarterly CO2 emissions and allowance auctions,
2008 to 2015 (mtons, millions).	152

Figure 9-4: 	New England RGGI states’ quarterly CO2 allowance auction proceeds and clearing price,
2008 to 2015 (million $ and $).	153

Figure 9-5: 	EPA Clean-Power-Plan-adjusted state CO2 emissions, 2012 baseline compared with
2014 emissions reached under RGGI, interim (2022 to 2029) mass-based reduction targets,
and final (2030) mass-based reduction targets, (short tons).	154

Figure 10-1: 	Areas (in blue), in Connecticut (left) and Massachusetts (right), where PV resources are likely
to trip off line because of low voltage in the event of a fault on the 345 kV transmission system.	163

Figure 11-1: 	Existing and planned FACTS devices in New England.	176

# Tables

Table 3-1 	Summary of Annual Gross Electric Energy Use and Gross Peak Demand Forecast
for New England and the States, 2015/2016 and 2024/2025	34

Table 3-2  	Summary of PDR and EE Forecast Annual Electric Energy Savings and Peak Demand Reductions
for New England and the States, 2015 and 2024 (GWh, MW)	36

Table 3-3 	New England States’ Annual and Cumulative PV Nameplate Capacities, 2015 to 2024 (MWAC)	40

Table 3-4 	Forecasted Growth of PV in the New England States, 2015 to 2024 (GWh)	40

Table 3-5 	Percentage Growth Rates of the Gross and Net Forecasts of Annual and Peak Electric
Energy Use, 2015 to 2024	44

Table 3-6 	2015 State and Systemwide Net Forecasts of Annual and Peak Electric Energy Use (MWh, MW)	44

Table 3-7 	Net Forecast of Demand in RSP Subareas, 2015 to 2024 (GWh, MW)	45

Table 4-1  	Actual and Representative New England Net Installed Capacity Requirements
and Resulting Reserves, 2015 to 2024 (MW, %)	48

Table 4-2 	Actual LSRs and MCLs for the 2015/2016 to 2018/2019 Capacity Commitment Periods (MW)	49

Table 4-3 	Summary of the FCA Obligations at the Conclusion of Each Auction (MW)	50

Table 4-4 	Results of the FCA by Capacity Zone at the Conclusion of Each Auction (MW, $/kW-month)	51

Table 4-5 	Capacity Supply Obligation for New Capacity Procured during the Forward Capacity
Auctions (MW)	54

Table 4-6 	Active and Passive Demand Response: CSO Totals by Capacity Commitment Period (MW)	55

Table 4-7  	Future Systemwide Needs (MW)	58

Table 4-8 	Results of the Transfer Capability Analysis for New England, 2015 to 2024,
Internal Interfaces (MW)	60

Table 4-9 	Results of the Transfer Capability Analysis for New England, 2015 to 2024,
External Interfaces (MW)	61

Table 4-10 	Projected New England Operable Capacity Analysis for Summer, 2015 to 2024,
Assuming 50/50 Loads (MW)	66

Table 4-11 	Projected New England Operable Capacity Analysis for Summer, 2015 to 2024,
Assuming 90/10 Loads (MW)	66

Table 4-12  	Representative Future Operating-Reserve Needs in Major New England Import Areas (MW)	70

Table 5-1 	RSP15 Generating Capacity by Subarea, State, and Load Zone, 2015 (MW, %)	75

Table 5-2  	2015 Summer Seasonal Claimed Capability for ISO New England Generating Resources,
by Assumed Operating Classification, Systemwide, and by RSP Subarea (MW)	76

Table 5-3 	Actual and Projected Summer SCC Generation Retirements and Additions, 2010 to 2018 (MW)	77

Table 5-4 	Summary of Queue Projects as of April 1, 2015	79

Table 5-5 	Desirable Amounts and Locations of MRA Additions (MW)	83

Table 6-1 	Estimated Cost of Reliability Projects as of June 2015 Plan Update (Million $)	110

Table 6-2 	Actual and Forecast Regional Transmission Service Rates, 2014 to 2019	111

Table 6-3 	ISO New England Transmission System Day-Ahead, Real-Time, and Total Congestion Costs
and Credits, 2003 to 2014 ($)	112

Table 6-4 	Net Commitment-Period Compensation by Type and Year (Million $)	114

Table 7-1 	Assumed External Interface Import Capability, Summer 2015 to Summer 2024 (MW)	122

Table 7-2 	Import Capacity Supply Obligations for Summer, FCA #6 to FCA #9 (MW)	123

Table 7-3 	Tie-Reliability Benefits Assumed from Neighboring Power Systems, Summer (MW)	123

Table 7-4 	Annual Net Energy Imports of System Net Energy for Load, 2010 to 2014 (GWh and %)	123

Table 7-5  	New England Energy Imports by Month, 2014 (GWh)	124

Table 8-1 	Comparison of 2014 and 2015 January and February Winter Futures Prices ($/MMBtu, $/MWh)	134

Table 8-2 	Comparison of LNG Deliveries for Winter 2013/2014 with Winter 2014/2015 (Mcf)	137

Table 8-3  	Summary of Pipeline Improvements Benefiting New England	140

Table 9-1 	New England Operating Nuclear Power Plants	155

Table 10-1  	Generic Capital Costs of New Supply-Side Resources	167

# Executive Summary

The 2015 Regional System Plan (RSP15) and ISO New England (ISO) system planning process identify the region’s electricity needs and actions for meeting these needs for 2015 through 2024. The plan updates the themes included in the 2014 Regional System Plan (RSP14); addresses stakeholder comments received throughout the planning process; and includes new information, such as the enhanced ISO forecast of photovoltaics (PV). RSP15 also continues the region’s focus on strategic planning issues, compliance with the Federal Energy Regulatory Commission’s (FERC) Order No. 1000, and other ISO initiatives. The ISO has fully coordinated all system planning activities with stakeholders for developing RSP15, which complies with all planning criteria and regulatory requirements. This section summarizes the key issues affecting the regional system planning process, the highlights of RSP15, and the results of various system and regional strategic planning studies.

## RSP15 Summary

The region has reached a turning point in addressing several key challenges to system reliability. New England increasingly relies on natural-gas-fired generation, which can expose the region to significant energy supply, reliability, and price issues. This need for greater fuel assurance is the result of the limited natural gas supply available to the region’s generators and the expected retirements of several coal, nuclear, and oil generators, which have begun to occur and are expected to continue. Environmental regulations addressing air and water emissions from thermal power plants remain in a state of flux but will likely reduce the operating capability and flexibility of these plants and could prompt additional retirements.

A number of ISO actions and market responses are addressing these challenges. The ISO’s 2014/2015 Winter Reliability Program and the improved coordination between the electric power and natural gas systems helped provide greater fuel certainty this past winter. The region was exposed to high natural gas prices during the winter that led to increased liquefied natural gas (LNG) deliveries to New England, and the increased use of oil provided additional supply. New resources are developing, and improved resource performance is anticipated beginning in 2018 in response to changes in the Forward Capacity Market (FCM). These changes reduce Forward Capacity Auction (FCA) price volatility, improve long-term financial stability for new resources, and provide incentives for resources to perform. The integration into the New England system of energy efficiency (EE) and variable energy resources (VERs), including wind and PV, also help address fuel-certainty issues. Improvements to the ISO’s wholesale energy and ancillary markets, the potential development of additional natural gas pipeline capabilities and dual-fuel capability, and the increased use of LNG during peak hours could further address these issues over the long term.

Public policies that promote energy efficiency and variable energy resources are reducing the need for more traditional resources. The operation of new VERs and EE in New England is assisting the region in meeting air and water regulations. Several new ties to eastern Canada have been proposed. If fully developed, these ties could bring additional hydroelectric energy into the region and help meet future regional environmental requirements as well as capacity and energy needs.

Transmission projects are progressing throughout the region. As of summer 2015, most of the projects of the Maine Power Reliability Program (MPRP) were in service. Transmission upgrades are in service in response to the retirement of the Vermont Yankee nuclear facility and the Salem Harbor generating station. Likewise, some transmission reinforcements are moving forward in Rhode Island in preparation for the retirement of Brayton Point Station. The New England East–West Solution (NEEWS) for Rhode Island and the Greater Springfield area is in service, and the Interstate Reliability Project is under construction. The final NEEWS component, the Central Connecticut Reliability Project, has been replaced by 115 kilovolt (kV) upgrades that will address the needs established for the Greater Hartford/Central Connecticut (GHCC) area. A preferred solution was selected to address the reliability needs of the Greater Boston area.

A number of factors, such as the growth of net system load, resource retirements, aging transmission infrastructure, and public policy objectives, will influence future transmission planning needs. Interregional planning also has become increasingly important, and the ISO continues to coordinate its planning activities with neighboring regions. The transmission planning process is changing in response to FERC’s final Order No. 1000 going into effect.

## Introduction to the Regional System Planning Process

The New England region supports the reliable and economical operation of the system through proactive planning, the completion of transmission projects and other improvements, the development of needed resources, and the overall competitiveness of the markets. Compliance with FERC’s final Order No. 1000 requires fundamental changes to the transmission planning process as conducted in New England since 2001. The order requires implementing a competitive solicitation process for transmission solutions that meet newly identified system needs beyond a three-year horizon. It also allows for transmission projects needed in the short term and projects currently under development to use the planning process in place before the order went into effect. Order No. 1000 also requires the planning process to address public policy objectives. The ISO compliance filing provides details on how the region will meet the new requirements for the planning process.

ISO New England, the New York ISO (NYISO), and the PJM Interconnection (PJM) follow a planning protocol that coordinates planning activities and addresses planning seams issues among the interregional planning authorities. FERC issued its final Order No. 1000 for interregional planning on May 14, 2015, which requires enhanced processes for interregional planning and cost allocation. RSP15 is consistent with this order. Building on their history of close cooperation, the three planning authorities have jointly made a compliance filing for FERC Order No. 1000.

The plan and planning process must satisfy the relevant standards, criteria, and other requirements established by the North American Electric Reliability Corporation (NERC), the Northeast Power Coordinating Council (NPCC), participating transmission owners (PTOs), and the ISO. As part of its compliance with Attachment K of the ISO’s Open Access Transmission Tariff (OATT), RSP15 specifically provides information on the timing of system needs and the quantity, general locations, and characteristics of the generation and demand resources that could resolve these needs and defer or eliminate the need for transmission projects.

For all RSP15 analyses, the ISO used a number of assumptions, which are subject to uncertainty over the course of the planning period. Changes in these assumptions may affect the results and conclusions of RSP15 analyses and could ultimately influence the development of transmission and generation and demand resources. For example, the demand forecast and resource expansion assumptions affect RSP studies of resource adequacy and transmission needs. RSP assumptions have been discussed with the PAC, and the ISO considers these factors for developing a comprehensive and flexible plan. While each RSP is a snapshot in time, the ISO updates the results of planning activities as needed, accounting for the status of ongoing projects, studies, and new initiatives.

## Highlights and Key Results of the Regional System Plan

This section discusses the highlights of RSP15 and the results of various system and regional strategic planning studies and other materials. The RSP15 sections indicated below contain more details, definitions of terms, and full citation information.

### Forecasts of the Annual and Peak Use of Electric Energy, Energy Efficiency, and Photovoltaic Capacity and Energy (Section 3)

The methodologies used for forecasting the gross demand, EE, and PV installations are generally similar to those used in RSP14. The historical loads and economic and demographic factors drive the forecasts of the gross peak and gross annual demand for electric energy—regionwide and in individual states and subareas. Public policies are key drivers for the growth of energy-efficiency resources and the development of photovoltaic facilities for the 10-year RSP planning horizon. The PV forecast also reflects PV participation in the wholesale energy markets, higher quality historical data of PV installations and production, and some key economic factors affecting future PV development. RSP15 also provides projections for PV energy production.

The ISO gross demand forecasts are estimates of the amount of electric energy the New England states will need annually and during seasonal peak hours. Energy efficiency is considered a resource, and behind-the-meter distributed generation is considered a reduction in demand, but for study purposes, their combined growth reduces the forecasts of gross peak demand and the gross annual use of electric energy. The resultant net demand forecasts are key inputs for determining the region’s resource adequacy requirements for future years, evaluating the reliability and economic performance of the electric power system under various conditions, and planning needed transmission improvements.

Key results discussed in Section 3 are as follows:

- The 10-year growth rate of the ISO’s net demand forecast is 0.6% per year for the summer peak demand and 0.0% per year for the annual use of electric energy. The RSP15 50/50 net summer peak forecast is 26,565 megawatts (MW) for 2015, which grows to 27,875 MW for 2024. The 90/10 net summer peak forecast, which represents more extreme summer heat waves, is 28,915 MW for 2015 and increases to 30,525 MW in 2024. The net energy for load, accounting for both EE and PV, is projected to decrease slightly from 128,173 gigawatt-hours (GWh) in 2015 to 127,698 GWh in 2024.

- The EE forecast drives the reduction of the growth rate of the 10-year gross winter peak demand from 0.7% to a net annual value of −0.1%. The relatively flat growth of the net peak load helps mitigate winter reliability concerns.

- Regional passive demand resources and energy efficiency are expected to grow from 1,685 MW in 2015 to 3,579 MW in 2024. New England states’ annual investments in EE programs are expected to be approximately $1 billion per year for 2015 through 2024. These EE investments remain a major factor in the expansion of passive demand resources in the region, which are projected to grow at an average rate of 210 MW per year across the 10-year horizon.

- Photovoltaic resources reached 908 MWac (nameplate rating) (i.e., the amount of electricity that PV could feed into the electrical system) by the end of 2014 and produced 864 GWh. These resources are expected to grow to 2,449 MWac nameplate rating by 2024 and are forecast to produce 2,593 GWh. These totals include PV resources participating in the ISO wholesale markets (i.e., FCM resources and “energy-only” resources that do not participate in the FCM) and behind-the-meter PV, which affects the net load forecast. The summer seasonal claimed capability (SCC) of PV resources is 40% of the AC nameplate value; the winter SCC is 0% of the AC nameplate value because the winter peak occurs after dusk.

### Projections of the Systemwide Need for Capacity and Operating Reserves (Section 4)

The ninth Forward Capacity Auction (FCA #9) attracted investment in new resources that help address New England’s resource needs. Key reforms to the Forward Capacity Market include improved incentives for resource performance, the use of a sloped system demand curve in the Forward Capacity Auctions to reduce price volatility, and allowing new resources to lock-in the capacity clearing price for up to seven years. Using the system demand curve and the supply curve bid by resources, the ISO procured 34,695 MW, which is 506 MW greater than the net Installed Capacity Requirement (ICR) of 34,189 MW. The auction cleared at $9.551/kilowatt-month (kW-month) and attracted new generation resources totaling 1,060 MW as well as 367 MW of new demand resources. FCA #9 procured a new 725 MW dual-fuel unit and two 45 MW units in Connecticut and a new 195 MW dual-fuel peaking power plant in the Southeast Massachusetts/Rhode Island (SEMA/RI) capacity zone.

The region’s net Installed Capacity Requirement is expected to grow from 33,391 MW in 2015 to a representative value of 36,000 MW by 2024. The net ICR increases approximately 290 MW per year, which is equivalent to 0.8% per year. Assuming all FCA #9 existing and new resources remain in service in 2018 and beyond, the region would have sufficient resources through 2023, according to RSP15 resource adequacy study results. Other study results show that Operating Procedure No. 4 (OP 4) actions will need to provide as much as 2,712 MW of load and capacity relief during extremely hot and humid summer peak-load conditions through 2024.

The ISO develops the representative operating-reserve requirements of major import areas as ranges to reflect the local reserve needs under the expected future system conditions while accounting for uncertainties about the availability of resources, load variations due to weather, and other factors. For 2015 through 2019, the representative operating-reserve requirements for Greater Southwest Connecticut range from 0 to 350 MW. Over the same period, the need for operating reserves in Greater Connecticut is as much as 850 MW during the summer, and similarly, the need for the BOSTON area is as much as 650 MW. Although each of these areas will likely have sufficient resources to meet its long-term representative reserve requirements, the placement in these areas of energy-efficiency and price-competitive resources, such as economical baseload resources, would help reduce local reserve needs and improve system performance, especially in the short term for BOSTON. Transmission projects that increase the transfer capability into these areas will also reduce local reserve needs.

When variable energy resources, particularly wind and PV, replace the capacity once provided by traditional generation, the need for flexible resources increases for providing operating reserves as well as other ancillary services, such as regulation and ramping. To date, increasing the 10-minute operating-reserve requirement and adding seasonal replacement reserves have improved the systemwide performance for meeting ramping needs in response to changing system conditions and contingencies. Natural-gas-fired combined-cycle units, fast-start units in service, and units listed in the ISO’s Generation Interconnection Queue (the queue) will likely help meet the long-term evolving needs for operating reserves.

### Existing and Future Resource Development in Areas of Need (Section 4 and Section 5)

The development of generation, demand, and import capacity resources for the region is required for providing the capacity needed to meet the ICR. The development of EE and PV resources, encouraged by public policies, and new generators, which have been responding to enhancements in the ISO’s wholesale markets, will help meet future requirements. Approximately 11,300 MW of generating resources were in the interconnection queue as of April 1, 2015. The processing of the interconnection requests in New England has progressed. With the exception of the Maine portion of the system (which has experienced a back log of mostly wind interconnection requests; see Sections 1.3.8 and 10.2), substantially all the requests made through 2014 have completed the system impact study phase or have moved to the Interconnection Agreement and commercialization phases.

The FCM sends market signals for resource development, which have been stronger in recent auctions for the Northeast Massachusetts (NEMA)/Boston and SEMA/RI capacity zones. In response to market incentives, in FCA #9, new generators cleared the market in SEMA and Connecticut (CT). The combined NEMA/SEMA/RI area was evaluated as a single capacity zone and will be modeled for the first time as a single import-constrained capacity zone in FCA #10, called the Southeast New England capacity zone. In the north, the Maine/New Hampshire/Vermont area was evaluated as a single capacity zone and will not be modeled as a single export-constrained zone for FCA #10. As in previous FCAs, Connecticut was evaluated as a potential import-constrained zone but was merged with the “Rest-of-Pool” capacity zone and will not be modeled as a separate import-constrained zone for FCA #10. The Western Massachusetts capacity zone will continue to form the basis of the Rest-of-Pool zone.

RSP15 results consider potential resource retirements and indicate locations where new resources would improve system reliability. Projections of generator summer seasonal claimed capabilities based on announced retirements show over 1,529 MW of generation resources retiring from 2016/2017 through the 2018/2019 capacity periods. The region is vulnerable to additional resource retirements that would advance the need for additional system resources. Studies of expected system conditions show that developing new resources in the combined NEMA/SEMA/RI area would provide the greatest reliability benefit.

Analysis of market resource alternatives provides theoretical locations for combinations of generation and demand-resource injections that could defer or displace otherwise needed transmission system enhancements. A market resource alternative study for the SEMA/RI area identified a need for approximately 1,540 MW of resources (1,495 MW of generation and 45 MW of demand resources spread across nine locations in SEMA/RI). The addition of these resources would remove many of the thermal constraints identified in the SEMA/RI transmission needs assessments. The interconnection of new resources at locations near load centers and deliverable to the central Massachusetts trading hub are the next most favorable locations for meeting systemwide capacity needs, as shown by the Strategic Transmission Analysis (STA) Retirement Study and the 2012 Economic Study.

### Transmission System Needs, Solutions, and Cost Considerations (Section 6)

New England’s transmission owners have placed in service transmission projects throughout the region to provide solutions to the needs identified through the regional planning process, as detailed in past RSPs and supporting reports. From 2002 to June 2015, 634 projects were placed in service, totaling approximately $7.2 billion of new infrastructure investment. As a result, the system has operated reliably, and the New England system has experienced dramatically reduced congestion. Costs associated with second-contingency and voltage-control payments have also been significantly reduced through transmission improvements. The region should continue to experience a high level of reliable and economic system operation with the planned addition of 210 projects costing $4.8 billion over the next 10 years. Major projects summarized in RSP15 include the following:

- The Maine Power Reliability Program includes the addition of significant new 345 kV and 115 kV transmission facilities and new 345 kV autotransformers at key locations in Maine. Most of the MPRP projects entered service by the first half of 2015. The Lewiston loop portions of the project are scheduled to enter service in 2017. The MPRP provides infrastructure needed to increase the ability to move power from New Hampshire into Maine and improves the ability of the transmission system within Maine to move power into local load pockets as necessary.

- The Rhode Island Reliability Project (RIRP) and the Greater Springfield Reliability Project (GSRP) components of the New England East–West Solution are in service and strengthen the backbone of the 345 kV system. The Interstate Reliability Project (IRP) is under construction. When completed, this project will address the much broader requirements of the overall New England system by addressing east–west and west–east transmission limitations.

- The 115 kV upgrades within Connecticut that will address the needs established for the Greater Hartford/Central Connecticut area have replaced the final NEEWS component, the Central Connecticut Reliability Project (CCRP).

- The Greater Boston Reliability Project and the Pittsfield Reliability Project have identified required upgrades to the system. Several short-term improvements have been identified for the SEMA/RI area to address immediate needs caused by the retirement of Brayton Point. Analysis identifying the longer-term needs for this area is well underway.

- The needs for the Vermont/New Hampshire area have been identified, and the preferred solution for Vermont was identified.

FERC accepted the ISO’s proposal to improve the administration of elective transmission upgrades (ETUs), which the ISO and stakeholders worked together to improve over the past year. The ETU process provides an option for project sponsors to propose, develop, and fund transmission development within New England or connecting to neighboring systems. This process involves the following tasks:

- Creating new ETU interconnection procedures, requirements, and obligations similar to those of generators so that ETUs can establish and maintain a meaningful position in the interconnection queue

- Defining a new form of interconnection service so that certain tie lines with neighboring areas can be used to deliver capacity into New England, preserving interconnection service rights as the New England system changes over time

- Conforming the market rules to ensure that these resources can qualify to deliver capacity and energy into the wholesale power markets

Such transmission may result in strengthening electrically weak portions of the regional transmission network, enhancing generator deliverability, or facilitating the integration of renewable resources. Ten ETUs were in the queue as of June 2015.

### Interregional Planning Coordination and Studies (Section 7)

Interconnections with neighboring regions provide opportunities for exchanging capacity, energy, reserves, and mutual assistance during capacity-shortage conditions. Tie-reliability benefits from the interconnections also lower the ICR. Additionally, imports can provide resource diversity and can lower regional generation emissions, especially imports of hydro and other renewable resources. Historically, New England has experienced net capacity and energy imports. The ISO expects imports to continue, given the level of import capacity supply obligations cleared in the Forward Capacity Auctions, the increasing amounts of net energy imports, and the number of tie-line projects in the ISO’s interconnection queue.

Identifying interregional system needs and the potential impacts that proposed generating units and transmission projects could have on neighboring systems helps support interregional reliability and economic performance. Joint study efforts with neighboring systems analyze the ability to import power from, and export power to, the eastern Canadian provinces and New York.

The ISO participates in national and interregional planning activities, developing coordinated system plans and proactively initiating planning studies with other regions. The ISO has worked with NYISO and PJM through the Northeastern Independent System Operator/Regional Transmission Operator (ISO/RTO) Planning Coordination Protocol and issued the 2013 Northeast Coordinated System Plan (NCSP13) that, through an open stakeholder process, addresses several key interregional issues and summarizes how the three ISO/RTOs coordinate planning studies of resource adequacy and transmission planning. The ISO/RTOs have coordinated their databases and system models and have conducted joint production cost studies and transmission analyses for planned system improvements and interconnections.

ISO New England and other planning authorities throughout the Eastern Interconnection are members of the Eastern Interconnection Planning Collaborative (EIPC). The EIPC addresses its portion of North American planning issues, coordinates plans, and conducts studies for the entire Eastern Interconnection through a transparent and collaborative process involving input from a broad base of interested stakeholders. ISO New England also served as a principal investigator for a project, funded as part of grant work from the US Department of Energy (DOE), that studied how the interface between the natural gas and electric power systems affects operations and planning in the Eastern Interconnection. In a separate effort, EIPC is also coordinating planning databases and conducting scenario analyses of electric power transmission systems for the entire Eastern Interconnection.

The ISO participates in several other national and regional system planning forums, such as NERC, the ISO/RTO Council, and the NPCC. Through the NPCC and NERC, the ISO has participated in interregional assessments, which coordinate planning studies and demonstrate compliance with all required planning standards, criteria, and procedures. NERC remains particularly concerned with the reliability of areas highly dependent on natural-gas-fired generators. NERC also plans to examine the reliability impacts of environmental regulations, including restricted operations and retirements.

### Fuel-Related Risks to System Reliability and Solutions (Section 8)

New England increasingly relies on natural gas as a primary fuel for generating electric energy and is decreasing its reliance on oil and coal. In 2014, the approximate percentages of the region’s generation capacity and electric energy production by fuel type were as follows:

- Natural gas: 43.2% capacity and 43.0% electric energy

- Oil: 21.1% capacity and 1.6% electric energy

- Coal: 6.8% capacity and 4.7% electric energy

- Nuclear: 14.9% capacity and 34.0% electric energy

- Hydro, pumped storage, and renewable resources: 14.1% capacity and 16.7% electric energy

The high regional use of natural-gas-fired generation is the result of the addition of new, efficient natural-gas-fired units over the past 14 years; the generally low price of natural gas; the displacement of older, less efficient oil- and coal-fired units in economic dispatch; and the recent retirements of non-natural-gas-fired generation. Natural-gas-fired generation’s proportion of the system capacity mix is expected to grow to approximately 49.2% by 2018 and 56.7% by 2024. Therefore, the current situation where natural gas fuel prices typically set the marginal price for wholesale electricity is projected to continue over the planning horizon.

The region’s reliance on the natural gas fuel-delivery system, however, continuously exposes the regional electric power system to potential reliability problems and an associated increased cost of electricity when natural gas prices are high. This is the result of limited gas pipeline capacity in New England, largely built to serve natural gas customers other than electric power generators. Pipelines can be constrained any time of the year, but cold-weather conditions and the subsequent heavy demand for space heating fueled by natural gas can exacerbate regional fuel-certainty issues when electrical imports from neighboring regions may not be readily available. Constraints on the regional gas supply (pipeline gas plus LNG) also result in higher spot prices for the limited amounts of natural gas capacity available to generators within the New England region.

The region addressed the risks associated with fuel certainty in winter 2014/2015. As part of that winter’s reliability program, demand resources were compensated, and oil-fired, dual-fuel generators and units contracting with LNG supplies were paid to secure fuel inventory. The 2014/2015 program included two permanent improvements over the 2013/2014 program. The first improvement helps dual-fuel resources more effectively manage fuel supply on days when the price of oil and natural gas approach convergence by eliminating the administrative requirement to prove that the unit burned the higher-priced fuel. The second enhancement requires dual-fueled generators to test their fuel-switching ability and for the ISO wholesale markets to compensate them for test expenses. Although the regional cost of electricity spiked during winter 2014/2015, the wholesale electric energy prices were tempered by the generators’ use of fuels other than natural gas from pipelines due, in large part, to reductions in the global price of oil and the increased availability of LNG to existing facilities in the region. The availability of additional LNG at existing facilities and the use of oil at generators could improve fuel-certainty.

The region has applied additional solutions to address fuel-certainty issues. Increased communications between the ISO and gas pipeline operators (assisted by FERC Order 787) verify whether natural gas generators scheduled to run will be able to obtain their fuel requirements. The ISO has implemented tools that help operations personnel more accurately predict the availability of natural gas supply for generators, improving unit-commitment decisions. ISO efforts have included mining data from various sources to estimate the availability of natural gas for electric energy purposes, analyzing capacity scenarios across different seasons using fuel-survey information from individual generators and pipeline operators, and establishing operating plans to manage different system conditions. Recent market rules, such as those addressing energy market offer flexibility, allow resources to more accurately reflect their variable costs in their energy offers during the operating day, which improves incentives to perform. Other new market rules have changed the timing of the Day-Ahead Energy Market to align more closely with natural gas trading deadlines, improved price-formation procedures in the energy and reserve markets, and strengthened incentives in the Forward Capacity Market (i.e., pay for performance). Increased flexibility of scheduling natural-gas-fueled units also allows generators to respond more reliably to system conditions.

Additional pipeline capacity is proposed for accessing the Marcellus natural gas supplies south and west of New England. These projects are primarily targeted at serving the local gas utilities but would also provide benefits to the wholesale electric markets. The Algonquin Incremental Market (AIM) project proposed by Spectra Energy will provide 342,000 dekatherms per day (Dth/d) of additional capacity to move Marcellus gas production to Algonquin City Gates, located near Boston. FERC approved the project in March 2015, and the estimated in-service date is the second half of 2016. The Connecticut Expansion project, proposed by Tennessee Gas Pipeline, targets Connecticut natural gas utilities and will provide an additional capacity of 72,000 Dth/d. The estimated in-service date for this project is November 2016. Additional pipeline projects are in various stages of planning and development that would serve the region.

The Eastern Interconnection Planning Collaborative completed scenario analyses that examined interactions between the natural gas system and the electric power system. The results of the scenarios and sensitivities studied show that, of all regions, ISO New England is at greatest risk of natural gas supply issues that could adversely affect the electric power system. The natural gas system for New England would be constrained for nearly all market conditions and resource mixes studied for winter 2018 and 2023, the two individual years studied.

The analysis assessed pipeline pressure limitations resulting from electric power system contingencies, as well as natural gas system contingencies that could constrain the ability of gas-fired units to generate electricity. The results showed acceptable natural gas pipeline system pressure for the increased use of the pipelines in response to contingencies on the electric power system. The study also confirmed that affected generators in New England typically have several hours to reduce output after a contingency event on the natural gas system. The use of dual-fuel capable units, the redispatch of other units, and other electric system operator actions would be necessary to mitigate adverse reliability consequences. However, while dual-fuel units may be an economical choice, environmental use permits may limit the extent of generator operations that burn oil. The EIPC assessment also discussed natural gas system operator actions that could help reduce the severity of natural gas system contingencies.

### Existing and Pending Environmental Regulations, Emissions Analyses, and Other Studies (Section 9)

Federal air, water, endangered species, and greenhouse gas standards could affect the economic performance of nuclear, renewable, and fossil-fired (coal, oil, and natural gas) generators by imposing operational constraints and additional capital costs for environmental controls. Other state and regional air, water, and carbon standards could require certain generators to minimize adverse environmental impacts, such as to reduce emissions, through the extended operation of pollution control devices or reduced electric energy production. Various elements of the power system are also subject to state, regional, federal, and international environmental land-use, permitting, and siting regulations, many of which have protracted review periods that can complicate or delay planning, development, or the implementation of proposed transmission and generation improvements.

The ISO has been assessing the potential impact of existing and proposed US Environmental Protection Agency (EPA) and state regulations on the operation of existing fossil steam units and other types of generation in the region. The actual compliance timelines will depend on the timing and substance of the final regulations and site-specific circumstances of the electric generating facilities, including their economic performance. Most of the at-risk capacity faces compliance or retirement decisions later this decade and extending into the early part of the next decade. The amounts of capacity affected by existing and pending regulations are as follows:

- Approximately 10.9 GW of existing fossil and nuclear capacity in New England may need to modify their cooling water intake structures for mitigating impingement. Existing facilities with a capacity factor below 8% over a two-year consecutive period may petition for less stringent standards for mitigating impingement. The regulation became effective October 14, 2014, and individual generating facilities are subject to case-by-case regulatory review.

- EPA-proposed revisions to the Effluent Limitation Guidelines under the Clean Water Act (CWA) are under court challenge but could affect up to 6 GW in New England. The agency is already considering the proposed rule in water permits under its review.

- EPA has finalized a more stringent ozone standard and implementation regulations on fine particulate matter, but these could require up to 17.45 GW of fossil-fueled generators across southern New England and 21 GW total across the entire region to make operational changes and potential pollution control retrofits.

- Most of the 6.4 GW of existing coal- and oil-fired generators comply with the Mercury and Air Toxics Standards, which went into effect April 16, 2015. On June 29, 2015, the US Supreme Court ruled that EPA interpreted the federal Clean Air Act (CAA) unreasonably when it failed to consider the cost of compliance and remanded the rule back to the lower court for further action. State air toxics regulations remain in force, however, and air toxics controls will continue to operate for most units in New England.

- Fossil fuel plants will likely achieve compliance with the Clean Power Plan for carbon emissions through the existing Regional Greenhouse Gas Initiative, which is a cap-and-trade system.

The ISO has calculated the historical systemwide emissions for several years. Although total energy production declined by 4% from 2012 to 2013, system emissions remained about the same during the same period. This was driven by a decrease in natural gas generation, resulting from high gas prices and the limited availability of this fuel in the winter, which was offset by an increase in oil and coal generation. Total nitrogen oxides (NOX) system emissions were 20.32 kilotons (ktons) for both 2012 and 2013. Sulfur dioxide (SO2) system emissions increased 9%, from 16.61 ktons in 2012 to 18.04 ktons in 2013. Carbon dioxide (CO2) system emissions decreased 3% during the same period, from 41,975 ktons in 2012 to 40,901 ktons in 2013. The 2013 system emission rates for NOX, SO2, and CO2 were higher than 2012 values, increasing by 3%, 14%, and 2%, respectively. Future regional emissions could increase even with more-stringent regulations, if oil-fired generating units need to operate during natural gas shortages or because nuclear units have retired or are on outages. The greater use of lower-emitting fuels, energy efficiency, wind and photovoltaic resources, imports from neighboring systems, and environmental controls could decrease regional emissions further.

FERC is pursuing an integrated relicensing review for several hydroelectric projects located on the Connecticut River, with a completion deadline of April 2018 for all relicensing activities. In addition to energy production, relicensing must take into consideration the requirements for adequately and equitably protecting and mitigating damage to fish and wildlife (and their habitats) and the recommendations of state and federal fish and wildlife agencies. The ISO is monitoring such proceedings to assess the impacts of operational restrictions, including the maintenance of minimum flows, on the ability of hydroelectric generators to offer regulation and reserve services.

### Integrating Renewable and Other Resources to Meet System Needs (Section 10)

National and state policies, such as state Renewable Portfolio Standards (RPSs), are stimulating the need for, and the development of, renewable resources and energy efficiency in the region, which reduce emissions. Options for meeting, or exceeding, the region’s RPS targets include developing the renewable resources in the ISO queue, importing qualifying renewable resource energy from neighboring areas, building new renewable resources in New England not yet in the queue, developing behind-the-meter projects, and using eligible renewable fuels in existing generators. In addition, load-serving entities can make state-established alternative compliance payments if their qualified renewable resources fall short of providing sufficient renewable energy credits (RECs) to meet the RPSs. Alternative compliance payments also can serve as a price cap on the cost of RECs.

A number of wind projects have interconnected to areas of the regional power system that have favorable wind conditions but are electrically remote and weak, and additional wind projects are proposed for these areas. These facilities pose operational and planning challenges associated with voltage and stability performance. In addition, the basic assumptions applied in the interconnection studies conducted for determining a facility’s specific interconnection requirements are not designed to address all possible system conditions that can arise during daily operating conditions of the system, which may further constrain wind output under stressed system conditions (e.g., during transmission maintenance outages). The existing transmission system is insufficient to support the integration of the northern Maine wind generation currently in the interconnection queue, and the system could require major upgrades to accommodate this generation. The ISO is working with regional stakeholders to reduce the processing time for generator interconnection requests involving inverter-based generator projects, which can help developers build needed network transmission. Needed system upgrades could be developed using several processes, among them, the ETU process, discussed in Sections 1.3.4 and 2.1.1.5.

Regional and industry efforts are assisting in integrating renewable resources, demand resources, and smart grid technologies into the system. The ISO has improved operating procedures and processes, participated in the development of industry standards, and conducted studies that inform developers and policymakers on how renewable resource development affects system performance.

The ISO implemented a process for independently forecasting wind generation, which improves situational awareness and assists asset owners with bidding in the wholesale markets. Plans call for further integrating wind into the economic dispatch. The ISO also is developing ways of improving the load-reducing effects of photovoltaics located behind the meter into the load-forecasting processes to support the efficient and reliable integration of increasing amounts of PV. The ISO and the states are addressing how to best maintain reliability with the growing penetrations of these PV installations, including implementing new rules for inverter-based resources that must meet revised interconnection requirements set by IEEE standards.

The ISO conducted a strategic transmission analysis for wind resource integration in subareas of Maine and Vermont. The studies identified transmission system constraints of both the local and regional transmission systems, and the analysis demonstrated the benefits of including robust local voltage-control capability to the wind-generation sites. The studies showed conceptual transmission improvements that would reliably integrate the wind resources while meeting NPCC bulk power system (BPS) requirements. The conceptual transmission improvements include static and reactive dynamic support to provide voltage control and two thyristor-controlled series compensators, which are a type of flexible alternating-current transmission system (FACTS). The study also showed the need for synchronous condensers that can help meet BPS requirements after the addition of the studied wind resources.

The results of the Strategic Transmission Analysis: Wind Integration Study will be used in the 2015 economic studies of onshore wind development in Maine. These studies will show the economic benefits of relieving transmission constraints in the Keene Road area and other areas of Maine. The results also may be used to identify the need for future market-efficiency transmission upgrades and for projects facilitating the integration of wind resources. A third 2015 economic study will examine the interconnection of offshore wind resources along the southeastern coast of New England.

### Federal, State, and Regional Initiatives that Affect System Planning (Section 11)

The ISO continuously works with a wide variety of policymakers and other regional and interregional stakeholders on initiatives that influence electric power system planning. These groups include the New England Conference of Public Utilities Commissioners (NECPUC), the New England States Committee on Electricity (NESCOE), the New England governors, the Consumer Liaison Group (CLG), and others. The planning process will continue to evolve in response to compliance with FERC orders and other policy developments, especially under FERC Order No. 1000. For example, Renewable Portfolio Standards promote the development of wind energy, and economic studies inform policymakers of the potential benefits of transmission expansion.

The Quadrennial Energy Review (QER) by DOE, which concluded in 2015, is a comprehensive analysis of the nation’s energy and electricity production and delivery systems. It includes discussions of natural gas bottlenecks affecting New England, the short-term benefits of the winter reliability program, and the long-term need for additional pipeline infrastructure that increases access to Marcellus shale gas.

The Connecticut Department of Energy and Environmental Protection (CT DEEP) and the electric distribution companies of Massachusetts and Rhode Island are in the process of issuing a request for proposals for clean energy and transmission. The purpose of the three‐state procurement is to identify projects that could help the procuring states meet their clean energy goals in a cost‐effective manner and that bring additional regional benefits, such as lower costs to consumers. The soliciting parties decided to act jointly to open the possibility of procuring large‐scale projects that no one state could procure on its own.

Regional initiatives continue to support the development and integration of new technologies and the enhancement of operating and planning procedures to improve system reliability. Several of the technology developments and challenges affecting the planning of the New England region involve integrating smart grid equipment, improving operator awareness and system modeling through the use of phasor measurement units (PMUs), and using high-voltage direct-current (HVDC) facilities and FACTS devices.

The ISO’s Transmission Planning Process Guide and Transmission Planning Technical Guide document the regional transmission planning process and identify technical requirements for planning studies. The ISO is revising the Transmission Planning Process Guide to align with final FERC Order No. 1000 requirements. In response to stakeholder requests, the ISO is also continuing to work with stakeholders to examine suitable assumptions for use in planning studies, which may more fully consider the probability of resource outages, system transfers, and system load levels. The Transmission Planning Technical Guide will be updated to reflect any required changes.

## Conclusions

The 2015 Regional System Plan identifies system needs and plans for meeting these needs for 2015 through 2024. RSP15 also discusses risks to the regional electric power system; the likelihood, timing, and potential consequences of these risks; and mitigating actions. Some of the highlights of RSP15, as discussed in Section 12, are as follows:

- Compliance with FERC Order No. 1000 requires competitive processes to select longer-term transmission infrastructure projects not already planned. The order also requires the determination of transmission projects for meeting public policy objectives and increased coordination with interconnected neighboring regions in the Eastern Interconnection. RSP15 complies with the intraregional and interregional planning processes required by the order.

- Forecasts of the regional net peak and annual energy show flat growth resulting from the additions of PV and EE, which are reflected in the planning processes.

- Needed capacity and operating reserves are provided through the wholesale markets, but resource retirements and the successful integration of variable resources pose future challenges to the reliable and economic operation of the system. Studies of expected system conditions show that developing new resources in the combined NEMA/SEMA/RI area would provide the greatest reliability benefit.

- The region has tremendous potential for developing renewable resources and is actively addressing several key technical challenges to the successful integration of these resources. For example, interconnection requirements and forecasting methods are being updated to improve the reliable operation of the system with increasing amounts of PV. Additionally, studies are ongoing to successfully integrate wind generators, most of which are in remote locations.

- Environmental regulations, other public policies, and economic considerations, all will affect the future mix of regional resources, such as to influence the retirement of oil and coal generators and the addition of natural-gas-fired generation.

- Transmission projects have improved regional reliability and continue to support the efficient operation of the markets. The Interstate Reliability Project, which is under construction, and the Greater Boston Reliability Project represent the most recent major 345 kV projects required to meet regional reliability. These projects will improve the ability to move power to all areas of the system. The interconnection process for elective transmission upgrades has been improved, and ETU projects are in various stages of development with the potential to provide access to renewable resources in remote areas of New England and neighboring regions, including Atlantic Canada and Québec.

- The need for ISO New England to coordinate planning activities with other systems will continue growing, particularly to provide access to a greater diversity of resources, including hydro and variable resources, and to meet environmental compliance obligations.

- The regional reliance on natural-gas-fired generation, coupled with natural gas pipeline constraints, pose reliability issues and can lead to price spikes in the wholesale electricity markets. Recent improvements to the wholesale markets have been designed to improve regional reliability and market efficiency and to decrease electricity price volatility, but winter reliability programs will also be necessary between now and 2018 when FCM improvements are in effect. The addition of natural gas pipeline capacity or the increased use of existing LNG facilities also could improve fuel assurance and regional reliability.

- Federal and state policies and initiatives will continue to affect the planning process, such as the effect of policies promoting EE, PV, and wind resources.

Through an open process, regional stakeholders and the ISO are addressing these issues, which could include further infrastructure development, as well as changes to the wholesale electricity market design and the system planning process. Through current and planned activities, the region is working toward meeting all challenges for planning and operating the system in accordance with all requirements.

# Overview of RSP15, the Power System,
and Regional System Planning

As the Regional Transmission Organization (RTO) for New England, ISO New England (ISO) operates the region’s electric power system, administers the region’s competitive wholesale electricity markets, and conducts the regional system planning process, which includes coordinating planning efforts with neighboring areas. The main objectives of the ISO’s system planning process are as follows:

- Identify system needs and potential solutions for ensuring the short-term and long-term reliability of the system

- Facilitate the efficient operation of the markets through resource additions and transmission upgrades that serve to reliably move power from various internal and external sources to the region’s load centers

- Provide information to regional stakeholders, who can further develop system improvements

To meet these objectives and in compliance with all portions of the ISO’s Transmission, Markets, and Services Tariff (ISO tariff), including the Open Access Transmission Tariff (OATT), the 2015 Regional System Plan (RSP15) describes the ISO’s ongoing system resource and transmission planning activities covering the 10-year period to 2024.

This section provides an overview of RSP15 and the ISO’s regional system planning process required by the ISO’s tariff. For background, the section also provides highlights of the power system and the wholesale electricity market structure in New England. A summary of the various regional subdivisions the ISO uses in system planning studies is also provided.

Throughout RSP15, italicized terms indicate that a definition for the term is included within the text or footnotes; links to other documents that more fully define the more complex terms are provided. Links to relevant technical reports; presentations; and other, more detailed materials also are included throughout the report. All website addresses are current as of the time of publication. Appendix A is a list of acronyms and abbreviations used in RSP15.

## Overview of the System Planning Process and RSP15

To assess how to maintain the reliability of the New England power system, while promoting the operation of efficient wholesale electricity markets, the ISO and its stakeholders analyze the system and its components as a whole. They account for the performance of these individual elements and the many varied and complex interactions that occur among the components and that affect the overall performance of the system.

Using information on defined system needs, a variety of established signals from ISO-administered markets, and other factors, stakeholders responsible for developing needed resources can assess their options for satisfying these needs and commit to developing market resource projects. For example, stakeholders can build a new power plant to provide additional system capacity and produce electric energy. Similarly, market participants can provide active demand resources and passive demand resources (PDRs) to meet capacity needs and reduce the amount of electric energy used. They also can develop and independently fund transmission upgrades to interconnect a merchant transmission facility (MTF) to the ISO system. These upgrades and supply and demand resource alternatives could result in modifying, offsetting, or deferring proposed regulated transmission upgrades. To the extent that stakeholder responses to market signals are not forthcoming or adequate to meet identified system needs, the planning process requires the ISO either to acquire transmission solutions through a competitive solicitation or to work with incumbent transmission owners to develop its own transmission solutions, depending on the identified year of need. All transmission upgrades must meet reliability performance requirements.

### Types of Transmission Upgrades

Attachment N of the OATT, “Procedures for Regional System Plan Upgrades,” defines several categories of transmission upgrades that can be developed to address various types of defined system needs, such as reliability and market efficiency. Transmission upgrades resulting from system changes proposed by individual proponents include, for example, generator-interconnection-related upgrades and elective transmission upgrades (ETUs). Section 6.5 discusses specific transmission upgrades.

#### Reliability Transmission Upgrades

Reliability transmission upgrades (RTUs) are necessary to ensure the continued reliability of the New England transmission system, in compliance with applicable reliability standards. An RTU also may provide market-efficiency benefits. To identify the transmission system facilities required to maintain reliability and system performance, the ISO evaluates the following factors using reasonable assumptions for forecasted load and the availability of generation and transmission facilities (based on maintenance schedules, forced outages, or other unavailability factors):

- Known changes in available supply resources and transmission facilities, such as anticipated transmission enhancements, considering elective transmission upgrades and merchant transmission facilities (see Section 2.1.1.5); the addition of demand resources or new or previously unavailable generators; or generator retirements

- Forecasted load, which accounts for growth, reductions, and redistribution throughout the grid

- Acceptable stability response

- Acceptable short-circuit performance

- Acceptable voltage levels

- Adequate thermal capability

- Acceptable system operability and responses (e.g., automatic operations, voltage changes)

#### Market Efficiency Transmission Upgrades

Market efficiency transmission upgrades (METUs) are primarily designed to reduce the total net production cost to supply the system load. The ISO categorizes a proposed transmission upgrade as a METU when it determines that the net present value of the net savings in the total cost to supply system load with and without the METU is greater than the net present value of the carrying cost of the identified upgrade. In determining the net present value of the costs of power system resources, the ISO takes into account applicable projected economic factors, as follows:

- Energy costs

- Capacity costs

- Cost of supplying total operating reserve

- System losses

- Changes in available supply resources and transmission facilities, such as through anticipated transmission enhancements, considering elective transmission upgrades and merchant transmission facilities; the addition of demand resources or new or previously unavailable generators; or generator retirements

- Load growth

- Fuel costs and availability

- Generator outages

- Release of locked-in generating resources

- Present-worth factors for each project specific to the owner of the project

- Present-worth period not exceeding 10 years

- Cost of the project

Analyses can include historical information from market reports and special studies, for example, and they report on cumulative net present value annually over the study period.

#### Public Policy Transmission Upgrades

A public policy transmission upgrade (PPTU) is an addition or upgrade designed to meet transmission needs driven by public policy requirements. The planning process for PPTUs includes opportunities for input from the New England States Committee on Electricity (NESCOE; see Section 11.2.1) and the Planning Advisory Committee (PAC; see Section 2.1.5). The ISO plans to initiate the public policy planning process, as set out in Attachment K, in accordance with its compliance filing for FERC Order No. 1000 (see Sections 2.1.7).

#### Generator Interconnection Upgrades and Generator-Interconnection-Related Upgrades

A generator interconnection upgrade is an addition or modification to the New England transmission system for interconnecting a new or existing generating unit whose capability to provide energy or capacity is materially changing and increasing, whether or not the interconnection is for meeting the Network Capability Interconnection Standard or the Capacity Capability Interconnection Standard. Costs of generator-interconnection-related upgrades typically are allocated to the generator owner in accordance with the OATT.

#### Elective Transmission Upgrades and Merchant Transmission Facilities

An elective transmission upgrade is an interconnection or upgrade to the pool transmission facilities (PTFs) that are part of the New England transmission system and subject to the ISO’s operational control pursuant to an operating agreement. ETUs are independently developed facilities funded by one or more entities that have agreed to pay for all the costs of the upgrade and thus assume the full market risk of development. ETUs are not reliability transmission upgrades, METUs, or generator-interconnection-related upgrades.

The ETU process is the mechanism available to integrate new merchant transmission facilities into the regional transmission system. The process provides an option for project sponsors to propose, develop, and fund transmission development within New England or connecting to neighboring systems. Such transmission may result in strengthening electrically weak portions of the regional transmission network, enhancing generator deliverability, or facilitating the integration of renewable resources.

The Federal Energy Regulatory Commission (FERC) accepted the ISO’s proposal to improve the administration of ETUs. This process involves several actions. It creates new ETU interconnection procedures, with requirements and obligations similar to those of generators, so that ETUs can establish and maintain a meaningful position in the ISO Generator Interconnection Queue (the queue). It also defines a new form of interconnection service so that certain tie lines with neighboring areas can be designed to deliver capacity into New England and have these interconnection service rights preserved as the New England system changes over time. The market rules will also be conformed to ensure that these resources can deliver capacity and energy into the wholesale power markets.

### Transmission Planning Guides

The ISO developed guides that document both the implementation of the regional planning process described in Attachment K of the OATT and the associated technical assumptions. The Transmission Planning Process Guide (Process Guide) contains details on the existing regional system planning process and how transmission planning studies are performed through the open regional stakeholder process. It discusses the development of needs assessments and solution studies, including the opportunities for stakeholder involvement. The Transmission Planning Technical Guide (Technical Guide) describes the current standards, criteria, and assumptions used in transmission planning studies of the regional power system. Both guides include stakeholder input.

The ISO has received valuable stakeholder feedback on its current practices and is reviewing the bases for these practices (see Section 11.3.2). The ISO also will revise the Process Guide to reflect changes in the planning process required by FERC Order No. 1000 (see Sections 2.1.7).

### Planning Studies Conducted for and Summarized in RSP15

The ISO conducts numerous regional and local-area studies throughout the year during all stages of planning for ensuring the reliability of the power system. FERC, interregional entities, the states, and others, also sponsor planning initiatives for improving the power system and interregional coordination. Throughout RSP15, the ISO’s major studies and initiatives, as well as those conducted by others, both individually and jointly with the ISO, are summarized consistent with the steps used in the planning process:

- Ten-year load forecasts through 2024 of peak demand and the annual use of electric energy

- Regional passive demand resources for 2015 to 2018 and an energy-efficiency (EE) forecast from 2019 to 2024

- A forecast of photovoltaic (PV) development in the region

- The development of a net forecast

- Analyses of the amount, operating characteristics, and locations of needed capacity and operating reserves

- Analyses of Forward Capacity Market and locational Forward Reserve Market resources that meet system needs

- Implications of generator retirements on transmission system requirements and potential locations for developing new resources (i.e., strategic transmission analyses)

- Studies that identify resource amounts and locations that can meet long-term system needs (i.e., market-resource alternatives [MRA] analysis)

- Assessments of systemwide and local-area needs (i.e., needs assessments) that include critical load levels, and transmission solutions to meet these needs (i.e., solution studies)

- Planning coordination studies and initiatives affecting the planning of the system

- Northern ISO/RTO planning coordination studies

- Eastern Interconnection Planning Collaborative (EIPC) activities

- Other joint planning studies with neighboring regions

- Assessments of regional strategic planning needs and solutions, including studies in support of the ISO’s Strategic Planning Initiative (SPI), which address the following topics:

- Resource performance and fuel certainty, including power system operating experience and the operation and infrastructure of the natural gas system

- Effects of generator compliance with environmental regulations on generator operating requirements and the need for remediation measures

  - Operating and planning for expansion of renewable resources, including the potential need for transmission development for wind generation and the identification of interconnection issues for distributed generation (DG)

  - Studies of the economic and environmental performance of the system for various future resource- and transmission-expansion scenarios

- ISO development and integration of new technologies and enhancements to operating and planning procedures to improve system reliability

- Federal, state, and regional initiatives and governmental activities and policies affecting the planning system

The material effects of the energy-efficiency forecast and the PV forecast have been reflected in all RSP analyses, including the following:

- Resource adequacy assessments

- Transmission needs assessments

- Transmission solutions studies

- Proposed Plan Application (PPA) studies

- System impact studies

- Economic studies

- Interregional studies

### Accounting for Uncertainty

Regional system planning must account for the uncertainty in assumptions made about the next 10 years stemming from changing demand, fuel prices, technologies, market rules, planning processes, and environmental requirements; the development and retirement of resources; the physical conditions under which the system might be operating; and other relevant events. The following major factors may vary RSP15 results and conclusions and ultimately affect the development and timing of needed transmission facilities and generation, demand, and market resources:

- Forecasts of demand, energy efficiency, and distributed generation, which are dependent on the economy, new building and federal appliance-efficiency standards, state goals for the implementation of EE and DG programs, and other considerations

- Resource availability, which is dependent on physical and economic parameters that affect the performance, development, and retirement of resources

- Environmental regulations and compliance strategies, which can vary with changes in public policies, economic parameters, and technology development

- The deployment of new technologies, which may affect the physical ability and economic viability of new types of power system equipment and the efficiency of operating the power system

- Fuel price forecasts, which change with world markets and infrastructure development

- Market rules and public policies, which can alter the development of market resources

- Siting and construction delays and changes to the system

While each RSP represents a snapshot in time, the planning process is continuous; the ISO revisits the results as needed when new information becomes available. The ISO has been improving the information provided to stakeholders, especially the required timing of transmission projects.

### Working with the Planning Advisory Committee and Other Committees

To conduct the system planning process, the ISO holds an open and transparent stakeholder forum with the Planning Advisory Committee (PAC). PAC membership is open to all and currently includes representatives from state and federal governmental agencies; participating transmission owners (PTOs); ISO market participants; other New England Power Pool (NEPOOL) members; consulting companies; manufacturers; and other organizations, such as universities and environmental groups. The PAC has met 14 times from fall 2014 to summer 2015 to discuss draft scopes of work, assumptions, and draft and final study results on a wide range of issues. In addition, subgroups of the PAC have discussed the energy-efficiency forecast, the distributed generation forecast, environmental issues, and economic studies.

Other committees are involved in the system planning process. The Reliability Committee (RC) provides advisory input on planning procedures, final Proposed Plan Applications, regional transmission cost allocations, and other activities that affect the design and oversight of reliability standards for the power system. The Transmission Committee provides advisory input on the general tariff provisions of the OATT and amendments to the Transmission Owner Agreement. The Markets Committee provides advisory input on changes proposed by the ISO to Market Rule 1 and market procedures. Stakeholders who advise ISO New England or its neighboring ISO/RTOs on system planning matters have the opportunity to meet as a unified group through the Interregional Planning Stakeholder Advisory Committee (IPSAC; see Section 7.5).

### Providing Information to Stakeholders

In addition to publishing the Regional System Plan and specific needs assessments and solutions studies to provide information to stakeholders, the ISO issues the RSP Project List. The list includes the status of transmission upgrades during a project’s lifecycle and is updated several times per year (see Section 6.5). RSP15 incorporates information from the June 2015 list.

Additionally, the ISO posts on its website detailed information supplemental to the RSP process, such as the Regional Electricity Outlook (REO), Annual Markets Report (AMR), Wholesale Markets Project Plan (WMPP), presentations, and other reports. The ISO also makes available databases used in its analyses and related information required to perform simulations consistent with FERC policies and the ISO Information Policy requirements pertaining to both confidential information and critical energy infrastructure information (CEII) requirements. Stakeholders can use this information and data to conduct their own independent studies.

### FERC Order No. 1000 on Transmission Planning and Cost Allocation

FERC Order No. 1000 requires revisions to the transmission planning and cost-allocation processes that changes the way ISO had been planning the transmission system in New England since 2001. On May 18, 2015, ISO New England made a compliance filing in response to FERC’s March 19, 2015, Order on Rehearing and Compliance. The March 19, 2015, order affirmed the elimination of a transmission owner’s exclusive right to build and own transmission projects pursuant to the regional system planning process that receive regional cost allocation, and it requires the relevant transmission owner(s) to submit a “backstop” solution. The order identified the projects that could be exempted from the competitive process, and as of May 18, 2015, transmission projects classified as proposed, planned, or under construction are exempt from this process. Projects needed within the latter of three years after May 18, 2015, or three years after the completion of the project’s needs assessment, as stated in the assessment, are not subject to the FERC Order No., 1000 competitive process.

FERC Order No. 1000 in New England includes the addition of a process for an entity to become a qualified transmission project sponsor (QTPS). Entities wishing to submit a proposal to address an identified transmission need must become a QTPS. The ISO presented the QTPS process to the PAC in May and June 2015. Refer to Section 6 for a summary of RSP15 transmission system needs and the status of transmission projects.

The March 19, 2015, order also requires the ISO to evaluate the solutions offered after a public policy transmission need is identified and to select the more cost-effective or efficient project for inclusion in the Regional System Plan. For public policy projects, absent an alternative cost allocation accepted for a specific project, 70% of the costs of upgrades must be allocated throughout the region. The remaining 30% of the cost must be allocated to those states with an identified need for the public policy project. FERC reasoned that this allocation is roughly commensurate with the regional benefits of network transmission and the more localized benefits to the states whose public policies drive the transmission needs. The ISO plans to implement the public policy portion of Order No. 1000, as set out in Attachment K. RSP15, however, discusses federal, state, and regional initiatives affecting the planning process and planning studies (see Section 11).

Another FERC Order No. 1000 change is to the interregional planning process and interregional cost allocation. The ISO coordinates RSPs with neighboring systems, including both the New York ISO (NYISO) and the PJM Interconnection LLC. (i.e., the RTO for all or parts of Delaware, Illinois, Indiana, Kentucky, Maryland, Michigan, New Jersey, North Carolina, Ohio, Pennsylvania, Tennessee, Virginia, West Virginia, and the District of Columbia). Working with interregional stakeholders through the Interregional Planning Stakeholder Advisory Committee (see Section 7.5), the three ISO/RTOs identify regional system needs, regional solutions, and opportunities for interregional projects that may more efficiently meet their respective regional needs. The revised interregional cost-allocation methodology compares the costs of regional transmission projects with interregional projects and proportionally splits the savings realized by the neighboring ISO/RTO regions.

### Meeting All Requirements

In addition to complying with the ISO tariff, which reflects the requirements of FERC orders, RSP15 complies with North American Electric Reliability Corporation (NERC) and Northeast Power Coordinating Council (NPCC) criteria and standards, as well as ISO planning and operating procedures. RSP15 also conforms to transmission owner criteria, rules, standards, guides, and policies consistent with NERC, NPCC, and ISO criteria, standards, and procedures.

## Overview of the New England Electric Power System

New England’s electric power grid has been planned and operated as a unified system of its participating transmission owners and market participants. The New England system integrates resources with the transmission system to serve all regional load regardless of state boundaries. Most of the transmission lines are relatively short and networked as a grid. Therefore, the electrical performance in one part of the system affects all areas of the system. Figure 2-1 shows key facts about the New England regional electric power system.

|  | - 6.5 million households and businesses; population 14 million - Approximately 350 generators - Approximately 500 participants in the marketplace (those who generate, buy, sell, transport, and use wholesale electricity and implement demand resources) - Over 8,600 miles of transmission lines - 13 interconnections to electricity systems in New York and Canada - 136,355 gigawatt-hours (GWh), all-time annual energy served, set during 2005 - All-time peak demand of 28,130 megawatts (MW), set on August 2, 2006 - Approximately 31,000 MW of total generation for 2014 - Approximately 2,300 MW of demand resources for 2014 - Market value in 2014: - $10.47 billion total - $9.08 billion energy market - $1.06 billion capacity market - $0.33 billion ancillary services market - Approximately $7.2 billion in transmission investment since 2002; approximately $4.8 billion planned |
| --- | --- |

Figure 2-1: Key facts about New England’s electric power system and wholesale electricity markets.

Source: The 2015–2024 Forecast Report of Capacity, Energy, Loads, and Transmission (2015 CELT Report) (May 1, 2015), http://www.iso-ne.com/system-planning/system-plans-studies/celt#, the RSP Project List for June 2015; and ISO market analysis and settlements data.

Notes: The 2,300 MW of ISO demand resources do not include behind-the-meter photovoltaic resources (BTM PV) and energy efficiency provided by other customer-based programs outside the ISO markets or are otherwise unknown to the ISO. The total load on August 2, 2006, would have been 28,770 MW had it not been reduced by approximately 640 MW, which included a 490 MW demand reduction in response to ISO Operating Procedure No. 4 (OP 4), Action during a Capacity Deficiency; a 45 MW reduction of other interruptible OP 4 loads; and a 107 MW reduction of load as a result of price-response programs, which are outside of OP 4 actions. (OP 4 guidelines contain 11 actions in total that can be implemented individually or in groups, depending on the severity of the situation.) More information on OP 4 is available at http://www.iso-ne.com/static-assets/documents/rules_proceds/operating/isone/op4/op4_rto_final.pdf.

## Overview of the New England Wholesale Electricity Market Structure

New England’s wholesale electricity markets facilitate the buying, selling, and transporting of wholesale electricity, as well as ensure proper system frequency and voltage, sufficient future capacity, seasonal and real-time reserve capacity, and system restoration capability after a blackout. Stakeholders also have the opportunity to hedge against the costs associated with transmission congestion. As shown in Figure 2-1, in 2014, approximately 500 market participants completed transactions in New England’s wholesale electricity markets totaling $10.47 billion. The wholesale electricity markets and market products in New England are as follows:

- Day-Ahead Energy Market—allows market participants to secure prices for electric energy the day before the operating day and hedge against price fluctuations that can occur in real time.

- Real-Time Energy Market—coordinates the dispatch of generation and demand resources to meet the instantaneous demand for electricity.

- Forward Capacity Market (FCM)—ensures the sufficiency of installed capacity, which includes demand resources, to meet the future demand for electricity by sending appropriate price signals to attract new investment, maintain existing investment, and encourage capacity to perform both where and when needed, including during shortage events.

- Financial Transmission Rights (FTRs)—allows participants to hedge against the economic impacts associated with transmission congestion and provides a financial instrument to arbitrage differences between expected and actual day-ahead congestion.

- Ancillary services

- Regulation Market—compensates resources that the ISO instructs to increase or decrease output moment by moment to balance the variations in demand and system frequency to meet industry standards.

- Forward Reserve Market (FRM)—compensates generators for the availability of their operational capacity not generating electric energy but able to be converted into electric energy within 10 or 30 minutes when needed to respond to system contingencies, such as unexpected outages.

- Real-time reserve pricing—compensates participants with on-line and fast-start generators for the increased values of their electric energy when the system or portions of the system are short of reserves. It also provides efficient price signals to generators when redispatch is needed to provide additional reserves to meet requirements.

- Voltage support—compensates resources for maintaining voltage-control capability, which allows system operators to maintain transmission voltages within acceptable limits.

One key feature of the region’s wholesale electricity markets is locational marginal pricing for electric energy, which reflects the variations in supply, demand, and transmission system limitations effectively at every location where electric energy enters or exits the wholesale power network. In New England, wholesale electricity prices are set at over 1,000 pricing points (i.e., pnodes) on the power grid. If the system were entirely unconstrained and had no losses, all locational marginal prices (LMPs) would be the same, reflecting only the cost of serving the next megawatt increment of load by the generator with the lowest-cost electric energy available, which would be able to flow to any point on the transmission system. LMPs would differ among the pnodes if each location’s marginal cost of congestion and marginal cost of line losses differed.

Transmission system constraints, which limit the flow of the least-cost generation and create the need to dispatch more costly generation, give rise to the congestion component of an LMP. Line losses are caused by physical resistance and subsequent heat loss in the transmission system as electricity travels through transformers, reactors, and other types of equipment, resulting in less power being withdrawn from the system than was injected. Line losses and their associated marginal costs are inherent to transmission lines and other grid infrastructure as electric energy flows from generators to loads. As with the marginal cost of congestion, the marginal cost of losses affects the amount of generation that must be dispatched. The ISO operates the system to minimize total system costs, while recognizing physical limitations of the system.

The ISO annually assesses the wholesale electricity markets to better understand problems to be addressed and to determine whether the market design or other measures warrant any changes. The ISO uses this information and the results of RSP studies to develop market design changes through an open stakeholder process. Several market design projects address some of the challenges identified in the Strategic Planning Initiative. For example, one project (i.e., modifications to the FCM) will provide incentives that encourage improved resource performance (see Section 8.4.3).

## Overview of System Subdivisions Used for Analyzing and Planning the System

To assist in modeling, analyzing, and planning electricity resources in New England, the region and the system have been subdivided in various ways. These categories are included in the discussions throughout the RSP and are summarized below.

The system’s pricing points include individual generating units, load nodes, load zones (i.e., aggregations of load pnodes within a specific area), and the Hub. The Hub is a collection of 32 locations in central New England where little congestion is evident. It typically has a price intended to represent an uncongested price for electric energy, which is used as a price index and point of exchange for bilateral transactions in the energy market. The Hub also facilitates energy trading and enhances transparency and liquidity in the marketplace. In New England, generators are paid the LMP for electric energy at their respective nodes, and participants serving demand pay the price at their respective load zones.

New England is divided into eight electric energy load zones used for wholesale energy market settlement: Maine (ME), New Hampshire (NH), Vermont (VT), Rhode Island (RI), Connecticut (CT), Western/Central Massachusetts (WCMA), Northeast Massachusetts and Boston (NEMA), and Southeast Massachusetts (SEMA). Import-constrained load zones are areas within New England that do not have enough local resources and transmission-import capability to serve local demand reliably or economically. Export-constrained load zones are areas within New England where the available resources, after serving local load, exceed the areas’ transmission capability to export the excess electric energy. Reliability regions, which reflect the operating characteristics of, and the major constraints on, the New England transmission system, can have the same boundaries as load zones.

A capacity zone is a geographic subregion of the New England Balancing Authority Area that may represent load zones that are export constrained, import constrained, or contiguous—neither export nor import constrained. The Forward Capacity Auctions (FCAs) use capacity zones, which are subject to annual review. FCA #9 capacity zones were Connecticut, NEMA/Boston, and SEMA/RI as import-constrained zones, and a “Rest-of-Pool” zone (i.e., the area excluding the other zones) (see Sections 4.1.2 and 4.1.3). For FCA #10, Southeast New England was identified as an import-constrained capacity zone, while the Northern New England capacity zone was evaluated but not identified as an export-constrained capacity zone. The West/Central Massachusetts load zone continues to form the basis for the Rest-of-Pool zone for FCA #10. Finally, the existing Connecticut capacity zone was evaluated but not modeled as an import-constrained capacity zone. The region also currently has four reserve zones—Greater Connecticut; Greater Southwest Connecticut (SWCT); NEMA/Boston; and the rest of the system (Rest-of-System, ROS), which excludes the other, local reserve zones.

Additionally, the region is divided into 19 demand-resource dispatch zones, which are groups of nodes used to dispatch real-time demand-response (RTDR) resources or real-time emergency generation (RTEG) resources. These allow for a more granular dispatch of active demand resources at times, locations, and quantities needed to address potential system problems without unnecessarily calling on other active demand resources. Figure 2-2 shows the dispatch zones the ISO uses to dispatch FCM active demand resources.

Figure 2-2: Active-demand-resource dispatch zones in the ISO New England system.

The ISO also has established 13 subareas of the region’s electric power system. These subareas form a simplified model of load areas connected by the major transmission interfaces across the system. The simplified model illustrates possible physical limitations to the reliable and economic flow of power that can evolve over time as the system changes.

Figure 2-3 shows the ISO subareas and three external balancing authority areas. While transmission planning studies and the real-time operation of the system use more detailed models, the subarea representation shown in Figure 2-3 is suitable for some RSP15 studies of resource adequacy, operating-reserve requirements, production cost, and environmental emissions.

|  | Subarea Designation | Region or State |
| --- | --- | --- |
|  | BHE | Northeastern Maine |
|  | ME | Western and central Maine/ Saco Valley, New Hampshire |
|  | SME | Southeastern Maine |
|  | NH | Northern, eastern, and central New Hampshire/eastern Vermont and southwestern Maine |
|  | VT | Vermont/southwestern New Hampshire |
|  | Boston (all capitalized) | Greater Boston, including the North Shore |
|  | CMA/NEMA | Central Massachusetts/ northeastern Massachusetts |
|  | WMA | Western Massachusetts |
|  | SEMA | Southeastern Massachusetts/ Newport, Rhode Island |
|  | RI | Rhode Island/bordering Massachusetts |
|  | CT | Northern and eastern Connecticut |
|  | SWCT | Southwestern Connecticut |
|  | NOR | Norwalk/Stamford, Connecticut |
|  | NB, HQ, and NY | New Brunswick (Maritimes), Hydro­Québec, and New York external balancing authority areas |

Figure 2-3: RSP15 geographic scope of the New England electric power system.

Notes: Some RSP studies investigate conditions in Greater Connecticut, which combines the NOR, SWCT, and CT subareas. This area has similar boundaries to the State of Connecticut but is slightly smaller because of electrical system configurations near the border with western Massachusetts. Greater Southwest Connecticut includes the southwest and western portions of Connecticut and consists of the NOR and SWCT subareas. NB includes New Brunswick, Nova Scotia, and Prince Edward Island (i.e., the Maritime provinces) plus the area served by the Northern Maine Independent System Administrator (USA).

# Forecasts of New England’s Peak Demand, Annual Use of Electric Energy, Energy Efficiency, and Distributed Generation

This section discusses the individual forecasts of gross demand, energy efficiency, and photovoltaics for 2015 through 2024. Energy efficiency is considered a resource, and behind-the-meter distributed generation is considered a reduction in demand, but for study purposes, their combined growth reduces the forecasts of gross peak demand and the gross annual use of energy. These resultant net demand forecasts provide key inputs for determining the region’s resource adequacy requirements for future years (see Section 4), evaluating the reliability and economic performance of the electric power system under various conditions (Section 10.4), and planning needed transmission improvements (Section 6). This section also discusses the application of both the net peak demand and the net annual energy forecasts to planning studies.

The methodology for forecasting the gross demand, energy efficiency, and photovoltaic installations in RSP15 are generally similar to RSP14’s methodology. The historical loads and both the economic and demographic factors drive the forecasts of the gross peak and gross annual demand for electric energy, New England-wide and in individual states and subareas. Public policies are key inputs to the growth of energy-efficiency and photovoltaic resources for the 10-year RSP planning horizon. The EE forecast reflects participation in the ISO’s Forward Capacity Market. The RSP15 PV forecast reflects PV participation in the wholesale energy markets, better quality historical data of PV installations and production, and some key economic factors affecting future PV development. RSP15 also provides projections for PV energy production.

## ISO New England Gross Demand Forecasts

The ISO gross demand forecasts are estimates of the amount of electric energy the New England states will need annually and during seasonal peak hours. This year’s gross demand forecast horizon runs from 2015 through winter 2024/2025. Each forecast cycle updates the data for the region’s historical annual use of electric energy and peak loads by adding another year of data to the sample, incorporating the most recent economic and demographic forecasts, and making adjustments for resettlement that include meter corrections.

The seasonal gross peak load and gross energy-use forecast, as published in the 2015–2024 Forecast Report of Capacity, Energy, Loads, and Transmission (2015 CELT Report) and used for planning studies, fully accounts for historical naturally occurring energy efficiency and future federal appliance standards. The gross forecast does not expressly reflect the future reduction in peak demand and energy use that will result from the passive demand resources that clear the Forward Capacity Auctions and the energy-efficiency forecast (described in Section 3.2). Similarly, behind-the-meter distributed resources are not fully accounted for in the gross load forecast (see Section 3.3). Other types of behind-the-meter distributed resources not participating in the FCM, however, are included in the gross load forecast as part of the historical growth of these types of resources.

The price of electricity and other economic and demographic factors drive the annual consumption of electric energy and the growth of the seasonal peak. Compared with the economic forecast in RSP14, the forecast in RSP15 shows less growth in 2013 to 2015, higher growth in 2016 to 2018, and the same growth for the remaining years. The RSP15 forecast continues to use real gross domestic product (GDP) for energy forecasting, with federal efficiency standards subtracted from the energy forecast.

Table 3-1 summarizes the ISO’s forecasts of gross annual electric energy use and gross seasonal peak load (50/50 and 90/10) for New England overall and for each state. RSP15 forecasts of gross annual energy use, and both summer and winter gross seasonal peak conditions are similar to those published in RSP14. Compared with the RSP14 forecast, the RSP15 50/50 load forecast for gross summer peak demand is 220 MW lower in 2015 and 50 MW lower in 2023.

Table 3-1
Summary of Annual Gross Electric Energy Use and Gross Peak Demand Forecast
for New England and the States, 2015/2016 and 2024/2025

| State(a) | Net Energy for Load (1,000 MWh) |  |  | Summer Peak Loads (MW) |  |  |  |  | Winter Peak Loads (MW) |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | 50/50 |  | 90/10 |  | CAGR(b) | 50/50 |  | 90/10 |  | CAGR(b) |
|  | 2015 | 2024 | CAGR(b) | 2015 | 2024 | 2015 | 2024 |  | 2015/16 | 2024/25 | 2015/16 | 2024/25 |  |
| CT | 34,430 | 37,580 | 1.0 | 7,450 | 8,185 | 8,135 | 8,925 | 1.0 | 5,770 | 6,020 | 5,940 | 6,190 | 0.5 |
| ME | 12,570 | 13,480 | 0.8 | 2,145 | 2,325 | 2,285 | 2,485 | 0.9 | 1,975 | 2,035 | 2,030 | 2,095 | 0.4 |
| MA | 63,825 | 70,915 | 1.2 | 13,125 | 15,000 | 14,155 | 16,160 | 1.5 | 10,400 | 11,220 | 10,695 | 11,515 | 0.8 |
| NH | 12,300 | 13,595 | 1.1 | 2,610 | 2,995 | 2,815 | 3,250 | 1.6 | 2,065 | 2,230 | 2,145 | 2,310 | 0.8 |
| RI | 8,875 | 9,490 | 0.7 | 1,965 | 2,205 | 2,210 | 2,490 | 1.3 | 1,435 | 1,500 | 1,480 | 1,545 | 0.5 |
| VT | 6,750 | 7,210 | 0.7 | 1,105 | 1,190 | 1,150 | 1,245 | 0.9 | 1,090 | 1,165 | 1,105 | 1,180 | 0.7 |
| ISO | 138,745 | 152,280 | 1.0 | 28,395 | 31,905 | 30,745 | 34,555 | 1.3 | 22,740 | 24,175 | 23,400 | 24,835 | 0.7 |

- A variety of factors cause state growth rates to differ from the overall growth rate for New England. For example, Connecticut has the fastest-growing economy in New England, and Maine has the slowest-growing economy in the region.

- “CAGR” stands for compound annual growth rate.

Net energy for load (NEL) is the generation output within an area, accounting for electric energy imports from other areas and electric energy exports to other areas. It also accounts for system losses and excludes the electric energy used to operate pumped-storage hydroelectric plants. The compound annual growth rate (CAGR) for the ISO’s electric energy use is 1.0% for 2015 through 2024, 1.3% for the summer peak, and 0.7% for the winter peak. The systemwide load factor (i.e., the ratio of the average hourly load during a year to peak hourly load) declines over the forecast horizon, from 55.8% in 2015 to 54.5% in 2024.

Figure 3-1 shows the ISO’s actual gross summer peak demand (i.e., the load reconstituted to include the megawatt reduction attributable to ISO New England Operating Procedure No. 4 [OP 4], Action during a Capacity Deficiency, and FCM passive demand resources), the 50/50 gross load forecast, and the 90/10 gross load forecast. The actual gross load has been near or has exceeded the 90/10 forecast six times over the last 23 years because of hot and humid weather conditions, and it has been near or above the 50/50 gross forecast 11 times during the same period.

Figure 3-1: The ISO’s actual summer peak loads (i.e., reconstituted to include the megawatt reductions from OP 4 actions and FCM passive demand resources) and the 50/50 and 90/10 forecasts, 1992 to 2013 (MW).

Note: The forecasted load values are the first-year values of the CELT forecast for each year. For example, the forecasted loads for 2014 are the loads for the first year of the 2014 CELT Report.

## Energy-Efficiency Forecast for New England

The FCM provides the ISO with a comprehensive understanding of the savings in energy use over the FCM horizon. RSP15 uses qualified EE resources as a short-term projection of EE development for 2015 through 2018. (See Section 4.1.3 for the summary of new capacity supply obligations [CSOs] for passive demand resources, which may be lower than the qualified EE resources due to market considerations.) The ISO’s regional energy-efficiency forecast, as summarized in this section for 2019 through 2024, is part of ongoing efforts to collect and analyze data in support of the long-term impacts of state-sponsored energy-efficiency programs on future demand. Individual program administrators and state regulatory agencies provide the ISO with the EE program performance and budget data used to create the forecast for 2019 to 2024. The ISO’s Energy-Efficiency Forecast Working Group assesses the forecast assumptions and offers input.

The final EE forecast for 2019 to 2024 projects the growth of annual savings in the average, total, and peak energy use for the region and each state. The results, which are based on an average annual program spending rate among the six states of $1.026 billion per year, show that the regional annual average savings in energy use attributable to new energy-efficiency measures (i.e., not cumulative from EE savings before 2019) is 1,616 GWh. The forecast for the total savings in energy use from the growth of EE projected for 2019 to 2024 is 9,696 GWh. The states’ growth of annual average savings in energy use ranges from a low of 58 GWh in New Hampshire to a high of 831 GWh in Massachusetts.

Table 3-2 shows the growth of regional passive demand resources and EE for 2015 through 2024. The ISO’s FCM-qualified EE resources are for 2015 to 2018, and the EE forecast is for 2019 to 2024. Over the entire forecast period, the regional annual peak demand is estimated to decrease by an average of 210 MW as a result of passive demand resources and energy efficiency. The forecast for the total decrease in peak demand attributable to PDRs and EE is 1,894 MW from 2015 to 2024. The states’ growth of the annual average savings in peak demand ranges from a low of 8 MW in New Hampshire to a high of 127 MW in Massachusetts.

Table 3-2 
Summary of PDR and EE Forecast Annual Electric Energy Savings and Peak Demand Reductions 
for New England and the States, 2015 and 2024 (GWh, MW)

| State | Annual Energy Savings (GWh) |  |  | Summer Peak Demand Reductions (MW) |  |  | Winter Peak Demand Reductions (MW ) |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 2015 | 2024 | CAGR(a) | 2015 | 2024 | CAGR(a) | 2015 | 2024 | CAGR(a) |
| CT | 2,554 | 4,655 | 6.9 | 420 | 732 | 6.4 | 412 | 673 | 5.6 |
| ME | 1,025 | 2,012 | 7.8 | 157 | 264 | 5.9 | 155 | 283 | 6.9 |
| MA | 4,382 | 12,018 | 11.9 | 760 | 1,904 | 10.7 | 752 | 1,782 | 10.1 |
| NH | 508 | 936 | 7.0 | 84 | 155 | 7.0 | 82 | 126 | 4.8 |
| RI | 720 | 1,860 | 11.1 | 139 | 315 | 9.5 | 138 | 306 | 9.2 |
| VT | 791 | 1,486 | 7.3 | 124 | 210 | 6 | 123 | 198 | 5.4 |
| ISO | 9,980 | 22,967 | 9.7 | 1,685 | 3,579 | 8.7 | 1,663 | 3,370 | 8.2 |

- “CAGR” stands for compound annual growth rate.

## Distributed Generation Forecast

Photovoltaic generation resources are growing significantly in New England. Because PV facilities constitute the largest segment of DG resources throughout New England and have been growing rapidly in recent years, the ISO’s analysis of DG and the DG forecast focuses exclusively on the growth of photovoltaics.

Almost all PV systems interconnect to the distribution system pursuant to state-jurisdictional interconnection standards. Because the ISO is not directly involved in the interconnection of many of these resources, it had not traditionally been aware of when and where they are installed.

The ISO sought assistance from stakeholders to help address the interrelated questions of exactly how much additional PV is anticipated in the ISO’s 10-year planning horizon and what impacts this future PV could have on the regional power grid. The ISO created a forecast of all future PV facilities—those that participate in the ISO New England markets as well as those that do not. To assist its development of a DG forecast and provide a forum to discuss DG integration issues, the ISO established the Distributed Generation Forecast Working Group (DGFWG) open to all interested parties. State agency representatives with strong knowledge of DG programs, as well as electric power distribution companies and DG program administrators, play a key role in the DGFWG. The DGFWG’s work and other stakeholder group contributions build on and contribute to other ISO efforts to address these challenges.

The ISO and the DGFWG reviewed the development of DG other than PV and concluded that either the gross load forecast or participation in the FCM captures the growth of these types of resources. The ISO, however, will continue to monitor the growth of non-PV DG and may revisit the need for developing a forecast of these resources in future RSPs.

### Development of a PV Forecast Methodology

The creation of a PV forecast must consider many uncertain factors. The viability of PV development depends on a complex interaction between both public policy and private investment. The future costs of PV and advances in its technology create additional uncertainties affecting the potential and realizable amounts of PV development. Further, as a variable energy resource (i.e., subject to variations in “fuel” determined by weather), the seasonal and diurnal fluctuations of the solar resource are important considerations. Therefore, the amounts, timing, performance characteristics, and geographic distribution of future PV development all must be factored into a PV forecast. New England state policies form the primary basis for the PV forecast. This forecast reflects an analysis of historical data and a study of economic drivers of PV.

### Data Collection and Analysis

The first step in developing the PV forecast was the compilation of information on state PV policy objectives for developing renewable resources. To this end, the ISO surveyed states for details on their specific PV policies and surveyed distribution utilities to identify existing amounts of PV.

Across the region, PV is being installed rapidly. Data gathered by the ISO indicate that, starting at relatively low levels in recent years about 250 MWAC of nameplate PV was installed in the region by the end of 2012. By the end of 2013, installed nameplate PV jumped to almost 500 MWAC, and by the end of 2014, it grew to over 900 MWAC. State policy drives much of this development. For example, Massachusetts reached its 250 MWDC PV goal four years early in 2013, and in May 2013, the commonwealth announced an expanded in-state PV goal of developing 1,600 MWDC by 2020.

How the economic building blocks or drivers that determine the cost-effectiveness of PV change will heavily influence the future path of PV deployment. These drivers include technology cost and performance, sources of financing and revenues, and federal and state incentive policies. To inform the review of PV deployment paths in New England, an ICF International analysis conducted for the ISO quantified and summarized 16 economic drivers of PV across 54 combinations of state, customer type, and project starting years. The study recognizes the complexity and uncertainties surrounding the economic drivers.

The results of the ICF report provided an analytic framework and observations that informed forecast deliberations held with the DGFWG. In summary, the largest economic drivers of PV tend to be as follows:

- System installed cost (i.e., first cost)

- Physical power revenue (e.g., wholesale, offsetting of on-site electricity loads, net metering)

- Renewable energy credit (REC) revenue

- Federal investment tax credit (ITC)

- Federal depreciation

The results also show that physical power revenues become increasingly important, while REC revenues and total federal support tend to decline. Under the study’s set of assumptions, PV projects are likely to continue to offer strong investment returns in the short term, and the current trend of development is likely to continue if all incentives can be realized. Policies implemented through periodic procurement will likely facilitate more gradual, incremental growth, while other policies will likely facilitate accelerated deployment. The relative viability of PV investment overall will decrease after the reduction in the federal investment tax credit at the end of 2016, and much more uncertainty concerning PV deployment in the region is expected for 2017 and beyond. This conclusion is despite the assumptions promoting the economic viability of PV, including the continued reductions in installed costs, improvements in system performance, increases in wholesale and retail electricity rates, and incentives from existing net-metering policies remaining intact without constraining future PV investment.

### PV Forecast

The ISO based its PV estimates on the states’ policy goals and adjusted the megawatt amounts for various factors, including a DC-to-AC nameplate conversion rate (where appropriate) and the application of the summer seasonal claimed capability (SSCC) factor. Importantly, because most states do not have PV-focused policies that extend through the ISO’s 10-year forecast horizon, the ISO assumed that PV would be installed at a constant rate equal to the last available policy year. However, because of significant uncertainty regarding how much PV existing and future PV policies will ultimately support, the ISO applied discount factors to the PV estimates. The discount factors are in addition to the above-noted adjustment factors.

#### State-by-State Annual and Cumulative PV Nameplate Capacities and Energy Production

Table 3-3 lists the state-by-state annual and cumulative PV nameplate capacities, after applying discount factors, forecast through the 10-year planning horizon. These projections include all existing and future PV in the FCM, as well as PV that does and does not participate in the ISO’s wholesale energy markets and that reduces the load the ISO observes. The corresponding total estimated summer seasonal claimed capability of the annual and cumulative capacities is 40% of the AC nameplate value. Solar typically has a zero or negligible winter SCC. Table 3-4 shows the values of PV energy production by state using state-specific capacity factors derived from three years of PV performance data in the region.

Table 3-3
New England States’ Annual and Cumulative PV Nameplate Capacities,
2015 to 2024 (MWAC)

| Year | Annual Sum of States | Annual Total Capacities (MW, AC nameplate rating) |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | CT |  | MA |  | ME |  | NH | RI | VT |
| Through 2014 | 908.8 |  | 118.8 |  | 666.8 |  | 10.4 | 12.7 | 18.2 | 81.9 |
| 2015 | 324.3 |  | 70.9 |  | 197.0 |  | 2.2 | 4.3 | 9.7 | 40.4 |
| 2016 | 386.9 |  | 89.9 |  | 229.8 |  | 2.2 | 4.3 | 20.4 | 40.4 |
| 2017 | 152.4 |  | 45.8 |  | 51.4 |  | 2.0 | 3.8 | 27.2 | 22.3 |
| 2018 | 141.7 |  | 43.1 |  | 48.4 |  | 1.8 | 3.6 | 31.0 | 13.9 |
| 2019 | 126.2 |  | 40.4 |  | 45.4 |  | 1.7 | 3.4 | 29.0 | 6.3 |
| 2020 | 117.8 |  | 40.4 |  | 45.4 |  | 1.7 | 3.4 | 20.6 | 6.3 |
| 2021 | 74.6 |  | 26.9 |  | 30.2 |  | 1.7 | 2.3 | 7.1 | 6.3 |
| 2022 | 72.9 |  | 26.9 |  | 30.2 |  | 1.7 | 2.3 | 5.4 | 6.3 |
| 2023 | 72.9 |  | 26.9 |  | 30.2 |  | 1.7 | 2.3 | 5.4 | 6.3 |
| 2024 | 70.8 |  | 26.9 |  | 30.2 |  | 1.7 | 2.3 | 5.4 | 4.2 |
| Total | 2,449.1 |  | 556.8 |  | 1,405.1 |  | 28.9 | 44.4 | 179.3 | 234.7 |

Table 3-4
Forecasted Growth of PV in the New England States,
2015 to 2024 (GWh)(a)

| Year | Annual Sum of States | States(b) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | CT | MA | ME | NH | RI | VT |
| 2014 | 864 | 104 | 661 | 10 | 11 | 21 | 58 |
| 2015 | 1,088 | 167 | 767 | 13 | 15 | 24 | 103 |
| 2016 | 1,461 | 257 | 985 | 15 | 19 | 38 | 146 |
| 2017 | 1,792 | 344 | 1,161 | 18 | 24 | 63 | 183 |
| 2018 | 1,955 | 397 | 1,213 | 20 | 28 | 94 | 204 |
| 2019 | 2,105 | 446 | 1,263 | 22 | 31 | 127 | 216 |
| 2020 | 2,240 | 493 | 1,310 | 24 | 35 | 156 | 222 |
| 2021 | 2,353 | 534 | 1,352 | 26 | 38 | 173 | 229 |
| 2022 | 2,434 | 566 | 1,384 | 28 | 40 | 180 | 236 |
| 2023 | 2,514 | 597 | 1,415 | 30 | 43 | 186 | 243 |
| 2024 | 2,593 | 629 | 1,447 | 32 | 45 | 192 | 249 |
| State Total |  | 4,534 | 12,956 | 239 | 329 | 1,256 | 2,088 |

(a) 	Forecast values include energy from FCM resources, non-FCM energy-only generators, and behind-the-meter PV (BTM PV) resources.

(b) 	The assumptions for the monthly in-service dates of PV are based on historical development of PV resources.

#### Types of PV Accounted for in the PV Forecast

Some types of PV facilities directly participate in the ISO’s wholesale electricity markets, and others act to reduce demand. The PV forecast appearing in the 2015 CELT Report accounts for four different types of PV, where each receives a different treatment in system planning studies:

- FCM resources with capacity supply obligations

- Energy-only resources (EORs), which are generation resources that participate in the wholesale energy markets but choose to not participate in the FCM

- Behind-the-meter resources already accounted for as part of the gross demand forecast

- Other behind-the-meter resources that need to be considered

System planning studies treat PV resources participating in the ISO wholesale markets as resources with sizes and locations visible to the ISO. PV resources with FCM capacity supply obligations are considered either generators or demand resources. Energy-only resources are registered in the ISO’s Customer Asset Management System (CAMS) and collect energy payments, but they do not necessarily supply the ISO with generator characteristics. Both FCM and EOR resources are market resources that do not reduce the gross demand forecast.

System planning studies, including Installed Capacity Requirement calculations, consider behind-the-meter PV as part of the demand forecast. BTM PV facilities do not participate in the ISO markets and are not registered in CAMs. For this reason, the ISO has an incomplete set of information on these resource characteristics, including their energy production data. The BTM PV resources placed in service before 2015 reduced the historical demand, which is used over the long term as a key input to the gross demand forecast. The long-term trend of historical demand, however, underestimates the future BTM PV development because recent BTM PV installations have occurred at a significantly faster rate than the long-term growth of historical demand. The ISO calculated the amounts of BTM PV already accounted for in the long-term gross demand forecast, referred to as behind-the-meter embedded load PV (BTMEL PV). The ISO then determined the additional amount of BTM PV that system planning studies must consider to be reductions to the gross demand forecast. This is called behind-the-meter nonembedded load PV (BTMNEL PV).

With stakeholder input from the DGFWG, the ISO classified the PV forecast into future megawatts assumed to participate in the wholesale markets (FCM and EOR PV resources) and assumed to be BTM PV (both already part of the long-term gross demand forecast and the remaining amounts in the PV forecast). The classification is based on information provided by distribution owners that comprehensively identifies PV installations across the region, information concerning PV participating in the ISO markets, and additional information supplied to the ISO by the six New England states. The method holds constant for each of the states the ratio of the total PV participating in the wholesale markets to the total BTM PV for 2014 and avoids double counting the PV megawatts, including BTM PV. Figure 3-2 shows the cumulative New England PV forecast over the RSP planning horizon for each classification of PV.

Figure 3-2: Cumulative New England PV forecast for each classification of PV, 2015 to 2024 (MW).

Notes: The FCM category reflects the PV nameplate of all or portions of the FCM-qualified resources. The FCM value is held constant for years beyond FCA #9 (see Section 4.1.3). The percentage of energy-only generation in each state is held constant at the 2014 value. The gross load forecast reflects reductions of BTMEL values as part of the gross load-forecast process. The totals may not equal the previous sum of PV because of rounding and may not exactly match other tables in this section.

## The Net Demand Forecast

The net forecast is the gross demand forecast lowered by the forecasted behind-the-meter embedded PV load reductions not already considered as part of the gross annual peak forecast (i.e., BTMNEL). The net forecast is also reduced by the existing FCM-qualified passive demand resources projected for 2015 to 2018 and the 2019 to 2024 energy-efficiency forecast.

The net forecast is detailed in Figure 3-3, Figure 3-4, and Table 3-5 to Table 3-7. Figure 3-3 shows the gross annual energy-use forecast (NEL), minus the BTM PV forecast not already considered as part of the gross annual energy-use forecast, and minus both the FCM-qualified passive demand resources projected for 2015–2018 and the results of the 2019–2024 energy-efficiency forecast. The results show essentially no long-run growth in electric energy use. Similarly, Figure 3-4 shows the amounts that BTM PV and EE reduce the gross summer peak load. Table 3-5 compares the gross energy and peak demand forecasts with the net forecasts. The net summer peak is projected to increase at a more modest rate, approximately half the projected growth rate of the forecast. The net winter peak is flat (i.e., negative 0.1%) over the 10-year forecast. The BTMNEL PV does not reduce the winter peak because the winter peak occurs after dark. Table 3-6 shows the net load forecast for each of the New England states, and Table 3-7 shows the net load forecast for each of the RSP subareas.

Figure 3-3: RSP15 annual energy-use forecast (diamond); energy forecast minus PV BTMNEL (circle); energy forecast minus PV and FCM #9 PDRs through 2018 (triangle); and energy forecast minus PV BTMNEL, minus FCM PDRs, minus the energy-efficiency forecast (square) for 2019 to 2024 (MW).

Figure 3-4: RSP15 summer peak demand forecast (90/10) (diamond); demand forecast minus PV BTMNEL (circle); demand forecast minus PV and FCM #9 PDRs through 2018 (triangle); and demand forecast minus PV BTMNEL, minus FCM PDRs, minus the energy-efficiency forecast (square) for 2019 to 2024 (MW).

Table 3-5
Percentage Growth Rates of the Gross and Net Forecasts
of Annual and Peak Electric Energy Use, 2015 to 2024

|  | Gross | Net(a) |
| --- | --- | --- |
| NEL | 1.0 | 0.0 |
| 50/50 and 90/10 Summer | 1.3 | 0.6 |
| 50/50 and 90/10 Winter | 0.7 | 0.1 |

(a)	The net forecast is the gross forecast minus BTMNEL PV, minus FCM PV, minus qualified passive demand resources for 2015 to 2018, and minus energy-efficiency forecast results for 2019 to 2024.

Table 3-6
2015 State and Systemwide Net Forecasts of Annual and Peak Electric Energy Use (MWh, MW)

| Area | Energy (1,000 MWh) |  |  | Summer Peak Loads (MW) |  |  |  |  | Winter Peak Loads (MW) |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | 50/50 Load |  | 90/10 Load |  |  | 50/50 Load |  | 90/10 Load |  |  |
|  | 2015 | 2024 | CAGR | 2015 | 2024 | 2015 | 2024 | CAGR | 2015/16 | 2024/25 | 2015/16 | 2024/25 | CAGR |
| CT | 31,729 | 32,327 | 0.2 | 6,998 | 7,276 | 7,683 | 8,016 | 0.5 | 5,358 | 5,347 | 5,528 | 5,517 | 0 |
| ME | 11,531 | 11,434 | −0.1 | 1,987 | 2,056 | 2,127 | 2,216 | 0.5 | 1,820 | 1,752 | 1,875 | 1,812 | −0.4 |
| MA | 59,120 | 58,229 | −0.2 | 12,287 | 12,933 | 13,317 | 14,093 | 0.6 | 9,648 | 9,438 | 9,943 | 9,733 | −0.2 |
| NH | 11,777 | 12,614 | 0.8 | 2,523 | 2,827 | 2,728 | 3,082 | 1.4 | 1,983 | 2,104 | 2,063 | 2,184 | 0.6 |
| RI | 8,151 | 7,588 | −0.8 | 1,825 | 1,881 | 2,070 | 2,166 | 0.5 | 1,297 | 1,194 | 1,342 | 1,239 | −0.9 |
| VT | 5,871 | 5,497 | −0.7 | 950 | 898 | 995 | 953 | −0.5 | 967 | 967 | 982 | 982 | 0 |
| ISO | 128,173 | 127,698 | 0 | 26,565 | 27,875 | 28,915 | 30,525 | 0.6 | 21,077 | 20,805 | 21,737 | 21,465 | −0.1 |

(a) 	The total load-zone projections are similar to the state load projections and are available at the ISO’s “2015 Forecast Data File,” http://www.iso-ne.com/static-assets/documents/2015/05/isone_fcst_data_2015.xls; tab #2, “ISO-NE Control Area, States, RSP15 Subareas, and Standard Market Design (SMD) Load Zones Energy and Seasonal Peak Load Forecast.”

(b) 	Totals may not equal the sum because of rounding and may not exactly match the results for other tables in this section.

Table 3-7
Net Forecast of Demand in RSP Subareas, 2015 to 2024 (GWh, MW)(a)

| Area | Energy (1,000 MWh) |  |  | Summer Peak Loads (MW) |  |  |  |  | Winter Peak Loads (MW) |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | 50/50 Load |  | 90/10 Load |  |  | 50/50 Load |  | 90/10 Load |  |  |
|  | 2015 | 2024 | CAGR | 2015 | 2024 | 2015 | 2024 | CAGR | 2015/16 | 2024/25 | 2015/16 | 2024/25 | CAGR |
| BHE | 1,660 | 1,649 | −0.1 | 287 | 296 | 307 | 316 | 0.3 | 263 | 254 | 273 | 264 | −0.4 |
| ME | 5,542 | 5,523 | 0 | 912 | 946 | 977 | 1,016 | 0.4 | 908 | 873 | 938 | 903 | −0.4 |
| SME | 4,028 | 3,978 | −0.1 | 722 | 752 | 777 | 807 | 0.4 | 613 | 590 | 628 | 610 | −0.3 |
| NH | 10,102 | 10,794 | 0.7 | 2,148 | 2,398 | 2,318 | 2,613 | 1.3 | 1,689 | 1,797 | 1,759 | 1,862 | 0.6 |
| VT | 6,911 | 6,700 | −0.3 | 1,201 | 1,194 | 1,271 | 1,274 | 0 | 1,142 | 1,168 | 1,167 | 1,193 | 0.2 |
| BOSTON | 26,845 | 25,700 | −0.5 | 5,656 | 5,794 | 6,126 | 6,314 | 0.3 | 4,307 | 4,096 | 4,442 | 4,226 | −0.6 |
| CMA/NEMA | 7,140 | 7,518 | 0.6 | 1,484 | 1,652 | 1,609 | 1,802 | 1.3 | 1,187 | 1,257 | 1,222 | 1,297 | 0.7 |
| WMA | 10,309 | 10,033 | −0.3 | 2,059 | 2,139 | 2,234 | 2,334 | 0.5 | 1,746 | 1,717 | 1,801 | 1,767 | −0.2 |
| SEMA | 13,300 | 13,242 | 0 | 2,766 | 2,966 | 3,006 | 3,241 | 0.8 | 2,169 | 2,102 | 2,234 | 2,167 | −0.3 |
| RI | 11,040 | 10,676 | −0.4 | 2,429 | 2,559 | 2,714 | 2,894 | 0.7 | 1,759 | 1,681 | 1,819 | 1,741 | −0.5 |
| CT | 15,372 | 15,527 | 0.1 | 3,392 | 3,490 | 3,722 | 3,850 | 0.4 | 2,595 | 2,580 | 2,680 | 2,660 | −0.1 |
| SWCT | 10,294 | 10,789 | 0.5 | 2,269 | 2,428 | 2,489 | 2,673 | 0.8 | 1,741 | 1,781 | 1,801 | 1,841 | 0.2 |
| NOR | 5,631 | 5,557 | −0.1 | 1,243 | 1,257 | 1,363 | 1,382 | 0.2 | 942 | 910 | 972 | 940 | −0.4 |
| ISO total(a, b) | 128,173 | 127,698 | 0 | 26,565 | 27,875 | 28,915 | 30,525 | 0.6 | 21,077 | 20,805 | 21,737 | 21,465 | −0.1 |

(a) 	The total load-zone projections are similar to the state load projections and are available at the ISO’s “2015 Forecast Data File; http://www.iso-ne.com/static-assets/documents/2015/05/isone_fcst_data_2015.xls, tab #2, “ISO-NE Control Area, States, RSP Subareas, and SMD Load Zones, and Seasonal Peak Load Forecast.”

(b) 	Totals may not equal the sum because of rounding and may not exactly match the results for other tables in this section.

## Summary of Key Findings of the Demand, Energy-Efficiency, and PV Forecasts

The RSP15 forecasts of annual energy use and peak loads are key inputs in establishing the system needs discussed in Section 4 through Section 7. The key points of the forecast are as follows:

- The gross forecasts for annual energy use and the summer and winter peaks are not materially different from the RSP14 forecast.

- The gross compound annual growth rate for the ISO’s electric energy use is 1.0% for 2015 through 2024, 1.3% for the summer peak, and 0.7% for the winter peak.

- The net forecasts of summer peaks differ from last year’s forecasts with the additional load reduction from the BTMNEL PV. The impacts to the annual energy use from BTMNEL PV are small relative to its impacts to the summer peaks. BTMNEL PV has no impact on the winter peak.

- The net compound annual growth rate for the ISO’s electric energy use is 0.0% for 2015 through 2024, 0.6% for the summer peak, and −0.1% for the winter peak.

# Resource Adequacy—Resources, Capacity, and Reserves

The ISO’s system planning process identifies the amounts, locations, and types of resources the system needs for ensuring resource adequacy and how the region is meeting these needs in the short term through the Forward Capacity Market and the locational Forward Reserve Market (FRM). The amount of capacity the system requires in a given year is determined through the Installed Capacity Requirement calculation, which accounts for uncertainties, contingencies, and resource performance under a wide range of existing and future system conditions. The procurement of operating reserves for the system and local areas addresses contingencies, such as unplanned outages. Collectively, the forecasts of future electricity demand (as discussed in Section 3), the ICR calculation, the procurement of capacity and reserves, and the operable capacity analyses that consider future scenarios of load forecasts and operating conditions are referred to as the resource adequacy process.

This section describes the requirements for resource adequacy over the planning period; the analyses conducted to determine the systemwide and local-area needs for ensuring resource adequacy; and the region’s efforts to meet the need for resources through the FCM, the FRM, and energy-efficiency resources supported by the states. This section also discusses the results of the net operable-capacity assessments of the system under a variety of deterministic stressed-system conditions. Additionally, this section summarizes studies that suggest the most reliable and economic places for developing new resources to meet resource adequacy requirements.

## Determining Systemwide and Local-Area Capacity Needs

The Installed Capacity Requirement forms the basis for determining the systemwide capacity needs. The planning process also determines the need for capacity in local capacity zones, accounting for export and import capabilities (or limitations) of these local zones. The annual Forward Capacity Auctions are intended to procure the needed capacity, systemwide and for capacity zones. The section provides the results of the systemwide and local-area analyses for the planning period.

### Systemwide Installed Capacity Requirements

RSP15 discusses the established ICR values for the 2015/2016 through 2018/2019 capacity commitment periods (CCPs) and illustrates representative net ICR values for the 2020/2021 through 2024/2025 periods. The actual net ICR values for the 2015/2016 through 2018/2019 capacity commitment periods reflect the latest ICR values approved by FERC and are based on the 2014 CELT Report. The representative net ICR values do not indicate the definitive amount of capacity the region will purchase for that period but provide stakeholders with a general forecast of the likely resource needs of the region.

Table 4-1 shows the actual and representative New England net Installed Capacity Requirements for 2015 to 2024. FERC approved the ICR and Hydro-Québec Interconnection Capability Credit (HQICC) values for the 2015/2016 through 2018/2019 commitment periods. The representative net ICR values for 2020/2021 through 2024/2025 are calculated deterministically but are assumed to meet the probabilistic resource adequacy criteria. The table also shows the resulting reserves using the 2015 CELT Report demand forecast, which are different for every capacity commitment period for the FERC-approved ICRs. The demand for these years is equal to the gross demand forecast minus the reductions from the behind-the-meter nonembedded PV load (BTMNEL PV) (see Section 3.3.3).

In the table, the calculated future net ICR for 2020/2021 to 2024/2025, rounded to the nearest 100 MW, is based on a representative value of 14.3% for resulting reserves. The resulting reserve value is associated with the representative net ICR values for 2019/2020 through 2023/2024 calculated with the same load and resource assumptions used to develop the FCA #9 net ICR values. As shown in Table 4-1, the region’s net ICR is expected to grow from 33,391 MW in 2015 to a representative value of 36,000 MW by 2024. This represents an average growth of approximately 290 MW per year, which is equivalent to approximately 0.8% per year. The net ICR growth percentage is faster than the growth of net peak demand because the calculation of net ICR assumes that tie-line benefits and actions available from OP 4 actions are constant.

Table 4-1 
Actual and Representative New England Net Installed Capacity Requirements
and Resulting Reserves, 2015 to 2024 (MW, %)

| Commitment Periods | 2015 CELT Forecast 50/50 Peak (MW)(a) | Actual and Representative Future Net ICR (MW)(b) | Resulting Reserves (%)(c) |
| --- | --- | --- | --- |
| 2015/2016 | 28,251 | 33,391 | 18.2 |
| 2016/2017 | 28,673 | 33,764 | 17.8 |
| 2017/2018 | 29,066 | 34,061 | 17.2 |
| 2018/2019 | 29,483 | 34,189 | 16.0 |
| 2019/2020 | 29,861 | TBD(d) | − |
| 2020/2021 | 30,182 | 34,500 | 14.3 |
| 2021/2022 | 30,487 | 34,800 | 14.2 |
| 2022/2023 | 30,804 | 35,200 | 14.3 |
| 2023/2024 | 31,131 | 35,600 | 14.4 |
| 2024/2025 | 31,455 | 36,000 | 14.4 |

- The 2015 CELT forecast 50/50 peak loads reflect the behind-the-meter load reductions from the PV forecast (from the BTMEL PV) (see Section 3.3).

- Net ICR values for 2015/2016 to 2018/2019 are the latest values approved by FERC. These net ICR values were developed using 2014 CELT Report loads.

- The resulting reserves percentage for 2015/2016 to 2018/2019, when calculated using their respective 2014 CELT Report loads, ranged from 13.9% to 16.7% (These values are not shown in the above table). Table 4-1 shows the resulting reserves percentage calculated using the 2015 CELT Report loads. The resulting reserves are approximately 2% higher than the percentages based on the 2014 CELT loads because the 2015 load forecasts reflect the behind-the-meter PV forecast for these years and are slightly lower than the 2014 load forecasts.

(d) 	In November 2015, the ISO will file with FERC the ICR and net ICR for 2019/2020.

As of the RSP15 publication date, the net ICR for 2019/2020 was under development and scheduled to be filed with FERC in November 2015. In December 2015 or early 2016, the ISO plans to provide the PAC with the representative net ICR values for 2020/2021 through 2024/2025 using the same probabilistic calculation techniques and assumptions used to determine the 2019/2020 net ICR values.

### Local Resource Requirements and Limits

While the ICR addresses New England’s total capacity requirement assuming the system overall has no transmission constraints, certain subareas are limited in their ability to export or import power. To address the impacts of these constraints on subarea reliability, before each FCA, the ISO determines the local sourcing requirement (LSR) and maximum capacity limit (MCL) for certain subareas within New England. An LSR is the minimum amount of capacity that must be electrically located within an import-constrained load zone to meet the ICR. An MCL is the maximum amount of capacity that can be procured in an export-constrained load zone to meet the total ICR for the New England region. Areas that have either an LSR or an MCL and that meet other market tests are designated as capacity zones in the Forward Capacity Auction. These designations help ensure that the appropriate amount of capacity is procured within these capacity zones to satisfy the ICR and contribute effectively to total system reliability. (See Section 4.1.3.2 and 4.2 for further discussion of capacity zones.)

The LSR and MCL values, associated with the respective capacity commitment period’s FCA, are included in Table 4-2 for the 2015/2016 through the 2018/2019 capacity commitment periods. Like the net ICR, the LSR and MCL capacity zones and values for FCA #10 were under development at the time of the RSP15 publication and will be filed with FERC in November 2015. In December 2015 or early 2016, the ISO plans to present to the PAC the representative LSR and MCL values for 2020/2021 through 2024/2025 using the same probabilistic calculation techniques and assumptions used for determining the 2019/2020 LSR and MCL values.

Table 4-2
Actual LSRs and MCLs for the 2015/2016 to 2018/2019
Capacity Commitment Periods (MW)(a)

| Commitment Period |  | LSR (MW) |  |  | MCL (MW) |
| --- | --- | --- | --- | --- | --- |
|  |  | CT | NEMA/Boston | SEMA/RI | Maine |
| 2015/2016 | FCA #6 | 7,542 | 3,289 | − | 3,888 |
| 2016/2017 | FCA #7 | 7,603 | 3,209 | − | 3,709 |
| 2017/2018 | FCA #8 | 7,319 | 3,428 | − | 3,960 |
| 2018/2019 | FCA #9 | 7,331 | 3,572 | 7,479 | − |

(a) 	Source: “Summary of ICR, LSR, and MCL for FCM and the Transition Period,” table, in Summary of Historical ICR Values spreadsheet (April 15, 2015), http://www.iso-ne.com/static-assets/documents/2014/12/summary_of_icr_values_expanded.xlsx. These are the latest values filed with FERC.

### Capacity Supply Obligations from the Forward Capacity Auctions

This section presents the results of the first through ninth Forward Capacity Auctions, including the amount of capacity that generation, import, and demand resources in the region will supply.

#### Capacity Supply Obligations for the First Nine FCAs

Table 4-3 shows the results of the nine FCAs held so far for 2010/2011 through 2018/2019 and provides the capacity supply obligation totals procured for FCA #1 through FCA #9 at the conclusion of each auction. This table also includes some details on the types of CSOs procured, including the total real-time emergency generation (see Section 2.4), self-supply obligation values that reflect bilateral capacity arrangements, and import capacity supply obligations from neighboring balancing authority areas.

Table 4-3
Summary of the FCA Obligations at the Conclusion of Each Auction (MW)(a)

| Commitment Period | ICR | HQICC | Net ICR(b) | Capacity Supply Obligation | RTEG Capacity Supply Obligation | RTEG Utilization Ratio | Self-Supply Obligation | Import Capacity Supply Obligation |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 2010/2011 | 33,705 | 1,400 | 32,305 | 34,077 | 875 | 0.686 | 1,593 | 934 |
| 2011/2012 | 33,439 | 911 | 32,528 | 37,283 | 759 | 0.791 | 1,696 | 2,298 |
| 2012/2013 | 32,879 | 914 | 31,965 | 36,996 | 630 | 0.952 | 1,935 | 1,900 |
| 2013/2014 | 33,043 | 916 | 32,127 | 37,501 | 688 | 0.872 | 2.698 | 1,993 |
| 2014/2015 | 34,154 | 954 | 33,200 | 36,918 | 722 | 0.831 | 3,176 | 2,011 |
| 2015/2016 | 34,498 | 1,042 | 33,456 | 36,309 | 617 | 0.972 | 4,164 | 1,924 |
| 2016/2017 | 34,023 | 1,055 | 32,968 | 36,220 | 262 | 1.000 | 4,662 | 1,830 |
| 2017/2018 | 34,923 | 1,068 | 33,855(c) | 33,702(d) | 270 | 1.000 | 3,330 | 1,237 |
| 2018/2019 | 35,142 | 953 | 34,189 | 34,695 | 137 | 1.000 | 1,287 | 1,449 |

  - Information regarding the results of annual reconfiguration auctions is available at http://www.iso-ne.com/markets/othrmkts_data/fcm/cal_results/index.html.

  - The net ICR equals the ICR minus the Hydro-Québec Interconnection Capability Credits. The ICR applies to the FCA, not the reconfiguration auction.

  - The ICR requirement for 2017/2018 will be met by procuring additional resources, if deemed necessary, in annual reconfiguration auctions to be held April 2015, August 2016, and March 2017, in accordance with the market rules.

  - Subsequent to the end of FCA #8 but before the ISO filed the results with FERC, an out-of-market resource from FCA #6 was deemed to have cleared and was assigned a 10 MW capacity supply obligation, increasing the total CSO to 33,712 MW.

#### FCA Results for Capacity Zones

Table 4-4 summarizes the detailed CSOs for the capacity zones modeled for each capacity commitment period, which are published in the 2015 CELT Report. The CSOs have been adjusted to reflect the 600 MW limit in the market rule for real-time emergency generation resources, which is the maximum quantity of this resource type that can be counted toward the ICR.

Table 4-4
Results of the FCA by Capacity Zone at the Conclusion of Each Auction (MW, $/kW-month)(a)

| Commitment Period | Modeled Capacity Zone | MCL | LSR | CSO | RTEG CSO | Self-Supply Obligation | Capacity Clearing Price | Payment Rate | RTEG Payment Rate |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | (MW) |  |  |  |  | ($/kW-month) |  |  |
| 2010/2011 | Rest-of-Pool |  |  | 30,572 | 838 | 1,584 | 4.500 | 4.254 | 2.918 |
|  | Maine | 3,855 |  | 3,505 | 37 | 9 | 4.500 | 4.254 | 2.918 |
| 2011/2012 | Rest-of-Pool |  |  | 33,468 | 727 | 1,687 | 3.600 | 3.119 | 2.467 |
|  | Maine | 3,395 |  | 3,815 | 32 | 9 | 3.600 | 3.119 | 2.467 |
| 2012/2013 | Rest-of-Pool |  |  | 33,099 | 597 | 1,925 | 2.951 | 2.535 | 2.413 |
|  | Maine | 3,275 |  | 3,897 | 33 | 9 | 2.951 | 2.465 | 2.347 |
| 2013/2014 | Rest-of-Pool |  |  | 33,476 | 655 | 2,693 | 2.951 | 2.516 | 2.194 |
|  | Maine | 3,187 |  | 4,025 | 33 | 6 | 2.951 | 2.336 | 2.036 |
| 2014/2015 | Rest-of-Pool |  |  | 32,960 | 691 | 3,171 | 3.209 | 2.855 | 2.374 |
|  | Maine | 3,702 |  | 3,958 | 31 | 5 | 3.209 | 2.885 | 2.374 |
| 2015/2016 | Rest-of-Pool |  |  | 32,374 | 582 | 4,157 | 3.434 | 3.129 | 3.044 |
|  | Maine | 3,888 |  | 3,935 | 35 | 7 | 3.434 | 3.129 | 3.044 |
| 2016/2017 | Rest-of-Pool |  |  | 20,182 | 80 | 4076 | 3.150 | 2.744 | 2.744 |
|  | Maine | 3,709 |  | 3,950 | 12 | 26 | 3.150 | 2.744 | 2.744 |
|  | Connecticut |  | 7,603 | 8,372 | 143 | 499 | 3.150 | 2.883 | 2.883 |
|  | NEMA/Boston(b) |  | 3,209 | 3,716 | 28 | 61 | 14.999 | New: 14.999 Existing: 6.661 | 6.661 |
| 2017/2018 | Rest-of-Pool |  |  | 15,901 |  | 2,238 | New: 15.000 Existing: 7.025 | N/A | 7.025 |
|  | Maine | 3,960 |  | 3,553 | 12 | 14 | New: 15.000 Existing: 7.025 | N/A | 7.025 |
|  | Connecticut |  | 7,319 | 9,191 | 138 | 1,017 | New: 15.000 Existing: 7.025 | N/A | 7.025 |
|  | NEMA/Boston(c) |  | 3,428 | 3,821 | 26 | 61 | 15.000 | N/A | 15.000 |
| 2018/2019 | Rest-of-Pool |  |  | 13,724 | 52 | 881 | 9.551 | N/A | 9.551 |
|  | SEMA/RI(d) |  | 7,479 | 7,241 | 24 | 256 | New: 17.728 Existing: 11.080 | N/A | 11.080 |
|  | Connecticut |  | 7,331 | 9,802 | 52 | 87 | 9.551 | N/A | 9.551 |
|  | NEMA/Boston |  | 3,572 | 3,927 | 9 | 62 | 9.551 | N/A | 9.551 |

    - Values are rounded and do not reflect proration.

    - Insufficient competition was triggered in NEMA/Boston for 2016/2017.

    - The Capacity Carry Forward Rule was triggered in NEMA/Boston. This rule addresses situations where a large resource meets a zonal need but eliminates any need for new resources in the subsequent auction (Market Rule 1, Section III.13.2.7.9).

    - Administrative pricing was triggered in SEMA/RI because the resources bidding into the auction were below the required amount.

Two capacity zones, Maine and the Rest-of-Pool, were used in FCA #1 through FCA #6 to address Maine’s designation as an export-constrained capacity zone. The potential import-constrained capacity zones were determined to have sufficient existing capacity to meet the local sourcing requirements for FCA #1 through FCA #6. In its March 30, 2012, order on tariff revisions to the FCM, FERC accepted the ISO’s proposal to model four capacity zones for FCA #7. These capacity zones were Maine, which was designated as an export-constrained capacity zone; NEMA/Boston and Connecticut, which were designated as import-constrained capacity zones; and the Rest-of-Pool, which combined the other four capacity zones. FCA #8 used the same four capacity zones as FCA #7.

For FCA #8, FERC accepted the ISO’s proposal to continue modeling the same four zones used in FCA #7. FERC also accepted the use of a stakeholder process for developing a zonal structure for the market that better reflects reliability needs of the system. Subsequent FCAs then reflected the criterion and processes for creating, modifying, or collapsing capacity zones. (Section 4.2 contains additional information on FCM capacity zones.)

After FCA #8, available capacity resources in the Connecticut capacity zone exceeded the resource adequacy requirements for the area by 1,872 MW. This is an increase of approximately 1,100 MW over the FCA #7 excess of 769 MW. In this zone for the 2017/2018 capacity commitment period, 9,191 MW of capacity resources will be used to meet the local sourcing requirement of 7,319 MW. An additional 100 MW of capacity also was procured in Connecticut to support an administrative export delist bid through that capacity zone.

FCA #9 included market changes to address strategic risks associated with infrastructure investment needs, natural gas dependence, and resource performance (see Section 8). First, the addition of a sloped demand curve mitigates capacity market price volatility by allowing the auction to clear at values higher or lower than the ICR value, depending on reliability requirements and price. Second, the revised market design locks in FCA clearing prices for seven years for new resources. This longer period, which was previously five years, improves financial stability and strengthens investment signals for new resource development. Finally, the pay-for-performance (PFP) market structure promotes system reliability by providing incentives to resources to perform when dispatched.

Figure 4-1 shows the sloped demand curve used for establishing the price for the systemwide capacity supply obligations. The figure shows that the systemwide quantity of capacity increases linearly as the price decreases below the FCA’s starting price of $17.728/kW-month (for FCA #9). FCA #9 also modeled three import-constrained capacity zones—NEMA/Boston, SEMA/RI, and Connecticut. Maine was not modeled as an export-constrained capacity zone but was included in the Rest-of-Pool capacity zone. The Rest-of-Pool capacity zone included Western/Central Massachusetts, New Hampshire, Vermont, and Maine.

Figure 4-1: Sloped demand curve for FCA #9.

Note: LOLE stands for loss-of-load expectation. An LOLE analysis is a probabilistic analysis used to measure how long, on average, the available capacity is likely to fall short of the demand. The system must meet an NPCC and ISO resource adequacy planning criterion to not disconnect firm load more than one time in 10 years (or 0.1 times per year). A “1 in 5” LOLE refers to the capacity needed to not disconnect load more than one time in 5 years or 0.5 times per year; and a “1 in 87” LOLE refers to the capacity needed to not disconnect load more than one time in 87 years. “Cap” refers to the maximum clearing price, and “foot” refers to the minimum clearing price.

The cost estimate for the 2018/2019 capacity period is approximately $4 billion. FCA #9 commenced with a starting price of $17.728/kW-month and then followed the rules of the descending-clock auction. Auction prices cleared lower in areas with adequate resources and higher in areas with resource shortages. In general, the auction attracted significant competition, and the market supported several new generating resources. In the NEMA/Boston, Connecticut, and Rest-of-Pool capacity zones, the auction concluded after three rounds. Resources in these zones will be paid $9.551/kW-month. The auction continued for one additional round for imports from New York AC ties, closing at $7.967/kW-month, and two additional rounds for New Brunswick imports, closing at $3.94/kW-month.

In the SEMA/RI capacity zone, the qualified resources were insufficient to meet the zone’s local sourcing requirement. As a result, bidding never opened in this zone, and the tariff’s administrative pricing provisions regarding insufficient competition were triggered. Under these rules, new resources in the SEMA/RI capacity zone will be paid at the auction starting price of $17.728/kW-month, and existing resources in the zone will be paid $11.08/kW-month.

Table 4-5 shows, by resource type, the amounts of new capacity procured during all the FCAs. FCA #9 attracted investment in new resources that help address New England’s resource needs. As a result of using the systemwide sloped demand curve, the ISO procured 34,695 MW, which is 506 MW greater than the net ICR requirement of 34,189 MW. FCA #9 procured new generating units totaling 1,060 MW, which included a 725 MW dual-fuel unit and two 45 MW units in Connecticut and a new 195 MW dual-fuel peaking power plant in SEMA/RI. Table 4-6 shows the decline of total active demand resource capacity in recent FCAs.

Table 4-5
Capacity Supply Obligation for New Capacity
Procured during the Forward Capacity Auctions (MW)(a)

| Capacity Resource | FCA #1 | FCA #2 | FCA #3 | FCA #4 | FCA #5 | FCA #6 | FCA #7 | FCA #8 | FCA #9 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Generation resources | 40 | 1,157 | 199 | 114 | 42 | 79 | 800 | 27 | 1,060(b) |
| Demand-resource total | 860 | 447 | 309 | 515 | 263 | 313 | 245 | 355 | 367 |
| Active demand resources | 576 | 185 | 98 | 257 | 42 | 66 | <1 | 14 | 81 |
| Passive demand resources | 284 | 262 | 211 | 258 | 221 | 247 | 245 | 341 | 286 |
| Import resources | 0 | 1,529 | 817 | 831 | 871 | 1,648 | 1,718 | 1,154 | 1,360 |

        - New RTEG capacity is not included in the table values because the FCA treats it as existing capacity. Repowered existing generating capacity (i.e., capacity that has undergone environmental upgrades), which is treated as new capacity in the FCA, has been removed as well. Refer to the full auction results at http://www.iso-ne.com/isoexpress/web/reports/auctions/-/tree/fcm-auction-results.

        - New generation resources include major facilities in the CT capacity zone (90 MW in Wallingford and 725 MW in Towantic) and in SEMA (194.8 MW in Medway).

Table 4-6
Active and Passive Demand Response: CSO Totals by Capacity Commitment Period (MW)

| Commitment Period | Active/Passive | Existing | New | Grand Total |
| --- | --- | --- | --- | --- |
| 2010/2011 | Active | 1,246.399 | 603.675 | 1,850.074 |
|  | Passive | 119.211 | 584.277 | 703.488 |
|  | Grand total | 1,365.610 | 1,187.952 | 2,553.562 |
| 2011/2012 | Active | 1,768.392 | 184.990 | 1,953.382 |
|  | Passive | 719.980 | 263.250 | 983.230 |
|  | Grand total | 2,488.372 | 448.240 | 2,936.612 |
| 2012/2013 | Active | 1,726.548 | 98.227 | 1,824.775 |
|  | Passive | 861.602 | 211.261 | 1,072.863 |
|  | Grand total | 2,588.150 | 309.488 | 2,897.638 |
| 2013/2014 | Active | 1,794.195 | 257.341 | 2,051.536 |
|  | Passive | 1,040.113 | 257.793 | 1,297.906 |
|  | Grand total | 2,834.308 | 515.134 | 3,349.442 |
| 2014/2015 | Active | 2,062.196 | 41.945 | 2,104.141 |
|  | Passive | 1,264.641 | 221.072 | 1,485.713 |
|  | Grand total | 3,326.837 | 263.017 | 3,589.854 |
| 2015/2016 | Active | 1,935.406 | 66.104 | 2,001.510 |
|  | Passive | 1,395.885 | 247.449 | 1,643.334 |
|  | Grand total | 3,331.291 | 313.553 | 3,644.844 |
| 2016/2017 | Active | 1,116.468 | 0.230 | 1,116.698 |
|  | Passive | 1,386.560 | 244.775 | 1,631.335 |
|  | Grand total | 2,503.028 | 245.005 | 2,748.033 |
| 2017/2018 | Active | 1,066.593 | 13.486 | 1,080.079 |
|  | Passive | 1,619.147 | 341.37 | 1,960.517 |
|  | Grand total | 2,685.740 | 354.856 | 3,040.596 |
| 2018/2019 | Active | 565.866 | 81.394 | 647.260 |
|  | Passive | 1,870.549 | 285.602 | 2,156.151 |
|  | Grand total | 2,436.415 | 366.996 | 2,803.411 |

#### Summary of New Capacity and Delist Bids

As part of the FCM rules, the ISO reviews each delist bid and nonprice retirement (NPR) request to determine whether the capacity associated with the delist bid or nonprice retirement is needed for the reliability of the New England electric power system. All reviews are performed in accordance with Planning Procedure No. 10 (PP 10), Planning Procedure to Support the Forward Capacity Market.

New Capacity Compared with Delist Requests. Static and dynamic delist bids are priced requests to remove capacity from the market for a single year. Delist bid requests, including Salem Harbor Station (FCAs #3 and #4) (see Section 6.4) and Vermont Yankee (VY) (FCAs #4, #5, #6 and #7) (Section 6.3), have influenced prices in the Forward Capacity Market and thereby provide incentives for new resources to be built. Figure 4-2 compares the amount of new resources participating in the FCM and receiving CSOs with resources—including demand resources—that chose to delist.

Figure 4-2: Summary of total capacity of new capacity and delist requests that cleared FCA #1 to FCA #9 (MW).

Nonprice Retirement Requests. Retirement requests, including the retirement of Salem Harbor Station (FCA #5), Vermont Yankee (FCA #8), and Brayton Point Station (FCA #8), also have influenced prices in the FCM and have thereby provided market signals for new resources to be built. If a resource seeking to retire is needed for reliability, it may retire regardless of the ISO’s determination. Figure 4-3 summarizes nonprice retirements, which includes Mount Tom (FCA #9).

Figure 4-3: Summary of total capacity of nonprice retirement requests, FCA #4 to FCA #9 (MW).

Outcomes of 2015 Delist Bids. In FCA #9, the delist bid situation differed from prior auctions. Although many delist bids, totaling 8,301 MW, were submitted for FCA #9, most were priced below the auction’s capacity clearing price and did not clear. However, pursuant to the ISO tariff, before the auction, some participants elected to withdraw their static delist bids. In addition, also before the auction, 97 MW of the delist bids were converted into nonprice retirement requests. As a result, 5,537 MW of static delist bids were reviewed for reliability. Because the systemwide auction price did not go below $9.551/kw-month and never went as low as $3.94/kW-month (i.e., the threshold for review of dynamic delist bids prescribed for the FCA #9), no dynamic delist bids were submitted, and most of the static delist bids did not clear. Finally, no permanent delist bids or export bids were submitted for the ninth FCA.

#### Representative Systemwide Resource Needs

The representative net ICR values for future years (see Section 4.1.1) indicates the systemwide capacity needs. Table 4-7 compares these systemwide needs with the resources procured in FCA #9, accounting for the future levels of behind-the-meter PV (Section 3.3.3), and the future levels of passive demand resources (Section 3.2). The projection of systemwide capacity needs assumes that all resources with capacity supply obligations through FCA #9 are in commercial service by the start of the ninth capacity commitment period commencing in June 2018 and that they remain in service for the 10-year planning horizon. As shown in Table 4-7, New England will be approximately 30 MW short of resources in 2024, the last year of the study period, assuming that the projected load and capacity assumptions materialize and no additional retirements occur.

Table 4-7 
Future Systemwide Needs (MW)

| Year | 50/50 Peak Load(a) | Representative Net ICR (Need) | FCA #9 (Known Resources)(b) | EE Forecast (New Resource)(c) | Resource Surplus/Shortage(d) |
| --- | --- | --- | --- | --- | --- |
| 2020/2021 | 30,182 | 34,500 | 34,695 | 477 | 672 |
| 2021/2022 | 30,487 | 34,800 | 34,695 | 695 | 590 |
| 2022/2023 | 30,804 | 35,200 | 34,695 | 900 | 395 |
| 2023/2024 | 31,131 | 35,600 | 34,695 | 1,093 | 188 |
| 2024/2025 | 31,455 | 36,000 | 34,695 | 1,274 | −31 |

(a)	The 50/50 peak loads reflect the behind-the-meter PV resources.

(b) 	FCA #9 resource numbers are based on FCA #9 auction results, assuming no retirements and the same level of imports (i.e., most imports need to requalify for every auction). Details are available at the ISO’s FERC filing, ISO New England Inc., Docket No. ER15-Informational Filing for Qualification in the Forward Capacity Market (November 4, 2014), http://www.iso-ne.com/static-assets/documents/2014/11/er15-___-000_11-3_14_fca_9_info_filing_public_version.pdf.

(c) 	EE forecast values are based on the 2015 EE forecast. Details are available at http://www.iso-ne.com/static-assets/documents/2015/04/iso_ne_final_2015_ee_forecast_2019_2024.pdf.

(d) 	Additional resources would be required if additional resources retired or less capacity imports obtain CSOs.

## Determining FCM Capacity Zones

Beginning with FCA #9, several tariff changes became effective that require a new methodology for determining the appropriate number of capacity zones to model in the Forward Capacity Market and the appropriate boundaries for these capacity zones. Under the changes, the ISO annually identifies and evaluates all the boundaries and interface transfer capabilities that could be relevant to FCA capacity zone modeling. The review must focus on the actual constraints observed and expected on the New England system and directly considers submitted retirements and rejected delist bids. This review is designed to be responsive to system changes, such as new transmission facilities and new capacity resources. Primary auctions, reconfiguration auctions, and FCM settlements all use the capacity zones.

The FERC-approved methodology for determining capacity zones is a two-step process. Step one identifies potential zonal boundaries and associated transfer limits to be tested for modeling in the auction. Step two uses objective criteria to determine whether or not a zone should be modeled for the pertinent capacity commitment period. With respect to step two, the trigger to model an import-constrained zone is based on the quantity of existing resources in the zone, whereas the trigger to model an export-constrained zone is based on the quantity of existing and proposed new resources that could qualify in the zone. Zones that are neither import- or export-constrained are merged into the Rest-of-Pool capacity zone.

### Identifying Potential Zonal Boundaries and Associated Transfer Limits to Be Tested for FCM Modeling

This section describes the outcomes of the first step of the methodology, namely, the identification of potential zonal boundaries and associated transfer limits to be tested for modeling in the FCM. In particular, the results of the annual assessment of transmission transfer capability are presented. The assessment was conducted pursuant to applicable NERC, NPCC, and ISO New England standards and criteria and identified the portions of the system with potential future transmission system weaknesses and limiting facilities that could affect the transmission system’s ability to reliably transfer energy in the planning horizon.

In preparation for FCA#10, the transfer capability analysis of the New England system incorporated the results of several recent studies. In some cases, the transfer limits were based on equipment thermal limitations during summer peak conditions. In other cases, voltage or transient stability limitations were identified at off-peak load levels. All the analyses included all transmission upgrades that had been certified and accepted to be in service in time for the tenth capacity commitment period (i.e., by June 1, 2019). FCA #10 transfer-capability analysis included the Greater Boston Project. It also included certified and accepted upgrades reflected in FCA #9, such as the interstate portions of the New England East–West solution (see Section 6.4 and 6.5). The transfer-capability assessment also modeled nonprice retirements, including Salem Harbor Station, Vermont Yankee nuclear facility, Norwalk Harbor Station, and Brayton Point Station (see Section 6.4). Table 4-8 and Table 4-9 show the transfer capabilities identified for multiple interfaces, internal and external, for all years on the RSP planning horizon.

Table 4-8
Results of the Transfer Capability Analysis for New England,
2015 to 2024, Internal Interfaces (MW)

| Interface(a) | Year |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 |
| Orrington South Export | 1,325 | 1,325 | 1,325 | 1,325 | 1,325 | 1,325 | 1,325 | 1,325 | 1,325 | 1,325 |
| Surowiec South | 1,500 | 1,500 | 1,500 | 1,500 | 1,500 | 1,500 | 1,500 | 1,500 | 1,500 | 1,500 |
| Maine–New Hampshire | 1,900 | 1,900 | 1,900 | 1,900 | 1,900 | 1,900 | 1,900 | 1,900 | 1,900 | 1,900 |
| Northern New England– Scobie + 394 | 3,100 | 3,100 | 3,100 | 3,100 | 3,100 | 3,100 | 3,100 | 3,100 | 3,100 | 3,100 |
| North–South(b) | 2,100 | 2,100 | 2,100 | 2,100 | 2,675(c) | 2,675 | 2,675 | 2,675 | 2,675 | 2,675 |
| East–West | 2,800 | 3,500(d) | 3,500 | 3,500 | 3,500 | 3,500 | 3,500 | 3,500 | 3,500 | 3,500 |
| West–East | 1,000 | 2,200(d) | 2,200 | 2,200 | 2,200 | 2,200 | 2,200 | 2,200 | 2,200 | 2,200 |
| Boston Import (N-1) | 4,850 | 4,850 | 4,850 | 4,850 | 5,700(c) | 5,700 | 5,700 | 5,700 | 5,700 | 5,700 |
| Boston Import (N-1-1) | 4,175 | 4,175 | 4,175 | 4,175 | 4,600(c) | 4,600 | 4,600 | 4,600 | 4,600 | 4,600 |
| SEMA/RI Export | 3,000 | 3,400(d) | 3,400 | 3,400 | 3,400 | 3,400 | 3,400 | 3,400 | 3,400 | 3,400 |
| SEMA/RI Import (N-1) | - | - | - | 786 | 1,280(e) | 1,280 | 1,280 | 1,280 | 1,280 | 1,280 |
| SEMA/RI Import (N-1-1) | - | - | - | 473 | 720(e) | 720 | 720 | 720 | 720 | 720 |
| Southeast New England Import (N-1) | - | - | - | - | 5,700 | 5,700 | 5,700 | 5,700 | 5,700 | 5,700 |
| Southeast New England Import (N-1-1) | - | - | - | - | 4,600 | 4,600 | 4,600 | 4,600 | 4,600 | 4,600 |
| Connecticut Import (N-1) | 3,050 | 2,950(d) | 2,950 | 2,950 | 2,950 | 2,950 | 2,950 | 2,950 | 2,950 | 2,950 |
| Connecticut Import (N-1-1) | 1,850 | 1,750(d) | 1,750 | 1,750 | 1,750 | 1,750 | 1,750 | 1,750 | 1,750 | 1,750 |
| SW Connecticut Import (N-1) | 3,200 | 3,200 | 3,200 | 3,200 | 3,200 | 3,200 | 3,200 | 3,200 | 3,200 | 3,200 |
| SW Connecticut Import (N-1-1) | 2,300 | 2,300 | 2,300 | 2,300 | 2,300 | 2,300 | 2,300 | 2,300 | 2,300 | 2,300 |
| Norwalk–Stamford | No limit for each year |  |  |  |  |  |  |  |  |  |

- The transmission interface limits are single-value, summer peak limits (except where noted to be winter), for use in subarea transportation models. The limits may not include possible simultaneous impacts and should not be considered as “firm.” (The bases for these limits will be subject to more detailed review.) For the years within the FCM horizon (2019, FCA #10 and sooner), only accepted certified transmission projects are included when identifying transfer limits. Certified transmission projects were presented to the Reliability Committee at their January 27, 2015, meeting (http://www.iso-ne.com/committees/reliability/reliability-committee). For the years beyond the FCM horizon (2020 and later), proposed plan approved transmission upgrades are included according to their expected in-service dates.

- The North–South transfer capabilities reflect the retirements of Brayton Point and Vermont Yankee.

(c) 	The ISO has accepted the certification of the Greater Boston upgrades project (see Section 6.4.2.1) to be in service by June 2019.

(d) 	The ISO has accepted the certification of the New England East–West Solution (NEEWS) Interstate Reliability Program (IRP) (see Sections 6.4 and 6.5) to be in service by December 2015.

(e) 	In response to the Brayton Point retirement, upgrades to the following Rhode Island area facilities are now planned (and are certified to be in service by the start of the tenth capacity commitment period [i.e., by June 1, 2019]): the V148N 115 kV line between Woonsocket and Washington, the West Farnum 345/115 kV autotransformer upgrade (already in service), and the Kent County 345/115 kV autotransformer (already in service).

Table 4-9
Results of the Transfer Capability Analysis for New England,
2015 to 2024, External Interfaces (MW)

| Interface(a) | Year |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 |
| New Brunswick–New England (energy import capability)(b) | 1,000 | 1,000 | 1,000 | 1,000 | 1,000 | 1,000 | 1,000 | 1,000 | 1,000 | 1,000 |
| New Brunswick–New England (capacity import capability) | 700 | 700 | 700 | 700 | 700 | 700 | 700 | 700 | 700 | 700 |
| HQ-NE (Highgate) (energy import capability)(c) | 217 | 217 | 217 | 217 | 217 | 217 | 217 | 217 | 217 | 217 |
| HQ-NE (Highgate) (capacity import capability) | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 |
| HQ-NE (Phase II) (energy import capability)(d) | 2,000 | 2,000 | 2,000 | 2,000 | 2,000 | 2,000 | 2,000 | 2,000 | 2,000 | 2,000 |
| HQ-NE (Phase II) (capacity import capability) | 1,400 | 1,400 | 1,400 | 1,400 | 1,400 | 1,400 | 1,400 | 1,400 | 1,400 | 1,400 |
| Cross–Sound Cable (CSC) (energy import capability)(e) | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 330 |
| CSC (capacity import capability) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |
| New York–New England (NY–NE) (energy transfer capability)(f) | 1,400 | 1,400 | 1,400 | 1,400 | 1,400 | 1,400 | 1,400 | 1,400 | 1,400 | 1,400 |
| NY–NE (capacity transfer capability) | 1,400 | 1,400 | 1,400 | 1,400 | 1,400 | 1,400 | 1,400 | 1,400 | 1,400 | 1,400 |

(a) 	The transmission interface limits are single-value, summer peak limits (except where noted to be winter), for use in subarea transportation models. The limits may not include possible simultaneous impacts and should not be considered as “firm.” (The bases for these limits will be subject to a more detailed review.) For the years within the FCM horizon (2019, FCA #10 and sooner), only accepted certified transmission projects are included when identifying transfer limits. Certified transmission projects were presented to the Reliability Committee at their January 27, 2015, meeting (http://www.iso-ne.com/committees/reliability/reliability-committee). For the years beyond the FCM horizon (2020 and later), proposed plan approved transmission upgrades are included according to their expected in-service dates.

(b) 	The electrical limit of the New Brunswick–New England (NB–NE) tie is 1,000 MW. When adjusted for the ability to deliver capacity to the ISO New England Balancing Authority Area, the NB–NE transfer capability is 700 MW because of downstream constraints, in particular, Orrington South.

(c) 	The capability for the Highgate facility is listed at the New England AC side of the Highgate terminal.

(d) 	The HQICC interconnection is a DC tie with equipment ratings of 2,000 MW. The PJM and NYISO systems may be constrained by the loss of this line. As a result, ISO New England has assumed that its transfer capability is 1,400 MW for capacity and reliability calculations. This assumption is based on the results of loss-of-source analyses conducted by PJM and NYISO.

(e) 	The import capability on the CSC is dependent on the level of local generation.

(f) 	The New York interface limits are without the CSC and with the Northport–Norwalk Cable at 0 MW flow. Simultaneously importing into New England and SWCT or CT can lower the NY–NE capability (very rough decrease = 200 MW). Conversely, simultaneously exporting to NY and importing to SWCT or CT can lower the NE–NY capability (very rough decrease = 700 MW).

### Transfer-Capability Assessment for FCA #10

In preparation for FCA #10 to identify potential future transmission system weaknesses and limiting facilities that could affect the system’s ability to transfer energy within the planning horizon, the ISO assessed the transfer capability of the transmission system. The assessment was conducted pursuant to NERC Reliability Standard FAC-013-2, “Assessment of Transfer Capability for the Near-Term Transmission Planning Horizon,” as well as NPCC and ISO standards and criteria.

As a result of the above reviews, the ISO proposed two new potential capacity zones for FCA #10. One of the new potential capacity zone boundaries is a combination of the existing NEMA/Boston capacity zone and the SEMA/RI capacity zone (collectively, the Southeastern New England capacity zone, or SENE capacity zone). A combination of the existing Maine, New Hampshire, and Vermont load zones (referred to as the Northern New England capacity zone, or NNE capacity zone) was also evaluated as a new potential capacity zone. No changes were proposed to the boundaries associated with the West/Central Massachusetts or Connecticut portions of the system.

The potential SENE capacity zone was proposed to be an import-constrained capacity zone, while the potential NNE capacity zone was proposed to be an export-constrained capacity zone. The West/Central Massachusetts load zone was proposed to form the basis for the Rest-of-Pool zone for FCA #10. Finally, the existing Connecticut zone was evaluated but not modeled as an import-constrained zone.

#### Southeast New England Capacity Zone

With respect to the SENE area, the transmission transfer capability was assessed through modeling that increased the output of source resources in Western New England (i.e., remote from the SENE area) and decreased the output of sink resources in the eastern portion of Massachusetts and Rhode Island. Under these conditions, a scenario analysis was performed with different sets of generation resources modeled as off line in the NEMA/Boston and SEMA/RI areas. The scenario analyses enabled the identification of certain transmission constraints and associated transfer limits.

The constraints observed in the transfer of power into the SENE area were found to be on or near the interface of the boundary formed by the combined existing SEMA/RI and NEMA/Boston capacity zones. These constraints were observed for the contingency loss of either generating resources or other transmission elements on or near the boundary formed by the combination of the capacity zones.

Resources in both NEMA/Boston and SEMA/RI are on the downstream side of the import constraints (and thus would unload the constraints) observed for the combined zone. The combined load within the overall zone was projected to be approximately 13,300 MW by 2018. After the inclusion of the Greater Boston upgrades, the N-1 import capability into the zone is projected to be approximately 5,700 MW.

The primary system change that led to the formation of the SEMA/RI import-constrained capacity zone in FCA #9 was the NPR request of the 1,535 MW Brayton Point Station in FCA #8. Since that time, two sets of system changes have led to the relief of the “stand-alone” SEMA/RI issues. First, the creation of the SEMA/RI capacity zone successfully led to the addition of 353 MW of new capacity resources in this zone in FCA #9. Second, the ISO has certified and accepted certain transmission upgrades for inclusion in FCA #10 that will allow the increase of the SEMA/RI N-1 and N-1-1 import capabilities by approximately 500 and 300 MW, respectively. NEMA/Boston and SEMA/RI were both modeled as import-constrained zones in FCA #9. The ISO’s system modeling, conducted in accordance with Attachment K, Section 3, showed that these portions of the system continue to be import constrained. However, now that the “stand-alone” SEMA/RI issues have been relieved, both zones share the same remaining constraints located on the outer boundaries of the combined SENE zone. For the conditions studied, no constraints were observed between NEMA/Boston and SEMA/RI within the SENE zone.

#### Northern New England Capacity Zone

With respect to the potential Northern New England capacity zone, the north–south interface has been an evaluated interface in planning and operation studies of the New England system for many years. The interface is approximately located along the combined southern borders of New Hampshire and Vermont and the northern border of Massachusetts. Planning studies conducted in accordance with Attachment K, Section 3, identified that the pattern of north–south flows had changed following the retirement of the Brayton Point Station and the earlier retirement of the Vermont Yankee nuclear facility. After these retirements, the north–south flows are now forecasted to be more concentrated along the lines connecting southeastern New Hampshire with eastern Massachusetts.

The existing capacity resources north of the north–south boundary all contribute to the transfer over the interface. Note that the Maine load zone is contained within the potential NNE capacity zone. In previous FCAs the Maine capacity zone was evaluated as an export-constrained zone. However, recent transmission improvements, known as the Maine Power Reliability Program (see Section 6.3), have increased the export capability out of the Maine area. The Maine zone was evaluated in FCA #9, and the objective criteria associated with the formation of an export-constrained capacity zone was not triggered. The increased export out of Maine, however, does add to the downstream north–south constraint. The existing qualified capacity for the combined NNE portion of the system was 8,394 MW in FCA #9. The 90/10 peak load of the combined NNE area was forecast to be approximately 6,500 MW in 2018. After the inclusion of the Greater Boston upgrades, the export capability out of the zone is projected to be 2,675 MW.

      - Zonal Modeling for FCA #10

On May 29, 2015, FERC approved the proposed new boundaries for use in FCA #10. Using the objective criteria for the modeling of capacity zones, the combined NEMA/SEMA/RI area was evaluated and will be modeled for the first time as a single import-constrained capacity zone in FCA #10, called the Southeast New England capacity zone. In the north, the Maine/New Hampshire/Vermont area was evaluated and will not be modeled as a single export-constrained zone for FCA #10. Similar to previous FCAs, Connecticut was evaluated as a potential import-constrained zone but was merged with the “Rest-of-Pool” capacity zone and will not be modeled as a separate import-constrained capacity zone for FCA #10. The Western Massachusetts capacity zone will continue to form the basis of the Rest-of-Pool zone.

### Capacity Zone Formation in Future Years of the Planning Horizon

The FERC-approved methodology for determining capacity zones is focused on the review of system conditions for the capacity commitment period associated with the upcoming FCA (in this case the 2019/2020 period associated with FCA #10). The final set of capacity zones for periods beyond FCA #10 will not be known until all the relevant system conditions have been identified and evaluated. In particular, the zone-formation process must be responsive to retirements, rejected delist bids, and other system changes.

The identification of import- or export-constrained capacity zones during the future years of the planning horizon will depend on prevailing system conditions at that time. The ISO will continue to evaluate the import constraints for those portions of the system with higher concentrations of load expected to be net-importing regions of power. The ISO also will continue to review the Southeast New England and Connecticut areas of the system for import constraints, unless this portion of the system has significant net additions of capacity resources. Import-constrained areas with large retirements will more likely be modeled as import-constrained capacity zones.

Maine and the other portions of the Northern New England capacity zone have historically been, and continue to be, net exporting areas of the system. Significant new additions of capacity resources will make these areas more likely to be export constrained.

## Analyzing Operable Capacity

The ISO performs systemwide operable capacity analysis to estimate the net capacity and determine the operable capacity margin that will be available under two scenarios (i.e., using the 50/50 and 90/10 forecasts of peak load). The analysis assumes that peak-load conditions are reduced to fully reflect behind-the-meter PV (i.e., both embedded and nonembedded PV; refer to Section 3.3). It also assumes that to meet the assumed peak demand plus operating-reserve requirements, the capacity in New England will only be equal to the net ICR, which, as stated in Section 4.1.1, relies on OP 4 actions and tie-line benefits. A negative margin for a specific scenario indicates the extent that possible mitigation actions would be required through predefined protocols, as prescribed in the ISO’s Operating Procedure No. 4, Action during a Capacity Deficiency, or Operating Procedure No. 7 (OP 7), Action in an Emergency.

Figure 4-4, Table 4-10, and Table 4-11 show the results of the ISO’s systemwide operable capacity analysis for 2015/2016 to 2024/2015 commitment periods. The analysis does not take into account operable capacity needs for RSP subareas. The results show that if the loads associated with the 50/50 forecast occurred, the ISO could expect New England to experience a negative operable capacity margin ranging from 6 MW to 160 MW for four of the 10 years of the study period. The ISO system operators potentially would have to rely on load and capacity relief from OP 4 actions to mitigate the possible capacity shortages.

Figure 4-4: Projected summer operable capacity analysis, 2015 to 2024 (MW).

Note: Each year indicates the starting year for the respective capacity commitment period. Total net capacity values for 2015/2016 to 2018/2019 are based on the net ICR approved by FERC. The net capacity for 2020/2021 to 2024/2025 is based on representative net ICR values calculated by applying an indicative reserve margin of 14.3% to the 50/50 load forecast for the year. The net capacity for 2019/2020 is the net ICR for 2019/2020 currently under development, which will be filed with FERC in November 2015.

Table 4-10
Projected New England Operable Capacity Analysis for Summer, 2015 to 2024,
Assuming 50/50 Loads (MW)

| Capacity Situation (Summer MW) | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Load (50/50 forecast) net of BTMNEL PV(a) | 28,251 | 28,673 | 29,066 | 29,483 | 29,861 | 30,182 | 30,487 | 30,804 | 31,131 | 31,455 |
| Operating reserves(b) | 2,375 | 2,375 | 2,375 | 2,375 | 2,375 | 2,375 | 2,375 | 2,375 | 2,375 | 2,375 |
| Total requirement | 30,626 | 31,048 | 31,441 | 31,858 | 32,236 | 32,557 | 32,862 | 33,179 | 33,506 | 33,830 |
| Installed capacity (net ICR)(c) | 33,391 | 33,764 | 34,061 | 34,189 | N/A | 34,500 | 34,800 | 35,200 | 35,600 | 36,000 |
| Assumed unavailable capacity | −2,100 | −2,100 | −2,100 | −2,100 | −2,100 | −2,100 | −2,100 | −2,100 | −2,100 | −2,100 |
| Total net capacity(d) | 31,291 | 31,664 | 31,961 | 32,089 | N/A | 32,400 | 32,700 | 33,100 | 33,500 | 33,900 |
| Operable capacity margin(e) | 665 | 616 | 520 | 231 | N/A | −157 | −162 | −79 | −6 | 70 |

(a)	These values are net of PV, consistent with the other projections in this section. Load in this section equals the gross forecast (which already accounts for BTMEL PV) and subtracts the BTMNEL PV. Because this table uses net ICR, the ISO does not subtract the EE forecast; EE is considered part of the resource mix meeting the ICR.

(b) 	The 2,375 MW value of operating reserves is based on the following assumptions: a first contingency of 1,400 MW plus a 25% increase in the 10-minute operating reserve to compensate for nonperformance of the reserve generating units (as discussed in Section 4.4.1) equal to 350 MW, and 30-minute reserves of 625 MW (one half of 1,250 MW).

(c)	Net ICR values for 2015/2016 to 2018/2019 are the latest values approved by FERC. These net ICR values were developed using 2014 CELT Report loads. The net ICR values for other years are consistent with the representative future net ICR values in Table 4-7.

(d) 	The net capacity values are equal to the net ICR minus the assumed unavailable capacity.

(e) 	“Operable capacity margin” equals “total net capacity” minus “total requirement.”

Table 4-11
Projected New England Operable Capacity Analysis for Summer, 2015 to 2024,
Assuming 90/10 Loads (MW)

| Capacity Situation (Summer MW) | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Load (90/10 forecast) net of BTMNEL PV | 30,600 | 31,053 | 31,481 | 31,933 | 32,341 | 32,697 | 33,037 | 33,389 | 33,746 | 34,104 |
| Operating reserves(a) | 2,375 | 2,375 | 2,375 | 2,375 | 2,375 | 2,375 | 2,375 | 2,375 | 2,375 | 2,375 |
| Total requirement | 32,975 | 33,428 | 33,856 | 34,308 | 34,716 | 35,072 | 35,412 | 35,764 | 36,121 | 36,479 |
| Installed capacity (net ICR)(b) | 33,391 | 33,764 | 34,061 | 34,189 | N/A | 34,500 | 34,800 | 35,200 | 35,600 | 36,000 |
| Assumed unavailable capacity | −2,100 | −2,100 | −2,100 | −2,100 | −2,100 | −2,100 | −2,100 | −2,100 | −2,100 | −2,100 |
| Total net capacity(c) | 31,291 | 31,664 | 31,961 | 32,089 | N/A | 32,400 | 32,700 | 33,100 | 33,500 | 33,900 |
| Operable capacity margin(d) | −1,684 | −1,764 | −1,895 | −2,219 | N/A | −2,672 | −2,712 | −2,664 | −2,621 | −2,579 |

(a)	The 2,375 MW value of operating reserves is based on the following assumptions: a first contingency of 1,400 MW plus a 25% increase in the 10-minute operating reserve to compensate for nonperformance of the reserve generating units (as discussed in Section 4.4.1) equal to 350 MW, and 30-minute reserves of 625 MW (one half of 1,250 MW).

(b) 	 Net ICR values for 2015/2016 to 2018/2019 are the latest values approved by FERC. These net ICR values were developed using 2014 CELT Report loads. The net ICR values for other years are consistent with the representative future net ICR values in Table 4-7.

(c) 	The net capacity values are equal to the net ICR minus the assumed unavailable capacity.

(d) 	“Operable capacity margin” equals “total net capacity” minus “total requirement.”

Figure 4-4 and Table 4-11 show that New England could experience large negative operable capacity margins of approximately 1,680 MW as early as summer 2015 if the 90/10 peak loads occurred. Thus, throughout the study period, New England could potentially rely on load and capacity relief from OP 4 actions if the projected 90/10 peak loads occurred. Assuming the exact amount of resources needed to meet the 0.1 day per year loss-of-load expectation (LOLE) analysis (refer to Figure 4-1) is purchased in the FCA (i.e., the net ICR), this negative operable capacity margin would increase to approximately 2,220 MW by 2018. Using an indicative reserve margin of 14.3%, the operable capacity margin stays relatively constant from 2020 through 2024 in the negative 2,600 MW to negative 2,700 MW range.

## Determining Operating Reserves and Regulation

In addition to capacity resources being available to meet the region’s actual demand for electricity, as discussed in Section 4.1, the system needs a certain amount of resources that can provide operating reserves and system regulation. The overall mix of resources providing operating reserves must be able to respond quickly to system contingencies stemming from equipment outages. The ISO may also call on these resources to provide regulation service for maintaining system frequency and external transactions with neighboring balancing authority areas or to serve load during peak demand conditions. A suboptimal mix of resources overall, with limited amounts of flexible operating characteristics, could result in the system’s dependence on more costly resources to provide these services. In the worst case, reliability would be degraded.

Several types of resources in New England have the operating characteristics to respond to contingencies, provide regulation service, and serve peak demand. The generating units that provide operating reserves can respond to contingencies within 10 or 30 minutes and can either be synchronized or not synchronized to the power system. Synchronized (i.e., spinning) operating reserves are on-line resources that can increase output. Nonsynchronized (i.e., nonspinning) operating reserves are off-line, fast-start resources that can be electrically synchronized to the system quickly, reaching maximum output within 10 minutes or within 30 minutes. During real-time daily operations, the ISO determines operating-reserve requirements for the system as a whole and for major import-constrained areas.

This section discusses the need for operating reserves, both systemwide and in major import areas, and the use of specific types of fast-start resources to fill these needs. An overview of the Forward Reserve Market and a forecast of representative future operating-reserve requirements for Greater Southwest Connecticut, Greater Connecticut, and BOSTON are provided. This section also discusses the likely need for additional flexible resources identified by the studies and other actions supporting the strategic planning of the region, as discussed in Section 8.

### Systemwide Operating-Reserve Requirements

The ISO’s operating-reserve requirements, as established in Operating Procedure No. 8, Operating Reserve and Regulation (OP 8), are used to protect the system from the impacts associated with a loss of generating or transmission equipment within New England. A certain amount of the power system’s resources must be available to provide operating reserves to assist in addressing systemwide contingencies.

To comply with OP 8, the ISO must maintain sufficient reserves in its balancing authority area during normal conditions to be able to replace within 10 minutes the first-contingency loss (N−1) in the New England Reliability Balancing Authority Area multiplied by the contingency-reserve adjustment (CRA) factor for the most recent completed quarter. The current total 10-minute operating-reserve requirement reflecting the CRA factor is 1.25% of the first-contingency loss. In addition, OP 8 requires the ISO to maintain sufficient reserves to address the uncertainties associated with resource nonperformance, as well as load-forecast error. To meet this need, the ISO must be able to replace at least 50% of the next-largest contingency loss (N−1−1) within 30 minutes plus a replacement reserve requirement of 180 MW during Eastern Standard Time and 160 MW during Daylight Savings Time. The higher amount set for the winter period is to accommodate the additional peak-load ramping and fuel uncertainty usually experienced during this period.

Typically, the largest first-contingency loss is between 1,300 and 1,700 MW, and 50% of the next-largest contingency loss is between 600 and 750 MW. These resources typically consist of some combination of the two largest on-line generating units or imports on the Phase II interconnection with Québec.

In accordance with NERC and NPCC criteria for power system operation, ISO Operating Procedure No. 19 (OP 19), Transmission Operations, requires system power flows to stay within applicable emergency limits of the power system elements that remain after the loss of any other power system element (N−1). This N−1 limit may be a thermal, voltage, or stability limit of the transmission system. OP 19 further stipulates that within 30 minutes of the loss of the first-contingency element, the system must be able to return to a normal state that can withstand a second contingency. To implement these OP 19 requirements, and as set forth in OP 8, operating reserves must be distributed throughout the system. This requirement is designed to ensure that the ISO can activate all reserves without exceeding transmission system limitations and that the operation of the system remains in accordance with NERC, NPCC, and ISO New England criteria and guidelines.

### Locational Reserve Needs for Major Import Areas

To maintain system reliability further, the ISO maintains certain reserve levels within major importing subareas of the system. The amount and type of operating reserves needed within these subareas depend on many factors, including load levels, the projected peak load of the subarea, and the economic and physical operating characteristics of the generating units within the subarea. The systemwide commitment and economic dispatch of generation, system topology, system reliability constraints, special operational considerations, possible resource outages, and other system conditions are additional factors that can affect the required levels of reserve within subareas.

The ISO analyzes and determines how the generating resources within the subareas must be committed to meet the following day’s operational requirements and withstand possible contingencies, including the most critical contingencies that determine the transmission import capability into the subarea. If maximizing the use of transmission import capability to meet demand is more economical, the subarea will require more local operating reserves to protect for contingencies. If using import capability to meet demand is less economical, generation located outside the subarea could provide operating reserves, thus reducing operating-reserve support needed within the subarea.

Table 4-12 shows representative future operating-reserve requirements for Greater Southwest Connecticut, Greater Connecticut, and BOSTON. These estimated requirements are based on the same methodology used to calculate the requirements for the locational FRM. The estimates account for representative future system conditions for load, economic generation, generation availability, N−1 and N−1−1 transfer limits, and normal criteria contingencies for generation and transmission in each subarea. The analysis accounts for transmission upgrades consistent with Table 4-9 (in Section 4.2.1). The representative values show a range to reflect the load and resource uncertainties associated with future system conditions. Table 4-12 also shows the existing amount of fast-start capability located in each subarea resulting from the fast-start resource offered into past FRM auctions. The total 10-minute operating reserve values associated with the FRM reflect the contingency reserve adjustment, but this adjustment does not affect the amount of reserves distributed to locations (i.e., the reserve values for BOSTON, SWCT, and Greater CT did not increase).

Table 4-12 
Representative Future Operating-Reserve Needs in Major New England Import Areas (MW)

| Area/Improvement | Year(a) | Range of Fast-Start Resources Offered into the Past Forward Reserve Auctions (MW)(b) | Representative Future Locational Forward Reserve Market Needs (MW) |  |
| --- | --- | --- | --- | --- |
|  |  |  | Summer(c) (Jun to Sep) | Winter(c) (Oct to May) |
| Greater Southwest Connecticut(d) | 2015 | 199–515 | 138(e) | 36(e) |
|  | 2016 |  | 50–300 | 0–50 |
|  | 2017 |  | 50–300 | 50–100 |
|  | 2018 |  | 100–350 | 100–150 |
|  | 2019 |  | 100–350 0, if CPV is in service | 50–100 0, if CPV is in service |
| Greater Connecticut(f, g) Interstate Reliability Project (IRP) of the New England East–West Solution (NEEWS)(f) | 2015 | 659–1,563(h) | 714(e) | 152(e) |
|  | 2016 |  | 300–850 0-400, if IRP is in service | 0–250 0, if IRP is in service |
|  | 2017 |  | 0–450 | 0 |
|  | 2018 |  | 0–500 | 0 |
|  | 2019 |  | 0–400 0, if CPV is in service | 0 |
| BOSTON(g, i) | 2015 | 0–441 | 331(e) | 0(e) |
|  | 2016 |  | 200–600 | 0–500 |
|  | 2017 |  | 200–650 | 0–50 |
|  | 2018 |  | 200–650 0, if Footprint is in service | 0 |
|  | 2019 |  | 250–650 0, if Footprint is in service | 0 |

- The market year is from June 1 through May 31 of the following year.

- These values are the range of the megawatts of resources used to meet historical needs.

- “Summer” means June through September of a capability year; “winter” means October of the associated year through May of the following year (e.g., the 2015 winter values are for October 2015 through May 2016). The representative values show a range to reflect uncertainties associated with the future system conditions. The operating limits shown below reflect those assumed at the time of the analysis.

- The assumed N−1 and N−1−1 values that reflect transmission import limits into Greater SWCT are 3,200 MW and 2,300 MW, respectively. The 2019 values for Greater Southwest Connecticut also show the forward-reserve needs, assuming that the 725 MW CPV Towantic generating station will be in service by June 2018.

- These values are actual locational forward-reserve needs. The projections of the needs for future years are based on assumed contingencies.

- For Greater Connecticut, the assumed import limits reflect an N−1 value of 3,050 MW and an N−1−1 value of 1,850 MW after the in-service of Greater Springfield Reliability Project (GSRP) (see Section 6.4.2) in 2013. With the Card–Lake Road line assumed in service at the end of 2016, the definition of the import interface will change, so that the assumed Greater Connecticut N−1 and N−1−1 import limits will be 2,800 MW and 1,600 MW respectively, increasing to 2,950 MW and 1,750 MW, respectively, starting in 2018. The 2019 values for Greater Connecticut also show the forward-reserve need, assuming that the 725 MW CPV Towantic generating station will be in service by June 2018.

- In some circumstances when transmission contingencies are more severe than generation contingencies, shedding some nonconsequential load (i.e., load shed that is not the direct result of the contingency) may be acceptable.

- These values include resources in Greater Southwest Connecticut.

- The assumed N−1 and N−1−1 values reflect the transmission import limits into BOSTON of 4,850 MW and 4,175 MW, respectively, and the impacts of the retirement of Salem Harbor units #1–#4 and the North Shore Upgrade. The operating-reserve values for BOSTON would be lower with transmission upgrades or without the consideration of the common-mode failure of Mystic units #8 and #9, which are assumed would trip (up to 1,400 MW) because of a failure of the units’ common fuel supply. The 2018 and 2019 values for NEMA/Boston also show the forward-reserve need, assuming that the 674 MW Footprint Power generating station will be in service by June 2017.

Because the local contingency needs in Greater SWCT are nested within CT (i.e., operating reserves meeting the Greater SWCT need also meet the Greater Connecticut need), resources installed in the Greater SWCT area also would satisfy the need for resources located anywhere in Greater Connecticut.

#### Greater Southwest Connecticut

As shown in Table 4-12, Greater SWCT is expected to require as much as 350 MW of operating reserves in the area during the study period. Consistent with ISO’s operating experience of recent years, the interface into Greater Southwest Connecticut is expected to be heavily loaded because of economical transfers into the area. As a result of the heavy loading of the interface capability, more reserves must be carried locally within Greater SWCT. The CPV Towantic generation, when in service, is expected to reduce the local reserve need starting in 2019.

#### Greater Connecticut

Past RSPs and market signals had identified the need for in-merit and fast-start resources in Greater Connecticut to meet reliability needs and reduce out-of-merit market costs. As a result of resource development, Greater Connecticut is now projected to have adequate fast-start resources, and the economic performance of this area is expected to improve. In the past, up to 1,563 MW of fast-start resources were available to meet Greater Connecticut’s locational FRM requirements. For 2015, approximately 1,200 MW of fast-start resources are available to meet the 714 MW of the reserve need. The analysis assumed that the NEEWS Interstate Reliability Project would be in service by the end of 2015 (see Section 6.4.2). This project would both increase system transfer capabilities and result in the Lake Road generating plant being electrically within Greater Connecticut. These changes would allow the ISO more flexibility in achieving the most economical energy production while maintaining an adequate amount of operating reserves for Greater Connecticut. Similar to Greater Southwest Connecticut, a reduced local reserve need is expected for Greater Connecticut starting in 2019 when the CPV Towantic generation is in service.

#### BOSTON

The operating-reserve needs for the BOSTON subarea shown in Table 4-12 reflect the possible simultaneous contingency loss of Mystic units #8 and #9. The retirement of the Salem Harbor units in 2014, which reduces the ability to serve load economically within the BOSTON subarea, and the heavy loading of the interface into Boston for economical energy transfer into the area, resulted in increased reserve needs for this area during summer 2015. However, the planned addition of Footprint Power (which increases local generation in this area) is expected to reduce the local reserve needs starting in 2018 (refer to Table 4-12, note i).

If the transmission lines were fully utilized to import lower-cost generation into BOSTON, this subarea would need to provide operating reserves to protect against the larger of (1) the loss of the largest generation source within the subarea and a transmission line or (2) the loss of two transmission lines into the subarea. As much as 441 MW of fast-start resources were offered into the past FRM auctions. The expected amount of existing fast-start resources located in BOSTON will likely meet the estimates of representative local reserve requirements for BOSTON during the study timeframe.

#### Summary of Operating Reserve Needs in Major Subareas

New England must meet its overall operating-reserve needs and have sufficient reserves in subareas to meet reliability requirements. The need for operating reserves has grown for Greater SWCT, but existing resources will be sufficient to meet this need. The recent and expected additions of fast-start resources in Greater Connecticut provide needed operating flexibility as well as operating reserves. BOSTON likely has sufficient operating reserves, especially with the addition of the Footprint Power generating plant. Planned baseload resources (i.e., those assumed to run for long continuous hours at a constant output with little flexibility) also would decrease the amounts of reserves required within these subareas. Any reduction in traditional baseload resources in these subareas would increase the operating-reserve need.

## Summary

Sufficient resources are projected for New England through 2023, and a shortfall of approximately 30 MW is projected for 2024. The planning analysis accounts for new resource additions that have responded to market improvements and low net-load growth, which reflects both the forecasts of energy efficiency resources and behind-the-meter PV. Although the recent trend of generation resource retirements has abated, additional resources are likely to retire. The ISO is committed to procuring adequate demand and supply resources through the FCM and expects the region to install adequate resources to meet the physical capacity needs that the ICRs will define for future years.

Further improvements to the wholesale markets aim to encourage the development of any future needed resources. In response to the FERC order on FCA #9, the ISO worked with stakeholders to explore how to apply the PV forecast in the Installed Capacity Requirement. The ISO accounts for the amounts of PV that participate in the FCM and the wholesale energy markets to ensure that each category is treated in accordance with market rules and that resources are not counted more than once.

The ISO also worked with stakeholders to implement criterion and processes for creating, modifying, or collapsing capacity zones, as appropriate. The results, combined with resource adequacy studies show that the most reliable and economic place for developing new resources is in NEMA/Boston and SEMA/RI. Other enhancements to the FCM and the FRM are designed to better meet operational needs. Additional approved and planned market incentives increase the likelihood of resource development where and when needed. The FCA clearing prices are now locked in for seven years for new resources. This longer period improves financial stability and strengthens investment signals for new resource development. Pay for performance is designed to promote system reliability by providing resources with incentives to perform when dispatched. FCA #9 introduced the sloped demand curve, and this auction successfully resulted in the addition of 1,060 MW of new generation resources.

By design, the level of the ICR specified for New England could necessitate the use of specific OP 4 actions because the ICR calculation relies on the load relief these actions provide to meet the system’s resource adequacy planning criterion. Several factors would affect the frequency and extent of OP 4 actions, including the amount of resources procured to meet capacity needs, their availability, and actual system loads. The results of operable capacity studies show that, beginning in 2020, the need for load and capacity relief by OP 4 actions will be approximately 2,600 MW to 2,700 MW during extremely hot and humid summer peak-load conditions. This amount is likely achievable through OP 4 actions by depleting operating reserves, scheduling emergency transactions with neighboring systems, operating real-time emergency generators, and implementing 5% voltage reductions.

This section shows that the region could meet representative operating-reserve requirements for the system as currently planned. Fast-start resources with a short lead time for project development can satisfy near-term operating-reserve requirements while providing operational flexibility to major load pockets and the system overall. Properly locating and sizing economical baseload resources within major load pockets decreases the amount of reserves required within the load pocket and reduces the reliance on transmission facilities. Transmission improvements also can allow for the increased use of reserves from outside these areas.

Preserving the reliable operation of the system will become increasingly challenging with potential retirements and the need for operating flexibility, particularly in light of the reliance on natural gas resources and the increased penetration of variable energy resources (see Section 8 and Section 10). These factors are expected to increase the need for reliable resources, especially flexible resources able to provide operating reserves and ramping capabilities. To help address this need, the ISO has procured additional 10-minute reserves and replacement operating reserve.

# Existing and Future Resource Development in Areas of Need

The development of resources can help meet the long-term needs of the system. This section reviews existing and future generating resources, including the capacity and claimed capability of existing resources, projects proposed through the ISO’s Generator Interconnection Queue, and generator retirements. It also discusses the results of an analysis of potential future retirements and of the development of market resource alternatives in load pockets, which show the most reliable and economic places for resource development.

## Existing Generating Capacity by Subarea, Load Zone, and State

Generating units located close to load centers typically reduce the need for transmission system improvements. Table 5-1 tabulates the existing generating amounts and locations by RSP subarea, load zone, and state.

Table 5-1
RSP15 Generating Capacity by Subarea, State, and Load Zone, 2015 (MW, %)(a)

| RSP Area | State | Load Zone | Summer |  |  | Winter |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Capacity Rating(b) (MW) | % of RSP Subarea | % of State | Capacity Rating(b) (MW) | % of RSP Subarea | % of State |
| BHE | Maine | ME | 917 | 100 | 29 | 895 | 100 | 27 |
| ME | Maine | ME | 846 | 100 | 27 | 928 | 100 | 27 |
| SME | Maine | ME | 1,428 | 100 | 45 | 1,552 | 100 | 46 |
|  | New Hampshire | ME | 0 | 0 | 0 | <1 | 0 | 0 |
|  |  |  | 1,428 | 100 | 45 | 1,552 | 100 | 46 |
| NH | Maine | NH | <1 | 0 | 0 | <1 | 0 | 0 |
|  | Massachusetts | WCMA | 16 | 0 | 0 | 17 | 0 | 0 |
|  | New Hampshire | NH | 4,209 | 99 | 100 | 4,344 | 99 | 100 |
|  | Vermont | NH | 1 | 0 | 0 | 1 | 0 | 0 |
|  |  | VT | 34 | 1 | 8 | 36 | 1 | 7 |
|  |  |  | 35 | 1 | 8 | 37 | 1 | 7 |
|  |  |  | 4,260 | 100 | 108 | 4,399 | 100 | 107 |
| VT | New Hampshire | NH | 1 | 0 | 0 | 2 | 1 | 0 |
|  |  | VT | 4 | 1 | 0 | 3 | 1 | 0 |
|  |  |  | 5 | 1 | 0 | 6 | 1 | 0 |
|  | Vermont | NH | 88 | 27 | 20 | 89 | 20 | 16 |
|  |  | VT | 238 | 72 | 54 | 342 | 78 | 63 |
|  |  |  | 325 | 99 | 74 | 431 | 99 | 79 |
|  |  |  | 330 | 100 | 74 | 437 | 100 | 79 |
| BOSTON | Massachusetts | NEMA | 2,659 | 100 | 21 | 3,068 | 100 | 23 |
|  |  | WCMA | 2 | 0 | 0 | 0 | 0 | 0 |
|  |  |  | 2,661 | 100 | 21 | 3,068 | 100 | 23 |
| CMA/NEMA | Massachusetts | WCMA | 183 | 100 | 1 | 173 | 100 | 1 |
| WMA | Massachusetts | WCMA | 3,593 | 98 | 28 | 3,822 | 98 | 29 |
|  | Vermont | WCMA | 78 | 2 | 18 | 77 | 2 | 14 |
|  |  |  | 3,671 | 100 | 46 | 3,898 | 100 | 43 |
| SEMA | Massachusetts | RI | <1 | 0 | 0 | 0 | 0 | 0 |
|  |  | SEMA | 3,208 | 93 | 25 | 3,103 | 92 | 23 |
|  |  |  | 3,208 | 93 | 25 | 3,103 | 92 | 23 |
|  | Rhode Island | RI | 243 | 7 | 13 | 279 | 8 | 13 |
|  |  |  | 3,451 | 100 | 38 | 3,382 | 100 | 36 |
| RI | Connecticut | RI | 753 | 14 | 9 | 857 | 15 | 10 |
|  | Massachusetts | RI | <1 | 0 | 0 | 0 | 0 | 0 |
|  |  | SEMA | 2,950 | 55 | 23 | 3,152 | 54 | 24 |
|  |  |  | 2,950 | 55 | 23 | 3,152 | 54 | 24 |
|  | Rhode Island | RI | 1,644 | 31 | 87 | 1,844 | 32 | 87 |
|  |  |  | 5,347 | 100 | 119 | 5,854 | 100 | 120 |
| CT | Connecticut | CT | 5,164 | 100 | 61 | 5,333 | 100 | 60 |
| SWCT | Connecticut | CT | 2,320 | 100 | 28 | 2,536 | 100 | 28 |
| NOR | Connecticut | CT | 170 | 100 | 2 | 192 | 100 | 2 |
| Total |  |  | 30,749 |  |  | 32,647 |  |  |

(a) Totals may vary because of rounding.

(b) The values shown are seasonal claimed capability based on the 2015 CELT.

## Summer Seasonal Claimed Capability of New England’s Generating Resources

Table 5-2 shows the megawatt amount of summer seasonal claimed capability of the generating resources, both systemwide and for each RSP subarea, categorized by the assumed operating classification of the resource.

Table 5-2 
2015 Summer Seasonal Claimed Capability for ISO New England Generating Resources,
by Assumed Operating Classification, Systemwide, and by RSP Subarea (MW)

| Area | Baseload(a) | Intermediate(b) | Peaking(c) | Variable(d) |
| --- | --- | --- | --- | --- |
| BHE | 221 | 488 | 160 | 48 |
| BOSTON | 673 | 1,674 | 297 | 17 |
| CMA/NEMA | 42 | 75 | 29 | 37 |
| CT | 3,896 | 712 | 551 | 5 |
| ME | 341 | 244 | 130 | 131 |
| NH | 2,853 | 1,274 | 65 | 68 |
| NOR | 0 | 0 | 170 | 0 |
| RI | 1,522 | 3,759 | 42 | 24 |
| SEMA | 1,903 | 1,367 | 142 | 39 |
| SME | 856 | 522 | 31 | 19 |
| SWCT | 540 | 1,007 | 768 | 5 |
| VT | 169 | 0 | 126 | 35 |
| WMA | 229 | 1,352 | 1,998 | 92 |
| Total(e) | 13,245 | 12,475 | 4,509 | 520 |

(a) 	Baseload units are assumed to run for long continuous hours at a constant output and have little flexibility. For operating classification purposes, bio/refuse, coal, fuel cell, pondage hydro, weekly hydro, nuclear, and thermal steam generators are assumed in the baseload category.

(b) 	Intermediate units have the ability to dispatch flexibly and can follow variations in the system load. Combined-cycle (CC) generators are assumed in the intermediate category.

(c)	Peaking generators can be dispatched to meet peak demand for relatively short periods. Internal combustion, gas turbine, and pumped-storage generators are assumed in the peaking category.

(d) 	Variable units produce energy subject to variations in “fuel” determined by weather. Run-of-river hydro, photovoltaic, and wind generators are assumed in the variable category.

(e) 	Totals may not equal the sum because of rounding.

## Generation Retirement and Additions in New England

Table 5-3 and Figure 5-1 show the actual and projected annual New England generating unit retirements and additions in megawatts of summer seasonal claimed capability for 2010/2011 through 2018/2019, which covers the FCA#1 through FCA #9 periods. Approximately 2,500 MW retired from 2010/2011 through 2015/2016, with 94% of these occurring from 2013 through 2015. The total for known generator retirements will reach approximately 4,050 MW by summer 2018, which includes approximately 1,500 MW of retirements occurring by summer 2017. Generating resource additions occurred throughout the nine-year period. Additional generating resources are expected beyond 2015, including 785 MW in 2016 and 1,022 MW in 2018. During the entire 2010 through 2018 period, the generating unit retirements will outpace additions by approximately 500 MW.

Table 5-3
Actual and Projected Summer SCC Generation Retirements and Additions,
2010 to 2018 (MW)

| Year | Generator Retirements (SCC MW)(a) | Generators Additions (SCC MW)(a) |
| --- | --- | --- |
| 2010 | 1 | 82 |
| 2011 | 5 | 193 |
| 2012 | 145 | 976 |
| 2013 | 469 | 81 |
| 2014 | 683 | 129 |
| 2015 | 1,216 | 267 |
| 2016 | 26 | 785(b) |
| 2017 | 1,498 | 14 |
| 2018 | 5 | 1,022 |
| Total | 4,048 | 3,549 |

(a) 	SCC values reflect generation in service and retired as of June 1.

(b) 	All values are consistent with the CELT report issued May 1, 2015. The number does not reflect the deferral of Footprint Power in service from 2016 to 2017.

Figure 5-1: Actual and Projected Summer SCC generation retirements and additions, 2010 to 2018 (MW).

Even though the region may experience more generating resource retirements than additions by summer 2018, the ISO expects that adequate resources will be available to meet net Installed Capacity Requirements, given the expected growth of PV and EE resources in the region and the 11,299 MW of generating resources actively seeking interconnection. FCA #9 results suggest that resources are responding to the FCM market signals.

## Generating Units in the ISO Generator Interconnection Queue

The interconnection requests in the ISO’s Generator Interconnection Queue reflect the region’s interest in building new generation capacity. Figure 5-2 shows the capacity of the withdrawn, active, and commercial generation-interconnection requests in the queue by RSP subarea as of April 1, 2015. As shown, over 90% of the active project proposals are in the BHE, WMA, BOSTON, SEMA, RI, and SWCT subareas. Together, these six subareas have approximately 10,283 MW under study or development out of 11,299 MW of active projects for New England.

Figure 5-2: Capacity of generation-interconnection requests by RSP subarea, November 1997 to April 2015 (MW).

Notes: All capacities are based on the projects in the ISO Generator Interconnection Queue as of April 1, 2015, that would interconnect with the ISO system. Projects involving only transmission or that did not increase an existing generator’s capacity were excluded. Projects with more than one listing in the queue, representing different interconnection configurations, were counted only once.

Table 5-4 is a summary of the projects in the queue as of April 1, 2015. Since the first publication of the queue in November 1997, 110 generating projects (15,138 MW) out of 410 total generator applications (totaling 79,591 MW) have become commercial. Since the queue’s inception, proposed projects totaling approximately 53,154 MW have been withdrawn, reflecting a megawatt attrition rate of 67%. The 79 active projects in the queue total 11,299 MW. Figure 5-3 shows the resources in the queue, by state and fuel type, as of April 1, 2015. Figure 5-4 shows the total megawatts of the same resources by RSP subarea, and Figure 5-5 shows the fuel types by subarea, expressed as a percentage of the total.

The processing of the interconnection requests in New England has progressed. With the exception of the Maine portion of the system (which has experienced a back log of mostly wind interconnection requests; see Sections 6.3.1 and 10.2), substantially all the generator interconnection requests made through 2014 have completed the system impact study phase or have moved to the Interconnection Agreement and commercialization phases.

Table 5-4
Summary of Queue Projects as of April 1, 2015

| Category of Projects | Projects | Total Capacity (MW) |
| --- | --- | --- |
| Commercial | 110 | 15,138 |
| Active(a) | 79 | 11,299 |
| Withdrawn | 221 | 53,154 |
| Total | 410 | 79,591 |

(a) 	Source: NEPOOL Participants Committee COO Report (April 2015), http://www.iso-ne.com/static-assets/documents/2015/04/april-2015-coo-report.pdf.

Figure 5-3: Resources in the ISO Generator Interconnection Queue, by state and fuel type, as of April 1, 2015 (MW and %).

Notes: The “Other Renewables” category includes wood, solar, and fuel cell capacity. The totals for all categories reflect all queue projects that would interconnect with the system and not all projects in New England.

Figure 5-4: Resources in the ISO Generator Interconnection Queue, by RSP subarea and fuel type, as of April 1, 2015 (MW).

Figure 5-5: Percentage of resources in the ISO Generator Interconnection Queue, by RSP subarea and fuel type, as of April 1, 2015.

The ISO is working with stakeholders to improve the interconnection process. The goal is to reduce the time taken to complete system impact studies for new inverter-based generators and address the Interconnection Queue backlog, particularly for generators in weak areas of the system, such as Maine. The initiative also seeks to address curtailment and performance issues in system operations for inverter-based generators and to meet the modeling and performance requirements that new NERC standards are introducing.

## Strategic Transmission Analysis—Generator Retirement Analysis

Over the past several years, the ISO has conducted several strategic transmission analyses. The initial phase of a strategic transmission analysis (STA) on potential generator retirements was completed in 2012, with additional sensitivity analyses continuing through 2013. This study assessed transmission issues associated with potential generator retirements, examining the loss of approximately 8,300 MW of coal- and oil-fired generating units. The study did not consider the regional exposure to the nonprice retirement of active demand resources, which remains another risk to meeting capacity requirements.

The results of this STA showed that these retirements would cause resource shortages and, to a lesser degree, transmission-reliability constraints in New England that would require over 6,000 MW of resources to be retained, repowered, or replaced to satisfy the region’s Installed Capacity Requirement (see Section 4.1.1). The repowering of many of these existing generator plants with natural gas would not require a major expansion of new system capacity resources or improvements to the electrical transmission system, although more natural gas transportation would be required. The addition of new capacity electrically located at the region’s energy trading hub (the Hub) (see Section 2.3), or the addition of new capacity deliverable to the Hub, would allow the region to serve most of its load reliably.

The SEMA, RI, NEMA, and CT load zones, however, may need some resources to address zonal or more local transmission reliability concerns that would vary depending on the timing and location of retirement requests. As noted in Section 4.1.3.3, of the potential generator station retirements studied, both Brayton Point and Norwalk Harbor have submitted nonprice retirement requests.

## Analysis of Market-Resource Alternatives

Developing resources in load pockets with potential generator retirements is beneficial to the system, especially in areas with growing transmission needs. In response to PAC requests for more details about system locations where resource development could meet system needs, the ISO applied the lessons learned from the Vermont/New Hampshire and Greater Hartford Central Connecticut studies to a study of the Southeast Massachusetts/Rhode Island area. By applying a hybrid approach that incorporated generation and demand-side management (DSM) injections simultaneously, this study was more robust than the previous MRA studies.

The study demonstrated how resources of various sizes and at various locations could meet thermal system performance requirements for 2022. The assumptions for this hybrid MRA study were the same as those used for the SEMA/RI N-1 and N-1-1 needs assessments and focused on resolving some of the violations identified in the two studies.

The MRA study provided theoretical signals to developers and stakeholders on desirable electrical injection locations in the area that could possibly address some of the thermal issues identified in the needs assessment. The study also provided a test combination of generation and demand-side management injections of approximately 1,540 MW total (1,495 MW of generation and 45 MW of demand-side management spread across nine locations in SEMA/RI) to remove many of the thermal constraints identified in the SEMA/RI needs assessments. Table 5-5 shows the subarea locations and types of resources that could relieve transmission overloads in SEMA/RI.

Table 5-5
Desirable Amounts and Locations of MRA Additions (MW)(a)

| MRA Subarea | Suggested MRA Locations | Suggested Type of Injection(b) | Test Scenario |  |
| --- | --- | --- | --- | --- |
|  |  |  | Injection (MW) | Lingering Transmission Needs after the Test Injection |
| Eastern RI–Brayton Pt. | Pawtucket region | Small gen/DSM | 10 | 2 transmission needs (Cumberland, RI region lines) |
|  | Brayton Pt. region | Large gen | 800 |  |
| Somerset–Tremont | Tiverton region | Large gen | 350 | 9 transmission needs (Swansea region line, Tremont region line, Acushnet region line, Portsmouth region 69 kV lines, and transformers) |
|  | North Portsmouth region | Large gen | 200 |  |
|  | West Dartmouth region | Small gen/DSM | 10 |  |
|  | Downtown Fall River region | Small gen/DSM | 25 |  |
| Cape | Mid-Lower-Outer Cape regions | Large gen | 100 | 5 transmission needs (Upper-Cape region lines) |
| Farnum–Western RI | Warwick region | Small gen | 20 | 1 transmission needs (North Kingstown region line) |
| W. Walpole–South Shore | Weymouth region | Small gen | 25 | 2 transmission needs (Millbury region line, Holbrook region transformer) |

(a) 	As a result of feedback from the PAC on the SEMA/RI MRA study, the ISO is considering the application of the capacity deliverability standard, as defined in ISO Planning Procedure No. 10, Planning Procedure to Support the Forward Capacity, in a future MRA study; http://www.iso-ne.com/static-assets/documents/rules_proceds/isone_plan/pp10/pp10.pdf (January 13, 2015).

(b)	 “Small gen” refers to a small generating unit (<20 MW and requiring small generator interconnection procedures). “Large gen” refers to a large generating unit (≥20 MW and requiring large generator interconnection procedures).

## Summary

Some of the 11,299 MW of resources in the interconnection queue will likely be developed to meet future resource needs. Resources fueled by natural gas are being proposed near the load centers in southern New England. Proposed onshore wind resources are predominantly in northern New England, and offshore resources are being proposed off the southeastern New England coast.

In general, new resources in electrical proximity to the Hub can reliably serve most of the region’s load. Resource development close to load pockets, and particularly the SEMA/RI and NEMA/Boston areas, improves system reliability. The ISO’s analysis of market resource alternatives in the SEMA/RI load pocket shows the critical load levels and hypothetical supply-side and load-reduction resources that could eliminate thermal overloads for normal and both N-1 and N-1-1 contingency conditions.

Section 8 discusses the region’s immediate concerns about the availability of natural-gas-fired and oil-fired generating units and their fuel certainty to produce electrical energy, especially during winter peak periods. That section also discusses the region’s Strategic Planning Initiative and other stakeholder efforts to address these challenges over the long term.

# Transmission System Performance Needs Assessments and Upgrade Approvals

The ISO and regional stakeholders have made significant progress developing transmission solutions in New England that address existing and projected transmission system needs. Major transmission projects and other projects help maintain system reliability and enhance the region’s ability to support a robust, competitive wholesale power market by reliably moving power from various internal and external sources to the region’s load centers.

This section discusses the need for transmission security and provides an overview of the New England transmission system, updates on the performance of the system, and the status of several transmission planning studies. The progress of current major transmission projects in the region and the various types of transmission upgrades taking place in the region as of June 2015 are also provided. The transmission planning studies account for known plans for resource additions and attritions (see Section 4 and Section 5) and the material effects of the EE forecast and the PV forecast (see Section 3). Previous RSPs, various PAC presentations, and other ISO reports contain information regarding the detailed analyses associated with many of these efforts.

The Transmission Planning Process Guide details the existing regional system planning process and how transmission planning studies are performed, and the Transmission Planning Technical Guide details the current standards, criteria, and assumptions used in transmission planning studies. The ISO anticipates revising the Transmission Planning Process Guide to be consistent with the final FERC Order No. 1000 requirements.

## The Need for Transmission Security

A reliable, well-designed transmission system that provides regional transmission service is essential for complying with mandatory reliability standards (see Section 2.1.8) and supporting the secure dispatch and operation of generation that delivers numerous products and services. The numerous products and services of a reliable transmission system include the following:

- Capacity

- Electric energy

- Operating reserves

- Load-following

- Automatic generation control

- Immediate contingency response to sudden resource or transmission outages

A secure transmission system also plays an important role in the following functions:

- Improving access to and the reliability of supply resources

- Regulating voltage and minimizing voltage fluctuations

- Stabilizing the grid after transient events

- Facilitating the efficient use of regional supply and demand resources

- Reducing the amount of reserves necessary for the secure operation of the system

- Facilitating the scheduling of equipment maintenance

- Assisting neighboring balancing authority areas, especially during major contingencies affecting their reliability, and ensuring the reliability of the interconnected system

## Overview of New England’s Transmission System

In New England, the power system provides electricity to diverse areas, ranging from rural agricultural to densely populated cities, and it integrates widely dispersed and varied types of power supply resources. Geographically, approximately 20% of New England’s peak loads are in the northern states of Maine, New Hampshire, and Vermont, and 80% are in the southern states of Massachusetts, Connecticut, and Rhode Island. Although the land area in the northern states is larger than the land area in the southern states, the greater urban development in southern New England creates the relatively larger demand and corresponding transmission density. This means that while the demands on the New England transmission system can vary widely, the system must reliably operate under the wide-ranging conditions present in the region at all times—in compliance with mandatory reliability standards—to move power from various internal and external sources to the region’s load centers.

The New England transmission system consists of mostly 115 kV, 230 kV, and 345 kV transmission lines, which in northern New England generally are longer and fewer in number than in southern New England. The region has 13 interconnections with neighboring power systems in the United States and Eastern Canada. Nine interconnections are with New York (NYISO) (two 345 kV ties; one 230 kV tie; one 138 kV tie; three 115 kV ties; one 69 kV tie; and one 330 MW, ±150 kV high-voltage direct-current (HVDC) tie—the Cross-Sound Cable interconnection). New England and the Maritimes (New Brunswick Power Corporation) are connected through two 345 kV AC ties, the second of which was placed in service in December 2007. New England also has two HVDC interconnections with Québec (Hydro-Québec). One is a 120 kV AC interconnection (Highgate in northern Vermont) with a 225 MW back-to-back converter station, which converts alternating current to direct current and then back to alternating current. The second is a ±450 kV HVDC line with terminal configurations allowing up to 2,000 MW to be delivered at Sandy Pond in Massachusetts (i.e., Phase II).

Because of the general age of the transmission system in New England, many assets are reaching their end of life and are requiring significant refurbishment. These activities are spread across the system and are being addressed either individually or as part of an ongoing solutions assessment.

Figure 6-1 shows the approximate geographic region of major 345 kV transmission projects throughout the six New England states.

Figure 6-1: Approximate geographic region of each of the major 345 kV transmission projects in New England, as of June 1, 2015.

Upgrades associated with asset condition have been ongoing for years, and from July 2014 to June 2015, equipment owners have made the following presentations to stakeholders:

- 1779 line (South Meadow–South Windsor Junction) Partial Rebuild

- Montville 345/115 kV Autotransformers Replacement

- Norwood Light and Electric Asset Replacement—447-508/509 Dean Street Tap

- Somerset Switchyard Rebuild

- Line 372 (Mystic–Kingston Street) Rebuild

- 345 kV Line Structure Replacements (312, 381, and 354 lines)

In addition, the needs assessment for the 136 line (Falmouth Tap–Hatchville–Mashpee) was presented to the PAC.

## Northern New England

The northern New England (NNE) area encompasses the transmission system in Maine, New Hampshire, and Vermont. Studies of each of these states are being conducted to address the transmission system’s short-term and long-term needs.

### Northern New England Transmission

New England and New Brunswick have two 345 kV interconnections leading into 345 kV corridors at Orrington, Maine. The corridors span hundreds of miles and eventually tie into Massachusetts. The transmission system throughout northern New England is limited in capacity; it is weak in places and faces numerous transmission security concerns. Underlying the limited number of 345 kV transmission facilities are a number of old, low-capacity, and long 115 kV lines. These lines serve a geographically dispersed load, as well as the concentrated, more developed load centers in southern Maine, southern New Hampshire, and northwestern Vermont.

The two most significant issues facing the area have been to maintain the general performance of the long 345 kV corridors, particularly through Maine, and to ensure sufficient system security to meet demand. The region faces thermal and voltage performance issues and stability concerns. The system of long 115 kV lines, with weak sources and high real- and reactive-power losses, is exceeding its ability to integrate generation and efficiently and effectively serve load. Also, in many instances, the underlying systems of 34.5 kV, 46 kV, and 69 kV lines are exceeding their capabilities, and some are being upgraded, placing greater demands on an already stressed 115 kV system.

Over the past several years, the addition of generation in Maine and New Hampshire, in combination with the area’s limited transfer capability, has increased the likelihood of many northern New England interfaces operating near their limits, creating restrictions on northern resources. Because these interface limits depend on generation dispatch, the reliable operation of the system becomes more complex and difficult. Additional concerns in northern New England include limited system flexibility to accommodate maintenance outages, limited dynamic reactive-power resources, and high real- and reactive-power losses. Power flows on some interfaces, which historically have been from north to south, at times have reversed and are moving from south to north, highlighting shifting market economics, generation dispatch patterns, and emerging system weaknesses, in addition to those already identified on the interfaces. The recent operating data in this corridor show that flows remain predominantly in the north to south direction.

A significant number of new wind generation projects have interconnected to the northern portions of the New England transmission system. Several additional proposed wind projects have applied to interconnect in these areas (see Section 5.4). These portions of the system are remote from the region’s load centers and are susceptible to poor voltage performance. Generation has also been restricted in these locations, especially when customer demand is low and the transmission system is being maintained. These types of restrictions are expected to continue in the absence of significant transmission expansion. Refer to Section 10.2 for a discussion of wind-integration activities.

### Northern New England Transmission System Studies

Study efforts are progressing in various portions of Maine, New Hampshire, and Vermont to address a number of transmission system concerns. Some of these studies have focused on defining short-term needs and developing solutions, while others have made significant progress in evaluating potential system conditions 10 years into the future.

#### Maine

The Maine Power Reliability Program (MPRP) was proposed in 2008 and received its most recent Proposed Plan Application (PPA) approval in 2010. These projects included the addition of significant new 345 kV and 115 kV transmission facilities and new 345 kV autotransformers at key locations in Maine. The majority of the MPRP project entered service by the first half of 2015.

The northern portion of the Maine transmission system continues to present challenges for reliable system planning and operations. Lengthy sections of 345 kV transmission in Maine connect the New Brunswick system to the greater New England network. Certain contingencies have the potential to cause high voltages, low voltages, high frequencies, the loss of a large amount of generation, or system separation from New Brunswick. A number of new generation projects and elective transmission upgrades are seeking to interconnect to this part of the system. The technical complexities mentioned above complicate the system’s ability to accommodate additional interconnections.

A transfer study identified the increase in transfer capability across the major interfaces in Maine and neighboring systems resulting from the addition of the MPRP project. The study, completed in 2012, evaluated thermal, voltage, and stability transfer limits and demonstrated a modest increase in transfer capability across the major interfaces in Maine, including Maine to New Hampshire. The overall limiting condition in setting the new transfer limits is the system’s stability response to faults in southern New England. The new transfer limits have been adopted in the appropriate planning and capacity market processes. The resulting new transfer limits indicate that the constraints within Maine will likely continue to limit the ability of the system to deliver some existing and new capacity.

In addition to the Surowiec South and Orrington South interfaces, subarea export constraints will continue to be restrictive with the MPRP transfer limits in place, especially under maintenance or line-out conditions. They include the Rumford Area, Bigelow/Upper Kennebec, and Northern Maine/Keene Road. Additional local constraints may emerge as more resources pursue interconnection.

In late 2014, a new needs assessment was published for the Maine portion of the transmission system. The study identified certain needs for 2023. For the most part, the needs were identified for post-second-contingency thermal and voltage issues associated with serving local area loads.

#### New Hampshire

A number of studies of the New Hampshire portion of the system have been conducted. These studies have identified the need for additional 345/115 kV transformation capability and the need for additional 115 kV transmission support in various parts of the state. Many of these upgrades already are being implemented, as described in Section 6.3.3.

#### Vermont

Vermont regulations require the Vermont Electric Power Company (VELCO), the owner and operator of Vermont's transmission system, to develop a 20-year Vermont Long-Range Transmission Plan every three years. The 2015 Vermont Long-Range Plan was published in July 2015. The plan identifies reliability concerns and the transmission alternatives to address these concerns. The plan also serves as the basis for considering whether alternatives, including new generation and energy efficiency, can meet Vermont's reliability needs. It provides information about transmission projects that may be needed to maintain grid reliability.

#### New Hampshire and Vermont Combined

A combined study of the New Hampshire/Vermont area was initiated in 2012 to capture the final long-term energy-efficiency forecast, as well as the latest Forward Capacity Auction results and the latest load forecast for 2022, according to the 2012 CELT. This study was further updated to incorporate the announced retirement of the Vermont Yankee generator and to incorporate the 2013 CELT load forecast. This 2023 New Hampshire/Vermont Needs Assessment resulted in a number of adjustments to the previously identified preferred solutions for the area because of several deferred needs, as follows:

- In northwestern Vermont, a proposed special protection system to cross-trip the PV-20 line to mitigate low voltages following certain contingencies in New York was cancelled.

- In southeastern Vermont, a section of the 381 (Vernon/Vermont border) 345 kV line upgrade was cancelled.

- In central Vermont/Connecticut River, the new Coolidge–West Rutland 345 kV line was cancelled.

The 2023 needs assessment confirmed the need to address thermal overloads on the existing Coolidge-Ascutney 115 kV line in southeast Vermont, as well as low-voltage issues in the Connecticut River Valley area near the Ascutney 115 kV substation.

A Vermont 2023 transmission solutions study was published in December 2014. The previously proposed new Coolidge–Ascutney 115 kV line was reevaluated along with the alternative of rebuilding the existing line. The following upgrades were identified as the preferred solution:

- Upgrade the existing K31 Coolidge-Ascutney 115 kV line with 1351 ACSS conductor

- Install a +50/−25 megavolt-ampere reactive (MVAR) static VAR compensator (SVC) at the Ascutney substation, and add a third bay to the Ascutney substation

- Split the Hartford 25 MVAR capacitor bank into two 12.5 MVAR capacitor banks

- Reconfigure the Chelsea 115 kV substation from a straight bus into a three-breaker ring substation

The 2023 needs assessment also identified post-second-contingency thermal and voltage concerns in the central, western, southern, and seacoast portions of New Hampshire.

### Northern New England Transmission Projects

The ISO has identified projects that address issues with transmission system performance, either individually or in combination. Some of the projects, as described in the previous sections, address subregional reliability issues and have the ancillary benefit of improving the performance of major transmission corridors and thus the overall performance of the system. The projects are as follows:

#### New Hampshire/Vermont 2020 Upgrades

A New Hampshire/Vermont transmission solutions study, with a study year of 2020, was published in April 2012. A companion follow-up reassessment analysis was also published. This reassessment incorporated an updated set of assumptions based on the 2011 “proof-of-concept” long-term energy-efficiency forecast, as well as assumptions for load, generation and demand resources, transmission system topology, and the use of existing transmission system devices. The final set of preferred solutions for the New Hampshire/Vermont area included the addition of a new 345/115 kV autotransformer and a new 230/115 kV autotransformer, several new 115 kV transmission lines, upgrades and rebuilds of several existing 115 kV lines, and several reactive device additions and substation upgrades. These reinforcements are needed to address post-contingency load-serving needs that had been identified throughout the New Hampshire and Vermont areas. The improvements will be placed in service over the coming years. Some upgrades are already in service, and all the upgrades are expected to be in place by the end of 2016. The following list summarizes the planned upgrades:

- Adams 115 kV substation reconfiguration and the addition of two circuit breakers

- Two 12.5 MVAR capacitor banks at the Bennington 115 kV substation

- Two 25 MVAR capacitor banks at Amherst 345 kV substation

- New Fitzwilliam–Monadnock 115 kV line

- Two 13.3 MVAR capacitor banks at Weare 115 kV substation

- A152 Chestnut Hill–Westport–Swanzey 115 kV line rebuild

- N186-2 Vernon Road tap–Chestnut Hill 115 kV line rebuild

- Terminal upgrades at Flagg Pond 115 kV substation

- Second 230/115 kV autotransformer at Littleton

- A 230 kV C203 Comerford–Moore line tap into Littleton substation

- Four 26 MVAR capacitor banks at Webster 115 kV substation

- Two 25 MVAR dynamic reactive devices at Saco Valley 115 kV substation

- Load transfer scheme that opens the 115/34.5 kV path at Lovell for loss of the 214 (Kimball Road to Lovell) line

- 345/115 kV autotransformer at new Eagle 345 115 kV substation

- Four 25 MVAR capacitor banks at Eagle

- 326-Eversource Scobie Pond–NH/MA border 345 kV line upgrade

- Scobie Pond series circuit breaker with breaker 802

- New Scobie Pond–Huse Road 115 kV line

- G146 Garvins–Deerfield 115 kV line upgrade

- P145 Oak Hill–Merrimack 115 kV line upgrade

- D118 Deerfield–Pine Hill 115 kV line rebuild

- H137 Merrimack–Garvins 115 kV line rebuild

- J114-2 Greggs–Rimmon 115 kV line upgrade

- Loop V182 line into Oak Hill substation (Garvins–Webster)

- Merrimack series circuit breaker with breakers BT12 and BT23

- Merrimack capacitor bank relocation within the substation

- K165 Eagle–Bridge St.–Power St. 115 kV line upgrade

- New Madbury–Portsmouth 115 kV line

- New Scobie–Chester 115 kV line

- Chester substation work associated with new 115 kV line

- Six 13.3 MVAR capacitor banks at Schiller 115 kV substation and series circuit breaker with breaker BT10

- H141 Chester–Great Bay 115 kV line upgrade

- R193 Scobie–Kingston tap 115 kV line upgrade

- Three Rivers 115 kV series circuit breaker with breaker R1690

#### Maine Power Reliability Program

The Maine Power Reliability Program (MPRP) projects included the addition of significant new 345 kV and 115 kV transmission facilities and new 345 kV autotransformers at key locations in Maine. The majority of the MPRP project entered service by the first half of 2015. The Lewiston loop portions of the project are scheduled to enter service in 2017.

The major 345 kV components of the current plan are as follows:

- New 345 kV line construction

- Orrington–Albion Road

- Albion Road–Coopers Mills

- Coopers Mills–Larrabee Road

- Larrabee Road–Surowiec

- Surowiec–Raven Farm

- South Gorham–Maguire Road

- Maguire Road–Eliot (formerly called Three Rivers)

- New 345/115 kV autotransformers

- Albion Road

- Cooper Mills (replace existing Maxcys T3)

- Larrabee Road

- Maguire Road

- South Gorham

- Separation of double-circuit towers (DCTs)

- 345 kV Kennebec River Crossing by the Maine Yankee−Buxton and Maine Yankee−Surowiec circuits (375/377)

- Rerating of 345 kV transmission lines

- Section 378 (345 kV Maine Yankee–Mason)

## Southern New England

The southern New England area encompasses the Massachusetts, Rhode Island, and Connecticut transmission system. Studies of these states are addressing a wide range of transmission system concerns, both short and long term.

### Southern New England Transmission

The 345 kV facilities that traverse southern New England comprise the primary infrastructure integrating southern New England, northern New England, and the Maritimes Balancing Authority Area with the rest of the Eastern Interconnection. This network serves the majority of New England demand, integrating a substantial portion of the region’s supply, demand, and import resources.

Despite recent improvements, the southern New England system continues to face thermal, low-voltage, high-voltage, and short-circuit concerns under some system conditions. The most significant concerns involve maintaining the reliability of supply to serve load and developing the transmission infrastructure to integrate generation throughout this area. In many areas, an aging low-capacity 115 kV system has been overtaxed and is no longer able to serve load and support generation reliably. Ongoing planning and power system upgrades will ensure the system can meet its current level of demand and prepare for future load growth (see Section 3).

### Southern New England Transmission System Studies

Study efforts in southern New England have been progressing on a wide range of system concerns. Initial efforts focused on load areas with the most significant risks to reliability and threats to the system, particularly Boston and Southwest Connecticut. Several 345 kV reliability projects have been completed in Boston. The Phase I and Phase II Projects have been completed in Southwest Connecticut, and other projects have been completed in Springfield and western Rhode Island. Additional studies are in progress to ensure the reliability of other parts of the system, particularly eastern Connecticut; eastern Rhode Island; and southeastern Massachusetts, including Cape Cod. Boston, Southwest Connecticut, and western Massachusetts have been reevaluated to address the changes in load and resources that have occurred since the initial set of upgrades was established and solution plans have been developed. Additionally, solution plans have been developed for Greater Hartford, central Connecticut, and central Massachusetts.

Two of the four New England East–West Solution (NEEWS) components have been completed and are in service: the Rhode Island Reliability Project (RIRP) and the Greater Springfield Reliability Project (GSRP). These projects have further strengthened the backbone of the 345 kV system in the Rhode Island and Springfield areas, respectively. The Interstate Reliability Project (IRP) is under construction. When completed, this project will address the much broader requirements of the overall New England east–west and west–east transmission limitations.

The components of the Interstate Reliability Project are as follows:

- Install new 345 kV line (366) between Millbury, MA, and West Farnum, RI

- Install new 345 kV line (3271) between Card and Lake Road, CT

- Install new 345 kV line (341) between Lake Road and West Farnum

- Upgrade the 345 kV line between ANP Blackstone, MA, NEA Bellingham, MA, and West Medway, MA (336 line)

- Reconductor the 345 kV line between Sherman Road, RI, and West Farnum (328 line)

- Eliminate the sag limit on the 115 kV line from Montville, CT, to Buddington, CT (1410 line)

- Upgrade the terminal equipment at Sherman Road (345 kV), West Medway (345 kV), and West Farnum (345 kV) substations

- Rebuild the Sherman Road (345 kV) switching station

Studies have shown that once the Interstate project is in service, Connecticut will no longer need large 345 kV reinforcements. Therefore, the 115 kV upgrades that will address the needs established for the Greater Hartford/Central Connecticut (GHCC) study have replaced the fourth NEEWS component, the Central Connecticut Reliability Project (CCRP) The GHCC study includes the Hartford, Middletown, northwestern Connecticut, and Barbour Hill areas. In combination, this study, the Eastern Connecticut (ECT) study, and the Southwest Connecticut (SWCT) study cover the entire load within the state. With the exception of the ECT study, preferred solution alternatives have been selected for the GHCC and SWCT studies.

The Boston area was reevaluated to reflect recently made changes in the cable-rating assumptions for downtown Boston and the addition of Footprint Power’s 674 MW combined-cycle units at the Salem Harbor site. The study evaluated two transmission proposals:

- An all AC solution with many of the same solution components as the previously preferred solution, proposed by National Grid and Eversource Energy, which involves the expansion of the 345 kV AC system between New Hampshire and Massachusetts

- An alternative solution proposed by New Hampshire Transmission, LLC, which incorporates an HVDC submarine cable (SeaLink HVDC Submarine Cable Project) extending from Seabrook, New Hampshire, to Boston

Both alternatives incorporate several common AC system reinforcements. The National Grid and Eversource Energy plan was selected as the preferred solution.

#### Massachusetts

Greater Boston area: A long-term reliability needs assessment was completed for the Greater Boston area, and solutions have been developed to address the criteria violations that resulted. Because of significant changes in the study area, two updates have been released since the needs assessment report was published in 2010—the 2018 needs assessment and the 2023 needs assessment. The changes that prompted the updates can be categorized into four topics: load forecast and demand resources, resource additions and retirements, transmission system topology, and system modeling:

- Changes in load forecast and demand resources

The net load in the study area decreased by 200 MW in the 2023 needs assessment compared with the 2018 needs assessment

- Resource additions and retirements

The most significant change in the study area was the availability of generation resources. As a result of a nonprice retirement (NPR) request (see Section 4.1.3.3), the Salem Harbor station retired in 2014. This retirement reduces generation resources in the area by approximately 750 MW, representing a loss of over 20% of the area resources. Because of this retirement, upgrades to five transmission lines in the North Shore area, north of Boston, were identified and have been placed in service. These transmission upgrades were needed to address immediate reliability concerns in the local area due to the retirement.

The 2018 and 2023 needs assessments reflect the retirement of Salem Harbor and the addition of Footprint Power, which was proposed with a capacity supply obligation of 674 MW.

- Transmission system topology

A number of solution alternatives were identified and advanced to resolve urgent needs in the Boston area. The following list summarizes these advanced upgrades:

  - 115 kV line reconductorings (all now in service):

- 320-507/508 Lexington–Waltham 115 kV

- 128-518/P-168 Chelsea–Revere 115 kV

- C-129N/201-502 Depot St. tap–Medway 115 kV

- D-130/201-501 Depot St. tap–Medway 115 kV

- 211-508 Woburn–Burlington 115 kV

  - New 115 kV line addition with switching station:

- 447-502 West Walpole–Holbrook 115 kV

- Three-breaker switching station at Sharon sectionalizing the 447-502, 447-508, and 447-509 lines, West Walpole–Holbrook

  - New autotransformer addition:

- 230/115 kV autotransformer at Sudbury

- 115 kV capacitor additions (both now in service):

- A 115 kV 36.7 MVAR capacitor bank at Hartwell

- A 115 kV 36.7 MVAR capacitor bank at Chelsea

- 115 kV station reconfigurations at North Cambridge

- System modeling

In 2012, the study was adjusted significantly to take into account the updated ratings for the underground cable systems in the Boston area.

The needs assessment results indicated a need to increase Boston import capability, as well as bolster the transmission system within the area, to serve the load reliably. Most of the needs observed in the 2018 needs assessment also were observed in the 2023 needs assessment, and most of the reliability issues exist at the 2013 load levels.

Additionally, part of the 2023 needs assessment was to assess the system under minimum load conditions. The results of this testing indicated the need for shunt reactive compensation in the study area to resolve high-voltage concerns.

The 2023 needs assessment also found that two 115 kV substations in downtown Boston have short-circuit concerns and a few other study area substations had limited short-circuit margins.

The solutions study update focused on developing solutions for four study subareas: northern (New Hampshire border to Boston, including the suburbs north of Boston); central (downtown Boston 115 kV system); western (suburbs west of Boston); and southern (suburbs south of Boston). The solutions for the northern, western, central, and southern areas have been identified and are described below. Note that these do not include the advanced projects discussed above.

The transmission solution for the northern area includes the following elements (all in Massachusetts, except where indicated):

- New 345 kV lines as follows:

  - Scobie, NH, to Tewksbury, overhead line

  - Wakefield to Woburn, underground line

- Line reconductorings on the 115 kV network in the North Shore area:

- Y-151 Power St., NH,–Dracut Junction (part of the line is in NH)

- M-139 Tewksbury–North Woburn Tap

- N-140 Tewksbury–North Woburn Tap

- F-158N Wakefield Junction–Maplewood

- F-158S Maplewood–Everett

- New 160 MVAR shunt reactors at Wakefield 345 kV and Woburn 345 kV

The transmission solution for the western and central areas includes the following upgrades (all in Massachusetts):

- New 115 kV lines as follows:

  - Between Sudbury and Hudson, overhead line

  - Between Mystic and Chelsea, underground line

  - Between Mystic and Woburn that runs parallel to the existing 211-514, underground line

- New autotransformer additions as follows:

  - 345/115 kV autotransformer at Woburn (replaces the existing Woburn autotransformer with a higher-rated autotransformer)

  - 345/115 kV autotransformer at Mystic

- New capacitor additions as follows:

  - 36.7 MVAR capacitor at Sudbury 115 kV

  - 54 MVAR capacitor at Newton 115 kV

- Reconfiguration of the following substations that included breaker additions and line reterminations:

  - Waltham 115 kV substation

  - North Cambridge 115 kV substation

  - Kingston 115 kV substation

  - K Street 115 kV substation

  - Woburn 345 kV substation

  - Chelsea 115 kV substation

  - Framingham 115 kV substation

- Separation of the following double-circuit towers:

  - X-24/E-157W (Millbury–Northboro Rd./Millbury–E. Main St.)

  - F-158N/Q-169 double-circuit tower (Wakefield–Maplewood/Wakefield–Lynn)

- Separation of the 110-522/240-510 double-circuit tower (Baker St.–Needham)

- Upgrade terminal equipment on the 533-508 115 kV line (Lexington–Hartwell Ave.)

- Upgrades on the 69 kV network in the central area

X-24 line refurbishment: Millbury–Northboro Rd.

W23W: Northboro–Woodside

The transmission solution for the southern area includes a new 345 kV breaker at the Stoughton, MA, 345 kV substation.

The short-circuit mitigation plan, as a part of the AC Plan, involves opening the terminals of four 115 kV cables in downtown Boston, which results in the radial energization of these cables. Additionally, the Wakefield and Woburn substations each require a 345 kV shunt reactor to resolve the high-voltage issues observed at minimum load. Also, Coopers Mills in Maine requires a 200 MVAR STATCOM (static synchronous compensator) to achieve acceptable stability performance, and five stations around the Boston area need bulk power system (BPS) upgrades.

Berkshire County/Pittsfield area: An updated reassessment of the needs, accounting for updates to the load forecast and changes in resources and energy efficiency, has been completed for the Pittsfield-Greenfield area of western Massachusetts, which shows that most of the identified needs existed before 2013 at the load levels of that year. The needs assessment shows no further need for the following solution components identified in the 2018 solutions study published in 2012:

- Reconductoring the 115 kV 1371 line (Woodland–Pleasant)

- Replacing the E131 115 kV breaker at Harriman substation

A new 2022 solutions study also has been completed to mitigate the needs from the needs reassessment, and the preferred solution components were presented to the PAC in April 2015. The solutions study did the following:

- Considered the latest system topology, load assumptions, and impacts of photovoltaic generation when verifying the needs identified in the 2022 needs assessment

- Confirmed which components of the solutions identified in the 2018 solutions study are still required and preferred

- Identified additional preferred solution components for addressing the needs identified in the 2022 needs assessment not identified in previous needs assessments

The solution components for the Pittsfield area are as follows:

- Expand and reconfigure Northfield Mountain 345 kV substation, and install a 345/115 kV autotransformer

- Build a three-breaker ring-bus switching station in Erving adjacent to the A127/B128 (Harriman–Millbury/Harriman–Millbury) right-of-way

- Loop the 115 kV A127 (Harriman–Millbury 115 kV) line into the new Erving switching station, and reconductor the A127 line from Erving to the Cabot tap (on the way to Harriman substation)

- Build a new 1.2 mile 115 kV single-circuit line connecting the new Northfield 345/115 kV autotransformer to the new Erving switching station

- Rebuild the 115 kV 1361 line (Montague–Cumberland)

- Disconnect Montague from the 115 kV B128 line at Cabot Junction, and reconnect to the A127 line (Harriman–Millbury)

- Reduce the sag limitation on the 115 kV 1421 and 1512 lines (Pleasant–Blandford–Granville Junction)

- Rebuild the 115 kV A127/Y177 double-circuit line from Montague to Cabot Junction on single-circuit structures

- Reconnect the Y177 line into the 3T/4T position at Montague substation

- Install a 115 kV 14.4 MVAR capacitor bank at Podick, Amherst, and Cumberland substations

- Install a bus-tie breaker between buses 1 and 2 at Harriman substation

- Replace five air-break disconnect switches on the A127E line between Erving and Barre

- Install a 115 kV 20.6 MVAR capacitor bank at Doreen substation

- Operate the Doreen 115 kV 13-T breaker normally open

- Build a new 115 kV three-breaker ring bus at or adjacent to the Pochassic 37R substation, and loop in the 115 kV line 1512

- Install a new 115 kV line between Pochassic and Buck Pond on the vacant side of the existing double-circuit structures

- Install a 345 kV 75–150 MVAR variable reactor at Northfield and Ludlow substations

- Install a scheme to transfer-trip the 230 kV E205W line (Bear Swamp substation [MA]–Eastover substation [NY]) at Bear Swamp for all cases where the E205W line is left open-ended at the Eastover substation

- Open the 69 kV J-10 line following any outage of the 345 kV 393/312 line (Alps substation [NY]–Berkshire substation [MA]–Northfield substation [MA]) or the Berkshire 345/115 kV autotransformer, as needed

#### Massachusetts/Rhode Island

A needs reassessment is in progress for the Southeast Massachusetts/Rhode Island (SEMA/RI) area, which reflects the upcoming retirement of Brayton Point station. On January 27, 2014, the owner of Brayton Point station provided notice that the station will be retired on or before June 1, 2017. Originally, the major goals of the study were to determine any long-term system needs required to integrally serve the broad SEMA and Rhode Island areas. Under the needs reassessment, the major goals remain the same, with the addition of evaluating the area without the presence of the Brayton Point station.

The thermal and voltage needs for SEMA/RI have been presented. The short-circuit analysis has not been completed. Past studies that included the Brayton Point plant have indicated a need to add transmission capacity to remove limits on moving power into and around the West Medway substation. The study has identified needs that require solutions to serve the broad southeast Massachusetts and Rhode Island load areas reliably.

With the announcement of the Brayton Point retirement, a short-term study has been conducted to ensure that the SEMA/RI area can operate reliably in the absence of the station. A similar type of retirement study was undertaken in 2010 when the Salem Harbor station announced its retirement. The transmission upgrades needed to address potential reliability concerns in the area due to the Brayton Point retirement are as follows:

- Reconductor the V148N line (Woonsocket–Washington)

- Increase the T175 transformer rating at West Farnum

- Increase the T3 transformer rating at Kent County

The solution to address the 1280 line (Whipple Junction–Mystic) and the 1870S line (Shunock–Wood River) thermal overloads requires further investigation and will be developed in the future.

The Aquidneck Island area of the SEMA/RI study has demonstrated a need to mitigate reliability concerns, and because these reliability concerns are independent of other needs shown in the SEMA/RI study, the Aquidneck Island area solution components were advanced. The Aquidneck Island area includes Portsmouth, Middletown, and Newport, Rhode Island. The Aquidneck Island needs and preferred solution were presented to PAC on April 28, 2015. The solution components are as follows:

- Rebuild and convert to 115 kV lines the 69 kV 61 and 62 lines from the Dexter to Jepson substations

- Relocate and rebuild the Jepson substation to accommodate new 115 kV sources

- Reconfigure the Dexter substation removing all 69 kV equipment

#### Connecticut

A long-term reliability needs assessment for 2018 was completed for the Southwest Connecticut area. A solutions study was completed to address the criteria violations based on the 2018 needs assessment. The solutions study focused on developing solutions for five study subareas: Frost Bridge–Naugatuck Valley, Housatonic Valley/Norwalk–Plumtree, Bridgeport, New Haven–Southington, and Glenbrook–Stamford. The Glenbrook–South End cable and the Mill River–Quinnipiac 8300 line reconfiguration included in the New Haven area solution alternatives (see Section 6.4.3, Southwest Connecticut Advanced Solutions) were developed to address independent subarea needs. Other solution alternatives were developed to address interdependent subarea needs.

A new needs assessment and solutions study, referred to as the 2022 SWCT Needs Assessment and Solutions Study, was initiated to take into account the latest assumptions, changes in topology resulting from the approval of new projects and the results of the latest FCA, and the inclusion of energy efficiency beyond the latest FCA. The 2022 SWCT needs were first presented to the PAC in May 2013. Bridgeport Harbor 2 has already retired, and Norwalk Harbor station will retire by June 2017. As a result, the 2022 SWCT needs were reevaluated, and the needs assessment was presented to the PAC in February 2014. Needs were still present in all subareas with the exception of the Glenbrook–Stamford subarea. The advanced Glenbrook–South End cable mitigated all the violations found in the earlier needs assessment.

A new 2022 SWCT solutions study has been completed to mitigate the needs from the 2022 SWCT needs reassessment; the preferred solution components were presented to the PAC in July 2014, and the solutions study report was posted to the PAC website in February 2015.

The major components of the preferred solutions for addressing the needs in the Frost Bridge–Naugatuck Valley and the Housatonic Valley/Norwalk/Plumtree subareas include the following components:

- Loop the 1570 line (Devon to Beacon Falls) in and out of the Pootatuck substation (formerly known as Shelton substation)

- Install two 115 kV capacitor banks at Ansonia substation

- Expand Pootatuck substation to a four-breaker ring bus and install a 115 kV capacitor bank

- Close the normally open breaker at Baldwin substation

- Install a 115 kV capacitor bank at Oxford substation

- Loop the 1990 line (Stevenson–Baldwin Street–Frost Bridge) in and out of the Bunker Hill substation

- Rebuild Bunker Hill substation to a nine-breaker, breaker-and-a-half configuration

- Reconductor the 1575 line between Bunker Hill and Baldwin Junction

- Reconductor the 1887 line between West Brookfield and West Brookfield Junction

- Install two 14.4 MVAR capacitor banks at West Brookfield substation

- Reduce the size of the capacitor at Rocky River substation from 25.2 MVAR to 14.4 MVAR

- Relocate a 37.8 MVAR capacitor bank within the Stony Hill substation

- Install one synchronous condenser at Stony Hill substation

- Reconfigure the 1887 line into a three-terminal line (Plumtree–W. Brookfield–Shepaug)

- Reconfigure the 1770 line into two two-terminal lines between Plumtree–Stony Hill and Stony Hill–Bates Rock

- Reconductor a portion of the 1682 line between Wilton and Norwalk, and upgrade Wilton substation terminal equipment

- Reconductor the 1470 line between Wilton and Ridgefield Junction and between Ridgefield Junction and Peaceable

- Install a 115 kV breaker in series with the existing 29T breaker at Plumtree Substation

- Install a new 115 kV line between Plumtree and Brookfield Junction

- Relocate one existing capacitor bank from the 115 kV B bus to the 115 kV A bus at Plumtree substation

- Upgrade the 1876 line terminal equipment at Newtown substation

- Replace two 115 kV circuit breakers at Freight substation

- Remove the Stony Hill and Bates Rock DVAR (dynamic voltage ampere reactive) devices

The preferred solution for addressing the needs in the Bridgeport and New Haven areas include the following components:

- Upgrade the Baird 115 kV bus

- Install two 115 kV capacitor banks at Hawthorne

- Upgrade the 115 kV bus system and 15 disconnects to 63 kiloamperes (kA) interrupting capability at Pequonnock

- Rebuild the 8809A/8909B lines between Baird and Congress

- Install a series breaker at East Devon

- Remove the Sackett phase-angle regulator (PAR)

- Install a series reactor on the 1610 line (Southington–June–Mix Ave) and two 115 kV capacitor banks at Mix Avenue

- Rebuild the 88005A/89005B lines between Devon tie and Milvon

- Replace two 115 kV breakers at Mill River to address transient recovery voltage (TRV) overduty issues

- Upgrade the 1630 line (North Haven–Wallingford–Walrec) relay at North Haven

- Separate the 3827 (Beseck–East Devon)–1610 (Southington–June–Mix Ave) DCTs

- Rebuild the 88006A/89006B lines between the Housatonic River Crossing and Barnum

- Rebulild the 88006A/88006B lines between Barnum and Baird

Two other study efforts in Connecticut—evaluations of the Hartford and Middletown areas—were combined with the Greater Hartford/Central Connecticut study. Load-supply issues exist under certain dispatch and transfer conditions. Additionally, the Greater Hartford transmission system can experience flow-through issues when its 115 kV circuits are called on, under contingency conditions, to carry the power normally supplied via the 345 kV system. Both voltage and thermal issues have been identified in the Middletown area under simulated future conditions with local generation unavailable and the Haddam 345/115 kV autotransformer out of service.

The Greater Hartford and Central Connecticut study area consists of about 35% of Connecticut load and spans the central and northwestern portions of the state. The objective of the study was to determine the reliability needs for both serving local load in the area and reassessing the needs that had driven the Central Connecticut Reliability Plan component of NEEWS. The CCRP project consists of a new 345 kV line from North Bloomfield to Frost Bridge that crosses the western Connecticut import interface. The need for the project was based on thermal violations on the 345 kV lines that form this interface.

The study area consists of four subareas: Greater Hartford, including the Southington station; Manchester–Barbour Hill; Middletown; and northwestern Connecticut. The study area, in general, consists of several load pockets with limited generation fed by limited transmission. The loss of two or more transmission paths into these load pockets results in the thermal overloads on the remaining transmission paths and low voltages within the load pocket. The needs assessment for this study shows that system needs exist in all four subareas at 2013 load levels. The needs were attributed to load-serving issues and the need for increased import capability into western Connecticut. However, most of the 345 kV violations that drove the need for the CCRP project were no longer observed, and the project in its original form will no longer be required. The final needs report was posted in April 2014.

An updated GHCC solutions study has been completed to mitigate the needs from the GHCC needs assessment; the preferred solution components were presented to the PAC in July 2014, and the solutions study report was posted to the PAC website in February 2015.

The major components of the preferred solutions for each subarea are highlighted below:

- Manchester–Barbour Hill

- Add a new 345/115 kV autotransformer at Barbour Hill

- Upgrade the 115 kV line between Manchester and Barbour Hill (1763)

- Add a series breaker at Manchester 345 kV switchyard

- Northwestern Connecticut

- Add a new 115 kV line between Frost Bridge and Campville substation

- Separate the 115 kV lines between Frost Bridge and Campville and from Thomaston to Campville DCT, and add a 115 kV breaker at Campville

- Upgrade terminal equipment on the 115 kV line between Chippen Hill and Lake Avenue Junction (1810-3)

- Reconductor the 115 kV line between Southington and Lake Avenue Junction (1810-1)

- Greater Hartford, including Southington

  - Replace the existing 3% series reactors on the 115 kV lines between Southington and Todd (1910) and between Southington and Canal (1950) with 5% series reactors

  - Replace the normally open 19T breaker at Southington with a 3% series reactor between Southington ring 1 and Southington ring 2 and associated substation upgrades

  - Add a breaker in series with breaker 5T at the Southington 345 kV switchyard

  - Add a new control house at Southington 115 kV substation

  - Add a new 115 kV underground cable between Newingtown and Southwest Hartford and associated terminal equipment, including a 2% reactor

  - Loop the 1779 line between South Meadow and Bloomfield into the Rood Avenue substation, and reconfigure the Rood Avenue substation

  - Reconfigure the Berlin 115 kV substation, including the addition of two 115 kV breakers and the relocation of a capacitor bank

  - Add a 115 kV 25.2 MVAR capacitor at Westside 115 kV substation

  - Reconductor the 115 kV line between Newington and Newington Tap (1783)

  - Separate the 115 kV DCT corresponding to the Bloomfield–South Meadow (1779) line and the Bloomfield–North Bloomfield (1777) line, and add a breaker at Bloomfield 115 kV substation

  - Install a 115 kV 3% reactor on the underground cable between South Meadow and Southwest Hartford (1704)

  - Separate the 115 kV DCT corresponding to the Bloomfield–North Bloomfield (1777) line and the North Bloomfield–Rood Avenue–Northwest Hartford (1751) line, and add a breaker at North Bloomfield 115 kV substation

- Middletown

  - Add a second 345/115 kV autotransformer at Haddam substation, and reconfigure the three-terminal 345 kV 348 line into two 2-terminal lines

  - Upgrade terminal equipment on the 345 kV line between Haddam and Beseck (362)

  - Separate the 115 kV DCT corresponding to the Branford–Branford RR line (1537) and the Branford–North Haven (1655) line, and add a series breaker at Branford 115 kV substation

  - Upgrade terminal equipment on the Middletown–Dooley line (1050)

  - Upgrade terminal equipment on the Middletown–Portland line (1443)

- Add a 37.8 MVAR capacitor bank at Hopewell 115 kV substation

- Separate the 115 kV DCT corresponding to the Middletown–Pratt and Whitney line (1572) and the Middletown–Haddam line (1620)

- Redesign the Green Hill 115 kV substation from a straight bus to a ring bus, and add a 37.8 MVAR capacitor bank

  - Add two 25.2 MVAR capacitor banks at Green Hill 115 kV substation

- Increase the size of the existing 115 kV capacitor bank at Branford substation from 37.8 MVAR to 50.4 MVAR

The eastern Connecticut area study is also in progress. The eastern Connecticut area is defined from the east by the Connecticut and Rhode Island border, from the south by the Long Island Sound, from the west by the eastern boundary of the western Connecticut import interface, and from the north by the border between Connecticut and Massachusetts. The study area is served electrically from autotransformers at Killingly, Card, and Montville and by a 115 kV line from Rhode Island. The study evaluates the retirement of the AES Thames generating unit among other issues. The needs assessment has been completed, and most of the needs are the result of the loss of the autotransformers at Card or Killingly or the 115 kV source from Rhode Island followed by another contingency. The needs assessment shows that most needs exist at 2013 load levels.

### Southern New England Transmission System Projects

A number of transmission projects in various stages are underway in southern New England. Many factors complicate the system performance in southern New England, such as load levels, system transfers, and unit commitment. The projects identified for this area must function reliably under a wide variety of conditions, and their development must support the operation of the overall system.

#### Webster–Harriman 115 kV Refurbishment (A127/B128)

A refurbishment has begun for the A127 and B128 115 kV lines that run westerly from the proximity of the Webster Street substation in Massachusetts to the Harriman substation in Vermont. This project currently is scheduled to be completed in 2015.

#### Central/Western Massachusetts Upgrades

Past studies developed a 10-year plan for central Massachusetts and portions of western Massachusetts. This plan calls for adding a second 230/115 kV autotransformer and replacing four 230 kV breakers at Bear Swamp, replacing a transformer at Pratts Junction and Carpenter Hill substations, adding a new 115 kV line from Millbury to Webster, and implementing several other 115 kV upgrades. Some of the upgrades have been placed in service, with the remaining scheduled through 2017.

#### Salem Harbor–Railyard Cable Replacement

The replacement of the underground cables between the Salem Harbor and Railyard substations is scheduled to be completed in 2016.

#### Auburn Reliability Project

Past studies of the area surrounding the Auburn Street substation in Massachusetts identified overloads of the existing 345/115 kV autotransformer and several 115 kV lines, voltage problems, and breaker overstresses. The solution to eliminate these reliability deficiencies includes rebuilding the 345 kV and 115 kV switchyards at the Auburn Street substation to accommodate new bay configurations, along with the installation of a second autotransformer, and the replacement of a number of breakers. The reconductoring of the 115 kV Auburn Street–Parkview and Bridgewater–East Bridgewater lines has been completed. The Bridgewater–Easton 115 kV line (formerly E1) has been extended to supply a new municipal substation in Mansfield. The new Avon substation will be constructed and tapped off the newly reconductored Auburn Street–Parkview line (A94). The addition of a second distribution transformer at Dupont requires associated terminal work. The project was completed in 2014.

#### Greater Rhode Island Project

Reliability concerns with the 115 kV system in the Bridgewater–Somerset–Tiverton areas of southeastern Massachusetts and the adjoining area in Rhode Island had been identified previously. The solutions to these concerns were a group of upgrades that had been combined with the advanced Rhode Island upgrades (associated with NEEWS studies) to become what is now known as the Greater Rhode Island (GRI) transmission reinforcements.

The advanced NEEWS upgrades, the new Berry Street 345/115 kV substation (MA) and the expansion of the Kent County substation (RI) with an additional 345/115 kV autotransformer, were placed in service in 2011.

The ongoing SEMA/RI study will address reliability concerns in the Bridgewater–Somerset–Tiverton areas of southeastern Massachusetts and the adjoining area in Rhode Island, previously addressed by the Aquidneck Island study. As a result, National Grid has withdrawn the Proposed Plan Applications for the outstanding GRI projects that include the following components:

- Somerset substation reinforcements

- New 115 kV circuit between Brayton Point and Somerset

- New 115 kV circuit between Somerset and Bell Rock

- Expansion of the Bell Rock substation

- Reconductoring of the M13 and L14 lines between Bell Rock and Dexter substations

- Modification of the 115 kV Dexter Substation

- Conversion of the 69 kV Jepson substation to 115 kV

#### Greater Boston Advanced Solutions

The advanced solutions for Greater Boston, which are not in service and are not anticipated to be in service in 2015, include the following elements:

- Sudbury autotransformer and capacitor bank project—The Greater Boston Needs Assessment analysis showed thermal and voltage issues due to line outages followed by a second line outage. In the worst-case scenario, the entire Sudbury load pocket of 300 MW of load would be lost. The solution to mitigate these issues is to install a new 230/115 kV autotransformer, five new 230 kV gas-insulated breakers, five 115 kV air-insulated breakers, and a new 115 kV capacitor bank. The project is expected to be completed by December 2016.

- Addition of a third 115 kV line from West Walpole to Holbrook—The Greater Boston Needs Assessment analysis showed thermal issues due to line outages followed by a second facility outage. In the worst-case scenario, an N-1 event resulted in the loss of over 300 MW. The solution to mitigate these issues is to install a third 115 kV line from West Walpole to Holbrook. The project is expected to be completed in 2017.

- Installation of a new 115 kV switching station in Sharon—Although a third 115 kV line is scheduled to be installed between West Walpole and Holbrook, the load (over 300 MW) in the area is still susceptible to being lost as a result of N-1-1 events. The solution to mitigate this issue is the installation of a new three-breaker switching station in Sharon. The project is expected to be completed by 2017.

- North Cambridge line and transformer terminal swaps—The Greater Boston Needs Assessment analysis showed thermal issues on the 329–530 or 329–531 lines (both between North Cambridge and Brighton) as a result of N-1-1 events. The solution to mitigate this issue is to swap terminal locations of the 329–530 line and transformer #1 and to swap the terminal locations of the 329–531 line and transformer #4. The project is expected to be completed by 2016.

## RSP Project List and Projected Transmission Project Costs

The RSP Project List is a summary of needed transmission projects for the region and includes information on project type, the primary owner, the transmission upgrades and their status, and the estimated cost of the pool transmission facility (PTF) portion of the project. The RSP Project List includes the status of reliability transmission upgrades, market efficiency transmission upgrades, elective transmission upgrades, and generator interconnection transmission upgrades (described in Section 2.1.1). The list also will include public policy transmission upgrades. The ISO updates this list at least three times per year. Additional information on the project classifications included in the RSP Project List is available in the draft Transmission Planning Process Guide.

The ISO regularly updates the PAC on RTU and METU (and eventually PPTU) study schedules, scopes of work, assumptions, draft and final results, and project costs. Projects are considered part of the Regional System Plan consistent with their status and are subject to transmission cost allocation for the region. RSP15 incorporates information from the June 2015 RSP Project List.

This section discusses RTUs underway and their costs and the status of the ETUs in the region. It also explains why no market-efficiency-related transmission upgrades have been needed and provides information on several transmission upgrades developed and paid for by generator developers.

### Reliability Transmission Upgrades

As of June 2015, the total estimated cost of transmission upgrades—proposed, planned, and under construction—was approximately $4.8 billion, as shown in Table 6-1.

Table 6-1
Estimated Cost of Reliability Projects as of June 2015 Plan Update (Million $)

| Projects | Project Costs (millions of $)(a) |
| --- | --- |
| Major projects |  |
| Maine Power Reliability Program | 1,459 |
| Greater Hartford and Central Connecticut | 357 |
| Long-Term Lower SEMA Upgrades | 114 |
| New England East–West Solution (NEEWS) | 1,620 |
| NEEWS (Greater Springfield Reliability Project)—$676.0 million |  |
| NEEWS (Rhode Island Reliability Project)—$362.3 million |  |
| NEEWS (Interstate Reliability Project)—$521.8 million |  |
| NEEWS (other)—$59.6 million |  |
| Greater Rhode Island Transmission Reinforcements (including Advanced NEEWS) | 151 |
| Pittsfield-Greenfield Project | 208 |
| Greater Boston—North, South, Central, Western Suburbs | 795 |
| New Hampshire Solution—Southern, Central, Seacoast, Northern | 352 |
| Vermont Solution—Southeastern, Connecticut River | 134 |
| Southwest Connecticut | 430 |
| Subtotal(b) | 5,620 |
| Other projects(c) | 6,192 |
| New projects(d) | 79 |
| Projects whose cost estimates were previously reported as “to be determined”(d) | 74 |
| Total(b) | 11,965 |
| Minus “concept” projects | 0 |
| Minus “in-service” projects | −7,178 |
| Aggregate estimate of active projects in the plan(b) | 4,787 |

(a) 	Transmission owners provided all estimated costs, which may not meet the guidelines described in Planning Procedure No. 4, Procedure for Pool-Supported PTF Cost Review, Attachment D, “Project Cost Estimating Guidelines” (September 17, 2010), http://www.iso-ne.com/rules_proceds/isone_plan/pp04_0/pp4_0_attachment_d.pdf.

(b) 	Totals may not sum exactly because of rounding.

(c) 	The "Other Projects" category is the sum of all other project costs in the RSP Project List not explicitly listed above. The cost estimates for projects in the “Major Projects” category move to the “Other Projects” category once they are completed.

(d) 	Reflects updated costs from the June 2014 project list update compared with the March 2014 update.

The PTO Administrative Committee provides annual informational filings to FERC on the current regional transmission service rates and annual updates to the ISO and NEPOOL on projected regional transmission rates, as shown in Table 5-2.

Table 6-2
Actual and Forecast Regional Transmission Service Rates, 2014 to 2019(a)

|  | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 |
| --- | --- | --- | --- | --- | --- | --- |
|  | Actual(b) |  | Forecast(c) |  |  |  |
| Estimated additions in service and CWIP ($ millions)(d) | N/A | N/A | 748 | 833 | 893 | 563 |
| Forecasted revenue requirement ($ millions) | 165 | 63 | 124 | 135 | 140 | 90 |
| Total revenue requirement | 1,888 | 1,951 | 2,075 | 2,210 | 2,350 | 2,440 |
| Year-prior 12 CP (kW)(e) | 20,910,580 | 19,763,032 | 19,763,032 | 19,763,032 | 19,763,032 | 19,763,032 |
| RNS rate increase from prior year ($/kW-year) | 5 | 8.4 | 6.3 | 7 | 7 | 4 |
| RNS rate ($/kW-year) | 90.28 | 98.70 | 105 | 112 | 119 | 123 |
| RNS rate forecast using a 59.4% load factor) ($/kWh) | N/A | N/A | 0.020 | 0.021 | 0.023 | 0.024 |
| TOUT service rate ($/kWh) | 0.0103 | 0.0113 | 0.012 | 0.013 | 0.014 | 0.014 |

(a) 	The figures may not agree because of rounding.

(b) 	2014 PTO-AC Informational Filing, Revised 11/19/2014; 2015 PTO-AC Informational Filing.

(c)	Source: RNS Rates: 2015–2019 PTF Forecast, PTO Administrative Committee Rates Working Group presentation at the NEPOOL Reliability Committee/Transmission Committee Summer Meeting (July 14–15, 2015), http://www.iso-ne.com/static-assets/documents/2015/07/a5_rates_five_year_forecast_presentation.pptx. The 2016-2019 rate forecast reflects PTO Administrative Committee estimated data and assumptions and is preliminary and for illustrative purposes only. Therefore, such estimates, assumptions, and rates are expected to change as current data become available.

(d)	“CWIP” refers to construction work in progress.

(e)	“12 CP” refers to the average of all the monthly regional network loads (per the OATT, Section 21.2) for the 12 months of the calendar year on which the rate is based.

### Lack of Need for Market-Efficiency-Related Transmission Upgrades

To date, the ISO has not identified the need for METUs, primarily designed to reduce the total net production cost to supply the system load, because of the following:

- Reliability transmission upgrades have resulted in market-efficiency benefits, particularly when out-of-merit operating costs were reduced.

- The development of economical resources and fast-start resources in response to the ISO’s wholesale electricity markets has also helped eliminate congestion and Net Commitment-Period (NCPC).

This section summarizes the historical systemwide congestion and NCPC. Economic studies are analyzing future system performance that may identify future need for METUs, particularly in the Keene Road area (see Section 10.4.1).

#### Transmission Congestion

As shown in Table 6-3, recent experience has demonstrated that the regional transmission system has little congestion among the New England load zones relative to the Hub. At approximately $32 million in 2014, the total day-ahead and real-time congestion costs remain low, and mitigation by additional transmission upgrades is not warranted. Planned reliability transmission upgrades could reduce congestion costs further, as well as reduce transmission system losses.

Table 6-3
ISO New England Transmission System Day-Ahead, Real-Time,
and Total Congestion Costs and Credits, 2003 to 2014 ($)

| Year | Day-Ahead Congestion (a, b) | Real-Time Congestion(a, c) | Total Congestion(a, d) |
| --- | --- | --- | --- |
| 2003 | −85,964,588 | −1,385,442 | −87,350,030 |
| 2004 | −82,384,177 | 2,833,577 | −79,550,600 |
| 2005 | −273,449,871 | 6,814,010 | −266,635,861 |
| 2006 | −192,419,271 | 12,683,233 | −179,736,038 |
| 2007 | −130,145,862 | 17,721,136 | −112,424,726 |
| 2008 | −125,358,187 | 4,295,716 | −121,062,471 |
| 2009 | −26,681,125 | 1,593,273 | −25,087,852 |
| 2010 | −37,321,849 | −622,287 | −37,944,136 |
| 2011 | −17,957,036 | −246,892 | −18,203,928 |
| 2012 | −29,326,997 | −174,471 | −29,501,468 |
| 2013 | −46,186,914 | −175,059 | −46,361,973 |
| 2014 | −34,218,158 | 2,177,658 | −32,040,500 |

(a) 	Negative numbers indicate charges to load; positive numbers indicate credits to load.

(b) 	Day-ahead congestion charges = the amount billed to load minus payments to the generators.

(c) 	Real-time congestion refers to deviations from day-ahead charges. Additional outages, problems, and non-day-ahead load issues that cause additional generator dispatch within the congested zone results in a credit to load. Less generation within the zone results in a real-time charge to load.

(d) 	Total congestion refers to money the ISO uses to pay FTR holders.

The highest mean annual difference in the congestion component of the LMPs was $0.41/MWh at the BOSTON RSP subareas relative to the Hub. The small congestion component of the locational marginal prices suggests that the system has little congestion. Portions of the system remote from load centers, especially northern Maine, have high negative loss components. The MPRP added 345 kV facilities and recently, shunt reactive compensation, which will reduce losses in Maine.

#### Transmission Improvements to Load and Generation Pockets Addressing Reliability Issues

The performance of the transmission system is highly dependent on embedded generators operating to maintain reliability in several smaller areas of the system. Consistent with ISO operating requirements, the generators may be required to provide second-contingency protection or voltage support or to avoid overloads of transmission system elements. Reliability may be threatened when only a few generating units are available to provide system support, especially when considering normal levels of unplanned or scheduled outages of generators or transmission facilities. This transmission system dependence on local-area generating units typically can result in reliability payments associated with out-of-merit unit commitments. The total cost for these reliability payments are a small portion of the overall wholesale electricity market costs in New England of $10.5 billion in 2014 (see Figure 2-1).

Some areas currently depend on out-of-merit generating units to some degree to maintain reliability, or have been dependent on these units until recently. The NCPC in the Boston area totaled approximately $23.6 million for 2014, approximately 61% of the New England total. After the upgrades being pursued as part of the Greater Boston projects are placed in service, the need to run units out of merit (and subsequent NCPC) is expected to decline (see Sections 6.4.2 and 6.4.3).

Generating units in load pockets may receive second-contingency or voltage-control payments for must-run situations. Table 6-4 shows the NCPC by type and year. The 2009, 2010, 2011, and 2012 figures showed a significant decrease from the preceding years, averaging less than $17 million per year. A modest upturn in charges occurred in 2013, and a slight decrease happened in 2014. Because reliability transmission upgrades improve the economic performance of the system, upgrading transmission solely to reduce NCPC is not often justifiable.

Table 6-4
Net Commitment-Period Compensation by Type and Year (Million $)

| Year | Second Contingency(a) | Voltage | Total(b) |
| --- | --- | --- | --- |
| 2003(c) | 36.0 | 14.4 | 50.4 |
| 2004 | 43.9 | 68.0 | 111.9 |
| 2005 | 133.7 | 75.1 | 208.8 |
| 2006 | 179.9 | 19.0 | 199.0 |
| 2007 | 169.5 | 46.0 | 215.5 |
| 2008 | 182.9 | 29.4 | 212.3 |
| 2009 | 17.5 | 5.0 | 22.5 |
| 2010 | 3.9 | 5.1 | 9.0 |
| 2011 | 6.0 | 5.8 | 11.9 |
| 2012 | 8.8 | 14.9 | 23.6 |
| 2013 | 38.0 | 16.6 | 54.6 |
| 2014 | 32.4 | 6.2 | 38.5 |

(a) NCPC for first-contingency commitment and distribution support is not included.

(b) Numbers may not add precisely due to rounding.

(c) NCPC under Standard Market Design began in March 2003.

In 2014, the ISO filed and the FERC approved revisions to Market Rule 1 that calculates NCPC.  These revisions ensure better consistency with market offer-flexibility rules and improve incentives for market participants to follow the ISO’s operating instructions.

Transmission solutions continue to be put in place where proposed generating or demand resources have not relieved transmission system performance concerns. The ISO is studying many of these areas, and while transmission projects are still being planned for some areas, other areas already have projects under construction and in service to mitigate dependence on generating units. Reliability transmission upgrades were used to address these system performance concerns, which contributed to a substantial reduction in out-of-merit operating costs.

### Required Generator-Interconnection-Related Upgrades

No significant transmission system upgrades resulted from the interconnection of generators. Most of the generator-interconnection-related upgrades are fairly local to the point of interconnection of the generator. The RSP Project List identifies the PTF upgrades (see Section 5.3).

### Elective Transmission Upgrades

A number of new elective transmission upgrades have been added to the ISO Generator Interconnection Queue. Many of these are focused on delivering zero or low-carbon resources to New England. As of June 1, 2015, 10 projects have active interconnection requests as elective transmission upgrades:

- Queue Project (QP)-498: 400 MW, 150 kV HVDC tie; New York Power Authority (NYPA) 230/115 kV substation to VELCO 345 kV New Haven substation

- QP-499: 1,090 MW, 300 kV HVDC/AC tie; HQ Des Cantons substation to Public Service of New Hampshire (PSNH) Deerfield substation

- QP-500: Keene Road ETU, Emera Keene Road substation

- QP-501: 1,000 MW HVDC tie—import only, HQ 735 kV substation to VELCO 345 kV Coolidge substation

- QP-506: 1,000 MW internal HVDC—north to south flow, Northern Maine Independent System Administrator (NMISA) to NSTAR 345 kV K Street substation

- QP-507: 75 MW AC tie—bidirectional; NMISA Mullen substation to Emera Keene Road substation

- QP-508: 600 MW HVDC tie from New York to western Massachusetts—bidirectional; NY Alps substation to Western Massachusetts Electric Company (WMECO) Berkshire substation

- QP-517: 1,000 MW HVDC from southern Maine to Mystic—bidirectional; Central Maine Power (CMP) 345 kV Maine Yankee substation to NSTAR 345 kV Mystic substation

- QP-518: 1,000 MW HVDC from southern Maine to K Street—bidirectional; CMP 345 kV Maine Yankee substation to NSTAR 115 kV K Street substation

- QP-519: 1,200 MW HVDC/AC tie—import only; HQ Des Cantons substation to PSNH Deerfield substation

## Summary

Significant transmission projects have been placed in service across New England since 2002. These projects reinforce critical load pockets, such as in Southwest Connecticut and Boston, and areas that have experienced significant load growth, such as northwestern Vermont. These projects also include a new interconnection to New Brunswick, which increases the ability of New England to import energy from Canada.

As of summer 2015, most of the projects of the Maine Power Reliability Program have entered service. Transmission upgrades were placed in service in preparation for the retirements of the Vermont Yankee nuclear facility and the Salem Harbor generating station. Some transmission reinforcements are moving forward in Rhode Island in preparation for the retirement of Brayton Point Station.

The New England East–West Solution series of projects has been identified to improve system reliability. The updated review of the need for the Interstate Reliability Project component of NEEWS is complete, and the preferred solution is unchanged. A reevaluation of the Central Connecticut Reliability Project has been completed with the Greater Hartford/Central Connecticut study. The project has been replaced with a number of 115 kV upgrades, which address both local Hartford area concerns and issues associated with imports into western Connecticut.

Costs associated with second-contingency and voltage-control payments have been mitigated through transmission improvements. Additional transmission plans have been developed, which reduce the dependence on generating units needed for reliability. An example is the Lower SEMA projects, whereby transmission improvements have reduced dependence on the Cape Cod Canal generating units.

From 2002 through June 2015, 634 projects have been put into service, with an investment totaling approximately $7.2 billion. Additional projects (proposed, planned, or under construction), totaling approximately $4.8 billion, are summarized in the RSP Project List, which is updated periodically.

Many new elective transmission upgrades have been proposed, which focus on delivering zero or low-carbon resources to New England. As of June 1, 2014, 10 projects are under study as elective transmission upgrades, and one has received its proposed plan application approval.

All transmission projects are developed to meet the reliability requirements of the entire region and are fully coordinated regionally and interregionally. Most projects on the RSP Project List remain subject to regional cost allocation. With transmission expansion in the region, the ISO meets all required transmission planning requirements, and little congestion is currently evident on the system.

The transmission planning process for newly identified transmission needs is changing as a result of the final FERC Order No. 1000 going into effect. A number of factors, including the low growth of net system load, new retirements, aging infrastructure, and public policies, will likely affect the newly identified physical needs.

# Interregional Coordination

Interconnections with neighboring systems allow for the exchange of capacity and energy. The tie lines facilitate access to a diversity of resources and compliance with environmental obligations and the more economic, interregional operation of the system. Quantifying these benefits, identifying potential needs for additional interconnections, and coordinating the planning of the interconnected system are becoming increasingly important.

The ISO coordinates its planning activities with neighboring systems and across the Eastern Interconnection. Consistent with the mandatory reliability requirements of the North American Electric Reliability Corporation, the ISO must identify and resolve interregional planning issues, as identified in needs assessments and solutions studies. With other entities within and outside the region, including neighboring areas, the ISO conducts studies that aim to, for example, improve production cost models, share simulation results, investigate the challenges to and possibilities for integrating renewable resources, and address other common issues affecting the planning of the overall system.

The ISO also participates in numerous interregional planning activities with the US Department of Energy (DOE), the Northeast Power Coordinating Council, and other planning authority areas in the United States and Canada. The overriding purpose of these projects is to enhance the widespread reliability of the interregional electric power system.

This section discusses the main collaborative efforts the ISO is undertaking with neighboring areas to analyze the interconnection-wide system, study and address interregional transfers and seams issues, and improve competitive electricity markets in North America.

## Eastern Interconnection Planning Collaborative Studies

The electric power planning authorities of the Eastern Interconnection, including ISO New England, formed the Eastern Interconnection Planning Collaborative (EIPC) in 2009 to address their portion of North American planning issues, combine the existing regional transmission expansion plans, and analyze the interconnection-wide system. EIPC received a grant from DOE to conduct studies on the Eastern Interconnection system. The six participating planning authorities leading this portion of the study are ISO New England, New York, PJM, the Tennessee Valley Authority (TVA), Midcontinent ISO (MISO) (formerly called the Midwest ISO), and Ontario. Section 8.5 contains more details on this DOE-funded study.

EIPC is continuing to coordinate base cases and conduct analyses without DOE funding. EIPC’s work in 2013 included developing and studying “roll-up” cases, which combined each region’s electric power system plan into a comprehensive model of the Eastern Interconnection. After an extensive stakeholder process, the final report of the roll-up cases was posted. The results show that the future transmission system, as currently planned, is capable of transferring power over long distances throughout the Eastern Interconnection above the long-term firm commitments modeled in the roll-up cases.

EIPC requested input from stakeholders for scenarios to be studied in 2014, for which it received seven proposals. A scenario proposed by the Eastern Interconnection States Planning Council (EISPC) (see Section 11.2.1) to study heat wave and drought conditions in the south was chosen. The focus of EIPC’s 2015 efforts, as in 2013, has been to develop and analyze roll-up cases for summer and winter 2025. The EIPC is building the cases, which then will be used in 2016 to analyze other scenarios.

## Electric Reliability Organization Overview

As the RTO for New England, the ISO is responsible for ensuring that its operations and planning comply with applicable NERC standards. In addition, the ISO participates in regional and interregional studies required for compliance.

Through its committee structure, NERC, which is the FERC-designated Electric Reliability Organization (ERO), regularly publishes reports that assess the reliability of the North American electric power system. Annual long-term reliability assessments evaluate the future adequacy of the power system in the United States and Canada for a 10-year period. The reports project electricity supply and demand, evaluate resource and transmission system adequacy, and discuss key issues and trends that could affect reliability. Summer and winter assessments evaluate the adequacy of electricity supplies in the United States and Canada for the upcoming peak demand periods in these seasons. Special regional, interregional, or interconnection-wide assessments are conducted as needed.

In November 2014, NERC issued its annual Long-Term Reliability Assessment (LTRA), analyzing reliability conditions across the North American continent. This report describes transmission additions, generation projections, and reserve capability by reliability council area. The 2014 LTRA identified three key findings, as follows, that will have an impact on the long-term reliability of the North American bulk power system (BPS) and will materially change the way the system is planned and operated:

- In several assessment areas, reserve margins are trending downward because of ongoing generation retirements, despite low load growth.

- Existing and proposed environmental regulations create uncertainty regarding the future operation of fossil-fueled generation (coal, oil, and natural gas), which require assessment.

- A changing resource mix requires new approaches for assessing reliability.

The NERC LTRA offers several recommendations in support of the key findings, including the following:

- Raising stakeholder awareness of resource adequacy issues

- Assessing generation and transmission adequacy

- Addressing fuel supply interruptions and the reliable integration of variable resources

NERC noted that declining reserve margins throughout the study area increase the need for broader probabilistic assessments of resource adequacy. These analyses provide stakeholders with an in-depth understanding of the interrelationships between resource availability and projected hourly demands. The studies identify key resource adequacy issues, which NERC plans to communicate to policymakers, such as state public utility regulators (e.g., public utilities commissions; PUCs).

NERC remains concerned with the potential reliability impacts from environmental regulations, which include restricted operations and retirements (see Section 9.1). NERC plans to conduct a reliability assessment once the US Environmental Protection Agency (EPA) finalizes Section 111(d) of the Clean Air Act (CAA) (see Section 9.1.2).

NERC recommends that areas with high levels of natural gas-fired resources examine the reliability need for more firm fuel transportation or units with dual-fuel capability. It also recommends that resource adequacy and other planning assessments consider fuel availability and deliverability. Other NERC recommendations are for system operators to develop or enhance coordination efforts for addressing potential fuel interruptions, especially before anticipated extreme weather events, and for generator owners to consider securing on-site secondary fuel in the event that nonfirm gas service is curtailed.

Additional NERC recommendations are as follows:

- Each region should investigate how changes to the resource mix in certain areas, particularly with the onset of variable energy resources, have affected their systems, including essential reliability services.

- The NERC Essential Reliability Services Task Force should develop additional metrics for measuring the impacts to reliability of a resource mix that is increasingly dependent on variable resources.

- The electric power industry should continue to examine how wind and solar plants can contribute to frequency response, and it should develop interconnection requirements for ensuring that system operators can maintain essential reliability services.

- NERC should consider using new approaches to evaluate the changing behavior of the bulk power system. These additional approaches should consider essential reliability services, probabilistic metrics, and transmission adequacy assessments—in conjunction with the existing reserve margin metric—to address and evaluate potential reliability issues in the future.

## IRC Activities

Created in April 2003, the ISO/RTO Council (IRC) is an industry group consisting of the nine functioning ISOs and RTOs in North America. These ISOs and RTOs serve two-thirds of the electricity customers in the United States and more than 50% of Canada‘s population. The IRC works collaboratively to develop effective processes, tools, and standard methods for improving competitive electricity markets across much of North America. Each ISO/RTO manages efficient, robust markets that provide competitive and reliable electricity service, consistent with its individual market and reliability criteria.

While the IRC members have different authorities, they have many planning responsibilities in common because of their similar missions. As part of the ISO/RTO authorization to operate, each ISO/RTO independently and fairly administers an open, transparent planning process among its participants. These activities include exchanging information, treating participants comparably, resolving disputes, coordinating infrastructure improvements regionally and interregionally, conducting economic planning studies, and allocating costs. This ensures a level playing field for infrastructure development driven efficiently by competition and meeting all reliability requirements.

The IRC has coordinated a number of reports, filings, and presentations with national government agencies. The IRC has worked with EPA, the states, and all interested parties on proposed carbon dioxide (CO2) regulations that respect electric power system reliability and are compatible with the efficient dispatch of the electric power grid. Additionally, the IRC has submitted FERC filings on issues of common concern for its members, such as proposed changes to the gas operating day and interstate pipeline scheduling practices for natural gas transportation service (see Section 8.4.3). IRC members also have coordinated on a number of technical issues, such as the use of software and the sharing of planning techniques.

## Northeast Power Coordinating Council Studies and Activities

The Northeast Power Coordinating Council is one of eight regional entities located throughout the United States, Canada, and portions of Mexico responsible for enhancing and promoting the reliable and efficient operation of the interconnected bulk power system. NPCC has been delegated the authority by NERC to create regional standards to enhance the reliability of the international, interconnected BPS in northeastern North America. As a member of NPCC, the ISO fully participates in NPCC-coordinated interregional studies with its neighboring areas.

NPCC assesses seasonal reliability and, periodically, the reliability of the planned NPCC bulk power system. It also evaluates annual long-range resource adequacy. All studies are well coordinated across neighboring area boundaries and include the development of common databases that can serve as the basis for internal studies by the ISO. ISO New England assessments demonstrate full compliance with NERC and NPCC requirements for meeting resource adequacy and transmission planning criteria and standards.

## Northeastern ISO/RTO Planning Coordination Protocol

ISO New England, NYISO, and PJM follow a planning protocol to enhance the coordination of planning activities and address planning seams issues among the interregional planning authority areas. Hydro-Québec TransÉnergie, the Independent Electric System Operator of Ontario, and the Transmission and System Operator Division of New Brunswick Power participate on a limited basis to share data and information. The key elements of the protocol are to establish procedures that accomplish the following tasks:

- Exchange data and information to ensure the proper coordination of databases and planning models for both individual and joint planning activities conducted by all parties

- Coordinate interconnection requests likely to have cross-border impacts

- Analyze firm transmission service requests likely to have cross-border impacts

- Develop the Northeast Coordinated System Plan

- Allocate the costs associated with projects having cross-border impacts consistent with each party’s tariff and applicable federal or provincial regulatory policy

To implement the protocol, the group formed the Joint ISO/RTO Planning Committee (JIPC) and the Inter-Area Planning Stakeholder Advisory Committee (IPSAC) open stakeholder group. Through the open stakeholder process, the JIPC has addressed several interregional, planning authority issues. The following list shows several key planning issues summarized in the 2013 Northeast Coordinated System Plan (NCSP13) that affect the broad region and additional studies that have been presented to the IPSAC:

- Coordination and sharing of transmission study databases, critical contingency lists, and short-circuit equivalents

- Identification of improved planning techniques, modeling, and software tools

- Coordination of interconnection queue studies and transmission improvements, such as upgrades for interconnecting the Cricket Valley Energy Center (Dover, NY) to the 345 kV line 398 (Pleasant Valley–Long Mountain)

- Coordinated production cost models and market-efficiency studies

- Evaluations of environmental regulations and their potential effects on the power systems

- Identification of issues and solutions facilitating the integration of variable energy resources

- Assessment of fuel diversity issues, including coordinated studies of the natural gas system

- Determination of the effect of demand resources on interregional planning

NCSP13 also serves as a baseline for interregional planning as the planning process continues evolving to comply with FERC Order No. 1000. JIPC activities have continuously addressed the issues discussed in NCSP13, and plans call for periodically issuing a revised document. The JIPC also coordinated compliance filings for the final FERC order, particularly on interregional planning and cost-allocation issues.

## Interregional Transfers

Interconnections with neighboring regions provide opportunities for exchanging capacity, energy, reserves, and mutual assistance during capacity-shortage conditions. Capacity imports help New England meet its Installed Capacity Requirements and promote competition in the FCA. The tie-reliability benefits from the interconnections also can lower the ICR. Additionally, imports provide resource diversity and can lower regional generation emissions, especially imports of hydro.

New England has 13 interconnections with neighboring power systems in the United States and Eastern Canada (see Section 6.2). Planning studies use the energy and capacity import capabilities of the interconnections the ISO has with neighboring power systems in the United States and Eastern Canada; see Table 7-1.

Table 7-1
Assumed External Interface Import Capability, Summer 2015 to Summer 2024 (MW)(a)

| Interconnection | Import Type | Assumed Import Capability |
| --- | --- | --- |
| New York–New England AC | Energy(b) | 1,400 |
|  | Capacity | 1,400 |
| Cross-Sound Cable | Energy(c) | 330 |
|  | Capacity | 0 |
| Maritimes–New England | Energy(d) | 1,000 |
|  | Capacity | 700 |
| Québec–New England (Highgate)(e) | Energy | 217 |
|  | Capacity | 200 |
| Québec–New England (Phase II) | Energy(f) | 2,000 |
|  | Capacity | 1,400 |

(a) 	Limits are for the summer period. These limits may not include possible simultaneous impacts and should not be considered as “firm.”

(b) 	The AC import capabilities do not include the Cross-Sound Cable and the Northport–Norwalk Cable. Simultaneously importing into New England and Connecticut can lower the New York to New England AC capability.

(c) 	Import capability on the Cross-Sound Cable is dependent on the level of local generation in Connecticut.

(d) 	The electrical limit of the New Brunswick–New England tie is 1,000 MW. When adjusted for the ability to deliver capacity to the greater New England control area, the New Brunswick–New England transfer capability becomes 700 MW.

(e) 	The capability listing for the Highgate facility is for the New England AC side of the Highgate terminal.

(f) 	The Hydro-Québec Phase II interconnection is a DC tie with equipment ratings of 2,000 MW. Because of the need to protect for the loss of this line at the full import level in the PJM and NY systems, ISO New England has assumed its transfer capability to be 1,400 MW for calculating capacity and reliability. This assumption is based on the results of loss-of-source analyses conducted by PJM and NY. The procedure and daily limits are shown at the ISO’s “Operations Report: Single-Source Contingency,” webpage (2015), http://www.iso-ne.com/isoexpress/web/reports/operations/-/tree/single-src-cont.

Historically, New England experienced net capacity and energy imports. The ISO expects this trend to continue, given the amount of import capacity supply obligations resulting from the Forward Capacity Auctions (see Section 4.1.3) and the number of tie-line projects in the ISO’s interconnection queue (see Section 5.4), which could provide additional opportunities for importing energy from neighboring power systems. Table 7-2 shows the summer CSOs for FCA #6 (for the 2015/2016 capacity commitment period) through FCA #9 (for the 2018/2019 period).

Table 7-2
Import Capacity Supply Obligations for Summer, FCA #6 to FCA #9 (MW)

| Summer CSOs | FCA #6 2015/2016 | FCA #7 2016/2017 | FCA #8 2017/2018 | FCA #9 2018/2019 |
| --- | --- | --- | --- | --- |
| New York | 633 | 891 | 678 | 1,054 |
| Maritimes | 248 | 290 | 202 | 177 |
| Québec | 456 | 435 | 357 | 218 |
| Total | 1,337 | 1,616 | 1,237 | 1,449 |

Table 7-3 shows the amount of tie-reliability benefits used in FCA #6 through FCA #9.

Table 7-3
Tie-Reliability Benefits Assumed from Neighboring Power Systems, Summer (MW)

| Tie benefits | FCA #6 2015/2016 | FCA #7 2016/2017 | FCA #8 2017/2018 | FCA #9 2018/2019 |
| --- | --- | --- | --- | --- |
| New York | 248 | 314 | 227 | 346 |
| Maritimes | 328 | 392 | 492 | 523 |
| Québec | 1,048 | 1,164 | 1,151 | 1,101 |
| Total | 1,624 | 1,870 | 1,870 | 1,970 |

Table 7-4 shows the annual net energy interchange (imports minus exports) and the net energy interchange as a percentage of the system net energy for load. During the past five years, net energy imports increased from approximately 4% to 16% of the total New England net energy for load requirement.

Table 7-4
Annual Net Energy Imports of System Net Energy for Load, 2010 to 2014 (GWh and %)

|  | 2010 | 2011 | 2012 | 2013 | 2014 |
| --- | --- | --- | --- | --- | --- |
| Net energy import (GWh) | 5,539 | 10,142 | 12,648 | 18,961 | 20,660 |
| System net energy for load (GWh) | 130,773 | 129,163 | 128,081 | 129,377 | 127,138 |
| Net energy import (%) | 4 | 8 | 10 | 15 | 16 |

Table 7-5 shows monthly energy imports (i.e., gross imports without accounting for exports) and that New England imported 23,268 GWh of energy during 2014. Over half of the energy imports were from Québec, which is predominantly a hydro system. Avoided New England emissions associated with energy imported from Québec were estimated using the 2013 New England system average emission rates. The estimated avoided emissions were 2.38 ktons of nitrogen oxides (NOx), 2.12 ktons of SO2, and 4,830 ktons of CO2.

Table 7-5
 New England Energy Imports by Month, 2014 (GWh)

| Month | New York | Maritimes | Québec | Total |
| --- | --- | --- | --- | --- |
| Jan | 687 | 438 | 1,146 | 2,271 |
| Feb | 864 | 451 | 1,030 | 2,345 |
| Mar | 669 | 380 | 1,173 | 2,221 |
| Apr | 461 | 223 | 1,101 | 1,784 |
| May | 325 | 88 | 1,053 | 1,467 |
| Jun | 476 | 133 | 977 | 1,585 |
| Jul | 371 | 306 | 1,070 | 1,747 |
| Aug | 300 | 293 | 1,184 | 1,777 |
| Sep | 480 | 227 | 1,060 | 1,767 |
| Oct | 400 | 292 | 1,025 | 1,718 |
| Nov | 614 | 311 | 1,180 | 2,105 |
| Dec | 841 | 404 | 1,237 | 2,482 |
| Total | 6,487 | 3,547 | 13,234 | 23,268 |

## Summary

The ISO’s planning activities are closely coordinated with neighboring systems. The ISO has achieved full compliance with all required planning standards and has successfully implemented the Northeastern ISO/RTO Planning Protocol, which has further improved interregional planning among neighboring areas and will continue to do so as part of regional compliance with Order No. 1000.

Interconnections with neighboring systems provide access to capacity and energy and reduce emissions within the New England area. The ISO coordinates planning activities with the Northeast Power Coordinating Council and throughout North America through NERC studies.

# Fuel-Certainty Risks to System Reliability and Solutions

New England has fuel certainty and flexibility issues for several reasons:

- The region relies heavily on natural-gas-fired capacity, and serious and growing reliability and cost issues have emerged because of fuel constraints of the natural gas delivery system and level of LNG utilization.

- The lack of firm contracts for natural gas has limited the availability of fuel transportation and funding for natural gas infrastructure expansion.

- Gas units with dual-fuel capability can present reliability risks due to limited on-site fuel storage and, for some resources, the extended time required to switch and replenish fuels.

- Infrequently operated and older oil and coal resources are exposed to diminished operating performance, as well as limited energy production, with oil units potentially experiencing issues with fuel availability, delivery, and other challenges caused by the sporadic operation of the units.

- New England also faces the retirement of non-gas-fired generation, which will likely increase the regional reliance on natural-gas-fired generation.

The ISO and other entities have been conducting many studies on these overarching and overlapping strategic risks and broad planning issues, the extent of these issues, and potential solutions. Some of the more specific topics analyzed have been as follows:

- Winter operating experience, which shows the region’s exposure to high natural gas prices, the reliability risks of limited fuel supplies, and the results of regional actions to address these issues

- The interaction between the natural gas and electric power systems, which quantify the need for improving fuel certainty to the region

- Improvements to the wholesale electricity markets and system operations and planning, which affect the reliable supply of electric energy to the region

This section discusses the electric power system’s reliance on natural-gas-fired generation, the associated reliability risks, the winter operating experience, and both short-term and long-term actions the region is taking to address these risks, including those through the ISO’s Strategic Planning Initiative.

## Capacity and Electric Energy Production in the Region by Fuel Type

New England’s capacity and electric energy production in 2014 indicates that the region is highly dependent on natural gas-fired generation. As shown in Figure 8-1, approximately 43% of the region’s capacity in 2014 was natural-gas-fired generation. This is about twice as large as oil-fired capacity, which was the next-largest type of generation resource in the region. Figure 8-1 also shows that natural gas power plants contributed 43% to the region’s electric energy production in 2014. Nuclear generation supplied 34% of the electric energy, but each of the other types of generating resources produced less than 7%. (Refer to Section 7.6 for a discussion on the role of imports that supply the region.)

Figure 8-1: New England’s summer seasonal claimed capability (MW, %) and electric energy production (GWh, %) by fuel type for 2014.

Note: The capacity and energy statistics illustrated in the figure exclude the capacity and energy associated with imports and behind-the-meter generation not registered in the region’s wholesale energy markets. In 2014, the NEL was 127,138 GWh, pumped storage consumed an additional of 1,877 GWh, and the net imports into the region were 20,660 GWh.

Sources: The capacity data are RSP14 data and the same as 2014 CELT Report data (http://www.iso-ne.com/static-assets/documents/trans/celt/report/2014/2014_celt_report_rev.pdf). The energy data are based on the March 1, 2015, 90-day resettlement of total electric energy production for 2014.

The region will continue to rely on natural-gas-fired generation and the addition of variable renewable resources in its fuel mix. Recent FCM auction results (see Section 4.1.3) have shown the retirement of coal- and oil-fired generators in the region and the loss of the Vermont Yankee nuclear plant. As additional generators retire, units in the ISO Generator Interconnection Queue, which primarily are natural-gas-fired generation and wind resources (see Section 5.4), will likely replace them. Further increases in the use of natural-gas-fired generation will likely occur, resulting from the loss of other types of generation subject to risks, such as nuclear and hydro units that may not be relicensed. The region also is beginning to experience the addition of wind-powered generation and photovoltaic (PV) resources, and future growth is expected.

Figure 8-2 shows the expected regional resource capacity mix for 2015, 2018, and 2024. As indicated, natural gas-fired generation in the capacity mix is expected to grow from approximately 44% in summer 2015 to 57% in 2024. The figure is based on several assumptions, as follows:

- The 2015 capacity values reflect the seasonal claimed capability of generating resources in the 2015 CELT Report.

- The 2018 capacity values reflect the qualified capacity of new resources cleared in FCA #9, net of nonprice retirements. The 2018 capacity also reflects projects in the April 2015 ISO interconnection queue considered likely to develop.

- The 2024 capacity reflects the 2018 resources plus other resources proposed in the ISO queue as of April 2015. While not all resources in the ISO queue are expected to develop, the queue resources are representative of the types of resources that will likely develop in the region, which consist primarily of natural gas and wind (refer to Section 5.4).

Figure 8-2: Generating resource summer capability by fuel type based on the 2015 CELT Report and the interconnection queue (MW, %).

Note: The figure does not include interchange with neighboring regions (see Section 7.6). It also does not include active demand resources, EE, and behind-the-meter PV (see Section 3). PV resources forecasted to participate in the ISO capacity and energy markets are shown as part of the hydro/renewables category. The wind resources have been derated to reflect their on-peak ratings used in transmission planning studies (i.e., onshore wind generation is modeled at 5% of nameplate; offshore wind is modeled at 20% of nameplate).

## Natural Gas Infrastructure

New England’s natural gas supply and delivery infrastructure, and its limitations, have become an area of focus for improving the region’s fuel availability. Natural-gas-fired generators receive fuel supply from six interstate pipelines currently serving New England:

- Three originate from the south and west:

  - Algonquin Gas Transmission (AGT) Pipeline

  - Tennessee Gas Pipeline (TGP)

  - Iroquois Gas Transmission System (IGTS)

- The Portland Natural Gas Transmission System (PNGTS) originates in the northwest portion of New Hampshire.

- The Maritimes and Northeast (M&N) Pipeline originates in the Canadian Maritime provinces.

- The Granite State Gas Transmission (GSGT) System is in Maine and New Hampshire and does not bring gas from outside New England into the region.

Four LNG import terminals also serve New England, two onshore and two offshore:

- Distrigas LNG in Massachusetts and New Brunswick’s Canaport LNG onshore terminals

- Neptune LNG and Northeast Gateway LNG offshore terminals

The Distrigas terminal is connected with the AGT and TGP pipelines and the local gas distribution company (LDC)—the gas utility that serves residential, commercial, and industrial customers. The Canaport terminal sends natural gas through the Brunswick pipeline, which directly connects to the M&N Pipeline. The M&N Pipeline also has the option of delivering natural gas to New England from the offshore natural gas production fields of the Sable Offshore Energy Project (SOEP) and Deep Panuke located offshore from Nova Scotia, Canada. Figure 8-3 shows the major existing natural gas infrastructure serving New England.

Figure 8-3: Overview map of the natural gas infrastructure serving New England.

Source: ICF International (ICF)

Notes: Several pipelines shown in the map indirectly serve New England: Emera New Brunswick owns and operates the Brunswick Pipeline. A subsidiary of Gaz Metro and TransCanada Pipeline owns the Trans Québec and Maritimes (TQM) Pipeline, which supplies Canadian gas into the PNGTS at Pittsburg, NH.

Figure 8-4 shows the sources of natural gas, including Marcellus shale gas, and Figure 8-5 shows the natural gas pipeline network in the lower 48 states as presented in the Department of Energy Quadrennial Energy Review (QER) (see Section 11.1.7). Comparing these figures shows that New England has relatively few pipelines that can access plentiful supplies of Marcellus shale gas.

Figure 8-4: Sources of natural gas, including Marcellus shale gas, in the Continental United States.

Source: EIA.

Figure 8-5: Natural gas pipeline network in the Continental United States.

Source: EIA.

## Natural Gas and Oil Fuel Certainty and Risks to System Reliability

Because natural gas plants make up such a large part of the generating fleet, the availability of this fuel has an immediate effect on power grid reliability. For example, the planned or unplanned outage of a major gas pipeline at any time of year may affect many thousands of megawatts of generation. Additionally, when gas-fired generators are unavailable to run or are derated, the ISO needs to commit significant amounts of additional generating resources—mostly oil and coal plants—to maintain system reliability. However, many of the oil and coal plants called on to run require a long time to start and ramp up, may have performance problems related to their age, and may not have enough fuel to run as long as needed. This creates challenges to operating the system reliably and economically. In addition, many of these resources are retiring, limiting the amount of replacement capacity that the ISO can call on during stressed system conditions (see Section 4.1.3.3 and 5.5).

### Fuel-Certainty Risks

The fuel-certainly risk occurs mostly during the winter, but can occur any time of the year. During the last several years, a number of factors have been affecting the ability of natural gas plants to get the fuel they need to perform:

- Inadequate infrastructure: The existing pipeline system in New England is reaching maximum capacity more often, especially in winter. The priority for a pipeline’s capacity goes to customers who have signed long-term firm contracts. In New England, these customers have been the local gas distribution companies.

- Interruptible fuel arrangements: Most natural gas plants procure, day to day, pipeline supply and transportation that is not being used by LDCs. As more people and businesses in New England convert to natural gas to take advantage of inexpensive shale gas, LDCs have had less pipeline capacity to release to the secondary markets. More competition also is taking place among the increasing numbers of gas-fired generators, which means generators risk not being able to obtain pipeline transportation for the gas needed to fuel their plants.

- Higher variable-cost peaking alternatives: Some generators can use LNG supplies when the region’s pipelines are fully congested. However, LNG tends to be more expensive than the typical price of gas emanating from the Marcellus shale.

- Limited fuel storage: Unlike generators that use others types of fuel, many natural gas plants in the region have limited or no on-site gas storage, making them even more vulnerable to the pipeline supply problems. Dual-fuel units can switch to using oil when necessary, but only about 40% of the region’s gas-capable units currently have this ability. More so, limitations in on-site fuel storage may constrain the operation of these generation units.

### Natural Gas Price Volatility

As shown in Figure 8-6, New England’s heavy reliance on natural gas-fired generation has resulted in natural gas fuel prices typically setting the associated price for wholesale electricity. Despite the increased use of oil-fired generators, during winter 2013/2014 and winter 2014/2015, the average monthly wholesale electricity prices reflected the daily volatility in natural gas fuel prices.

Figure 8-6: Monthly average fuel prices and real-time Hub LMPs compared with regional natural gas prices ($/MWh; $/MMbtu).

Note: Underlying natural gas data furnished by ICE. The regional natural gas price is the average Massachusetts price, which is the volume-weighted average of pricing points for Algonquin, Tennessee, and Dracut.

Figure 8-7 shows wholesale electricity and natural gas market data for New England trading hubs and the Marcellus price. Although the development of Marcellus shale is a growing source of natural gas, pipeline limitations into and within New England typically cause price separation between New England and Marcellus supplies. LNG supplies New England locally and can mitigate higher New England prices by providing supply during peak demand periods, but the higher unit cost of this supply still results in higher electric energy prices in New England than near the wellhead in Marcellus. Winter 2014/2015 spot natural gas prices for the Algonquin Pipeline (near Boston) and the Tennessee Gas Pipeline (near Dracut, MA) averaged $9.387/MMBtu and $9.014/MMBtu respectively, while approximately 300 miles southwest in the Marcellus shale at the Tennessee Gas Pipeline pricing point, prices averaged $1.733/MMBtu.

Figure 8-7: Natural gas market data, November 2013 to April 2015 ($/MMBtu).

Notes: SNL spot natural gas pricing at New England (Algonquin City Gate, Tennessee Gas Pipeline Dracut, MA), and Marcellus (Dominion South and Tennessee Gas Pipeline Zone 4 Marcellus) trading points. Marcellus spot pricing at TGP Z 4 Marcellus inaugurated on March 3, 2014.

Source: SNL Financial (Accessed May 6, 2015), http://www.snl.com/.

As shown Table 8-1, the natural gas futures prices for winter of 2014/2015 were much higher for New England than other areas. These higher prices—some of the highest prices in the world—attracted several “destination-flexible” and other LNG cargoes to the region. LNG vaporization at Canaport, Distrigas, and Excelerate LNG (offshore buoy), provided gas supplies directly to the northeastern part of the natural gas system, which improved regional gas grid reliability.

Table 8-1
Comparison of 2014 and 2015 January and February Winter Futures Prices
($/MMBtu, $/MWh)(a)

|  | Location | 2014 Futures(b) | 2015 Futures(b) |
| --- | --- | --- | --- |
| Natural gas ($/MMBtu)(c) | Algonquin (New England) | 11.76 | 21.45 |
|  | Transco Zone 6 non-NY (Mid-Atlantic) | 4.78 | 9.09 |
|  | Dominion South (Marcellus) | 3.66 | 2.85 |
|  | Southern California border | 3.95 | 4.30 |
|  | Henry Hub | 3.87 | 4.08 |
| Power ($/MWh)(d) | Massachusetts hub | 99.88 | 183.88 |
|  | PJM western hub | 44.90 | 72.60 |
|  | Northwest (Mid-Columbia trading point)(e) | 37.73 | 35.75 |
|  | Southern California (SP-15)(f) | 42.25(f) | 6.13 |

(a) 	Sources: Derived ICE and Nymex data and FERC, 2014-2015 Winter Energy Market Assessment Presentation (October 16, 2014), slide 11, http://www.ferc.gov/market-oversight/reports-analyses/mkt-views/2014/10-16-14-A-3.pdf.

(b) 	January and February 2014 futures pricing is as of October 1, 2013. January and February 2015 futures pricing is as of October 1, 2014.

(c) 	Gas prices ($/MMBtu) shown are regional futures prices (the sum of the Henry Hub future contract price plus the regional basis futures).

(d) 	Power prices ($/MWh) shown are peak financial swap prices.

(e) 	The Mid-Columbia electric trading point is a center point along the Columbia River on the border between Washington and Oregon states.

(f) 	SP-15 refers to CAISO’s zone covering southern California. The futures pricing for SP-15 2014 is as of October 31, 2013.

## Addressing Fuel-Certainty and Cost Risks

A number of solutions to the fuel-certainty and cost-volatility risk are underway. These measures include improved electric power system and natural gas sector coordination, winter reliability programs, revised wholesale electricity market rules, and pipeline infrastructure expansion and enhancements.

### Electric Power System and Natural Gas Sector Coordination

The implementation of operating procedures and improved communications between electric power and natural gas system operators over the past several years have improved the coordination between the natural gas and electric power systems and have prevented certain operational risks. ISO efforts have included mining data from various sources to estimate the availability of natural gas for electric energy purposes, analyzing capacity scenarios across different seasons using information gathered from fuel surveys and pipelines, and establishing operating plans to deal with different system conditions.

In November 2013, FERC issued regulations that allow the ISO system operators and operators of the gas transmission system to share a broad range of nonpublic information to promote the reliability and integrity of each system. The ISO filed tariff revisions to permit the newly authorized communications in New England starting in early 2014. The changes have improved communications and information exchange between the control rooms of the gas and electricity networks for more informed decision making.

FERC also recently decided on revisions to the natural gas scheduling practices used by interstate pipelines to better align the natural gas and wholesale electricity markets (see Section 11.1.2). The revisions include moving the timely nomination cycle later and adding another intraday nomination opportunity. The revised regulations in this final rule also provide additional contracting flexibility to firm natural gas transportation customers through the use of multiparty transportation contracts.

The ISO continues to work with the natural gas industry to address the challenges of the increasing interdependency between the gas and electric power industries. Ways in which the gas sector could assist with reliability efforts include having gas suppliers provide generators with additional opportunities to obtain fuel outside normal business hours, having pipelines offer more flexible scheduling, offering additional services, and improving real-time information on the status of the pipeline system. In addition, the ISO can continue to monitor planned upgrades to natural gas infrastructure to maintain operational awareness of the changing capacity of the natural gas system.

### Winter Reliability Programs to Address Fuel Certainty

For a second year, in winter 2014/2015, the ISO implemented a special program outside its markets to mitigate winter reliability risks associated with the retirements of key non-gas-fired generators, gas pipeline constraints, and generators’ difficulties in replenishing on-site oil supplies. As part of the 2014/2015 program, demand resources were compensated, and oil-fired, dual-fuel generators and units contracting with LNG supplies were paid to secure fuel inventory. These generators also were compensated for any unused end-of-season fuel inventory and were subject to nonperformance charges. As a result, the high availability of fuel oil and LNG supported winter 2014/2015 operations despite the cold weather.

The 2014/2015 program included two permanent improvements, as well. To help dual-fuel resources more effectively manage fuel supply on days when the price of oil and natural gas approach convergence, the market monitoring rules eliminated the administrative requirement to prove that the higher-priced fuel was burned. The ISO also gained the ability to test resources’ fuel-switching capability and to compensate them for running these tests.

As shown in Figure 8-8, the overall amounts of on-site fuel oil inventories (both heavy and light oil) at all regional fossil stations were substantially higher than those amounts from the prior winter. The regional electric power sector consumed approximately 45,000 blue barrels (bbls) in December 2014, approximately 390,000 bbls in January 2015, and approximately 2.38 million bbls during February 2015, bringing the three-month total amount of fuel oil used to approximately 2.8 million bbls. The consumption of oil provided reliable fuel certainty and mitigated the effects that high natural gas prices have on the wholesale electric system markets.

Figure 8-8: On-site fuel oil inventories (both heavy and light oil) at all New England fossil-fuel stations, winter 2013/2014 and 2014/2015 (beginning of each month) (million barrels)

Note: All values were taken from surveys submitted on the first day of each month, except for March 2015, which was taken from surveys submitted February 15, 2015.

Table 8-2 shows the increase in LNG supplies delivered to the region for the past two winters. Winter 2014/2015 had almost double the amount of LNG supplies at approximately 32 billion cubic feet (Bcf) compared with approximately 16 Bcf in the prior winter. The ISO has observed on the regional pipeline electronic bulletin boards an increased LNG sendout, which is a result of the recently improved availability of spot-market gas within the Northeast and contracts made in advance of the winter.

Table 8-2
Comparison of LNG Deliveries for Winter 2013/2014 with Winter 2014/2015 (Mcf)

| Port | December |  | January |  | February |  | Seasonal Total |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 2013 | 2014 | 2014 | 2015 | 2014 | 2015 | Winter 2013/2014 | Winter 2014/2015 |
| Distrigas | 1,013,199 | 707,137 | 815,439 | 5,634,040 | 932,475 | 4,450,831 | 2,761,113 | 10,792,008 |
| Canaport | 3,237,722 | 2,681,902 | 6,609,209 | 6,177,325 | 3,419,294 | 9,270,340 | 13,266,225 | 18,129,567 |
| Northeast Gateway |  |  |  | 1,070,443 |  | 1,605,378 |  | 2,675,821 |
| Total | 4,250,921 | 3,389,039 | 7,424,648 | 12,881,8080 | 4,351,769 | 15,326,549 | 16,027,338 | 31,597,396 |

Sources: Based on information provided by NatGas Analyst Tool by Genscape, a part of DMG Information (DMGI); http://www.genscape.com.

### Improvements to the Wholesale Electric Markets

The ISO through its open stakeholder process made several changes to the wholesale electric markets, which are addressing fuel-certainty reliability concerns.

#### Energy Market Offer Flexibility

Implemented in December 2014, this major revision to the ISO’s markets allows generators to reflect fuel costs in their wholesale energy bids as those costs change throughout the day. This improvement to real-time price formation assures that resources will receive appropriate compensation for the costs they incur to operate, providing them the incentive to perform. Energy market offer flexibility (EMOF) helps electricity suppliers reflect any changes in gas prices between and within the electric power operational days. Resource owners are able to do the following:

- Submit power supply offers that vary by hour in the Day-Ahead Energy Market, in contrast with previous rules requiring the same offer for the entire operating day

- Change supply offers in the Real-Time Energy Market (until 30 minutes before the hour in which the offer applies) instead of being restricted under the prior rules to changing offers only during a brief “reoffer period” the previous day

- Submit negative offers as low as –$150/MWh

In addition, this project expanded the biddable range of many resources, enabling energy prices to be set more competitively. This change is particularly helpful during low-demand conditions.

#### Improvements to Gas-Electric Coordination

In 2013, changes to the wholesale electric markets accelerated the Day-Ahead Energy Market and Reserve Adequacy Analysis timelines to better align the timing of the wholesale electricity and natural gas markets, with the goal of improving reliability. The ISO found that, one year later, the modifications had already incrementally improved gas-electric coordination, including positive impacts on system operations, with fewer units committed day-ahead that were eventually unavailable in real time due to gas-procurement issues. FERC orders further improved gas-electric coordination by changing the coordination and scheduling of spare natural gas pipeline capacity with electricity markets.

#### Focus on Price Formation

Many of the ISO’s recent and upcoming market-rule changes are designed to improve “price formation”—the ability of the wholesale electricity markets to set prices that more accurately reflect a power resource’s operating costs under a variety of system conditions. Accurate, transparent pricing motivates and compensates resources to make cost-effective investments—at the right times, in the right amounts, and in the right locations—for delivering the energy that consumers demand and maintaining the operating reserves that assure power system reliability.

#### FCM Pay-for-Performance

The ISO’s determination that the market was not providing sufficient incentives for resource performance prompted the pay-for-performance (PFP) change made to the FCM. This resulted in resources that sometimes failed to produce energy when needed most—despite receiving capacity payments—posing a serious threat to power system reliability. PFP goes into effect with FCA #9 (see Section 4.1.3) for the June 2018 to May 2019 capacity commitment period. It applies a two-settlement capacity market design:

- Resources that clear the auction will receive base capacity payments, as they did previously.

- A second settlement will take place during the delivery year. When scarcity conditions exist in a capacity zone, resources in the zone that perform well will receive a payment, while those that do not will receive a charge.

Pay for performance will create stronger financial incentives for capacity suppliers to achieve the following:

- Perform when called on during periods of system stress: With PFP, a resource that underperforms will effectively forfeit some or all capacity payments. Resources that perform in its place will get the payment instead. This means that the financial risk of nonperformance is placed on resource owners who have accepted capacity obligations; the capacity market price is not affected during times of system stress, thus protecting consumers.

- Make investments to ensure performance: The specific investment is not prescribed. Examples of the many available options include ensuring robust maintenance practices and adequate staffing, upgrading to dual-fuel capability, entering in noninterruptible gas-supply agreements, and investing in new fast-responding assets. Adding dual-fuel capability, however, could increase generator emissions and fuel costs.

By creating incentives for generators to firm up their fuel supply, pay for performance may indirectly provide incentives for the development of oil or LNG fuel storage or gas pipeline infrastructure. However, PFP will not take effect until 2018 and will not reach full effectiveness until the seven-year phase-in of the new performance payment rate is complete. Until that time, the region may be challenged to meet power demand any time pipeline capacity is constrained. PFP may also hasten the retirement of inefficient resources with poor historical performance and the entrance of new, efficient, better-performing resources. Ultimately, PFP is an efficient and effective way to promote investments necessary to improve performance, to provide a stable revenue stream to high-performing resources for maintaining their viability, and to ensure continued predictable capacity prices and long-term reliability for consumers.

### Pipeline Improvements

Interstate pipeline companies serving the Northeast region (including the Mid-Atlantic region) have added numerous interconnections from the Marcellus gas production area’s large and small producers, and annual natural gas production volumes in the Northeast are projected to rise from 3.92 trillion cubic feet (Tcf) in 2013 to 6.66 Tcf in 2024. New England, however, cannot access the full benefit of Marcellus shale production. Figure 8-9 shows the proposed natural gas pipeline expansions that could benefit New England.

Figure 8-9: Proposed natural gas pipeline expansions benefiting New England, 2015.

Note: Prepared from Northeast Gas Association publicly available information; all project locations are approximate. The green boxes indicate projects approved by FERC (updated through October 2015).

At present, of the 19 proposed pipeline-expansion projects under development across the Northeast, eight projects, as shown in Table 8-3, would specifically bring either new or incremental pipeline capacity to New England and regional access to additional natural gas supplies.

Table 8-3
 Summary of Pipeline Improvements Benefiting New England

| Project (Developer) | Additional Capacity Dekatherms per day (Dth/d) | Location | Regulatory Status |
| --- | --- | --- | --- |
| Algonquin Incremental Market (AIM) (Spectra Energy) | 342,000 | CT and MA | FERC granted approval, March 2015; late 2016 in-service date |
| Connecticut Expansion Project (Tennessee Gas Pipeline) | 72,000 | Primarily CT, some NY and MA | Filed for FERC approval; estimated November 2016 in-service date |
| Continent to Coast (C2C) Expansion Project (PNGTS, TransCanada, Iroquois) | 168,000 – 300,000 | Québec, NY, and ME | Estimated November 2017 in-service date |
| Atlantic Bridge Project (Spectra Energy) | 222,000 Involves incremental expansion on the AGT and M&N pipelines to serve emerging gas markets in northern New England and the Canadian Maritimes | CT, RI, MA, NH, and ME | Estimated 2017 in-service date |
| Northeast Energy Direct (NED) Project (Tennessee Gas Pipeline, Kinder Morgan) | Up to 2,200,000 Involves construction of pipeline, additional meter stations, and compressor stations and additional modifications to existing facilities | PA, NY, CT, MA, and NH | Estimated November 2018 in-service date |
| Access Northeast (Spectra Energy, Eversource Energy, National Grid) | Up to 1,000,000 Existing pipeline expansion project involving Algonquin and Maritimes pipeline systems and market area storage assets in New England | CT, RI, MA, NH, and ME | Open season completed, May 2015 |
| Iroquois South to North Project (Iroquois Gas Transmission System) | Up to 650,000 Reverse flow on Iroquois offering physical transport to US/Canada border. The project would transport gas from Iroquois’ existing interconnects with Dominion in Canajoharie, NY, and Algonquin in Brookfield, CT, as well as the proposed Constitution Pipeline in Wright, NY. | Upstate NY | Open season held December 2013 to January 2014; relaunch of open season, January 2015 to February 2015; estimated 2017 in-service date |
| Iroquois Wright Interconnect Project (Iroquois Gas Transmission System) | Up to 650,000 Will enable delivery of gas from the terminus of the proposed Constitution Pipeline in Schoharie County, NY, into both Iroquois and the Tennessee Gas Pipeline under a 15-year capacity lease agreement with Constitution | Mid-state NY | Announced January 2013; filed with FERC in June 2013. FERC issued final Environmental Impact Statement (EIS) in October 2014. FERC authorized, December 2, 2014; estimated in-service date is second half of 2016. |

Source: Northeast Gas Association’s May 4, 2015, update of its Planned Enhancements, Northeast Natural Gas Pipeline Systems (table); http://www.northeastgas.org/pdf/system_enhance0515.pdf.

Unlike the electric power industry, which builds infrastructure in anticipation of demand, interstate natural gas pipeline companies require gas shippers and customers to enter into long-term firm commitments before the infrastructure can be developed. Although the natural gas pipelines serving the region are at or near capacity, they will not be expanded until customers make firm commitments. In fact, FERC, which must approve interstate pipeline projects, bases its decision that a pipeline project is in the public convenience and a necessity in large part on the existence of firm contractual commitments. The ISO will continue to monitor when any power generators within New England sign a firm contract for any portion of these regional upgrades that will improve fuel assurance.

The recent and planned expansion and other upgrades to the regional and interregional natural gas infrastructure provide initial steps for expanding access to natural gas sources to meet New England’s increasing demand for natural gas to generate electric power. More expansion will most likely be required, however.

## EIPC Gas-Electric System Interface Study

Several studies have quantified potential shortfalls in natural gas supply to electric power generators, and additional studies are underway. RSP14 summarized a white paper that quantified the extent of the regional fuel-diversity risk and assessed the ability of the regional gas supply and delivery system to serve the gas demands of New England’s power supply. RSP14 also discussed a scenario analysis that identified potential shortfalls of natural gas supply to generating units.

In response to a DOE request, the Eastern Interconnection Planning Collaborative (EIPC) contracted with Levitan and Associates, Inc. (Boston, MA), to conduct a study of the interactions between the natural gas and the electric power systems across portions of the Eastern Interconnection. The study examined several scenarios and divided the work into four targets:

- Develop a baseline assessment of the existing natural gas and electric power system infrastructures

- Evaluate the capability of the natural gas system to meet the needs of the electric power system

- Identify contingencies on the natural gas system that could adversely affect electric power system reliability and vice versa

- Review operational, planning, and economic issues related to fuel-assurance, including the options for enhancing dual-fuel-capability compared with adding incremental firm gas transportation

Most of the technical analysis was conducted during 2014, and draft reports were provided for stakeholder input for each of the targets. All four final draft reports have been posted on the EIPC website. EIPC submitted the final reports to DOE on July 2, 2015.

### Target 1

The Target 1 baseline report discussed gas pipelines, LDCs, and storage facilities, and defined pipeline and LDC transportation options for generators. The report assessed generator contracting and proposed fuel-assurance practices. It also evaluated the secondary market for released natural gas transportation capacity. Target 1 results showed the ISO is at the greatest risk of natural gas supply of all the participating planning authorities.

### Target 2

Target 2 evaluated the adequacy of the interstate gas pipeline network to meet the coincident peak demands of local gas distribution companies serving firm residential, commercial, and industrial (RCI) customers, as well as gas-capable electric power generators across the study region. The study showed sufficient natural gas system infrastructure for the Independent Electricity System Operator of Ontario (IESO), TVA, and MISO, but depending on location, the gas infrastructure is either adequate or moderately constrained in PJM. The natural gas system for both NYISO and ISO New England was constrained in winter 2018 and 2023, the two years studied, under nearly all market conditions and resource mixes in the scenarios and sensitivities tested.

The Target 2 constraints for ISO New England reflect both commodity supply and transportation deficits. Nearly all the gas-fired generators in New England lack primary firm entitlements, thereby limiting access to natural gas during cold snaps. The deliverability shortfall is explained by upstream transportation bottlenecks into New England along the major pipeline pathways linking Marcellus with New York and New England, as well as the anticipated continued decline in traditional imports from eastern and western Canada. Limiting receipts at the LNG import facilities in New Brunswick and Massachusetts increases the deliverability shortfall in New England, particularly on the Algonquin and Tennessee mainlines around Boston. Several recently announced and FERC-approved pipeline projects were incorporated into the base scenario analysis, including Spectra Energy’s AIM, Atlantic Bridge, and Salem Lateral projects; Tennessee Gas Pipeline’s Connecticut Expansion project; and Iroquois Gas Transmission’s Wright Interconnect project,

The results show the mitigation of the region’s high reliance on gas-fired generation in 2018 and 2023 when high daily spot-market gas prices place oil-fired generation, and, to a much lesser extent, coal-fired generation, in merit. In case sensitivities, the postulated more complete utilization of the LNG import terminals at both Canaport and Distrigas materially lessens the amount of affected natural gas-fired generation. No constraints are present in summer 2018, but by summer 2023, growth in electricity loads increases gas transportation deficits affecting some generators throughout the region.

### Target 3

The Target 3 report built on the Target 2 assumptions by considering several scenarios of natural gas system and electric power system contingencies and quantified the interactions between these systems. The study identified reductions in natural gas-fired generation resulting from key natural gas system contingencies, including compressor outages, pipeline ruptures, and the loss of major storage deliverability. The electric power system contingencies covered the loss of transmission system facilities and major non-gas-fired generating stations, which resulted in the need to increase the use of natural gas-fired generation and stresses on the natural gas system. The report also identified gas-sector operational measures that could mitigate the adverse effects of gas and electric power system contingencies.

The Target 3 analysis of the natural gas system contingencies identified pipeline pressure limitations that constrain the ability of gas-fired units to generate electricity. The affected generators in New England typically need to reduce output several hours after a contingency event. The use of dual-fuel capable units, the redispatch of other units, and other actions of electric power system operators could mitigate adverse reliability consequences. Natural gas system operator actions also could reduce the severity of natural gas system contingencies.

Like ISOs/RTOs, natural gas pipelines are well positioned to provide mutual assistance to interconnected pipelines when severe operating conditions or contingencies occur; however, the pipelines are not mandated to do so. Likewise, LDCs are organized to provide mutual assistance to both pipeline and neighboring LDCs when severe operating conditions or contingencies occur. Pipeline operator protocols are incorporated in the model solutions that can mitigate the adverse impacts of a gas or electric power system contingency on gas-fired generation. Communication initiatives among the participating planning authorities, pipelines, and LDCs can strengthen available mitigation measures in response to heightened gas/electric power interdependencies across the study region in 2018 and 2023. Pipeline tariff innovations and continued efforts to harmonize the gas and electric day scheduling procedures also can provide greater flexibility to gas and electric power control room operators when contingencies occur on either system.

The Target 3 reliability assessment also showed acceptable natural gas pipeline system pressure for increased usage resulting from contingencies on the electric power system. For example, the loss of a nuclear generator could result in the need for operating reserves provided by natural-gas-fired generation.

### Target 4

The Target 4 report summarized issues with new gas-fired plants using ultra-low-sulfur diesel (ULSD) as the primary backup fuel, which has a robust supply chain. Air permits typically cap oil use to 720 hours, but some permits have established lower annual hourly limits and restrictions during ozone season. In establishing the tank size and target inventory level for backup fuel, owners are likely to consider the following factors:

- The frequency and duration of pipeline limitations on the scheduling of natural gas during the peak heating season (January, February, and December) to match the required dispatch profiles, even without forced curtailments of natural gas

- The times the generator is expected to be in economic merit when using the alternative fuel

- The delivery lag time for backup fuel delivery

- The impact of severe weather events on the delivery capacity of backup fuel

- The effect on a plant’s net revenues of a failure to deliver dispatched energy or to offer into the market due to fuel unavailability

The Target 4 analysis also compared the annual fixed costs of adding dual-fuel capability with obtaining firm pipeline transportation for gas-fired generators. The annual fixed costs of dual-fuel capability include fixed operation and maintenance costs for maintaining additional equipment, incremental property taxes and insurance, periodic liquid fuel tests, and carrying costs of back-up fuel inventory. For each analyzed location, a net cost of firm transportation for natural gas was established. The net cost was based on the reservation cost for incremental capacity on the most likely pipeline path from a source (such as Marcellus) to the location.

The Target 4 report concluded that the fixed costs of adding dual-fuel capability is much lower for a new combined-cycle plant compared with procuring firm transportation from a new natural gas pipeline. Although dual-fuel capability would improve electric power system reliability at lower annual fixed costs, other commercial reasons may otherwise induce generators to invest in firm transportation.

## Summary

The operational challenges experienced during winter periods highlight the need for the ISO to manage energy production limitations of electric power generators, especially natural gas-fired generators. The constrained ability of natural gas pipelines to deliver fuel to generating units results in the need for oil and coal generators to produce electricity. Siting and permitting new dual-fuel facilities that have sufficient operating flexibility when access to natural gas is limited remains challenging. Fuel constraints physically challenge the reliable operation of the system and results in increased prices for electricity, especially during the winter months or whenever pipeline capacity is reduced.

The region has implemented several measures and is developing others to improve the reliable and economic performance of the power system. The region successfully applied short-term mitigation measures, including the following, which bolstered winter reliability:

- Modifications to the day-ahead and real-time markets

- Procurement of additional reserves

- Improved coordination and communication among the ISO, generating units, and natural gas pipelines

- Energy market offer-flexibility enhancements

- Expanded winter reliability program to include LNG and dual-fuel conversions

Recent changes to increase the flexibility for scheduling natural gas will allow generators to more reliably respond to system conditions. Revisions to the Forward Capacity Market should support longer-term solutions to meeting New England’s need for fuel certainty. Planned improvements to the regional and interregional natural gas infrastructure also would help. Greater fuel certainty could be further improved in a number of ways:

- Firm contracts with natural gas pipelines would support the building of new natural gas pipeline capacity.

- Firm contracts with natural gas suppliers, including LNG operators, would improve the availability of natural gas for electric power generation.

- The use of existing and new dual-fuel capability at generating plants would provide alternative supplies of fuel when natural gas supplies are limited.

- Adequate on-site storage of liquid fuels would increase generation reliability at dual-fuel power plants.

- Increased efficient use of natural gas and electricity would allow greater use of available pipeline capacity by generators.

# Impacts of Environmental Regulations and Siting Requirements on Generators and the Power System

Various elements of the power system are subject to state, regional, federal, and international environmental land use, permitting, and siting regulations, many of which have protracted review periods that can complicate or delay planning, development, or the implementation of proposed transmission and generation improvements. Compliance with environmental requirements may necessitate major investments in remediation measures or changes in generator operations.

This section summarizes environmental regulations affecting generators and relicensing timelines for hydroelectric generators and nuclear units. The section also summarizes regional emissions for 2013, the latest available data.

## Federal, State, and Regional Environmental Regulations Affecting Generators

Compliance obligations for generators from existing and pending state, regional, and federal environmental requirements are likely to impose operational limits on new and existing generators. However, these requirements pose less risk on unit retirements and system reliability compared with earlier assessments. Federal air, water, endangered species, and carbon standards could affect the economic performance of nuclear, renewable, and fossil-fired generators by imposing operational constraints and additional capital costs for pollution control retrofits. Other state and regional air, water, and carbon standards could require certain generators to further reduce emissions and other adverse environmental impacts through the extended operation of pollution control devices or curtailment in operation.

The US Environmental Protection Agency (EPA) is developing and implementing several air and water quality rules in the following areas that will have an impact on existing and new generators:

- Surface water withdrawals (for cooling water use and consumption)

- Wastewater discharges into surface water

- Mercury, acid gas, and other toxic air emissions

- Ozone (O3) transport and fine particulate matter (PM2.5) and sulfur dioxide (SO2) emissions

- Greenhouse gases (GHGs)/carbon emissions

Several New England states and EPA are developing or implementing air and water quality requirements for generators and GHG reduction targets under the Regional Greenhouse Gas Initiative (RGGI) or through Clean Energy Performance Standards.

System reliability could suffer if the aggregate impact and timing of all these requirements limit generator energy production, reduce capacity output, or contribute to unit retirements. However, EPA has provided compliance options in several major recent rules, recognizing the reliability value that low-capacity fossil steam generators provide in maintaining system fuel diversity (see Section 8.2). Compliance with many of these requirements begins in 2015 and will continue through 2022.

### Emerging Impacts of Clean Water Act Regulations on the Region’s Generators

EPA and state regulators are implementing several major revisions to Clean Water Act (CWA) standards affecting electric generators, including the final § 316(b) Cooling Water Intake Rule and the proposed § 304 Effluent Limitation Guidelines (ELGs). In New England, 8.79 GW of existing thermal electric capacity relies on larger once-through cooling systems subject to the § 316(b) Cooling Water Intake Rule and could incur additional compliance costs (operational changes or retrofits). Another 3.22 GW of existing capacity has partially compliant cooling systems, and 2.92 GW of existing capacity (mainly newer facilities with combined cycle units) have already-compliant recirculating cooling systems. Any new thermal electric energy capacity most likely will comply with the regulations by installing dry, hybrid, or closed-cycle cooling systems or controlling or eliminating certain wastewater discharges under new discharge requirements.

#### Cooling Water Intake Rule Requirements

EPA and New England states are implementing the final Clean Water Act 316(b) Cooling Water Intake Structure Rule requirements to mitigate the adverse impacts to aquatic life of once-through cooling systems with a design intake flow of at least 2 million gallons per day (MGD). According to US Geological Survey (USGS) data summarized in Figure 9-1, 12 GW of existing steam electric generators (nuclear, coal, oil, natural gas, and bio/refuse) in New England withdraw cooling water using once-through systems engineered with a design intake flow of 2 MGD or greater. Electric generators equipped with such once-through cooling water systems are required to reduce fish impingement (i.e., when fish or wildlife are trapped against the intake structure due to the velocity of a facility’s water withdrawals). Regulators will select from among seven mitigation technologies or operational options to satisfy the Clean Water Act 316(b) requirement for best technology available (BTA) for reducing impingement. Facilities must comply with the impingement standards as soon as possible after receiving their final permits containing the new 316(b) entrainment requirements, with EPA anticipating most retrofits occurring between 2018 and 2022. The costs for mitigating impingement are expected to average $3,500/MW—for installing exclusion devices that protect aquatic life and potentially changing operations, such as to restrict seasonal flows to protect certain aquatic species.

Figure 9-1: Capacity and total water consumption by thermoelectric generators with once-through cooling in New England, 2010 (MW, MGD).

Note: A total of 12 GW of existing system capacity in New England has an estimated annual maximum water withdrawal greater than 2 MGD, and 10.9 GW has withdrawal capacity greater than 125 MGD, according to USGS (excluding resources retired in 2014 or recently converted to recirculating cooling).

Sources: ISO New England 2014 CELT; US Geological Survey Circular 1405 (November 2014).

Generators withdrawing at least 125 MGD for once-through cooling systems face more stringent obligations for gathering and submitting information. They will initially need to assess and report to regulators regarding the extent of the impacts of their cooling system entrainment (i.e., when aquatic life is removed into the cooling system) for use in permitting reviews. EPA considered, but did not adopt, a specific BTA for mitigating fish and wildlife mortalities caused by entrainment, instead opting to require site-specific assessments. Entrainment-characterization studies generally must be submitted no later than July 2018 as part of the NPDES permit renewals. Regulators will consider system reliability, the severity of the impacts to fish and wildlife populations, including protected and threatened species, and other factors in determining whether operational restrictions, conversion of once-through cooling systems to recirculating cooling systems, or other changes are required.

The latest Clean Water Act 316(b) rule also requires the agency and delegated states in New England to safeguard threatened and endangered species and critical habitats federally listed and designated under the US Endangered Species Act, considering design enhancements and operational requirements to reduce impingement mortality. Additional interim and permanent measures also may be required to protect shellfish and fragile species.

Approximately 10.9 GW of existing fossil and nuclear capacity in New England may need to modify their cooling water intake structures for impingement mitigation. Existing facilities where each generator has a low annual capacity factor (i.e., below 8% averaged over a two-year consecutive period) may petition for less stringent impingement-mitigation standards. In such instances, after conferring with any appropriate state coregulators (such as public utilities commissioners) and with RTOs, ISOs, or other planning authorities, regulators may assess the significance of the unit’s operation in relation to the overall reliability of electric power in the area.

#### Changing Wastewater Discharge Requirements

To address changes in the toxicity of wastewater discharges from power plants, EPA revised the steam electric Effluent Limitation Guidelines under the Clean Water Act on September 30, 2015, requiring many thermal generating stations to reduce or remove certain contaminants from their wastewater discharges between 2017 and 2023. Up to 6 GW in New England, including nuclear, coal-, oil- and natural gas-fired steam thermal generators, may be affected.

The proposed power plant ELGs present the largest uncertainty in the near term for these generators, particularly those operating air-pollution control devices creating concentrated wastewater discharges. The units affected in New England are coal-fired generators equipped with wet scrubbers.

### Clean Air Act Requirements and Regional and Federal Greenhouse Gas Regulations

Many Clean Air Act (CAA) actions affecting New England’s fossil-fuel power generators and the region’s air emissions are ongoing. The Mercury and Air Toxics Standards (MATS) and other air-quality rules are being implemented, the impacts of which are shown by the trends in regional emissions. Regional and federal greenhouse gas regulations also present a range of environmental and economic implications.

EPA finalized a more stringent ozone standard in October 2015, requiring operational changes and potential pollution control retrofits for larger fossil-fuel-fired generators’ capacity across southern New England by 2017. Once adopted, the revised ozone standard will trigger more stringent technology-based performance standards for new or modified fossil-fuel-fired electric generators.

#### Implementation of Mercury and Air Toxics Standards

Most of the 6.4 GW of existing coal- and oil-fired generators comply with the Mercury and Air Toxics Standards, which went into effect April 16, 2015. On June 29, 2015, the US Supreme Court ruled that EPA interpreted the Clean Air Act unreasonably when it failed to consider the cost of compliance and remanded the rule back to the lower court for further action. State air toxics regulations also remain in force, however, and air toxics controls will continue to operate for most units in New England.

Mercury soil and water concentrations are higher in the eastern United States, including New England, and USGS data indicate coal-fired electric generators remain the single-largest source category of mercury emissions in the United States. Most coal- and oil-fired fossil steam generators greater than 25 MW in capacity in New England are already complying with the standard’s emissions limits for acid gases, toxic metals, and mercury based on maximum achievable control technologies (MACTs) or are exempted due to individual unit capacity factors. An operator petitioned for and was granted a one-year compliance extension until April 2016 to complete the design and retrofit activities at two coal-fired generators.

#### Clean Air Act Regional Air Pollution Reduction

As much as 17.45 GW of existing fossil capacity in southern New England and potentially 21 GW across the entire region could be affected by future state, regional, and federal rules implementing various air quality and performance standards required under the Clean Air Act for a range of air pollutants. State and federal air regulators are expected to address deteriorating air quality trends across southern New England (particularly due to ozone and fine particulate matter), possibly resulting in more stringent emissions limits for fossil generators. Ozone and fine particulate matter generated far upwind of New England has hampered considerable regulator efforts to improve local air quality.

#### Regional Emissions Trends

The ISO tracks the system emissions, rates, and trends for nitrogen oxides (NOX), sulfur dioxide (SOX), and carbon dioxide (CO2) to help gauge the potential effects of future environmental regulations on the system and in response to historical requests from the states for emissions data. The ISO’s most recent air emissions report, the 2013 ISO New England Electric Generator Air Emissions Report, provides detailed historical trends and emissions rate data using methodologies developed with input from stakeholders.

A shift in the fuel mix powering the region directly contributes to the changing regional emissions, Since 2004, the annual total NOX emissions have decreased by 60%; SO2, by 88%; and CO2, by 28%. The reductions in emissions resulted primarily from the regional shift away from electrical energy production by older oil- and coal-fired generation to efficient natural gas-fired generation and increasing reliance on imports (see Section 7.6). Other factors that lowered emissions include the high capacity factors achieved by nuclear generators; the growth of both energy efficiency and renewable resources with low or zero emissions; the addition of environmental controls to generators, which reduce the production of pollutants; and transmission improvements, which decrease the dispatch and commitment of high-polluting generators. Figure 9-2 shows the regional annual emissions for New England.

Figure 9-2: 2004 to 2013 New England system annual emissions of NOX, SO2, and CO2, 2004 to 2013 (ktons).

Source: 2013 ISO New England Electric Generator Air Emissions Report (December 2014), http://www.iso-ne.com/static-assets/documents/2014/12/2013_emissions_report_final.pdf.

While total generation energy production declined 4% in 2013 from 2012, system emissions changed relatively little, despite 19% less natural gas generation, 40% more coal-fired generation, and 38% more oil-fired generation in 2013 than in the 2012. Total NOX system emissions did not change, while SO2 system emissions increased 9%, and CO2 system emissions decreased 3%. The system emission rates for 2013 were higher than 2012 values. The 2013 NOX, SO2, and CO2 emission rates increased by 3%, 14%, and 2%, respectively, from their 2012 values.

#### Implications of Regional and Federal Greenhouse Gas Regulations

In New England, fossil-fuel-fired generators larger than 25 MW have been subject to the Regional Greenhouse Gas Initiative since 2009 and face additional federal regulations for reducing greenhouse gases. RGGI states completed a comprehensive program review in 2013, lowering the overall CO2 budget (annual cap) to 91 million tons (mtons) beginning in 2014, reducing the cap by 2.5% each year through 2020. Figure 9-3 shows the total New England allowances for each of the auctions and the total CO2 emissions from the New England sources. In years where CO2 emissions exceeded the amount of allowances, some New England generators needed to either use banked allowances or purchase available allowances, which may be available from other states or the secondary market.

Figure 9-3: New England RGGI states’ quarterly CO2 emissions and allowance auctions, 2008 to 2015 (mtons, millions).

Source: RGGI (March 11, 2015), http://www.rggi.org/rggi.

In February 2013, a cost-containment reserve (CCR) was added. A CCR is a holding allowance released when a predetermined trigger price is reached during any quarterly auction. This occurred in 2014 with a trigger price of $4. The trigger price for the 2015 auctions is $6; for 2016, $8; and for 2017, $10. Other changes included adding an interim compliance deadline that requires affected generators to hold allowances covering at least 50% of their emissions during the first two years of each three-year compliance period. As Figure 9-4 shows, auction prices increased in 2014, reaching the 2014 CCR trigger price during Auction 23 (March 2014), which resulted in the release of all 5 million CCR allowances for 2014 (subsequent-year CCR reserves are 10 million allowances). Auction reports indicate that affected generators remain active participants, acquiring the majority of allowances offered during the current control period.

Figure 9-4: New England RGGI states’ quarterly CO2 allowance auction proceeds and clearing price, 2008 to 2015 (million $ and $).

Source: RGGI, (March 11, 2015), http://www.rggi.org/rggi.

In August 2015, EPA finalized the Clean Power Plan (CPP), for existing fossil-fuel-fired power plants under Section 111(d) of the Clean Air Act. The final CPP requires affected fossil power plants to reduce carbon emissions 32% nationwide by 2030 from a 2005 baseline, with the initial reductions due by an interim 2022 deadline and additional milestones before the final 2030 deadline. As shown in Figure 9-5, the New England states have differing obligations for reducing carbon emissions by 2030, which depends on their existing fossil generating capacity. If regional compliance is adopted, the states’ aggregate reduction targets in any given CPP compliance year (2022 to 2030) will be above the annual emission levels reached in 2014 under RGGI. The greater use of lower-emitting fuels, energy efficiency, wind and photovoltaic resources, and imports from neighboring systems and added environmental controls could decrease regional emissions further.

Figure 9-5: EPA Clean-Power-Plan-adjusted state CO2 emissions, 2012 historic baseline compared with 2014 emissions reached under RGGI, interim (2022 to 2029) mass-based reduction targets, and final (2030) mass-based reduction targets, (short tons).

Notes: EPA calculated adjusted 2012 state baselines and interim (2022 to 2029) and final (2030) targets. Annual 2014 CO2 emissions from RGGI states are shown for comparison purposes but not regional projections of emissions.

Sources: EPA, Clean Power Plan Technical Support Document: Emissions Performance Rate and Goal Computation, EPA Technical Support Document CPP performance rate goal computation appendix-1-5 (August 2015); http://www.epa.gov/airquality/cpp/tsd-cpp-emission-performance-rate-goal-computation-appendix-1-5.xlsx. EPA “Air Markets Program Data,” webpage (2015), Regional Greenhouse Gas Initiative, 2014 emissions, state-level data, http://ampd.epa.gov/ampd/.

The Clean Power Plan requires states opting for individual compliance approaches to submit 111(d) State Plans (SPs) by September 2016, while states participating in multistate 111(d) submittals need to submit preliminary plans by September 2016 and have until June 2018 to submit final joint plans. Individual 111(d) SP submittals are expected to use wide-ranging approaches, but regardless of the compliance option selected, state plans must provide detailed criteria, enforceable requirements for individual generators, monitoring, and recordkeeping requirements. In New England, states may use RGGI participation in part, along with complementary policies, to satisfy all 111(d) obligations.

### Cost of Compliance with Environmental Regulations

The Strategic Planning Initiative identified as a near-term issue the retirement of generating units resulting from the costs to comply with environmental obligations. Most of the at-risk capacity faces compliance or retirement decisions later this decade and extending into the early part of the next decade, which is expected to affect positions in upcoming FCA auctions. The actual compliance timelines and costs will depend on the timing and substance of the final regulations and site-specific circumstances of the electric generating facilities. The ISO continues to identify such generators and study potential impacts.

## Update of Regional Nuclear Generation Licensing Renewals

New England has four nuclear generating generators: two in Waterford, Connecticut (Millstone), and one each in Seabrook, New Hampshire, and Plymouth, Massachusetts (Pilgrim). Vermont Yankee notified the ISO on August 27, 2013, that it would cease commercial operation. It negotiated a retirement agreement with the State of Vermont and ceased operation on December 29, 2014, after exhausting its fuel cycle. All remaining nuclear generators require an operating license, which is subject to renewals or extensions, as summarized in Table 9-1.

Table 9-1
New England Operating Nuclear Power Plants

| Unit Name | Operating (OP)/ Renewed License Dates | License Expiration Date | Reactor Type | Electrical Output (MWe)(a) | Reactor Vendor/Type |
| --- | --- | --- | --- | --- | --- |
| Millstone 2 | September 26, 1975/ November 28, 2005 | July 31, 2035 | Pressurized water | 884 | Combustion Engineering (vendor) |
| Millstone 3 | January 31, 1986/ November 28, 2005 | November 25, 2045 | Pressurized water | 1,227 | Westinghouse/ four-loop |
| Pilgrim | June 8, 1972/ May 29, 2012 | June 8, 2032 | Boiling water | 685 | General Electric/ type 3 |
| Seabrook | OP: March 15, 1990 | March 15, 2030 | Pressurized water | 1,295 | Westinghouse/ four-loop |

        - “MWe” stands for electrical megawatts. Nameplate electrical output was obtained from the Nuclear Regulatory Commission’s (NRC) website, http://www.nrc.gov/info-finder/reactor/.

The Nuclear Regulatory Commission finalized a replacement rulemaking, the Continued Storage Rule in November 2014, revising the general environmental impacts of spent nuclear fuel storage operations at closed reactors sites nationwide, including 11 sites in New England.

## Update on Hydroelectric Generation Relicensing

Conventionally, hydroelectric generators are among the oldest generators on the system, which include 1,482 MW, or 4.8%, of the regional summer claimed capability, and represent 7,303 GWh, or 6.7%, of all generation in 2014. In addition to providing capacity and electric energy, hydroelectric units traditionally have been well suited to provide regulation and reserves, but they may lose some of their ability to operate flexibly as part of their relicensing requirements.

The licenses for 1,945 MW of existing hydroelectric generators, including 1,720 MW of pumped-storage capacity, will expire between 2014 and 2022. FERC is pursuing an integrated relicensing review for several hydroelectric projects located on the Connecticut River, with a completion deadline of April 2018 for all relicensing activities. Relicensing must take into consideration the requirements for adequately and equitably protecting and mitigating damage to fish and wildlife (and their habitats) and the recommendations of state and federal fish and wildlife agencies. The ISO is monitoring such proceedings to assess the impacts of operational restrictions, including the maintenance of minimum flows, on the ability of hydroelectric generators to offer regulation and reserve services.

## Conclusions

Existing and pending state, regional, and federal environmental regulations will require many generators to consider adding air-pollution control devices; modifying or reducing water use and wastewater discharges; and, in some cases, limiting operations. The actual compliance timelines and costs will depend on the timing and substance of the final regulations and site-specific circumstances of the electric generating facilities. Some generators needing to make major investments in environmental compliance measures may become uneconomical and retire, but others can recover their capital investment by locking into FCM prices for up to seven years.

Regional generator emissions remain relatively low compared with historical levels, resulting from the greater use of natural gas generation. Higher emissions, however, occur during the winter months because of the burning of oil by generators.

# Integration of Variable Energy Resources

The integration of large amounts of variable energy resources, including wind and photovoltaics poses new challenges to the electric power system. To address these challenges, the ISO has been conducting a number of studies, gathering operational data and observations, and participating in other projects assessing the development and integration of variable energy resources.

## Potential System Impacts on Fossil Fuel Generators of Integrating Wind and Solar Resources

The US Department of Energy's National Renewable Energy Laboratory (NREL) released the second phase of a study examining the potential impacts of increasing wind and solar power generation on the operators of coal and gas plants in the West (including parts of Canada and Mexico). The report found that to accommodate higher amounts of wind and solar power on the electric power grid, utilities will need to ramp up and ramp down conventional generators more frequently than with less wind and solar on the grid. This report assessed various scenarios of wind and solar penetration and concluded that with wind and solar facilities supplying about 25% of the power in 2020, the projected cost savings of needing less fuel far outweighed the costs associated with increased ramping. In addition, according to this report, overall emissions of SO2 and NOX would be reduced despite the impacts of increased ramping.

The ISO will continue to track industry research and monitor the effects that increased amounts of variable energy resources have on system performance, including ramping. The ISO will identify regional needs and work through the stakeholder process to develop regional solutions to any identified issues.

## Integration of Wind Resources

New England has tremendous potential for developing wind resources. The region has developed approximately 850 MW, and almost 4,100 MW is in the interconnection queue. As the amount of wind generation grows, operational forecasts of this variable energy resource take on increasing importance.

### Wind Forecasting and Dispatch

On January 15, 2014, the ISO began incorporating wind forecasting into ISO processes, scheduling, and dispatch services. (As of May 2013, the ISO has offered a preliminary informational wind power forecast.) The wind power forecast is exceeding expectations regarding accuracy. In addition to the ISO’s use of the wind forecast, wind resources can download the forecast of expected output for their individual units, which can help them build a strategy for bidding in the Day-Ahead Energy Market. As part of phase 1 of this project, the ISO has also created displays that improve operators’ situational awareness and is now maintaining historical wind data for future use by the forecast service and in auditing and other analyses. The ISO is working toward the full economic dispatch of wind resources, as well as automated publishing of the aggregate wind energy forecast for the region in phase 2 of this project.

### Strategic Transmission Analysis—Wind Integration Study

ISO New England is conducting transmission system reliability assessments to identify the nature of the transmission system reinforcements necessary to integrate significant amounts of wind resources into the system. RSP14 discussed how much additional wind energy could be integrated in the State of Maine without major transmission system investment, particularly new lines. RSP15 updates the RSP14 transmission analysis in Maine by more fully accounting for the dynamic regional system behavior and discusses the wind integration analysis for the State of Vermont.

Base case power flow models were developed by adding representative stations for all wind resources in the ISO’s queue at the time of the scoping of each portion of the study. Several load conditions were examined, and all wind resources within the area being investigated were increased from zero until a thermal limit was reached for transfer out of the region. System voltage and stability performance were then tested at these thermal limits to determine whether those other limits were more constraining. The studies identified the lower-cost improvements that increased the transfer limit for a region, such as adding reactive devices or series circuit breakers or rebuilding a short transmission line. The generators were modeled with the assumption of robust local voltage control capability at the generation sites. Additional system improvements would be required for interconnections without adequate local voltage control.

The assessment examined the following specific regions:

- Keene Road region in Maine

- Bangor region in Maine

- Wyman region in Maine

- Rumford region in Maine

- Northern region in Vermont

- Central region in Vermont

- Southern region in Vermont

The assessments analyzed thermal, voltage, and stability limits for both local transmission interfaces and broader regional constraints to moving the aggregate wind and other resources from the local regions. The assessments also examined the need for improvements to meet NPCC bulk power system requirements.

#### Summary Results for the Maine Regional Constraint Analysis

Summary results for the Maine regional constraint analysis show that additional wind resources would displace traditional synchronous generator technology and the stability performance benefits of these types of machines.  A dynamic reactive device of up to 500 MVAR capability located in central Maine would likely be needed to integrate new wind resources effectively. At the same time, ensuring that these wind resources directly aid dynamic voltage control could improve the overall system performance during both normal and critical extreme contingencies.

The testing of the regional transmission interfaces in Maine identified the need for additional system reinforcements. These reinforcements include two 345 kV 25 ohm thyristor-controlled series-compensation (TCSC) devices and up to 480 MVAR of 115 kV shunt capacitors throughout Maine. The TCSC devices are necessary to prevent system separation and the interruption of large amounts of resources following severe contingency events in southern New England. The shunt capacitors are required for voltage support in Maine.

The above improvements are insufficient to both improve the performance of the bulk power system and increase regional transfer limits. The study suggests that both these requirements could be met by adding transmission upgrades, such as 1,000 MVAR of synchronous condensers in Maine, in addition to the 500 MVAR dynamic reactive device previously mentioned. The alternative to addressing the BPS performance requirement with the synchronous condensers is the possibility of continually needing widespread substation upgrades throughout southern New England.

#### Summary Results for the Local Maine Regions

The results for the four local Maine regions are summarized below.

Keene Road Region. The ability to accommodate 229 MW (nameplate capability) of wind capacity in this region was analyzed. The studied system would probably not experience thermal violations at this generation level, but a voltage stability issue would occur at levels of wind generation above the simulated amount of 144 MW, and the performance of the system could be unacceptably degraded during extreme contingency conditions. Major transmission construction would likely be needed to address local constraints to additional generation.

Bangor Downeast Region. This area was analyzed for its ability to accommodate 186 MW (nameplate capability) of wind capacity. The 115 kV loop in this region is vulnerable to thermal overloads when a contingency occurs. Low 115 kV voltages also would occur at exports above approximately 130 MW, and the performance of the system could be unacceptably degraded during extreme contingency conditions.

The 186 MW of existing and proposed generation could be integrated with a few relatively small transmission upgrades. System performance is highly sensitive to the location of new plants and the electrical distance from the 115 kV loop. Voltage/transient stability problems are anticipated with amounts of generation greater than the 186 MW studied; major transmission construction would likely be needed to address these voltage/stability constraints.

Wyman Hydro Region. The ability to integrate 418 MW (nameplate capability) of wind capacity, including existing resources, was analyzed for this region. The 2015 system would probably not experience significant thermal violations during the summer and winter but likely would experience thermal constraints during spring and fall when high hydro and wind conditions exist. Low 115 kV and 345 kV voltages could be experienced, and the performance of the BPS could be unacceptably degraded during extreme contingency conditions.

These local constraints to the added wind generation may be addressed without major transmission construction for up to 418 MW of wind capacity. This result recognizes reasonably anticipated seasonal variations of plant output, provided that each new wind plant is interconnected with a physically and economically realistic amount of dynamic reactive compensation. Transmission improvements would include items such as the addition of series circuit breakers, the rebuilding of short sections of transmission lines, and the addition of reactive devices.

Rumford Region. This area was analyzed for its ability to accommodate 130 MW (nameplate capability) of wind capacity. No thermal limitations would be expected at this generation level. Low 115 kV and 345 kV voltages could be experienced for normal design contingencies, and the performance of the system could be unacceptably degraded during extreme contingency conditions.

Upgrades would be needed to integrate existing and proposed generation. Local constraints could be addressed without major transmission line construction. System performance is interdependent with the Wyman Hydro region, and the transmission upgrades indicated for this region would also address constraints for Rumford region’s generators. This analysis does not indicate the extent to which generation could be added before minor or major transmission construction would become necessary.

#### Summary Results for the Local Vermont Regions

The results for the three local Vermont regions are summarized below:

Northern Vermont Region. The ability to accommodate 287 MW (nameplate capability) of wind in this area was analyzed. The Highgate HVDC connection to Québec was modeled at full import of 216 MW (measured at the New England side of the terminal) during the analysis. Due to the single loop nature of the transmission system in this region, a thermal limit of 213 MW was observed under winter load and line-rating conditions, when the wind would be expected to be at its maximum output. The analysis also considered the integration of the wind resources under summer, shoulder load, and light-load conditions. Thermal transmission constraints caused the summer limit on wind generation to be 120 MW of operating capability. However, the expected typical output of 287 MW of nameplate wind generation in the summer period was estimated to be 86 MW, and the expected maximum output was estimated to be 186 MW.

Similarly, in the shoulder and light-load scenarios, limitations were identified that would permit expected wind generation output under typical output conditions but be restrictive under maximum expected output levels for these seasons. No minor transmission upgrades were identified that could increase the thermal limits identified in the analysis. Stability analysis revealed that additional reactive support would be required at Jay Tap and Highgate to meet the minimum operating voltage requirement at Highgate and accommodate wind up to the seasonal thermal limits. In total, a little over 100 MVAR of reactive support would need to be added in these two locations, a mix of static capacitors and synchronous condensers.

Central Vermont Region. The ability to accommodate 165 MW (nameplate capability) of wind in this area was analyzed. This area has a relatively strong 345 kV backbone, so no thermal or stability reliability violations were observed at this level of wind output. Therefore, no major transmission improvements would be necessary at this level of wind production. The existing system could accommodate 231 MW (nameplate capability) of wind generation, operating at full output, before the 115 kV system would begin to experience thermal overloads.

Southern Vermont Region. The ability to accommodate 95 MW of wind in this area was analyzed. Under winter conditions, this area could accommodate most of this capacity—93 MW. However, during summer-, light-, and shoulder-load periods, summer rating thermal constraints on the 69 kV transmission system would limit the total amount of wind that could be accommodated to 81 MW. While this is only 85% of the nameplate capacity of the wind studied, it is above the reasonably expected maximum output of these wind plants in these load periods. This suggests that the 95 MW of nameplate capacity can be accommodated under most reasonably anticipated conditions during the rest of the year.

#### Strategic Transmission Analysis Conclusions

The STA examined the integration of 1,113 MW of wind resources in Maine and 547 MW in Vermont. Of these amounts, all but 85 MW in Maine could be accommodated without major new transmission investment. Transmission system improvements are necessary to address a combination of local and regional transmission constraints and address BPS performance concerns. Additional wind resources planned for the Wyman Hydro and Rumford regions could likely be accommodated without a major new transmission line to the local regions. However, the Keene Road and Bangor regions cannot support much additional wind capacity beyond the amount studied without major new transmission facilities.

Northern Vermont would require new reactive support to accommodate additional wind and would still be thermally constrained below the amount of wind studied but less so in the winter than in other seasons. Central Vermont showed no constraints to the amount of wind in the queue studied (165 MW) and, the study determined that this area would be capable of integrating about 231 MW of wind. Southern Vermont showed only minor constraints. Some risk of curtailment remains at higher wind load levels in the northern and southern regions if only nonmajor upgrades are applied. Major upgrades would be necessary to eliminate the maximum wind-condition restrictions; however, no curtailment would be required at typical wind levels.

## Large-Scale Adoption of Photovoltaic Resources and Other Distributed Generation Resources

New England has witnessed significant growth in the development of solar photovoltaic resources over the past few years, and continued growth of PV is anticipated (see Section 3.3.3). PV installations not counted as ISO resources reduce the summer peak load, and the technology holds promise as a nonemitting source of electric energy that can be reliably and economically integrated into the system. Reliably and economically integrating PV to the electric power system, however, poses some challenges.

Regional PV installations are predominantly small (i.e., less than 10 MW) and state-jurisdictionally interconnected to the distribution system. State policies largely influence the spatial distribution of PV, such that states with more-supportive PV policies (e.g., Massachusetts) are experiencing the most growth of the resource. Existing amounts of PV have not caused noticeable effects on system operation, but impacts are anticipated as penetrations grow. To examine and prepare for the potential effects of large-scale PV development in the region, the ISO has engaged in the initiatives summarized below.

### Operational Solar Forecasting

Because the ISO cannot observe or dispatch most PV in the region, these projects act as a modifier of system load that must be accurately forecasted in the short-term to support the efficient administration of the day-ahead market and the reliable operation of the system. As PV penetrations continue to grow and displace energy production from other resources, PV power production will introduce increased variability and uncertainty to the system and eventually will have an impact on system operations (e.g., result in the need for increased reserve, regulation, and ramping). As such, new forecasting techniques will be required to account for PV generation appropriately.

In early 2013, the ISO began participating in a three-year, DOE-funded project to improve the state of the science of solar forecasting. The results of this project will assist the ISO in developing ways of incorporating the load-reducing effects of PV into improved load-forecasting processes required to support the efficient and reliable integration of increasing amounts of PV.

### Potential Reliability Impacts of PV

Because of the differences between the state-jurisdictional interconnection standards that apply to most PV facilities and the FERC-jurisdictional standards that apply to larger, conventional generators, PV exhibits different electrical characteristics during system conditions typical of grid disturbances (e.g., low-voltage conditions during an unexpected outage of a large generator or transmission facility). The ISO participated in an EPRI evaluation of the potential reliability impacts of large amounts of distributed generation, such as PV.

The ISO asked the region’s utilities about their interconnection standards, and the responses indicated that most PV units meet the existing IEEE 1547 standards. These standards were designed for relatively small penetrations of DG and do not require PV resources to be able to “ride through” a fault on the transmission system.

A high-level screening conducted by the ISO showed the potential loss of PV resulting from faults on the transmission system. The following maps in Figure 10-1, of Connecticut and Massachusetts, show the areas where PV facilities are likely to trip off line because of low voltage in the event of a fault on the 345 kV transmission system. This could result in thermal or stability problems and could cause the need for additional transmission upgrades. As PV penetrations grow, the severity of this potential problem could also grow.

Figure 10-1: Areas (in blue), in Connecticut (left) and Massachusetts (right), where PV resources are likely to trip off line because of low voltage in the event of a fault on the 345 kV transmission system.

Notes: The key refers to per-unit voltage. Also see Impacts of Transmission System Contingencies on Distributed Generation—Overview, PAC presentation (December 16, 2013), http://www.iso-ne.com/static-assets/documents/committees/comm_wkgrps/othr/distributed_generation_frcst/2013mtrls/dec162013/dg_transmission_impacts.pdf.

A sensitivity analysis also was conducted, which indicates that low voltage will be more widespread when local generation is not operating, for example, on a spring day with light load and high wind and solar generation.

The ISO is working with the New England states, distribution utilities, and IEEE and other international experts to ensure that the future interconnection standards for PV (and other inverter-interfaced DG resources) better coordinate with broader system reliability requirements. The ISO will participate in revising the IEEE standards with the aim of improving the coordination of distribution system needs and transmission system performance requirements without imposing barriers to the development of distributed generation.

The ISO also will continue to actively track the growth of PV in the region and evaluate its potential impacts on the efficient administration of wholesale electricity markets and the reliable operation and planning of the region’s electric power system. Because many other regions of North America also are witnessing the large-scale adoption of PV, the ISO also is engaging with other ISO/RTOs to share relevant methods and experience.

### Other Challenges of PV Integration

The growth in DG presents some challenges for grid operators and planners. Challenges for the ISO include the following:

- Difficulty obtaining and managing the amount of data concerning DG resources, including their size, location, and operational characteristics

- A current inability to observe and control most DG resources in real time

- A need to better understand the impacts on system operations of the increasing amounts of DG, including ramping, reserve, and regulation requirements

The ISO’s work with the regional stakeholders will help position the region to best integrate rapidly growing DG resources in a way that maintains reliability and allows the states to realize the public policy benefits they have identified as the basis for their DG programs.

### Eastern Renewable Generation Integration Study

NREL is nearing completion of the Eastern Renewable Generation Integration Study (ERGIS). The study simulated operations of the Eastern Interconnection with high penetrations of wind and solar generation and sought to advance the state-of-the-art of previous large-scale renewables integration studies, such as the Eastern Wind Integration and Transmission Study (EWITS). The ERGIS study was the first to examine large penetrations of solar power in the eastern United States, including scenarios with solar penetrations of up to 174 GW, and used the most detailed representation of the entire Eastern Interconnection to date.

## Economic Performance of the System and Other Studies

Economic studies provide metrics depicting various system-expansion scenarios and the pros and cons associated with selected possible future scenarios. These scenarios could assess system performance at a higher level, such as possible additional imports from Canada, resource retirements, and resource additions, but do not assess scenarios and the performance of individual asset owners. The key metrics developed include estimates of production costs, transmission congestion, electric energy costs for New England consumers, and a number of others. These metrics suggest the most economical locations for resource development and the least economical locations for resource retirements.

### 2011 to 2013 Economic Studies and 2015 Economic Study Request

The 2011, 2012, and 2013 economic studies analyzed several of the strategic issues the region is addressing.

- The 2011 Economic Study examined the effects of integrating varying amounts of wind on production costs, load-serving entity (LSE) expenses, and emissions, as well as the need for transmission development, to enable wind resources to serve the region’s load centers.

- The 2012 Economic Study highlighted the least suitable locations for unit retirements and the most suitable locations for developing new resources using congestion as the key metric associated with each location. The study showed the effects of using various amounts of energy efficiency and low-emitting resources, including renewable energy, as well as other technologies.

- The 2013 Economic Study examined the economic and environmental effects of increasing the acceptable loss-of-source (LOS) limits in New England.

The ISO did not conduct a 2014 economic study because it did not receive any requests for one or propose one.

The ISO received three economic study requests in 2015 to assess the following topics:

- Onshore wind development in the Keene Road area of northern Maine and the effects of upgrading the Keene Road Interface.

- Onshore wind development in Maine and the effects of implementing the conceptual improvements identified in the Strategic Transmission Analysis: Wind Integration Study.

- Offshore wind development and the effects of adding transmission improvements that relieve potential bottlenecks

Approximately 320 MW of wind resources are located in the Keene Road area, and over 90 MW of additional future development is proposed for interconnecting to the 115 kV system in the area. The first economic study will develop metrics to quantify the effects of curtailments expected on the post MPRP system (see Section 6.3). The effect of potential improvements in the Keene Road area will then be evaluated to quantify the possible benefits associated with market efficiency transmission upgrades (see Sections 2.1.1.2 and 6.5.2) that could allow the wind resources to operate without the current level of constraints. Additional analysis beyond the economic study would be required to fully develop any METUs.

The second proposed economic study will investigate scenarios of wind-resource development and will show the effect of the conceptual transmission system expansion in Maine. As discussed in Section 10.2.2, the Strategic Transmission Analysis: Wind Integration Study identified a number of conceptual transmission upgrades that could relieve constraints to existing and planned onshore wind development throughout Maine. This study may inform the region on the cost and benefits of pursuing these transmission upgrades.

The third 2015 economic study will examine offshore wind development near Rhode Island and Southeast Massachusetts. The analysis includes the effects of imports from Canada over new interconnections and the development of onshore wind generation in northern New England. The study also considers the retirement of older nuclear, coal-fired, and oil-fired generating units. This study may also inform the region of the need to pursue public policy transmission upgrades.

### Generic Capital Costs of New Supply Resources

The comparison of the energy market revenues with the annual revenue requirements (also called annual carrying charges) provides some relative measures of the economic viability of different resource types and how these measures change under various scenarios. Each resource type’s annual fixed costs include its capital, operations, and maintenance costs. These fixed costs can be calculated from estimates of annual carrying charges derived from representative capital costs for each resource type. These typically are 15% to 25% of the capital costs.

In support of the economic studies for 2015, the ISO updated the generic capital costs for new resources, as shown in Table 10-1. The focus of this update was on the resource technologies in the ISO Generator Interconnection Queue and those participating in the FCM. The updated plant costs are from DOE’s Energy Information Administration (EIA), the Electric Power Research Institute (EPRI), the Brattle Group, ISO New England, and the Western Electricity Coordinating Council (WECC).

Table 10-1 
Generic Capital Costs of New Supply-Side Resources

| Technology Type(a) | Plant Size(b) (MW) | Heat Rate(b) (Btu/kWh) | Total Plant Cost(c) ($/kW) |
| --- | --- | --- | --- |
| Advanced combined cycle (CC) | 340–400 | 6,430–7,525 | 1,020–2,085 |
| Advanced gas turbine (GT) | 190–210 | 9,090–9,750 | 675–1,430 |
| Biomass | 20–100 | 12,350–13,500 | 3,600–8,180 |
| Conventional CC | 550–730 | 7,000–7,525 | 825–1,150 |
| Conventional GT | 85–420 | 10,575–10,815 | 630–970 |
| Natural gas fuel cells | 10 | 9,500 | 7,045 |
| Offshore wind | 200–400 | N/A | 3,100–6,190 |
| Onshore wind | 50–200 | N/A | 1,750–2,400 |
| Solar photovoltaic | 5–150 | N/A | 2,000–3,565 |

(a)	Technology types in the queue as of April 1, 2015.

(b) 	Additional information about these data is available in the ISO PAC presentation, Generic Capital Costs of Supply-Side Resources (April 28, 2015), http://www.iso-ne.com/static-assets/documents/2015/04/a4_generic_costs_of_supply_resources.pdf.

(c)	The total plant costs are also referred to as the overnight construction costs or overnight capital costs.

Specific project costs may differ from generic estimates due to a number of different factors, such as the following:

- Resource size

- State of technology development

- Changes in material, labor, and overhead costs

- Supply-chain backlogs or oversupply

- Specific site requirements

- Regional cost differences

- Difficulties in obtaining site and technology approvals

In addition, experience suggests that many construction projects encounter unforeseen design and construction problems that tend to increase costs.

## Summary

The ISO continues to analyze wind integration and advance the implementation of wind forecasting and dispatch. While the level of wind resources has not yet triggered additional requirements, the ISO is working toward increasing system flexibility and has increased its operating reserve to address resource performance issues. The ISO is improving the modeling of wind resources and has updated the process for pursuing elective upgrades.

The Strategic Transmission Analysis: Wind Integration Study developed conceptual additions to the transmission system that would enable onshore wind resources to reliably serve load. Economic studies are showing the effects of integrating varying amounts of wind generation on production cost, load-serving energy expenses, and congestion. These studies also are indicating the need for transmission development to enable wind resources to serve the region’s load centers. The ISO will continue to engage stakeholders on the issues challenging the wind-interconnection process and the performance of the system with wind resources in locally constrained areas.

Economic studies have examined various scenarios of changes in transfer capabilities, resource expansion, and retirement scenarios. When completed, the 2015 economic study of the Keene Road area may identify needs that could lead to a market efficiency transmission upgrade. The 2015 economic studies of onshore wind expansion and offshore wind expansion may trigger the need for further analysis leading to public policy transmission upgrades.

Additional work remains on incorporating the effects of PV in improved short-term load-forecasting tools for use by system operators and fully addressing the potential reliability risks posed by growing penetrations of PV.

# Federal, Regional, ISO, and State Initiatives

State, regional, and federal initiatives and policies have a significant impact on the wholesale electricity markets and transmission developed to meet system needs, specifically influencing the timing, type, and location of resources and transmission infrastructure. Federal initiatives, by FERC, DOE, and the White House, address reliability and security issues. Initiatives and policies by each of the six New England states address energy infrastructure, renewable energy, and environmental concerns. ISO initiatives focus on new technologies and enhancing operating and planning procedures. This section discusses major initiatives at each of these levels.

## Federal Initiatives

The Energy Policy Act of 2005 (EPAct) requires the US Department of Energy and the Federal Energy Regulatory Commission to implement several reliability provisions. The requirements include ensuring the reliability of the transmission infrastructure and implementing enforceable reliability standards administered by the North American Electric Reliability Corporation.

### FERC Order No. 1000

In Order No. 1000, FERC adopted a comprehensive package of changes to the transmission planning and cost-allocation processes. The order eliminates a transmission owner’s exclusive right to build and own transmission for projects built pursuant to the regional system planning process that receive regional cost allocation. This order also affirmed FERC’s decision to allow the utilities to have backstop authority for a project needed within three years of the date stated in the project’s needs assessment. Another provision of the order covers cost allocation for public policy projects. The ISO discussed compliance filing issues through the NEPOOL committee process. Section 2.1.7 contains more details about FERC Order No. 1000.

### FERC Actions to Better Align Natural Gas and Wholesale Electricity Markets

On April 16, 2015, FERC issued a final rule addressing the schedule of the natural gas day. FERC kept the start of the natural gas day at 9:00 a.m. Central Time but changed the timing of the Timely Nomination Cycle deadline to 1:00 p.m. Central Time (from 11:30 a.m.) and added an additional intraday nomination cycle to the gas operating day. The ISO is fully compliant with FERC’s directives, as summarized in the filing. Refer to Section 8.4.1 for additional information on coordination between the natural gas and electric power sectors.

### FERC ISO/RTO Performance Metrics

In 2010, FERC requested that the regional ISOs and RTOs track the performance of their operations and markets in delivering benefits to the consumers in their jurisdictions. In response, ISO New England, along with PJM, the California ISO (CAISO), the Midcontinent ISO (MISO), NYISO, and Southwest Power Pool (SPP) jointly submitted several reports to FERC, each containing “common metrics” for five-year periods that addressed the reliability and operations of their regional power systems and wholesale markets. The 2010 report contains data for 2005 to 2009, and the 2011 report contains data for 2006 to 2010. The metrics on power system reliability cover dispatch operations, forecasting accuracy, outage coordination, transmission planning, and generation interconnection, among other categories. The wholesale electricity markets metrics address market competitiveness and pricing, marginal cost, energy market convergence, congestion management, resource availability, fuel diversity, renewables production, and several other topics. The organization-effectiveness metrics provide information and data on administrative costs, customer satisfaction, and billing controls. Subsequent to these reports, FERC requested similar metrics reporting from utilities in non-ISO/RTO areas.

In August 2014, FERC staff issued a report with a set of 31 common metrics for both the regional organizations and utilities. The FERC report covers dispatch reliability, transmission planning, the marginal cost of energy, and resource availability. FERC uses this information to evaluate reliability and systems operations performance across the different regions and utilities. In August 2015, FERC issued a request for the 2015 Metrics Report covering data for 2010 to 2014, which the ISOs and RTOs submitted in October 2015.

### FERC Directive on Physical Security

In November 2014, FERC issued Order No. 802, which approved a final rule to strengthen the physical security of critical infrastructure of the bulk electric system. In March 2014, the commission directed NERC to design and submit physical security standards, which it did in May 2014. The final FERC rule includes a three-part compliance process. First, entities that own and operate bulk electric system infrastructure must identify critical facilities. Second, these entities must identify the vulnerabilities of these facilities, which a third party must verify. Finally, to protect these facilities, the entities must design and implement a plan based on the possible threats identified.

    - Executive Order on Cybersecurity

On February 13, 2015, President Obama released a cybersecurity-focused executive order to spur greater information sharing between the federal government and the private sector. The order encourages the creation of information-sharing and analysis organizations (ISAOs). ISAOs would be similar to an organization such as the Electricity Sector Information-Sharing and Analysis Center (open to registered entities in the North American electricity sector), and may consist of a combination of public and private sector organizations formed as for-profit or nonprofit entities. The order directs the National Cybersecurity and Communications Integration Center to continually collaborate with ISAOs to share information on cybersecurity risks and incidents, address these risks and incidents, and strengthen information-security systems.

### US Department of Energy Congestion Studies

DOE is required to conduct a study every three years on electricity transmission congestion and constraints within the Eastern and Western Interconnections. Using the results of these studies and comments provided by the states and other stakeholders, the US Secretary of Energy may then designate any geographic area experiencing constraints or congestion on electricity transmission capacity as a National Interest Electric Transmission Corridor (National Corridor). A designation as a National Corridor merits federal concern and may enable FERC to exercise backstop authority to site transmission facilities. This would occur only under limited circumstances, such as when a state agency has failed to act on a siting application within a National Corridor for more than one year. In its September 2015 Report Concerning Designation of National Interest Electric Transmission Corridors, DOE concluded that neither the information collected for the latest congestion study, the National Electric Transmission Congestion Study, or the public comments submitted on the study provided a basis for designating any National Corridors.

The congestion study, also published in September 2015, shows that transmission congestion is minimal in New England because of sustained investment in transmission in the region in recent years and the construction of major new transmission projects (see Section 6.5.2). Other key findings in the DOE study for the Eastern Interconnection are as follows:

- Compared with 2008 and years prior, transmission constraints in the Northeast from 2009 to 2011 have limited transmission flows in fewer hours per year.

- Generation additions in the Northeast in recent years also have contributed to lower overall congestion, particularly in New England.

- In the economic recovery after the 2008–2009 recession, electricity demand has been lower than its long-term historical trend compared with the rate of economic growth, which typically leads to lower transmission usage and lower congestion.

- The implementation of robust demand-response programs by utilities, ISOs, and RTOs have reduced consumption during periods of peak demand, which has tended to lower system peak demand and energy consumption and thus congestion. Aggressive energy-efficiency programs also have reduced congestion.

- The availability of abundant, low-cost natural gas supplied to efficient generators located in load areas is shifting transmission usage and reducing congestion.

- The recent trend in the retirement of nuclear and coal-fired plants has changed transmission flows in many areas of the country.

- New environmental regulations affect the composition and usage of regional generation, and grid operators are modifying dispatch patterns according to the economics of available generation and transmission capacity. They take actions to maintain grid reliability, but congestion may increase or decrease in specific locations.

- Some congestion still exists, however. Much of the congestion that remains in the Northeast reflects three factors:

- Transmission constraints continue to restrict the delivery of power into load centers in central New York and the New York City and Long Island areas.

- Increased levels of low‐cost wind generation in concentrated locations west of the major load centers of the Northeast exceed the capability of transmission facilities.

- The Northeast is addressing administrative and institutional issues arising from different market rules, scheduling practices, and transmission reservations that obstruct the more effective use of facilities between neighboring RTOs and ISOs.

The DOE intends to release its transmission data document as a stand-alone report rather than combining it with the triennial congestion studies.

### DOE Quadrennial Energy Review

On April 21, 2015, DOE released the first iteration of its Quadrennial Energy Review (QER), examining a broad array of issues affecting the transmission, distribution, and storage of energy infrastructure in the United States and North America.

The QER provides analysis of the energy challenges facing New England, many of which were discussed at QER stakeholder meetings in Providence, RI, and Hartford, CT, in April 2014. The QER notes that natural gas pipeline constraints are leading to both high energy prices and reliability concerns in the region, and it discusses issues around expanded gas pipeline capacity. The report highlights the ISO’s winter reliability programs and market changes as ways the region is dealing with the uncertainty caused by pipeline constraints. Beyond New England, the QER also examines various interdependencies between the electric power grid and other critical digital infrastructure in the United States. DOE also dedicates a significant amount of the report to international energy cooperation and infrastructure, including the importance of large-scale hydropower from Canada.

## Regional Initiatives

This section discusses several policies, laws, and activities at the regional level that affect the regional power system.

### Coordination among the New England States

The New England states have worked together continually to identify, discuss, and address energy issues of common interest. Even with this history of cooperation, each state has a unique set of energy policy objectives and goals.

Each of the New England states is actively involved in the ISO’s regional planning process, individually and through the New England States Committee on Electricity (NESCOE). NESCOE serves as one forum for representatives from the states to participate in the ISO's decision-making processes, including those dealing with resource adequacy and system planning and expansion.

On April 23, 2015, the governors participated in the Northeast Forum on Regional Energy Solutions in Hartford, Connecticut, to discuss regional energy challenges, potential solutions, and their positions on the region’s energy infrastructure needs. After the forum, they released an official statement reaffirming their commitment to work together toward regional energy infrastructure solutions.

The governors also released a joint statement regarding regional cooperation on energy infrastructure. A supporting document highlights the states’ efforts to continue to support energy efficiency and distributed generation and outlines some of the states’ use of existing authority to procure clean energy generation and transmission. The joint statement also reviews the states’ efforts to secure individual state authority to address infrastructure challenges. Refer to Section 11.2.3 for a discussion of the partnership between Massachusetts, Connecticut, and Rhode Island to issue a request for proposal (RFP) for clean energy resources.

In addition to NESCOE, the ISO works collaboratively with the New England Conference of Public Utilities Commissioners (NECPUC), the New England governors’ offices, and the states’ consumer advocates. The ISO provides monthly updates to the states on regional stakeholder discussions regarding the regional planning process and the wholesale electricity markets.

The New England states are active participants in the interconnection-wide planning for the Eastern Interconnection. The Eastern Interconnection States Planning Council (EISPC) is an organization of 39 states and eight Canadian provinces in the Eastern Interconnection electric transmission grid, including representatives from New England, responsible for participating with the planning authorities that are part of the EIPC (see Section 7.1). Initially funded by a DOE Funding Opportunity Announcement, the EISPC comprises public utilities commissions, governors' offices, energy offices, and other key government representatives and provides input to the EIPC study effort. As a planning authority, the ISO has provided technical support to the EISPC. The ISO, NESCOE, and NEPOOL work closely to coordinate New England’s participation in all EISPC and EIPC activities.

### Consumer Liaison Group

The ISO and regional electricity market stakeholders created the Consumer Liaison Group (CLG) in 2009 as an additional means to facilitate the consideration of consumer interests in determining the needs and solutions for the region’s power system. With representatives from state offices of consumer advocates and attorneys general, large industrial and commercial consumers, chambers of commerce, and others, the CLG meets quarterly to address various consumer issues. With the input of CLG members, a Coordinating Committee guides CLG meeting agendas and ideas for special guest speakers and discussion topics.

In 2014, the CLG’s discussions focused on New England’s reliance on natural gas for power generation, the region’s constrained natural gas pipeline system, and associated impacts on consumers. On March 10, 2015, the CLG Coordinating Committee and the ISO issued the 2014 Report of the Consumer Liaison Group, which summarizes the activities of the CLG in 2014. It also provides an update on ISO activities and initiatives, as well as wholesale electricity costs and retail electricity rates.

### Southern New England States’ RFP

The Connecticut Department of Energy and Environmental Protection (CT DEEP) and the electric distribution companies of Massachusetts and Rhode Island issued a Request for Proposals for Clean Energy and Transmission. The purpose of the three‐state procurement is to identify projects that could help the procuring states meet their clean energy goals in a cost‐effective manner and that bring additional regional benefits. The soliciting parties in the three states decided to act jointly to open the possibility of procuring large‐scale projects that no one state could procure on its own.

The RFP allows the states to consider projects for the delivery of clean energy through any combination of the following: (1) traditional Power Purchase Agreements that do not require transmission upgrades, (2) Power Purchase Agreements that require transmission, and (3) transmission projects containing clean energy delivery commitments but without any associated Power Purchase Agreements.

The soliciting parties released a draft RFP for public comment in early 2015 and expect to issue a final RFP later in 2015, following regulatory approvals in Massachusetts and Rhode Island.

## ISO Initiatives

The ISO is involved in a number of initiatives aimed at developing and integrating new technologies, and enhancing operating and planning procedures to enhance system reliability.

### Updates on Developing and Integrating Smart Grid and Other New Technologies

The ISO strives to keep up to date with new technologies that can have an impact on the region’s electric power grid. As policymakers set targets and allocate public funds for developing smart grid initiatives and renewable resource generation, the ISO analyzes the effects of these technologies on system operations and reliability. Several of the technology developments and challenges affecting the planning of the New England region involve integrating smart grid equipment, improving operator awareness and system modeling through the use of phasor measurement units (PMUs), and using HVDC facilities and flexible alternating-current transmission system (FACTS) devices.

#### Participation in Developing Industry Standards and Other Professional Activities

Several municipal electric utilities and distribution system owners have installed advanced metering infrastructure (AMI) and technology. These technologies facilitate the installation of distributed resources and price-responsive demand. The ISO currently participates in several research projects sponsored by DOE, the Power System Engineering Research Center (PSERC), and the Electric Power Research Institute (EPRI) that support the successful integration of advanced technologies.

EIA notes that many commercial and industrial customers appear to have lower penetration rates for advanced metering infrastructure because they likely have already installed more sophisticated analog meters enabling participation in time-of-use or interruptible tariffs. EIA reports that the 2013 AMI penetration rate in New England was 22.7% of 6.27 million reported meters.

The ISO also is actively participating in the development of the national smart grid interoperability standards to establish protocols that provide common interfaces for smart grid equipment through the Smart Grid Interoperability Panel (SGIP). Additionally, the ISO is providing technical and other support for the development of demand-response-related standards by the North American Energy Standards Board (NAESB). The ISO staff and stakeholders remain professionally active in the Institute of Electrical and Electronics Engineers (IEEE), a society that serves to educate its members and the public at large, as well as develops standards for the interconnection and operation of smart grid technologies.

#### Operational Efficiencies through Advanced Technology

To satisfy an increasing number of required transmission plan studies, the ISO is exploring an innovative use of cloud computing to enhance the ISO’s ability, speed, and costs of using more detailed and sophisticated system models and scenarios. The initiative—the first of its kind for large-scale power system simulation studies in the industry—is already yielding successful early results. In addition, various projects to create new systems and tools for greater operational and planning efficiencies and performance are also underway. The ISO remains a leader in the application of phasor measurement units, which include projects related to voltage stability, control room visualization, and power system modeling.

Where appropriate and cost-effective, the application of power electronics to the power system through high-voltage direct-current and flexible alternating-current transmission system technologies can address performance concerns on the transmission system. HVDC and FACTS use a combination of solid-state switches and computerized automation that enables nearly instantaneous customized control of real or reactive power flows—far faster than traditional electromechanical switches. As part of its planning process, the ISO has reaffirmed the need for specific FACTS devices, several of which are old. Figure 11-1 shows retired, refurbished, and planned HVDC and FACTS devices in New England.

Figure 11-1: Existing and planned FACTS devices in New England.

Notes: (a) The acronyms and abbreviations in the key refer to the following terms: HVDC = high voltage, direct current. VSC = voltage source converter. SVC = static voltage ampere reactive (V) compensator. STATCOM = static synchronous compensator. DVAR = dynamic voltage ampere reactive. (b) Plans exist to replace the DVAR at Stony Hill and Bates Rock with a synchronous condenser at Stony Hill.

The integration of variable resources on the distribution system poses issues such as voltage regulation and power quality, which distribution utilities must address. Distribution utilities and local customers may apply the use of local storage technologies, such as batteries and quick-responding automated demand response, and other smart grid technologies to improve electrical performance. The ISO is monitoring the application of these technologies to anticipate their potential effect on regional system performance.

### Transmission Planning Process Guide and Transmission Planning Technical Guide

The ISO’s Transmission Planning Process Guide (Process Guide) discusses the development of needs assessments and solution studies, including the opportunities for stakeholder involvement. The Transmission Planning Technical Guide (Technical Guide) describes the current standards, criteria, and assumptions used in transmission planning studies of the regional power system (refer to Section 2.1.2). The ISO will update the Process Guide to reflect FERC Order No. 1000’s required changes to the planning process (see Section 2.1.7). The ISO also is examining how to better represent system conditions through probability and statistical analyses of load levels, generator outages, the dispatch of variable resources, and other factors. This effort may inform assumptions used in planning studies and assist with identifying new simulation tools. This stakeholder process will likely extend beyond 2015.

## State Initiatives, Activities, and Policies

The New England states have worked together continually to identify, discuss, and address energy issues of common interest. Even with this history of cooperation, each state has a unique set of energy policy objectives and goals. This section summarizes actions taken by the individual New England states pertaining to regional system planning, including several recently implemented laws, policies, and initiatives.

### Connecticut

In 2015, the Connecticut General Assembly passed legislation, An Act Concerning Affordable and Reliable Energy, to secure cost-effective energy resources to serve several purposes. One is for providing more reliable electricity service for the state’s electricity ratepayers, and a second is for meeting the state’s energy and environmental goals and policies established in the Integrated Resources Plan and the Comprehensive Energy Strategy.

The legislation gives the commissioner of the Department of Energy and Environmental Protection the authority to issue multiple solicitations for a variety of resources, including, demand-response resources, Class I renewable energy resources, and interstate natural gas transportation capacity. It also allows DEEP to direct the state’s electric power distribution companies to enter into long-term contracts for any combination of these resources, provided that the benefits of these contracts to electricity customers outweigh the costs. In evaluating these proposals, DEEP must consider, among other things, the project’s ability to improve the reliability of the electric power system, including during winter peak demand. The Public Utilities Regulatory Authority (PURA) must review and approve any agreements entered into pursuant to this legislation. Electric distribution companies can recover the costs associated with these contracts through retail electricity rates for all customer classes in Connecticut.

Legislation passed in 2011 charges DEEP with assessing the state’s energy and capacity resources every two years, and developing an Integrated Resource Plan that identifies how best to meet projected demand and lower the cost of electricity. The 2014 plan, finalized by DEEP on March 17, 2015, contains eight key recommendations for achieving “reliable, clean, and cost-effective energy supply” for Connecticut:

- Continue to invest in cost-effective energy efficiency

- Pursue options to retain demand resources (advocate for resolution of legal issues and, as needed, revive state programs to retain cost-effective demand response)

- Monitor ISO New England’s capacity market and plan for tightening capacity supplies

- Procure resources to address winter peak demand (advance regional solutions to address natural gas infrastructure constraints)

- Provide support for increasing the deployment of combined heat and power (CHP)

- Support deployment of additional Class I renewables

- Re-evaluate regulatory policies and incentives for modernizing the grid and better integrating distributed resources

- Gradually phase down renewable energy credit (REC) values for Class I biomass and landfill methane gas beginning in 2018

The 2014 plan describes the inadequate supply of infrastructure to meet the needs of New England’s increasingly gas-dependent generation fleet as one of the most pressing problems facing Connecticut and New England. In the absence of a credible market solution, the 2014 plan recommends a regional solution that involves some combination of expanding New England’s natural gas pipeline capacity by roughly 1 Bcf/day, procuring approximately 5,000 MW of non-gas-fired generation, or reducing the demand for electricity.

### Maine

In March 2014, the Maine PUC (MPUC) released a study, A Review of Natural Gas Capacity Options, describing the potential costs and benefits associated with additional natural gas pipeline capacity into New England. It commissioned the study pursuant to the Omnibus Energy Act passed in 2013. The report describes the impact of pipeline capacity on electricity prices and concludes that incremental natural gas pipeline capacity into the region would lower regional natural gas prices and benefit customers in Maine and New England overall. The PUC solicited proposals from gas pipeline developers and contracted with a consultant to analyze the proposals. In June 2015, the consultant’s report, Maine Energy Cost Reduction Act: Cost Benefit Analysis of ECRC [Energy Cost Reduction Contract] Proposals, concluded that the cost to Maine from entering into the proposed contracts would outweigh the benefits if the state were to act alone to develop gas pipeline projects.

The MPUC has been investigating ways to improve the reliability of electricity service in the northern portion of the state not connected to the transmission system administered by the ISO. Potential solutions include adding local generation and demand response in northern Maine, adding transmission reinforcements with New Brunswick, and directly interconnecting Maine Public Service to the rest of New England. The initial analysis recommended making relatively minor upgrades to existing infrastructure and continuing to investigate interconnection options with ISO New England.

The legislature passed a resolve in 2015 requiring the Efficiency Maine Trust (EMT) to study options for a state demand-response program that will benefit the grid and electricity consumers and that will allow and encourage participation of Maine electricity consumers in the program. This legislation will require EMT to survey other states in New England regarding their interest in demand-response programs at the state or regional level and consider demand-response program rules that do not unreasonably burden or discourage consumer participation. EMT is required to issue a draft report and accept comments from the public and other interested parties. By February 1, 2016, EMT will submit a study report to the Maine Legislature that includes conclusions and recommended legislation.

### Massachusetts

In November 2014, the Massachusetts Department of Public Utilities (MA DPU) issued an order requiring each electricity distribution company to develop and submit to the DPU a 10-year strategic grid-modernization plan. On August 19, 2015, the electric distribution companies submitted, for approval by the DPU, their grid-modernization plans.

The DPU also issued an order adopting a policy framework for the implementation of time-varying rates for basic service. The order notes that time-varying rates are necessary and appropriate to advance grid-modernization objectives. These rates and advanced-metering technology can empower customers to shift demand; decrease electricity bills; and reduce wholesale electricity market prices and the need for new generation, transmission, and distribution investment.

In spring 2015, the DPU opened an investigation (DPU 15-37) into the means by which new natural gas delivery capacity may be added to the New England market, including actions to be taken by the electric distribution companies. As part of the investigation, the DPU will consider whether it has the authority and should allow the state’s electric distribution companies to contract for new natural gas delivery capacity, with cost recovery through electric distribution rates.

### New Hampshire

New Hampshire is investigating the long-term viability of Eversource’s (formerly Public Service Company of New Hampshire [PSNH]), continued ownership of in-state generating assets and the current “hybrid” model for providing default service to Eversource customers. In March 2015, the state and Eversource announced the framework of a settlement agreement that would require the company to divest its remaining generation assets. In June 2015, the state passed a law that requires the NH Public Utilities Commission (NH PUC) to determine whether the settlement is in the public interest. The law also empowers the NH PUC to authorize the issuance of bonds to fund expenditures associated with a possible sale of Eversource’s generation assets. On October 21, 2015, the NH PUC provided the legislature with a status report and plans to hold additional hearings in early 2016.

On September 2, 2014, the New Hampshire Office of Energy and Planning (OEP) released the State Energy Strategy. The strategy’s recommendations for the electric power sector focused on increasing energy efficiency, modernizing the electric power grid, and promoting renewable power generation. To achieve these goals, the state seeks to create incentives for attracting private investment, open new NH PUC study dockets, and educate the public through consumer outreach initiatives. The strategy also recognizes that New Hampshire operates in a regional context. In June 2015, the New Hampshire Legislature passed a bill to begin implementing the strategy. The bill requires the NH PUC to, among other things, open a docket on grid modernization by August 2015 and establish a goal for reducing the peak use of electricity by July 2016.

New Hampshire is continuing to adjust its siting process. In 2014, the state passed legislation that changed the composition of the Site Evaluation Committee (SEC), increased public participation in the application process, and created more specific criteria for wind projects. The SEC is currently reviewing public comments on the committee’s new administrative rules and must adopt final rules by November 1, 2015.

The NH PUC opened a docket to establish an energy-efficiency resource standard (EERS) for both electric and gas utilities (DE 15-137). The docket is scheduled to complete a series of stakeholder sessions by April 2016 and have the EERS take effect in January 2017.

The NH PUC opened another docket to investigate approaches to ameliorating the effect of adverse wholesale electricity market prices in New Hampshire (IR 15-124). On September 15, 2015, the NH PUC released a report on the docket, which concluded that expanding natural gas pipeline capacity in New England would help moderate the region’s wholesale electricity prices and that New Hampshire’s electric distribution companies likely have the legal authority to enter into gas capacity contracts for the benefit of gas-fired generators. The report also recommended that the regional process for procuring gas capacity be open, transparent, and demonstrably competitive and results in the lowest possible costs to consumers. The PUC accepted comments on the report through October 15, 2015.

### Rhode Island

Rhode Island’s Office of Energy Resources (OER) is in the process of updating the Rhode Island State Energy Plan to provide a long-term, comprehensive energy strategy for the state. The plan’s vision is to provide, by 2035, energy services across all sectors, including electricity, thermal, and transportation, using a secure, cost-effective, and sustainable energy system. To realize this vision, the plan sets out measurable goals and targets for transforming Rhode Island’s energy system. In meeting these targets, the plan recommends an “all-of-the-above” clean energy strategy that accomplishes the following:

- Maximizes energy efficiency in all sectors

- Promotes local and regional renewable energy

- Develops markets for alternative thermal and transportation fuels

- Makes strategic investments in energy infrastructure

- Mobilizes capital and reduces costs

- Reduces greenhouse gas emissions

OER released the draft plan at the end of 2014, and the State Planning Council is expected to consider a final plan for adoption in 2015.

Rhode Island's Renewable Energy Standard (RES), established in June 2004, requires the state's retail electricity providers to supply 16% of their retail electricity sales from renewable energy resources by the end of 2019. Existing resources (in service before December 31, 1997) can be used to meet only 2% of the RES. On February 10, 2014, the Rhode Island Public Utilities Commission (RI PUC) issued an order delaying the 1.5% increase in the state’s RES scheduled for 2015 upon a finding by the PUC of potential inadequacy of renewable energy supplies during that period. With a one-year delay of the 1.5% increase in 2015, the state’s RES will reach 14.5% by the end of 2019 instead of 16%.

Rhode Island has been active in regional energy infrastructure discussions, due in large part to legislation passed in 2014 called the Affordable Clean Energy Security Act. The act gives Rhode Island the authority to participate in developing and issuing regional or multistate competitive solicitations for the development and construction of regional natural gas pipeline infrastructure and regional electric power transmission projects. With this authority, Rhode Island joins Massachusetts and Connecticut in participating in a multistate procurement of clean energy and transmission to deliver clean energy. Section 11.2.3 discusses the partnership between these three states to issue an RFP for clean energy resources.

### Vermont

The development of renewable energy resources has long been a priority for Vermont. Since 2005, the primary incentives for retail electricity providers to develop renewable resources were the renewable energy targets established in the state’s Sustainably Priced Energy Development (SPEED) program. The development of the Standard Offer program (a form of feed-in tariff) augmented the SPEED program in 2009.

#### Vermont Renewable Portfolio Standard

In 2015, Vermont adopted a new regime similar to the other states’ Renewable Portfolio Standards. The new initiative, known as the Renewable Energy Standard Program, will replace the SPEED program but maintains the Standard Offer program. The RES program has three tiers:

- Tier 1: Total Renewable Electric Requirement—requires utilities to obtain 55% of annual electricity sales from renewable resources in 2017, rising to 75% by 2032

- Tier 2: Distributed Generation—requires 1% of utility sales to come from small, distributed renewable resources (less than 5 MW in size) in 2017, rising to 10% by 2032

- Tier 3: Energy Innovation Projects—requires 2% of utility sales (Btu equivalency) to come from projects that reduce customer fossil fuel consumption and save money starting in 2017, rising to 12% in 2032. Such projects could include promoting weatherization, biomass heat, cold-climate heat pumps, storage technologies, and electric vehicles and related infrastructure.

The legislation creating the RES program does not change existing Vermont law that defines large-scale hydroelectricity as a renewable resource. Vermont utilities are anticipated to meet most of their tier 1 RES obligations with hydroelectric power through contracts with Hydro-Québec.

The siting of renewable energy resources, particularly wind and solar facilities, has begun to raise some concerns in Vermont. In response, the RES legislation established mandatory setbacks for ground-mounted solar resources. Pursuant to this requirement, solar arrays will need to be sited at specified distances from public roads. The legislation also authorizes municipalities to develop screening standards to minimize the visual impacts of ground-mounted solar facilities.

#### Solar Microgrid

Green Mountain Power is developing an innovative solar microgrid in Rutland, VT. The $10 million, 2 MW solar farm, called Stafford Hill, will be backed up by a 4 MW battery storage system. The state expects the project to be in service by the end of 2015.

### Summary of Renewable Portfolio Standards

The New England states have targets for the proportion of electric energy that load-serving entities must provide using renewable resources and energy efficiency. In 2015, Vermont became the sixth state in New England to adopt a Renewable Portfolio Standard. Options for meeting, or exceeding, the region’s RPS targets include developing the renewable resources in the ISO queue, importing qualifying renewable resource energy from adjacent balancing authority areas, building new renewable resources in New England not yet in the queue, developing behind-the-meter projects, and using eligible renewable fuels in existing generators. In addition, load-serving entities can make state-established alternative compliance payments if their qualified renewable resources fall short of providing sufficient renewable energy credits to meet the RPSs. Alternative compliance payments also can serve as a price cap on the cost of RECs.

State RPS targets for 2020 range from 10% to 55% and have driven new proposals for renewable energy. This trend is expected to continue as state targets increase incrementally between now and 2020. The wide range of RPS percentages results from the different definitions of renewable resources in the region.

## Summary of Initiatives

The ISO’s planning activities are closely coordinated among the six New England states, with neighboring systems, across the Eastern Interconnection, and nationally. The ISO has achieved full compliance with all required planning standards and regulatory requirements. Each New England state has a unique set of energy policy objectives and goals and continues to implement laws, policies, and initiatives that affect the regional system planning in New England.

# Key Findings and Conclusions

In accordance with all requirements in the Open Access Transmission Tariff, ISO New England’s 2015 Regional System Plan discusses the electrical system needs and the amounts, locations, and types of resource development that can meet these needs from 2015 through 2024. RSP15 also discusses the status of transmission system assessments, transmission system planning studies, and projects needed for meeting reliability requirements and improving the economic performance of the system. Other discussions include interregional planning requirements and strategic planning challenges expected over the same 10-year planning horizon and how the region is analyzing and addressing these challenges. This section summarizes the key findings of RSP15 and conclusions about the outlook for New England’s electric power system over the next 10 years.

## Changes in the Planning Process

The New England region supports the reliable operation of the system through proactive planning, the completion of transmission projects and other improvements, the development of needed resources, and the overall competitiveness of the markets. Compliance with FERC’s final Order No. 1000 requires fundamental changes to the transmission planning process as conducted in New England since 2001. The order requires opening the planning process to nonincumbent transmission developers and implementing a competitive solicitation process for transmission solutions that meet newly identified system needs beyond a three-year planning horizon. The order also requires the planning process to address public policy objectives and to change interregional planning, especially for transmission cost allocation. The ISO compliance filings provide details on how the region will meet the new requirements, which also allows for use of the pre-Order 1000 planning process for transmission projects well under development. RSP15 is consistent with the new intraregional and interregional Order No. 1000 requirements.

## Forecasts of Peak Load, Energy Use, Energy Efficiency, and PV

RSP15 10-year net forecasts for peak and annual energy use fully account for the growth of demand, savings reductions resulting from energy-efficiency programs, and the growth of distributed resources. These resultant net demand forecasts provide key inputs for determining the region’s resource adequacy requirements for future years, evaluating the reliability and economic performance of the electric power system under various conditions, and planning needed transmission improvements. Low growth in summer peak demand and flat growth in winter peak demand and in the annual use of electric energy characterize the planning period. This trend is due in part to the increased penetration of PV and EE.

The ISO distributed generation forecasts explicitly account for the rapid growth of PV classified as either behind the meter or participating in the wholesale electric markets. Total photovoltaics are growing rapidly, reaching 908 MWac nameplate rating by the end of 2014, which was about a year ahead of the RSP14 projection for PV development. PV facilities are expected to grow to 2,449 MWac nameplate rating by 2024 and are forecast to produce 2,593 GWh. Although distributed generation resources other than PV are not growing rapidly, they are fully reflected in the ISO planning processes. These other types of DG are either participating in the ISO wholesale markets or are part of the historical demand trends used for developing the gross demand forecast.

The ISO also is improving ways of incorporating the load-reducing effects of PV into operational and planning load-forecasting processes required to support the efficient and reliable integration of increasing amounts of PV. It also will continue to monitor the development of non-PV distributed generation.

## Systemwide and Local Area Needs and Meeting These Needs

Recently implemented FCM changes are designed to reduce price volatility and incent electric power system performance for both reliability and economic benefits. The ninth Forward Capacity Auction had high clearing prices that attracted investment in new resources. FCA #9 procured a new 725 MW dual-fuel unit and two 45 MW units in Connecticut and a new 195 MW dual-fuel peaking power plant in SEMA/RI. FCA #9 also attracted 367 MW of new demand resources.

While RSP15 shows the region could have sufficient resources through 2023, the retirements of several older, fossil fuel generating facilities could likely accelerate the need for more new capacity in the region. Market incentives are being implemented to encourage the improved performance of existing resources and to develop needed new resources. Existing resources, the development of some of the 11,299 MW of generators in the interconnection queue, imports from neighboring regions, and new demand resources will likely meet the capacity needs of the system.

The ISO develops the representative operating-reserve needs of major import areas as ranges to account for future uncertainties about the availability of resources, load variations due to weather, and other factors. Although each of the Greater CT, SWCT, and NEMA/Boston areas are likely to have sufficient resources in the long term to meet their representative reserve requirements, the placement of fast-start, energy-efficiency, and economical baseload resources in these areas would improve system performance, especially in the short term for the NEMA/Boston area. Transmission projects that increase the transfer capability into these areas, or in other ways improve the electrical access of these areas to economical resources, also would enhance the economical and reliable performance of the system.

Replacing retired traditional generation with variable resources, particularly wind and PV, will increase the need for flexible resources to provide operating reserves as well as other ancillary services, such as regulation and ramping. To date, increasing the 10-minute operating-reserve requirement and adding seasonal replacement reserves have improved the systemwide performance for meeting peak load, ramping during changing system conditions, and the system response to contingencies. The use of natural-gas-fired combined-cycle units and fast-start units in the ISO’s interconnection queue will likely meet the long-term needs for additional operating reserves.

Studies show the most reliable and economic place for developing new resources is the combined NEMA/SEMA/RI area. The SEMA/RI area had high prices in FCA #9, and transmission analysis identified the combined NEMA/SEMA /RI as a likely future import-constrained capacity zone beginning with FCA #10. Analysis of market resource alternatives provides theoretical locations for combinations of generation and demand-side management injections of approximately 1,540 MW total (1,495 MW of generation and 45 MW of demand-side management spread across nine locations in SEMA/RI). The addition of these resources would remove many of the thermal constraints identified in the SEMA/RI needs assessments.

The Strategic Transmission Retirement Study and the 2012 Economic Study showed that locations near load centers and the Hub are the next-most economical and reliable places for interconnecting new resources. The Maine/New Hampshire/Vermont area has the potential to be export constrained, Western Massachusetts is expected to continue to form the Rest of Pool zone, and Connecticut will continue to be evaluated for upcoming Forward Capacity Auctions beyond FCA #10.

## Transmission Projects

New England’s transmission owners have placed in service transmission projects throughout the region to provide solutions to the needs identified through the regional planning process, as detailed in past RSPs and supporting reports. The Interstate Reliability Project, which is under construction, and the Greater Boston Reliability Project represent the most recent major 345 kV projects required to meet regional reliability. These projects will improve the ability to move power to all areas of the system.

In addition to the reliability benefits, transmission upgrades are supporting market efficiency, reflected by the low amounts of congestion and other out-of-merit charges, such as second-contingency and voltage-control payments. Additionally, elective and merchant transmission facilities are in various stages of analysis and development in the region and have the potential to provide access to renewable resources in remote areas of New England and neighboring regions, including Atlantic Canada and Québec. The administration of elective transmission upgrades has improved with  the FERC’s acceptance of the ISO’s proposal for process improvements.

The transmission planning process for newly identified transmission needs is changing in response to the final FERC Order No. 1000 going into effect. A number of factors, including the low growth of net system load, resource retirements, aging transmission infrastructure, and public policy objectives, will likely affect newly identified physical needs.

## Interregional Coordination

Identifying interregional system needs and the potential impacts that proposed generating units and transmission projects could have on neighboring systems is beneficial for supporting interregional reliability and economic performance. Joint studies with neighboring systems explore the ability to import power from, and export power to, the eastern Canadian provinces and New York and participate in national and regional planning activities.

ISO New England proactively coordinates activities with neighboring systems through NPCC, across the Eastern Interconnection through the Eastern Interconnection Planning Collaborative, and nationally through NERC. The ISO, NYISO, and PJM have built upon their history of close cooperation and have jointly made a compliance filing for FERC Order No. 1000, which requires changes to the interregional planning process and interregional cost allocation. The recent trend of sharing more supply and demand resources with other systems will likely continue, particularly to provide access to a greater diversity of resources, including variable resources, and meet environmental compliance obligations.

## Fuel Flexibility and Certainty

The regional reliance on natural-gas-fired generation, coupled with natural gas pipeline constraints, pose reliability issues and cause price spikes in the wholesale electric markets. Operating experience and studies, including the recently completed EIPC study of the interregional natural gas system highlight these issues. Environmental and economic considerations continue to influence the retirement of oil and coal generating resources and the addition of natural-gas-fired generation, further exposing the region to a dependence on a single type of fuel.

Capital improvements to the natural gas delivery system are under development to access Marcellus shale gas production. Additional pipeline projects, however, would improve electric power system reliability and reduce prices for the wholesale electricity markets. The New England states are considering additional means of funding new pipeline capacity into the region and are examining possible electric transmission infrastructure upgrades for improving the access to Canadian hydropower as an alternate source of generation. The winter peak load is flat as the result of energy-efficiency programs; these programs, coupled with the more efficient use of natural gas, would allow generators the greater use of available pipeline capacity.

A fuel-reliability program and improved coordination of electric power and natural gas system operations resulted in more reliable resource performance during winter 2014/2015 and acted to reduce regional LMPs. Increased flexibility of scheduling natural gas also allows generators to more reliably respond to system conditions. Recently implemented improvements to the day-ahead and real-time markets have helped achieve shorter-term system reliability, and they supplement improvements of the FCM that are part of the longer-term reliability solution. Winter reliability programs, however, will be needed as a bridge between now and 2018 when FCM design changes are in effect to include resource performance incentives.

## Environmental Regulations and Initiatives

Existing and pending state, regional, and federal environmental regulations will require many generators to consider adding air-pollution control devices; modifying or reducing water use and wastewater discharges; and, in some cases, limiting operations. The actual compliance timelines and costs will depend on the timing and substance of the final regulations and site-specific circumstances of the electric generating facilities. Some generators needing to make major investments in environmental compliance measures may become uneconomical and retire, but others can recover their capital investment by locking into FCM prices for up to seven years. Compliance with environmental regulations over a broader footprint can provide reliability and economic benefits. For example, New England is a tightly integrated system and participation in RGGI facilitates compliance with CO2 emission limits.

Regional generator emissions remain relatively low, compared with historical levels, resulting from the greater use of natural gas generation. Higher emissions, however, occur during the winter months because of the need for generating units to burn oil when access to inexpensive sources of natural gas is limited. A future reliability challenge to the system could be the limitations in energy production by units using liquid fuels to comply with emissions regulations.

Relicensing of hydro units must take into consideration the requirements for adequately and equitably protecting and mitigating damage to fish and wildlife (and their habitats) and the recommendations of state and federal fish and wildlife agencies. The ISO is monitoring such proceedings to assess the impacts of operational restrictions, including the maintenance of minimum flows, on the ability of hydroelectric generators to offer regulation and reserve services.

## Planning for and Integration of Variable Energy Resources

The region has significant potential for developing renewable resources and energy efficiency, encouraged by Renewable Portfolio Standards, the Regional Greenhouse Gas Initiative, and other environmental regulations and public policy objectives. While variable energy resources can provide additional fuel diversity, integrating wind or solar resources could place additional stresses on the transmissions system. Generators could be stressed as well if system operators call on them to change output on short notice to provide system balancing and reserves.

### Wind Resources

Wind resources have requested interconnections in remote portions of the system, which can require significant transmission upgrades. In response, the ISO improved the process for reviewing elective transmission upgrades in the interconnection queue. To further facilitate wind integration, the ISO has incorporated wind forecasting into ISO processes, scheduling, and dispatch services.

The ISO continues engaging stakeholders on the issues challenging the wind-interconnection process and the performance of the system with wind resources in locally constrained areas. The wind-integration component of the strategic transmission analyses developed conceptual additions to the transmission system that would enable onshore wind resources to reliably serve load. Economic studies are showing the effects of integrating varying amounts of wind generation on production cost, load-serving energy expense, and congestion, as well as the need for transmission development to enable wind resources to serve the region’s load centers.

The ISO is conducting three economic studies in response to stakeholder requests. The studies of onshore wind development in the Keene Road area and other areas of northern Maine and the effects of relieving transmission system constraints will provide metrics that could lead to market efficiency transmission upgrades. The economic studies of onshore wind development in Maine and the study of offshore wind development also may be used in evaluating the need for projects that facilitate the integration of wind resources. These studies could lead to analysis of public policy transmission upgrades under Order No. 1000.

### Photovoltaics

Photovoltaic resources are rapidly developing in New England and are predominately situated in southern New England. The large-scale development of photovoltaic and other distributed resources poses particularly complex issues that the ISO is beginning to address with stakeholders. The ISO cannot directly observe or control most of these resources, which may respond differently to grid disturbances compared with larger, conventional generators.

Additional work remains for incorporating the effects of PV in short-term load forecasting tools for use by system operators. The ISO and the states are addressing the potential reliability risks posed by growing penetrations of PV installations, such as by supporting revisiions to PV interconnection requirements found in the relevant IEEE standards.

## Federal, Regional, ISO and State Initiatives

Several federal initiatives and requirements include ensuring the reliability of the transmission infrastructure and implementing enforceable reliability standards administered by the North American Electric Reliability Corporation. In addition, DOE studies inform policymakers and planning authorities on the effects of integrating variable energy resource and other key issues. The Quadrennial Energy Review examines a broad array of issues affecting the transmission, distribution, and storage of energy infrastructure in the United States and North America. The analysis recognizes that New England is at the end of major natural gas pipeline routes and does not have sufficient capacity to fully access large reserves in the nearby Marcellus shale.

New England is a leader in applying advanced technologies. FACTS and HVDC improve the use of transmission system infrastructure by efficiently using existing transmission system capabilities, making more efficient use of rights-of-way, and increasing the ability to move power over long distances. The ISO is using phasor measurement units to improve situational awareness and system models.

The ISO continuously works with a wide variety of state policymakers and other regional stakeholders through its planning process. Regional initiatives have improved the wholesale electricity markets, developed and integrated advanced technologies, and issued the PV forecast, which is used in the planning studies. The ISO has continued to provide technical support to a number of state agencies and groups, such as NECPUC, NESCOE, the New England governors, the Consumer Liaison Group, and others. State policies affect system planning, as shown by the New England states continued support for the development of energy efficiency, renewable resources, and smart grid technologies. The six states are also considering the development of new natural gas infrastructure and the means of attracting additional renewable sources of power into New England.

The ISO will continue to work with stakeholders as the planning process evolves in response to FERC orders and other governmental policy developments. State and regional policies will inform the ISO process for planning for public policy under Order No. 1000.

## Looking Ahead

The regional energy landscape is undergoing a dramatic change in terms of the composition of generation, transmission, demand resources, and wholesale markets. This evolution poses a series of challenges the ISO is addressing through a collaborative effort of the New England states and market participants, as well as neighboring regions. Several changes to the planning process and improvements to the wholesale electricity markets, which will affect the reliable and economic operation of the system, are in effect. Discussions of key issues with the region’s stakeholders will be ongoing, and the ISO will provide an update on strategic planning issues and studies in RSP16.

Active involvement by all stakeholders, including public officials, state agencies, NESCOE, market participants, and other PAC members, are key elements of an open, transparent, and successful planning process. As needed, the ISO will continue to work with these groups, as well as NEPOOL, its individual members, and other interested parties, to support regional and federal policy initiatives. The ISO also will continue to provide required technical support to the New England states and the federal government as they formulate policies for the region.

The RSP15 is compliant with Attachment K of the OATT, and the region is successfully implementing revisions to the planning process.

Acronyms and Abbreviations

| Acronym/Abbreviation | Description |
| --- | --- |
| ¢/kWh | cent(s) per kilowatt-hour |
| $/kW-mo; $/kW-m | dollar(s) per kilowatt-month |
| $/kW-yr | dollar(s) per kilowatt-year |
| $/MMBtu | dollar(s) per million British thermal units |
| $/MWh | dollar(s) per megawatt-hour |
| 50/50 | Refers to a 50/50 peak load—a peak load with a 50% chance of being exceeded because of weather conditions, expected to occur in the summer in New England at a weighted New England-wide temperature of 90.2°F, and in the winter, 7.0°F |
| 90/10 | Refers to a 90/10 peak load—a peak load with a 10% chance of being exceeded because of weather conditions, expected to occur in the summer in New England at a weighted New England-wide temperature of 94.2°F, and in the winter 1.6°F |
| ABS | absolute value |
| AC; ac | alternating current |
| ACP | alternative compliance payment |
| AEO | Annual Energy Outlook (EIA) |
| AGT | Algonquin Gas Transmission |
| AIM | Algonquin Incremental Market (Spectra Energy project) |
| AMI | advanced metering infrastructure |
| AMRXY | 20XY Annual Markets Report |
| bbl | blue barrel |
| Bcf; Bcf/d | billion cubic feet; billion cubic feet per day |
| BHE | 1) RSP subarea of northeastern Maine 2) Bangor Hydro Electric (Company) |
| BOSTON, BOST | RSP subarea of Greater Boston, including the North Shore (all capitalized) |
| BPS | bulk power system |
| BTA | best technology available |
| BTM | behind the meter |
| BTMEL | behind-the-meter embedded load (photovoltaics) |
| BTMNEL | behind-the-meter nonembedded load (photovoltaics) |
| Btu | British thermal unit |
| CAA | Clean Air Act (US) |
| CAGR | compound annual growth rate |
| CAISO | California Independent System Operator |
| CAMS | Customer Asset-Management System |
| CC | combined cycle |
| CCP | capacity commitment period |
| CCR | cost-containment reserve |
| CCRP | Central Connecticut Reliability Project |
| CEII | critical energy infrastructure information |
| CELT | capacity, energy, loads, and transmission |
| 2014 CELT Report | 2014–2023 Forecast Report of Capacity, Energy, Loads, and Transmission |
| 2015 CELT Report | 2015–2024 Forecast Report of Capacity, Energy, Loads, and Transmission |
| CFR | Code of Federal Regulations |
| CHP | combined heat and power |
| Cir. | Circuit (court) |
| CLG | Consumer Liaison Group |
| CMA/NEMA | RSP subarea comprising central Massachusetts and northeastern Massachusetts |
| CMP | Central Maine Power (Company) |
| CO2 | carbon dioxide |
| COO | chief operating officer |
| CPP | Clean Power Plan (US EPA) |
| CRA | contingency reserve adjustment (factor) |
| CSC | Cross-Sound Cable |
| CSO | capacity supply obligation |
| CT | 1) State of Connecticut 2) RSP subarea that includes northern and eastern Connecticut 3) Connecticut load zone |
| CWA | Clean Water Act (US) |
| CWIP | construction work in progress |
| DC | direct current |
| D.C. | District of Columbia |
| D.C. Cir. | District of Columbia Circuit (US Court of Appeals) |
| DCT | double-circuit tower |
| DE | Delaware |
| DEEP | Department of Energy and Environmental Protection (CT) |
| DG | distributed generation |
| DGFWG | Distributed Generation Forecast Working Group |
| DMGI | DMG Information (Daily Main and General Trust publicly listed company) |
| DOC | Microsoft Word file |
| DOE | Department of Energy (US) |
| DPU | Department of Public Utilities (MA) |
| DSM | demand-side management |
| Dth/d | dekatherms per day |
| DVAR | dynamic voltage ampere reactive |
| ECRC | Energy Cost Reduction Contract (ME) |
| ECT | eastern Connecticut |
| EE | energy efficiency |
| EEF | energy-efficiency forecast |
| EERS | Energy-Efficiency Resource Standard (NH PUC) |
| EIA | Energy Information Administration (US DOE) |
| EIPC | Eastern Interconnection Planning Collaborative |
| EIS | Environmental Impact Statement |
| EISPC | Eastern Interconnection States Planning Council |
| ELG | Effluent Limit Guidelines (for Electric Steam Generation) (US EPA) |
| EMOF | energy market offer flexibility |
| EMT | Efficiency Maine Trust |
| EOR | energy-only resource |
| EPA | Environmental Protection Agency (US) |
| EPAct | Energy Policy Act of 2005 |
| EPRI | Electric Power Research Institute |
| ERCOT | Electric Reliability Council of Texas |
| ERGIS | Eastern Renewable Generation Integration Study (DOE, National Renewable Energy Laboratory) |
| ERO | Electric Reliability Organization |
| ETU | elective transmission upgrade |
| EWITS | Eastern Wind Integration and Transmission Study (DOE, National Renewable Energy Laboratory) (EWITS) |
| F.3d | Federal Reporter, third series |
| FACTS | Flexible Alternating-Current Transmission System |
| FCA | Forward Capacity Auction |
| FCA #N | nth Forward Capacity Auction |
| FCM | Forward Capacity Market |
| Fed. Reg. | Federal Register |
| FERC | Federal Energy Regulatory Commission |
| fps | feet per second |
| FR | Federal Register |
| FRM | Forward Reserve Market |
| FTR | Financial Transmission Right |
| GDP | gross domestic product |
| GHCC | Greater Hartford/Central Connecticut (part of NEEWS) |
| GHG | greenhouse gas |
| Greater Connecticut | RSP study area that includes the RSP subareas of NOR, SWCT, and CT |
| Greater Southwest Connecticut | RSP study area that includes the southwestern and western portions of Connecticut and comprises the SWCT and NOR subareas |
| GRI | Greater Rhode Island |
| GSGT | Granite State Gas Transmission |
| GSRP | Greater Springfield Reliability Project |
| GT | gas turbine |
| GW | gigawatt |
| GWh | gigawatt-hour(s) |
| HB | House Bill |
| HE | hour ending |
| HQ | Hydro-Québec Balancing Authority Area |
| HQICC | Hydro-Québec Installed Capability Credit |
| (the) Hub | ISO New England energy trading hub |
| HV | high voltage |
| HVDC | high-voltage, direct current |
| ICE | Intercontinental Exchange, Inc. |
| ICF | ICF International, Inc. |
| ICR | Installed Capacity Requirement |
| IEEE | Institute of Electrical and Electronics Engineers |
| IESO | Independent Electric System Operator (Ontario, Canada) |
| IGTS | Iroquois Gas Transmission System |
| IPSAC | Inter-Area Planning Stakeholder Advisory Committee |
| IRC | ISO/RTO Council |
| IRP | Interstate Reliability Project |
| ISAO | information-sharing and analysis organization |
| (the) ISO | Independent System Operator of New England; ISO New England |
| ISO/RTO | Independent System Operator/Regional Transmission Organization |
| ISOs | Independent System Operators |
| ISO tariff | ISO New England’s Transmission, Markets, and Services Tariff |
| JIPC | Joint ISO/RTO Planning Committee |
| kA | kiloampere |
| ktons | kilotons |
| kV | kilovolt(s) |
| kW | kilowatt |
| kWh | kilowatt-hour |
| large gen | a large generating unit ≥20 MW and requiring large generator interconnection procedures |
| lb | pound |
| LDC | local distribution company |
| LLC | limited liability company |
| LMP | locational marginal price |
| LNG | liquefied natural gas |
| LOLE | loss-of-load expectation |
| LOS | loss of source |
| Lower SEMA; LSM | lower southeastern Massachusetts |
| LSE | load-serving entity |
| LSR | local sourcing requirement |
| LTRA | Long-Term Reliability Assessment (NERC) |
| M&N | Maritimes and Northeast (Pipeline) |
| MA | Massachusetts |
| MACT | maximum achievable control technology |
| MA DPU | Massachusetts Department of Public Utilities |
| MATS | Mercury and Air Toxics Standard (US EPA) |
| Mcf | 1,000 cubic feet |
| MCL | maximum capacity limit |
| MDth/d | thousand dekatherms per day |
| ME | 1) State of Maine 2) RSP subarea that includes western and central Maine and Saco Valley, New Hampshire 3) Maine load zone |
| METU | market efficiency transmission upgrade |
| MGD | millions gallons per day |
| MISO | Midcontinent Independent System Operator (formerly called the Midwest ISO) |
| MMBtu | million British thermal units |
| MPRP | Maine Power Reliability Program |
| MPUC | Maine Public Utilities Commission |
| MRA | market resource alternative |
| MTF | merchant transmission facility |
| mtons | million tons |
| MVAR | megavolt-ampere reactive |
| MW | megawatt(s) |
| MWAC | the megawatts converted from the direct-current electricity produced by the photovoltaic panels to alternative current, which typically is supplied to utility customers |
| MWDC | the megawatts generated by photovoltaic panels, which produce direct-current electricity |
| MWe | electrical megawatts (of nuclear power plants) |
| MWh | megawatt-hour(s) |
| N-1 | first-contingency loss |
| N-1-1 | second-contingency loss |
| N/A | not applicable |
| NAESB | North American Energy Standards Board |
| NB | New Brunswick |
| NB–NE | New Brunswick–New England |
| NBSO | New Brunswick System Operator |
| NCPC | Net Commitment-Period Compensation |
| NCSPXY | Northeast Coordinated System Plan 20XY |
| n.d. | no date |
| NECPUC | New England Conference of Public Utilities Commissioners |
| NED | Northeast Energy Direct project |
| NEEWS | New England East–West Solution |
| NEGC | New England Governors' Conference |
| NEL | net energy for load |
| NEMA | 1) RSP subarea for northeast Massachusetts 2) Northeast Massachusetts load zone |
| NEMA/Boston | combined load zone that includes northeast Massachusetts and the Boston area |
| NEPOOL | New England Power Pool |
| NERC | North American Electric Reliability Corporation |
| NESCOE | New England States Committee on Electricity |
| NESHAP | National Emission Standard for Hazardous Air Pollutant |
| NG | natural gas |
| NGA | Northeast Gas Association |
| NGCC | natural gas combined cycle |
| NH | 1) State of New Hampshire 2) RSP subarea comprising northern, eastern, and central New Hampshire; eastern Vermont; and southwestern Maine 3) New Hampshire load zone |
| NIST | National Institute of Standards and Technology |
| NJ | New Jersey |
| NMISA | Northern Maine Independent System Administrator, Inc. |
| NNE | northern New England |
| No. | number |
| NOR | RSP subarea that includes Norwalk and Stamford, Connecticut |
| NOX | nitrogen oxide(s) |
| NPCC | Northeast Power Coordinating Council, Inc. |
| NPRR | nonprice retirement request |
| NRC | Nuclear Regulatory Commission (US) |
| NREL | National Renewable Energy Laboratory (US DOE) |
| NWVT | Northwest Vermont |
| NY | New York Balancing Authority Area |
| NYISO | New York Independent System Operator |
| NYPA | New York Power Authority |
| O3 | ozone |
| OATT | Open Access Transmission Tariff |
| OEP | Office of Energy and Planning (NH) |
| OER | Office of Energy Resources (RI) |
| OP 4 | ISO Operating Procedure No. 4, Action during a Capacity Deficiency |
| OP 7 | ISO Operating Procedure No. 7, Action in an Emergency |
| OP 8 | ISO Operating Procedure No. 8, Operating Reserve and Regulation |
| OP 14 | ISO Operating Procedure No. 14, Technical Requirements for Generators, Demand Resources, Asset-Related Demands, and Alternative Technology Regulation Resources |
| OP 19 | ISO Operating Procedure No. 19, Transmission Operations |
| PA | Pennsylvania |
| PAC | Planning Advisory Committee |
| PAR | phase-angle regulator |
| PDF | Adobe Portable Document Format file |
| PDR | passive demand resource |
| PFP | pay for performance |
| PJM | PJM Interconnection LLC; the RTO for all or parts of Delaware, Illinois, Indiana, Kentucky, Maryland, Michigan, New Jersey, North Carolina, Ohio, Pennsylvania, Tennessee, Virginia, and the District of Columbia |
| PM | particulate matter |
| PM2.5 | fine particulate matter |
| PMU | phasor measurement unit |
| PNGTS | Portland Natural Gas Transmission System |
| pnode | pricing node |
| PP 10 | ISO Planning Procedure No. 10, Planning Procedure to Support the Forward Capacity Market |
| PPA | Proposed Plan Application |
| PPT | Microsoft PowerPoint file |
| PPTU | public policy transmission upgrade |
| PSERC | Power System Engineering Research Center (US DOE) |
| PSNH | Public Service of New Hampshire |
| PTF | pool transmission facility |
| PTO | participating transmission owner |
| Pub. L. | public law |
| PUC | Public Utilities Commission (ME, NH, RI) |
| PURA | Public Utilities Regulatory Authority (CT) |
| PV | photovoltaic |
| QER | Quadrennial Energy Review (US DOE) |
| QP | queue project |
| QTSP | qualified transmission project sponsor |
| queue (the) | ISO Generator Interconnection Queue |
| RC | Reliability Committee |
| RCI | residential, commercial, and industrial |
| REC | renewable energy credit; renewable energy certificate |
| REO | Regional Energy Outlook |
| RES | Renewable Energy Standard (RI, VT) |
| RFP | request for proposals |
| RGGI | Regional Greenhouse Gas Initiative |
| RI | 1) State of Rhode Island 2) RSP subarea that includes the part of Rhode Island bordering Massachusetts 3) Rhode Island load zone |
| RIRP | Rhode Island Reliability Project |
| RNS | Regional Network Service |
| ROS | Rest-of-System (reserve zone) |
| RPS | Renewable Portfolio Standard |
| RSP | Regional System Plan |
| RSPXY | 20XY Regional System Plan |
| RTDR | real-time demand response |
| RTEG | real-time emergency generation |
| RTO | Regional Transmission Organization |
| RTU | reliability transmission upgrade |
| SB | Senate Bill |
| SBC | systems benefits charge |
| SCC | seasonal claimed capability |
| SDNY | US District Court Southern District of New York |
| SEC | Site Evaluation Committee (NH) |
| SEMA | 1) RSP subarea comprising southeastern Massachusetts and Newport, Rhode Island 2) Southeastern Massachusetts load zone |
| SGIP | Smart Grid Interoperability Panel (not small generator interconnection procedure in this document) |
| SIP | State Implementation Plan |
| small gen | a small generating unit <20 MW and requiring small generator interconnection procedures |
| SMD | Standard Market Design |
| SME | RSP subarea for southeastern Maine |
| SO2 | sulfur dioxide |
| SOEP | Sable Offshore Energy Project |
| SOR | settlement-only resource |
| SPI | Strategic Planning Initiative |
| SP | State Plans (US EPA) |
| SPEED | Sustainably Priced Energy Development |
| SPP | Southeast Power Pool |
| SPS | special protection system |
| SREC | solar renewable energy credit (MA) |
| SSC | Stakeholder Steering Committee (EIPC) |
| SSCC | summer seasonal claimed capability |
| STA | strategic transmission analysis |
| STATCOM | static synchronous compensator |
| SVC | static voltage ampere reactive (VAR; V) compensator |
| SWCT | RSP subarea for southwestern Connecticut |
| tbd | to be determined |
| TC | Transmission Committee |
| tcf | trillion cubic feet |
| TCSC | thyristor-controlled series compensation |
| TGP | Tennessee Gas Pipeline |
| TMSR | 10-minute spinning reserve |
| TOUT | through-or-out (service) |
| TQM | Trans-Québec and Maritimes (pipeline) |
| TRV | transient recovery voltage |
| TVA | Tennessee Valley Authority |
| ULSD | ultra-low-sulfur diesel |
| US | United States |
| USC | United States Code |
| USGS | US Geological Survey |
| VAR | voltage-ampere reactive |
| VELCO | Vermont Electric Power Company |
| VER | variable energy resource |
| VSC | voltage source converter |
| VT | 1) State of Vermont 2) RSP subarea that includes Vermont and southwestern New Hampshire 3) Vermont load zone |
| VY | Vermont Yankee |
| WCMA | Western/Central Massachusetts load zone |
| WECC | Western Electricity Coordinating Council |
| WIP | Wright Interconnection Project (of the Iroquois Gas Transmission System) |
| WMA | RSP subarea for western Massachusetts |
| WMECO | Western Massachusetts Electric Company |
| WMPP | Wholesale Markets Project Plan |
| XLS | Microsoft Excel file |
| yr | year |
| ZREC | zero-emission renewable energy credit (CT) |

2014 Regional System Plan (November 6, 2014), http://www.iso-ne.com/static-assets/documents/2014/11/rsp14_110614_final_read_only.docx.

FERC, Order on Compliance Filings (May 17, 2013), http://www.iso-ne.com/static-assets/documents/regulatory/ferc/orders/2013/may/er13_193_er13_196_5_17_13_order_on_order_1000_compliance_filings.pdf. Order on Rehearing and Compliance, 150 FERC ¶ 61,209 (March 19, 2015), http://www.iso-ne.com/static-assets/documents/2015/03/er13-193_er13-193_order_on_rehearing_and_order_no_1000_compliance_filings.pdf.

However, reliability remains vulnerable in the intervening years until the FCM changes that will improve performance incentives are in effect. These vulnerabilities will necessitate the continuation of winter reliability programs each year until then.

Third Order No. 1000 Regional Compliance Filing of ISO New England Inc. and the Participating Transmission Owners Administrative Committee, Docket No, ER13-193-___ (May 18, 2015), http://www.iso-ne.com/static-assets/documents/2015/05/er13-196-004.pdf and http://www.iso-ne.com/static-assets/documents/2015/05/er13-193-005.pdf. (Several appeals and court decisions are pending.)

PJM is the RTO for all or parts of Delaware, Illinois, Indiana, Kentucky, Maryland, Michigan, New Jersey, North Carolina, Ohio, Pennsylvania, Tennessee, Virginia, West Virginia, and the District of Columbia.

FERC, Order on Compliance Filings, 151 FERC ¶ 61,133 (May 14, 2015), http://www.iso-ne.com/static-assets/documents/2015/05/er13-1957-000_et_al_5-14-15_Order_on_Ordr__1000_compliance_filing.pdf.

Compliance Filing of Revised Amended and Restated Northeastern ISO/RTO Planning Coordination Protocol on behalf of ISO New England Inc., New York Independent System Operator, Inc., and PJM Interconnection, L.L.C., Docket No. ER13-1957-___ and Amendments to the ISO New England Inc. Transmission, Markets and Services Tariff in Compliance with May 18, 2015 Order, Docket No. ER13-1960-__, FERC filings (July 13, 2015), http://www.iso-ne.com/static-assets/documents/2015/07/er13-1957-___-7-13-15_second_order_1000_interregional_compliance_filing_protocol_agree.pdf and http://www.iso-ne.com/static-assets/documents/2015/07/er13-1960-001_7-13-15_second_order_1000_interregional_compliance_filing_tariff_rev.pdf.

Information on NERC requirements is available at http://www.nerc.com. Information on NPCC is available at http://www.npcc.org/. In June 2015, NPCC audited the ISO’s compliance with its planning standards. The NPCC audit team found no areas of concern and made no recommendations or suggestions for improvement.

ISO tariff Section II, Open Access Transmission Tariff, Attachment K, “Regional System Planning Process” (January 1, 2014), http://www.iso-ne.com/regulatory/tariff/sect_2/oatt/sect_ii.pdf.

The generation output by individual behind-the-meter distributed resources is not visible to the ISO, but it does observe a net reduction in demand resulting from the operation of these resources.

The actual load has been near or above the 50/50 forecast 11 times during the last 23 years because of weather conditions; six of these 11 times, the load has been near or has exceeded the 90/10 forecast.

The mix of capacity resources could change. Updates are included in the ISO’s monthly chief operating officer (COO) report to the NEPOOL Participants Committee; http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/prtcpnts/mtrls/index.html.

PV units convert approximately 83% of the power generated using direct current (dc) to alternating current (ac).

Seasonal claimed capability reflects the expected production at the time of peak load conditions for hour ending (HE) 2:00 p.m. to 6:00 p.m. during the summer and HE 6:00 p.m. to 7:00 p.m. during the winter.

A sloped demand curve, used for the first time in FCA #9, allows the auction to clear at values higher or lower than the ICR value, depending on reliability requirements and price, which mitigates capacity market price volatility.

The net ICR values for 2015/2016 to 2018/2019 are the latest values approved by FERC and are available at http://www.iso-ne.com/system-planning/resource-planning/installed-capacity-requirements.

The increase in the net ICR is greater than the growth of net demand because the ICR calculation assumes that tie-line benefits and available Operating Procedure No. 4 (OP 4) actions are constant over the planning period. Operating Procedure No. 4, Action during a Capacity Deficiency (August 12, 2014), http://www.iso-ne.com/static-assets/documents/rules_proceds/operating/isone/op4/op4_rto_final.pdf.

See OP 4 citation in footnote 17.

To conduct some RSP studies, the region is divided into various areas associated with their electrical system characteristics. Greater Connecticut is an area that has boundaries similar to the State of Connecticut but is slightly smaller because of electrical system limitations near Connecticut’s borders with western Massachusetts and Rhode Island. Greater Southwest Connecticut includes southwestern and western portions of Connecticut. The BOSTON area (all capitalized) includes the city of Boston and northeast Massachusetts (see Section 2.4).

ISO New England, RSP13, Section 6.9 (November 8, 2013), http://www.iso-ne.com/trans/rsp/index.html. 2012 Economic Study, final report (April 30, 2014), http://www.iso-ne.com/static-assets/documents/committees/comm_wkgrps/prtcpnts_comm/pac/reports/2014/a9_2012_economic_study_final.pdf.

Past RSPs are archived at http://www.iso-ne.com/trans/rsp/index.html. For access to supporting reports, contact ISO Customer Service at 413-540-4220.

FERC, Order Accepting Proposed Tariff Revisions [on ETUs], letter order, 151 FERC ¶ 61,024 (April 14, 2015), http://www.iso-ne.com/static-assets/documents/2015/04/er15-1050-000_er15-1051-000_4-14-15_etu_order.pdf.

FERC, Communication of Operational Information between Natural Gas Pipelines and Electric Transmission Operators, Order No. 787, final rule (November 15, 2013), http://www.ferc.gov/CalendarFiles/20131115164637-RM13-17-000.pdf.

Individual New England states have set goals for 2020, ranging from 10% to 55% of statewide energy consumption.

New Generator Interconnection: Modeling and Performance, Reliability Committee presentation (July 15, 2015), http://www.iso-ne.com/static-assets/documents/2015/07/a13_generator_interconnection_process.pdf.

DG interconnection Issues Update, PAC presentation (July 7, 2015), http://www.iso-ne.com/static-assets/documents/2015/07/a2_dg_interconnection_issues_update.pdf.

Strategic Transmission Analysis: Wind Integration Study—Stage 1—Maine, Regional Constraints, PAC presentation (May 21, 2014), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2014/may212014/a4_strategic_transmission_analysis_wind_power_update.pdf. Strategic Transmission Analysis: Wind Integration Study—Vermont, PAC presentation (June 17, 2015), https://smd.iso-ne.com/operations-services/ceii/pac/2015/06/a4_strategic_transmission_analysis_wind_integration_study_vermont.pdf.

Meeting NPCC bulk power system requirements prevents faults or disturbances from having a significant impact outside the local area.

Synchronous condensers stabilize the system by providing dynamic voltage support and inertia.

DOE, Quadrennial Energy Review (2015), http://energy.gov/sites/prod/files/2015/05/f22/QER%20Full%20Report_0.pdf.

CT DEEP, MA Department of Energy Resources, Eversource Energy, National Grid, and Unitil, “New England Clean Energy RFP,” webpage (2015), http://cleanenergyrfp.com/documents/.

Likewise, the markets and market changes may help meet future system needs by providing incentives for the development of new resources. Market changes are subject to a different stakeholder process and are described in the ISO’s Annual Markets Report (AMR) (accessible at http://www.iso-ne.com/markets-operations/market-monitoring-mitigation/internal-monitor) and Wholesale Markets Project Plan (WMPP) (http://www.iso-ne.com/markets-operations/markets-development/wholesale-markets-project-plan).

ISO New England Inc. Transmission, Markets, and Services Tariff (ISO tariff) (2015), http://www.iso-ne.com/regulatory/tariff/index.html, including Section II. ISO New England Open Access Transmission Tariff, http://www.iso-ne.com/regulatory/tariff/sect_2/oatt/sect_ii.pdf.

A demand resource is a capacity product, type of equipment, system, service, practice, or strategy that verifiably reduces end-use demand for electricity from the power system. Active demand resources (i.e., demand response) reduce load quickly or continuously in response to a request from the ISO for system reliability reasons or in response to a price signal. Passive demand resources are nondispatchable resources that reduce electric energy consumption that generation resources would have otherwise served and include energy-efficiency (EE) measures and “behind-the meter” (on-site) distributed generation (DG) in locations that have net metering (see more on DG below). Net metering allows power customers who generate their own electricity, such as from wind or solar power, to feed their unused electricity back into the grid.

A merchant transmission facility is an independently developed and funded facility subject to the operational control of the ISO, pursuant to an operating agreement specific to each facility.

See the OATT, Section II.B, Attachment N, “Procedures for Regional System Plan Upgrades,”
http://www.iso-ne.com/static-assets/documents/regulatory/tariff/sect_2/oatt/sect_ii.pdf.

FERC, ISO New England Inc. Order on Compliance Filings (May 17, 2013), http://www.iso-ne.com/regulatory/ferc/orders/2013/may/er13-193_er13-196_5-17_13_order_on_order_1000_compliance_filings.pdf. Also see “Order No. 1000—Transmission Planning and Cost Allocation,” FERC webpage (2015), http://www.ferc.gov/industries/electric/indus-act/trans-plan.asp.

The Network-Capability Interconnection Standard is an energy-only standard that includes the minimum criteria required to permit a generator to connect to the transmission system so that it has no adverse impacts on the reliability, stability, or operation of the system, including the degradation of transfer capability for interfaces affected by the generating facility. The Capacity-Capability Interconnection Standard is a capacity and energy standard that includes the same criteria as the Network-Capability Interconnection Standard but also includes criteria to ensure intrazonal deliverability by avoiding the redispatch of other capacity network resources. Before October 29, 1998, generator-interconnection-related upgrades included cost responsibility for additional upgrades beyond those required to satisfy the minimum interconnection standard. The OATT, Section 22, defines the standards; http://www.iso-ne.com/static-assets/documents/regulatory/tariff/sect_2/sch22/sch_22_lgip.pdf.

Pool transmission facilities are the facilities rated 69 kilovolts (kV) or above owned by the participating transmission owners, over which the ISO has operating authority in accordance with the terms set forth in the Transmission Operating Agreements. Refer to the OATT, Section II.49, 109, for additional specifications, http://www.iso-ne.com/static-assets/documents/regulatory/tariff/sect_2/oatt/sect_ii.pdf.

The filing for the addition or modification to the transmission upgrade must be in accordance with the OATT, Section II.47.2, on a date after the RSP Project List (as of the date of that application) already has documented the addition or modification, other than as an elective transmission upgrade. (See Section 2.1.6 for more on the RSP Project List.)

FERC, Order Accepting Proposed Tariff Revisions [on ETUs], letter order, 151 FERC ¶ 61,024 (April 14, 2015), http://www.iso-ne.com/static-assets/documents/2015/04/er15-1050-000_er15-1051-000_4-14-15_etu_order.pdf.

The ISO’s Generator Interconnection Queue includes the requests submitted by generators to interconnect to the ISO New England-administered transmission system; see Section 5.4.

OATT, Attachment K, http://www.iso-ne.com/regulatory/tariff/sect_2/oatt/sect_ii.pdf.

Transmission Planning Process Guide (June 10, 2015), http://www.iso-ne.com/system-planning/transmission-planning/transmission-planning-guides.

Transmission Planning Technical Guide, (December 2, 2014), http://www.iso-ne.com/system-planning/transmission-planning/transmission-planning-guides.

A critical load level is the load level at which a system problem could occur and therefore a solution would be needed. Refer to the OATT, Attachment K, Section 4.1 and 4.2 for complete definitions for needs assessments and solutions studies; http://www.iso-ne.com/regulatory/tariff/sect_2/oatt/sect_ii.pdf.

A distributed generation resource is generation provided by a relatively small, on-site installation directly connected to a distribution facility or retail customer facility and not the regional power system (i.e., it is behind the meter), which can alleviate or prevent regional power system transmission or distribution constraints or reduce or eliminate the need to install new transmission or distribution facilities. A small (24 kilowatt) photovoltaic system installed by a retail customer is an example of distributed generation. DG can use other technologies in addition to PV, including wind, fuel cells, combined heat and power, and hydroelectric.

Any stakeholder can designate a representative to the PAC by providing written notice to the ISO. PAC materials (2001–2015) are available at http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/index.html. PAC agendas; minutes; materials; draft reports, including stakeholder questions and ISO responses; and final reports are posted on the ISO website.

NEPOOL members serve as ISO stakeholders and market participants. More information on NEPOOL participants is available at http://www.iso-ne.com/participate/governing-agreements/nepool-agreement.

A Transmission Operating Agreement is an agreement between a Regional Transmission Operator and a transmission-providing utility whereby the RTO pays the utility for its transmission system costs in exchange for control of the transmission.

Market Rule 1 (ISO tariff, Section III) (2015), http://www.iso-ne.com/regulatory/tariff/sect_3/index.html.

The current list is available at http://www.iso-ne.com/system-planning/system-plans-studies/rsp (filters: Regional System Plan document type; XLS file type).

Recent and archived RSP materials are available at http://www.iso-ne.com/trans/rsp/index.html. The latest and archived editions of the REO, AMR, and WMPP are available at http://www.iso-ne.com/static-assets/documents/2015/02/2015_reo.pdf, http://www.iso-ne.com/markets/mkt_anlys_rpts/annl_mkt_rpts/, and http://www.iso-ne.com/markets-operations/markets-development/wholesale-markets-project-plan. The needs assessments and solutions studies presented to the PAC and posted on the ISO website can be obtained by contacting ISO Customer Service at 413-540-4220.

Stakeholders also can obtain publicly available models of the transmission system network through the FERC 715 process, which requires transmitting utilities that operate facilities rated at or above 100 kV to submit information to FERC annually; see http://www.ferc.gov/docs-filing/forms/form-715/overview.asp. ISO New England Information Policy (ISO tariff, Attachment D) (2014) contains the requirements for controlling the disclosure of CEII and confidential information; see http://www.iso-ne.com/static-assets/documents/regulatory/tariff/attach_d/attachment_d.pdf.

Third Order No. 1000 Regional Compliance Filing of ISO New England Inc. and the Participating Transmission Owners Administrative Committee, Docket No, ER13-193-___ (May 18, 2015), http://www.iso-ne.com/static-assets/documents/2015/05/er13-196-004.pdf and http://www.iso-ne.com/static-assets/documents/2015/05/er13-193-005.pdf. FERC, Order on Rehearing and Compliance, 150 FERC ¶ 61,209 (March 19, 2015), http://www.iso-ne.com/static-assets/documents/2015/03/er13-193_er13-193_order_on_rehearing_and_order_no_1000_compliance_filings.pdf.FERC. (Several appeals and court decisions are pending.)

FERC, Order on Compliance Filings (May 17, 2013), http://www.iso-ne.com/static-assets/documents/regulatory/ferc/orders/2013/may/er13_193_er13_196_5_17_13_order_on_order_1000_compliance_filings.pdf. “Transmission Operating Agreements,” webpage, http://www.iso-ne.com/regulatory/toa/index.html.

FERC stated that the ISO could grandfather existing projects no longer subject to either evaluation or reevaluation as of the effective date, which would not be subject to the competitive process.

Qualified Transmission Project Sponsor (QTPS) Qualification Process, PAC presentation (May 21, 2015), http://www.iso-ne.com/static-assets/documents/2015/05/a5_ferc_order_1000_qtps_qualification_process_presentation_rev1.pdf. Qualified Transmission Project Sponsor (QTPS) Process, PAC Presentation (June 17, 2015), http://www.iso-ne.com/static-assets/documents/2015/06/a5_ferc_order_1000_qtps_process_part_2.pdf.

Order No. 1000 Compliance Filing of ISO New England Inc. and the Participating Transmission Owners Administrative Committee, parts 1 and 2 (October 25, 2012), http://www.iso-ne.com/static-assets/documents/regulatory/ferc/filings/2012/oct/er13_193_000_10_25_12_order_1000_compliance_part_1.pdf and http://www.iso-ne.com/static-assets/documents/regulatory/ferc/filings/2012/oct/er13_196_000_10_25_12_order_1000_compliance_part_2.pdf.

FERC, Order on Compliance Filings, 151 FERC ¶ 61,133 (May 14, 2015), http://www.iso-ne.com/static-assets/documents/2015/05/er13-1957-000_et_al_5-14-15_Order_on_Ordr__1000_compliance_filing.pdf.

Compliance Filing of Revised Amended and Restated Northeastern ISO/RTO Planning Coordination Protocol on behalf of ISO New England Inc., New York Independent System Operator, Inc., and PJM Interconnection, L.L.C., Docket No. ER13-1957-___ and Amendments to the ISO New England Inc. Transmission, Markets and Services Tariff in Compliance with May 18, 2015 Order, Docket No. ER13-1960-__, FERC filings (July 13, 2015), http://www.iso-ne.com/static-assets/documents/2015/07/er13-1957-___-7-13-15_second_order_1000_interregional_compliance_filing_protocol_agree.pdf and http://www.iso-ne.com/static-assets/documents/2015/07/er13-1960-001_7-13-15_second_order_1000_interregional_compliance_filing_tariff_rev.pdf.

ISO New England, “Rules and Procedures” webpage, http://www.iso-ne.com/participate/rules-procedures. FERC, Preventing Undue Discrimination and Preference in Transmission Service, 18 CFR Parts 35 and 37, Order No. 890 (February 16, 2007), http://www.ferc.gov/whats-new/comm-meet/2007/021507/E-1.pdf. NERC Reliability Standards (2013), http://www.nerc.com/page.php?cid=2|20. NPCC Regional Standards (2015), https://www.npcc.org/Standards/default.aspx.

“Transmission Operating Agreements” webpage, http://www.iso-ne.com/regulatory/toa/index.html.

The ISO is not responsible for portions of northern and eastern Maine. The Northern Maine Independent System Administrator, Inc. (NMISA) is a nonprofit entity responsible for the administration of the northern Maine transmission system and electric power markets in Aroostook and Washington counties. The 2015 peak load forecast for NMISA is approximately 136 MW. NMISA, Seven-Year Outlook: An Assessment of the Adequacy of Generation and Transmission Facilities on the Northern Maine Transmission System (June 2015), p. 3, https://nmisa.com/docs/2015-Seven-Year-Oulook.pdf.

For more information on New England wholesale electricity markets, see the ISO’s 2014 Annual Markets Report (AMR14) (May 20, 2015), http://www.iso-ne.com/static-assets/documents/2015/05/2014-amr.pdf.

Installed capacity is the megawatt capability of a generating unit, dispatchable load, external resource or transaction, or demand resource that qualifies as a participant in the ISO’s Forward Capacity Market according to the market rules. Additional information is available at http://www.iso-ne.com/markets-operations/markets/forward-capacity-market.

Regulation is the capability of specially equipped generators to increase or decrease their generation output every four seconds in response to signals they receive from the ISO to control slight changes on the system.

According to NERC, NPCC, and ISO criteria, a contingency is the sudden loss of a generation or transmission resource. A system’s first contingency (N−1) is when the power element (facility) with the largest impact on system reliability is lost. A second contingency (N−1−1) takes place after a first contingency has occurred and is the loss of the facility that, at that time, has the largest impact on the system. A forced outage is a type of unplanned outage or unexpected removal from service of a generating unit, transmission facility, or other facility or portion of a facility because of an emergency failure or the discovery of a problem that needs to be repaired as soon as crews, equipment, or corrective dispatch actions can perform the work.

Fast-start resources can be electrically synchronized to the system quickly and reach claimed capability (i.e., a generator’s maximum production or output) within 10 to 30 minutes to respond to a contingency and serve demand.

See the ISO’s Wholesale Markets Project Plans at http://www.iso-ne.com/markets-operations/markets-development/wholesale-markets-project-plan.

The ISO tariff allows loads that meet specified requirements to request and receive nodal pricing.

See Market Rule 1, Section III.2.7, of the ISO tariff, http://www.iso-ne.com/participate/rules-procedures/tariff/market-rule-1.

On April 28, 2014, FERC approved an updated methodology for evaluating and modeling capacity zones, which was in place for FCA #9, held February 2015. FERC, ISO New England Inc. Order Accepting Compliance Filing (April 28, 2014), http://www.iso-ne.com/regulatory/ferc/orders/2014/apr/er12-953-004-4-28-14_order_accept_cap_zone_compliance.pdf.

RTDRs are demand resources that must curtail electrical usage within 30 minutes of receiving a dispatch instruction from the ISO. Real-time emergency generation is distributed generation the ISO calls on to operate during certain voltage-reduction or more severe actions but must limit its operation to 600 MW to comply with the generation’s federal, state, or local air quality permit(s), as well as the ISO’s market rules. RTEG operations result in curtailing load on the grid, as the distributed energy provided by the emergency generator begins serving demand.

The ISO’s Capacity, Energy, Load, and Transmission (CELT) Reports and associated documentation contain more details on the short-run and long-run forecast methodologies, models, and inputs; weather normalization; regional, state, subarea, and load-zone forecasts of annual electric energy use and peak loads; high- and low-forecast bandwidths; and retail electricity prices. They are available at the “CELT Reports,” webpage, http://www.iso-ne.com/system-planning/system-plans-studies/celt. Also see the 2015 CELT Report (http://www.iso-ne.com/system-planning/system-plans-studies/celt) and the ISO NE Seasonal Peaks since 1980 (April 22, 2014), which can be accessed at the “Energy, Load, and Demand Reports,” webpage, http://www.iso-ne.com/isoexpress/web/reports/load-and-demand/-/tree/net-ener-peak-load.

Non-PV distributed generation has been growing at approximately 40 MW per year, one-third of which has been diesel generation. April 2015 Distributed Generation Survey Results, Distributed Generation Forecast Working Group (DGFWG) presentation (June 12, 2015), http://www.iso-ne.com/static-assets/documents/2015/06/survey_results_06122015.pdf.

Preliminary ISO-NE Annual Energy and Seasonal Peak Forecast 2015-2024, PAC presentation (February 18, 2015), http://www.iso-ne.com/static-assets/documents/2015/02/a5_new_england_load_forecast_update.pdf (Preliminary Forecast 2015–2024).

The 50/50 “reference” case peak loads have a 50% chance of being exceeded because of weather conditions. For the reference case, the summer peak load is expected to occur at a weighted New England-wide temperature of 90.2°F, and the winter peak load is expected to occur at 7.0°F. The 90/10 “extreme” case peak loads have a 10% chance of being exceeded because of weather. For the extreme case, the summer peak is expected to occur at a temperature of 94.2°F, and the winter peak is expected to occur at a temperature of 1.6°F.

Preliminary ISO-NE Annual Energy and Seasonal Peak Forecast 2014–2023, PAC presentation (Preliminary Forecast 2014–2023) (February 19, 2014), http://www.iso-ne.com/static-assets/documents/committees/comm_wkgrps/prtcpnts_comm/pac/mtrls/2014/feb192014/a7_preliminary_iso_load_forecast_2014_2023.pdf.

The generation output includes output from settlement-only resources (SORs), which are less than 5 MW but not centrally dispatched by the ISO control room and not monitored in real time.

The compound annual growth rate (CAGR) is calculated as follows:

Preliminary Forecast 2015–2024 presentation, slide 22, http://www.iso-ne.com/static-assets/documents/2015/02/a5_new_england_load_forecast_update.pdf.

OP 4 actions implemented during a capacity deficiency include Action 2, the dispatch of real-time demand resources, and Action 6, the dispatch of real-time emergency generation. Operating Procedure No. 4, Action during a Capacity Deficiency (August 12, 2014), http://www.iso-ne.com/static-assets/documents/rules_proceds/operating/isone/op4/op4_rto_final.pdf.

Weather conditions during the actual peak summer loads were slightly below the expected 90/10 weather conditions for 1994, 1999, 2001, and 2002, and weather conditions were slightly above the expected 90/10 weather during the 2006, 2011, and 2014 peaks. A spreadsheet containing historical annual peak loads and associated weather conditions since 1980 is available at http://www.iso-ne.com/isoexpress/web/reports/load-and-demand/-/tree/net-ener-peak-load.

State-sponsored EE programs consist of various efforts designed to reduce energy consumption. These efforts generally are funded by multiple sources, including a system benefits charge (SBC) that electricity providers apply to customer bills, the Regional Greenhouse Gas Initiative (RGGI) auction revenues (see Section 9.1.2.4), and state EE policy funds. More information on the methodology used to develop the EE forecast is available at the ISO’s “Energy-Efficiency Forecast Working Group,” webpage, http://www.iso-ne.com/committees/planning/energy-efficiency-forecast. ISO New England Energy-Efficiency Forecast for 2019–2024 (May 1, 2015), http://www.iso-ne.com/static-assets/documents/2015/05/eef-report-2019-2024.pdf.

State-jurisdictional standards are typically applicable for all solar projects, including both “rooftop” and MW-scale solar “farms.” New England presently does not include any FERC-jurisdictional PV project (~500 MW total); however, two projects currently in the ISO queue (see Section 5.4) seeking interconnection may be FERC-jurisdictional and would need to meet the ISO’s small generator interconnection procedures or Small Generator Interconnection Agreement or both. See the OATT, Schedule 23, “Small Generator Interconnection Procedures” (July 25, 2012), http://www.iso-ne.com/static-assets/documents/regulatory/tariff/sect_2/sch23/sch_23_sgip.pdf.

The DGFWG, chaired by a representative of the ISO, is not a formal NEPOOL committee or subcommittee. More information on the DGFWG, including the group’s scope of work (September 25, 2013) is available at http://www.iso-ne.com/static-assets/documents/committees/comm_wkgrps/othr/distributed_generation_frcst/2013mtrls/sep302013/draft_dgfwg_scope_of_work.pdf.

Since its inception, the ISO has accounted for DG in its resource and load forecasts. Existing and future DG with obligations in the FCM are considered resources and contribute to meeting New England’s ICR. Existing non-FCM DG resources registered in the wholesale energy markets are counted as “generating load assets” (i.e., settlement-only resources). Load reductions from the remainder of existing DG (i.e., installations that do not participate in the wholesale markets) are embedded in the historical loads used to develop the ISO’s 10-year load forecast. Also see the ISO’s April 2015 Distributed Generation Survey Results, DGFWG presentation (June 12, 2015), http://www.iso-ne.com/static-assets/documents/2015/06/survey_results_06122015.pdf.

State PV policy data presented to the DGFWG is available at the ISO’s “Distributed Generation Forecast” webpage, http://www.iso-ne.com/system-planning/system-forecasting/distributed-generation-forecast.

The DC nameplate rating of a PV installation is equal to the sum of the ratings of its solar panels, whereas its AC nameplate rating is determined by the sum of the rating(s) of its inverter(s). Generically, the nameplate rating is a measure of a piece of equipment’s ability to produce or transmit electricity

Of the DC electricity that PV panels generate, 83% is converted into AC electricity, which is commonly used by utility customers.

ICF International, Economic Drivers of PV Report for ISO New England (February 27, 2015), http://www.iso-ne.com/static-assets/documents/2015/02/icf_economic_drivers_of_pv_report_for_iso_ne_2_27_15.pdf. The study does not analyze the cost-effectiveness of federal, state, or utility PV policies nor make value judgments about the need for, or appropriateness of, such policies.

A renewable energy credit is a tradable, nontangible commodity representing the eligible renewable generation attributes of 1 MWh of actual generation from a grid-connected renewable resource.

Policies implemented though periodic procurement include Connecticut’s zero-emissions renewable energy credits (ZREC) (http://www.ct.gov/deep/cwp/view.asp?a=4120&Q=503720), Rhode Island’s Renewable Energy Growth (https://www.nationalgridus.com/narragansett/business/energyeff/4_dist_gen.asp), and Vermont’s Standard Offer (http://vermontspeed.com/standard-offer-program/). Other policies include Massachusetts’ solar renewable energy credits (SREC) (http://www.mass.gov/eea/energy-utilities-clean-tech/renewable-energy/solar/rps-solar-carve-out/current-status-of-the-rps-solar-carve-out-program.html) and, in all New England states, the growth of net-metered projects until caps are reached.

Seasonal claimed capability is a generator's maximum production or output during a particular season, adjusted for physical and regulatory limitations.

A full explanation of the various discount factors, other modeling assumptions, and other details on the development of the PV forecast are available at http://www.iso-ne.com/static-assets/documents/2015/04/2015_solar_forecast_details_final.pdf.

Various planning studies may use values that differ from the SSCC, depending on the study assumptions and intent.

See footnote 96.

Settlement-only resources and non-FCM generators, as defined in Operating Procedure No. 14 (OP14), Technical Requirements for Generators, Demand Resources, Asset-Related Demands, and Alternative Technology Regulation Resources, are included in this market type. Refer to OP 14 (January 29, 2015), at http://www.iso-ne.com/static-assets/documents/rules_proceds/operating/isone/op14/op14_rto_final.pdf.

Deterministic analyses are snapshots of assumed specific conditions that do not quantify the likelihood that these conditions will actually materialize. The results are based on analyzing the assumed set of conditions representing a specific scenario.

Established ICR values refer to the values that FERC has approved. Representative net ICR values are the representative ICRs for the region, minus the tie-reliability benefits associated with the Hydro-Québec Interconnection Capability Credits (HQICCs). (As defined in the ISO’s tariff, the HQICC is a monthly value that reflects the annual installed capacity benefits of the HQ Interconnection, as determined by the ISO using a standard methodology on file with FERC.) The ISO calculates representative net ICR values solely to inform New England stakeholders; it does not file these values with FERC for approval. The values for FCA #10 for the 2019/2020 capacity commitment period are scheduled to be filed with FERC in November 2015. For additional information about ICRs, see the ISO’s “Installed Capacity Requirements,” webpage at http://www.iso-ne.com/system-planning/resource-planning/installed-capacity-requirements.

ISO New England, 2014–2023 Forecast Report of Capacity, Energy, Loads, and Transmission (May 2014), http://www.iso-ne.com/static-assets/documents/trans/celt/report/2014/2014_celt_report_rev.pdf.

Footnote 101 defines the HQICC monthly value used to modify the ICR.

Resulting reserves are the amount of capacity in excess of the forecast 50/50 peak load. Percentage resulting reserves = [{(Net ICR − 50/50 peak load) ÷ 50/50 peak load} × 100].

Based on the representative net ICR values presented to the PAC in January 2015, the average value of the resulting reserves for 2019/2020 through 2023/2024 is 14.3%, derived from the following values: 14.1% for 2019/2020, 14.2% for 2020/2021, 14.3% for 2021/2022, 14.4% for 2022/2023 and 14.6% for 2023/2024. This is the percentage reserve multiplier applied to the 2015 CELT demand forecast to derive the representative net ICR values covering 2020/2021 through 2024/2025. The January 2015 presentation, Future Representative Capacity Requirements for 2019/20–2013/24 (January 21, 2015), is available at http://www.iso-ne.com/static-assets/documents/2015/01/a7_representative_icr_values_2019_2023_rev1.pdf.

LSRs and MCLs are based on network models using transmission facilities that will be in service no later than the first day of the relevant capacity commitment period.

The ICR requirements for 2013/2014 to 2017/2018 are available in the FERC filings at
http://www.iso-ne.com/regulatory/ferc/filings/2011/mar/er11-3048-000_03-08-11_icr_2014-2015.pdf,
http://www.iso-ne.com/regulatory/ferc/filings/2012/jan/er12-756-000_01-03-12_icr_2015-2016_filing.pdf,
http://www.iso-ne.com/regulatory/ferc/filings/2012/nov/er13-334-000_11-06-12_icr_2016-2017_filing.pdf
http://www.iso-ne.com/regulatory/ferc/filings/2013/nov/er14-328-000_11-5-13__icr_2017-2018_.pdf
http://www.iso-ne.com/static-assets/documents/2014/11/er15-___-000_11-6-14_2018-2019_icr_filing.pdf.

A capacity supply obligation is a requirement for a resource to provide capacity, or a portion of capacity, to satisfy a portion of the ISO’s Installed Capacity Requirement acquired through a Forward Capacity Auction, a reconfiguration auction, or a CSO bilateral contract through which a market participant may transfer all or part of its CSO to another entity. FCM reconfiguration auctions take place before and during the capacity commitment period to allow participants to buy and sell capacity obligations and adjust their positions.

The 2015 CELT Report, Section 3 and Appendix D (May 2015) (http://www.iso-ne.com/system-planning/system-plans-studies/celt) contains the FCM capacity supply obligations for all capacity resources by load zone.

FERC, Order on Tariff Revisions to the Forward Capacity Market (March 30, 2012), http://www.iso-ne.com/regulatory/ferc/orders/2012/mar/er12-953-000_3-30-12_order_fcm_redesign_ext.pdf.

ISO New England, Compliance Filing Revisions to Forward Capacity Market Rules (December 3, 2012), http://www.iso-ne.com/regulatory/ferc/filings/2012/dec/er12-953-001_12-3-12_fcm_redesign_compl.pdf. FERC, Order Accepting in Part, and Rejecting in Part, FCM Compliance Filing (February 12, 2013), http://www.iso-ne.com/regulatory/ferc/orders/2013/feb/er12-953-001_2-12-13_order_fcm_compliance.pdf; FERC, Order on Compliance Filing (May 31, 2013), http://www.iso-ne.com/regulatory/ferc/orders/2013/may/er12-953-002_5-31-13_order_accept_fcm_compliance.pdf.

Most of this increase is attributable to the certification of the Interstate Reliability Project (IRP) (see Section 6.4), which results in the Lake Road Station being considered inside the CT import interface, starting with the 2017/2018 capacity commitment period.

An administrative export delist bid is a type of bid submitted during a Forward Capacity Auction for a capacity export resource associated with multiyear contracts but wanting to opt out of a capacity supply obligation. This type of bid may have an opportunity-cost component as part of the supporting cost data.

Market Rule 1, III.13.2.8.2.

A dual-fuel unit is a gas generator that can switch to burning oil.

A delist bid is a submission in an FCA for an existing FCM resource indicating that the resource wants to opt of the auction before the deadline for qualifying its existing capacity and does not want a CSO below a certain price. A nonprice retirement request is an irrevocable request submitted in an FCA to retire the entire capacity of a resource, subject to an ISO review for reliability impacts and that supersedes any other delist bids submitted. If the ISO determines the resource is needed for reliability, the resource owner can either retire the resource as requested or continue to operate it until the reliability need has been met and then retire the resource. NPR requests, determination letters, and resource responses are available at http://www.iso-ne.com/system-planning/resource-planning/nonprice-retirement.

Planning Procedure No. 10, Planning Procedure to Support the Forward Capacity Market, (January 13, 2015), http://www.iso-ne.com/static-assets/documents/rules_proceds/isone_plan/pp10/pp10.pdf.

A static delist bid is submitted for a resource before an FCA—and that cannot be changed during the auction—requesting for the resource to opt out of a CSO and reflecting either the cost of the resource or a reduction in ratings as a result of ambient air conditions. The ISO may be required to submit a static delist bid on behalf of a resource that would not be able to supply its awarded capacity during the winter because its summer-qualified capacity is greater than its winter-qualified capacity. A dynamic delist bid indicates that a resource wants to opt out of a CSO below a certain price in the auction.

The delisting includes permanent, static, and dynamic delist bids but does not include nonprice retirement requests. A permanent delist bid prohibits a resource from participating in any future FCA or assuming any CSO unless it qualifies for and clears as a new resource in a subsequent FCA.

ISO tariff, Section III.13.1.2.3.2.1.1.2, “Review of Static Delist Bids.”

ISO New England, Compliance Filing of ISO New England Inc., FERC filing (January 31, 2014), http://www.iso-ne.com/regulatory/ferc/filings/2014/jan/er12-953-004_1-31-2014_comp_12-953-002.pdf. FERC, Order Accepting Compliance Filing, FERC order (April 28, 2014), http://www.iso-ne.com/regulatory/ferc/orders/2014/apr/er12-953-004-4-28-14_order_accept_cap_zone_compliance.pdf.

Forward Capacity Market: 2015 Network Topology Certifications, Reliability Committee presentation (January 27, 2015), http://www.iso-ne.com/static-assets/documents/2015/01/a6_2015_network_topology_certification.pptx.

ISO New England, “FCM 2014 Network Topology Certifications,” memo to the NEPOOL Reliability Committee (February 13, 2014), http://www.iso-ne.com/committees/comm_wkgrps/relblty_comm/relblty/mtrls/2014/feb182014/a_rc_memo_2014_fcm_irp_certification.pdf.

2017-2018 Capacity Commitment Period—Evaluation of Nonprice Retirements, RC presentation (October 15, 2013), http://www.iso-ne.com/static-assets/documents/committees/comm_wkgrps/relblty_comm/relblty/mtrls/2013/oct152013/a5_npr_summary.pptx.

Transmission Interface Transfer Capabilities: 2015 Regional System Plan Assumptions, PAC presentation (December 18, 2015), http://www.iso-ne.com/static-assets/documents/2014/12/a5_rsp15_zonal_interfaces_transfer_capability_assumptions_1.pptx.

Transmission Interface Transfer Capabilities: 2015 Regional System Plan Assumptions—Part 2, PAC presentation (January 21, 2015), http://www.iso-ne.com/static-assets/documents/2015/01/a8_rsp15_zonal_interfaces_transfer_capability_assumptions.pdf.

Transmission Interface Transfer Capabilities: 2015 Regional System Plan Assumptions—Part 3, PAC presentation (January 28, 2015), http://www.iso-ne.com/static-assets/documents/2015/01/a5_rsp15_transfer_capability_assumptions_part_3.pdf.

Transmission Interface Transfer Capabilities: 2015 Regional System Plan Assumptions—Part 4, PAC presentation (March 24, 2015), https://smd.iso-ne.com/operations-services/ceii/pac/2015/03/a2_rsp15_zonal_interfaces_transfer_capability_assumptions.pdf.

Transmission Interface Transfer Capabilities: 2015 Regional System Plan Assumptions— Update, PAC presentation (June 17, 2015), https://smd.iso-ne.com/operations-services/ceii/pac/2015/06/a8_rsp15_transfer_capability_assumptions_update.pdf.

Identification of Potential New Capacity Zone Boundaries, FERC filing (April 06, 2015), http://www.iso-ne.com/static-assets/documents/2015/04/er15-___-000_identification_of_potential_new_capacity_zone_boundaries.pdf.

The process is described in the PAC presentations listed in footnote 125 and described in the FERC filing, Compliance Filing of ISO New England Inc., Docket No. ER12-953-002 (January 31, 2014), http://www.iso-ne.com/regulatory/ferc/filings/2014/jan/er12-953-004_1-31-2014_comp_12-953-002.pdf.

The upgrades include the uprate of the V148N 115 kV line between Washington and Woonsocket in Rhode Island and the increase of 345/115 kV autotransformer ratings at West Farnum and Kent County (see Section 6.4).

OATT, Attachment K, http://www.iso-ne.com/regulatory/tariff/sect_2/oatt/sect_ii.pdf.

FERC, Order Accepting Filing Identifying Two Potential New Boundaries for Capacity Zones for ISO-NE's FCA 10, 151 FERC ¶ 61,183 (May 29, 2015), http://www.iso-ne.com/static-assets/documents/2015/05/er15-1462-000_5-29-15_ordr_accepting_cap_zones_fca10.pdf.

Operating Procedure No. 4, Action during a Capacity Deficiency (October 5, 2013), and Operating Procedure No. 7, Action in an Emergency (August 12, 2014), http://www.iso-ne.com/participate/rules-procedures/operating-procedures.

RSP15 Resource Adequacy and Related Studies, PAC presentation (April 28, 2015), http://www.iso-ne.com/static-assets/documents/2015/04/a2_rsp15_resource_adequacy_and_related_studies.pdf.

ISO Operating Procedure No. 8, Operating Reserve and Regulation (May 2, 2014), http://www.iso-ne.com/rules_proceds/operating/isone/op8/op8_rto_final.pdf.

Ramping up and ramping down refer to generators’ increasing or decreasing output to meet changing load levels, such as in the morning, which typically involves ramping up, and in the evening, which typically involves ramping down.

ISO Operating Procedure No. 19, Transmission Operations (June 15, 2015), http://www.iso-ne.com/rules_proceds/operating/isone/op19/op19_rto_final.pdf.

While the estimates for operating-reserve requirements are based on expected future operating conditions, annual market requirements are based on historical data that reflect the actual previous seasonal system conditions, as adjusted for transmission topology changes and resource retirements and additions. The ISO calculates market requirements immediately before each locational FRM procurement period.

Market Rule 1, Standard Market Design (ISO tariff, Section III) (2014), defines the types of reserves that can meet these requirements; http://www.iso-ne.com/regulatory/tariff/sect_3/index.html.

Economic-merit order (i.e., in merit or in merit order) is when the resources with the lowest-price offers are committed and dispatched first, and increasingly higher-priced resources are brought on line as demand increases. Out-of-merit dispatch occurs when resources are run less economically to respect system reliability requirements.

Although physically in Connecticut, the Lake Road generating plant is considered electrically part of Rhode Island without the completion of the NEEWS Interstate Reliability Project.

In some circumstances, when transmission contingencies are more severe than generation contingencies, shedding some load may be acceptable.

Higher tie-reliability benefits and reductions in the net ICR would increase the frequency and depth of OP 4 actions.

The ISO provides monthly updates on the status of active generation interconnection requests, NEPOOL Participant Committee COO Report for Monthly Updates (Monthly COO Report). See the April 2015 monthly COO Report in the http://www.iso-ne.com/static-assets/documents/2015/04/april-2015-coo-report.pdf.

The SME subarea in Maine and the NOR subarea in Connecticut have no megawatts proposed in the active queue.

In addition to the Monthly COO Reports, information on the queue is available at http://www.iso-ne.com/system-planning/transmission-planning/interconnection-request-queue.

The projects proposed but discontinued faced problems associated with financing, licensing, insufficient market incentives, or other issues.

New Generator Interconnection: Modeling and Performance, Reliability Committee presentation (July 15, 2015), http://www.iso-ne.com/static-assets/documents/2015/07/a13_generator_interconnection_process.pdf.

RSP13, Section 6.9 (November 8, 2013), http://www.iso-ne.com/trans/rsp/index.html.

A repowered generator may require transmission system improvements to qualify for the FCM, as identified by an FCA overlapping interconnection impact analysis, which the ISO conducts for each new supply-side resource to assess whether the resource can provide useful capacity and electric energy without negatively affecting the ability of other capacity resources to provide these services also.

Nontransmission Alternatives Analysis: Results of the NH/VT Pilot Study, PAC presentation (May 26, 2011), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2011/may262011/nta_analysis.pdf.

Market Resource Alternative Analysis—Final Supply-Side Results Greater Hartford and Central Connecticut, PAC presentation (December 13, 2012), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2012/dec132012/ghcc_mra.pdf, and Market Resource Alternative Analysis—Demand-Side Results Greater Hartford and Central Connecticut, revised, PAC presentation (November 14, 2012), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2012/nov142012/ghcc_mra_november.pdf.

Market Resource Alternative Analysis—Southeast Massachusetts/Rhode Island, PAC presentation (January 28, 2015), https://smd.iso-ne.com/operations-services/ceii/pac/2015/01/a2_sema_ri_mra_n_1_1.pdf.

Demand-side management injections may include active and passive demand resources.

Southeastern Massachusetts and Rhode Island (SEMA/RI) Area Needs Assessment (N-1) (February 19, 2014), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2014/feb192014/a8_sema_ri_needs_assessment.pdf.

Southeastern Massachusetts and Rhode Island (SEMA/RI) Area Needs Assessment (N-1-1) (July 15, 2014), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2014/jul152014/a5_sema_ri_area_needs_2_n_1_1_rev1.pdf.

Further details about individual transmission projects can be obtained by contacting ISO Customer Service at (413) 540-4220.

Past RSPs are available at http://www.iso-ne.com/trans/rsp/index.html. PAC materials and reports are available at http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/index.html.

ISO New England, Transmission Planning Process Guide, (June 10, 2015) and Transmission Planning Technical Guide (December 2, 2014), http://www.iso-ne.com/system-planning/transmission-planning/transmission-planning-guides.

One exception is that Aroostook and Washington Counties in Maine receive electric service from New Brunswick.

1779 Line Partial Rebuild, PAC presentation (July 15, 2014), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2014/jul152014/a6_1779_line_partial_rebuild.pdf.

Montville 345/115 kV Autotransformer Replacement Project, PAC presentation (July 15, 2014), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2014/jul152014/a7_montville_autotransformer.pdf.

Norwood Light and Electric Asset Replacement—Two H-Frame Overhead Transmission Circuits, PAC presentation (September 17, 2014), https://smd.iso-ne.com/operations-services/ceii/pac/2014/a8_norwood_transmission_circuit_replacement.pdf.

Somerset Switchyard Rebuild—Needs and Preferred Solution, PAC presentation (January 28, 2014), https://smd.iso-ne.com/operations-services/ceii/pac/2015/01/a4_ngrid_sommerset_switchyard_rebuild_project_needs_preferred_solutions.pdf.

Northeast Utilities, Line 372 (Mystic to Kingston Street) Rebuild, PAC presentation (January 28, 2014; reposted February 2015), https://smd.iso-ne.com/operations-services/ceii/pac/2015/01/a3_nu_line_372_reconductor_project.pdf.

345 kV Line Structure Replacements—Northfield Mountain to Berkshire 312 Line, Northfield Mountain to MA/NH Border 381 Line, and Northfield Mountain to Ludlow 354 Line, PAC presentation (July 2015), http://www.iso-ne.com/static-assets/documents/2015/07/a4_eversource_345kv_line_structure_replacement_project.pdf.

136 Line 136 (Falmouth Tap–Hatchville–Mashpee) Needs Assessment, PAC presentation (July 2015), https://smd.iso-ne.com/operations-services/ceii/pac/2015/06/a8_line_136_needs_assessment.pdf.

The flows vary with system conditions, as shown by the 2014 historical market data, which include the occurrence of northbound flows. See RSP15 2014 Historical Market Data: Locational Marginal Prices, Interface MW Flows, PAC presentation (January 21, 2015), http://www.iso-ne.com/static-assets/documents/2015/01/a5_2014_lmps_interface_mw_flows.pdf.

Wind Development in Constrained Areas, PAC presentation (March 21, 2013), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2013/mar212013/a5_wind_development_in_constrained_areas_new.pdf.

Maine Power Reliability Program Transmission Alternatives—Revised, PAC presentation (January 24, 2008), https://smd.iso-ne.com/trans/sys_studies/rsp_docs/pres/2008/amprprevised.pdf. Final Report Maine Power Reliability Program Transmission Alternatives Assessment for the Maine Transmission System (June 10, 2008), https://smd.iso-ne.com/trans/sys_studies/rsp_docs/pres/2008/mprp_final_report.pdf. The Maine Power Reliability Program Transmission Alternatives Assessment for the Maine Transmission System (May 30, 2008) describes the original version of this project in more detail. The CMP Maine Power Reliability Program Proposed Plan Application Analyses Addendum Report (February 6, 2009) updates the project descriptions.

Northern Maine System Performance, PAC presentation (September 21, 2010), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2010/sep212010/northern_maine.pdf.

Maine Power Reliability Program: Transfer Capability Study Results, PAC presentation (December 13, 2012), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2012/dec132012/mprp_transfer_limits.pdf.

Wind Development in Constrained Areas, PAC presentation (March 21, 2013), see footnote 164.

Maine Transmission System 2023 Needs Assessment (December 2014), https://smd.iso-ne.com/operations-services/ceii/pac/2014/final_maine_2023_needs_assessment_tpl_001_4_compliance_report.pdf.

VELCO, 2015 Vermont Long-Range Transmission Plan (June 25, 2015), http://www.velco.com/our-work/planning/long-range-plan.

New Hampshire/Vermont 2022 Needs Assessment Study Scope (June 2013), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/reports/2013/a_final_nh_vt_2022_needs_scope.pdf.

New Hampshire/Vermont 2023 Needs Assessment Update (March 2014), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2014/mar172014/a7_nh_vt_2023_needs_assessment.pdf.

New Hampshire/Vermont 2022 Needs Assessment Results (June 2013), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2013/jun192013/a2_nh_vt_2022_needs_assessment.zip.

Vermont Transmission System 2023 Solutions Study Report (December 2014), https://smd.iso-ne.com/operations-services/ceii/pac/2014/vermont_2023_solutions_report_final.pdf.

ACSS refers to aluminum conductor steel supported.

VAR stands for voltage-ampere reactive.

New Hampshire/Vermont Transmission Solutions Study Report (April 2012), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/reports/2012/nhvt_solutions_report.pdf.

Follow-Up Analysis to the New Hampshire/Vermont Solutions Study (NH/VT Solutions Study Follow Up) (April 2012), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/reports/2012/final_nhvt_solutions_followup.pdf.

Although the capacitor banks were part of the 2020 upgrades, they were being reassessed as part of the 2023 effort because Eversource Energy had concerns regarding the feasibility of their implementation.

The 345 kV Reliability Project in Boston added new 345 kV cables between Stoughton, Hyde Park, and K Street substations and is often referred to as the Stoughton Cables Project. In Southwest Connecticut, the Phase I Project added a new 345 kV circuit between Plumtree and Norwalk substations and often is referred to as the Bethel–Norwalk Project. The Phase II Project added a new 345 kV circuit between Beseck, East Devon, Singer, and Norwalk substations and is often referred to as the Middletown–Norwalk Project.

Greater Hartford and Central Connecticut Area Transmission 2022 Needs Assessment (May 2014), zip file, https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/reports/2014/ghcc_needs_assessment_report_rev2.zip.

Greater Boston Preferred Solution (February 18, 2015), PAC presentation, http://www.iso-ne.com/static-assets/documents/2015/02/a2_isone_greater_boston_preferred_solution_non_ceii.pdf.

Greater Boston Area Transmission Needs Assessment (July 2010) can be accessed at http://www.iso-ne.com/system-planning/key-study-areas/greater-boston. Draft Greater Boston Area Transmission Solutions Study (June 30, 2015), https://smd.iso-ne.com/planning/ceii/reports/2010s/greater_boston_solution_study_report_draft.pdf.

The ISO had previously identified a preferred AC solution from several considered alternatives for the area. At the request of stakeholders, the ISO began evaluating another alternative offered after the close of the original alternative review and after a preferred solution was identified. ISO New England, “Greater Boston Key Study Area,” webpage, http://www.iso-ne.com/system-planning/key-study-areas/greater-boston.

Evaluation of Need for Footprint Combined Cycle for the 2016/2017 and 2017/2018 Capacity Commitment Periods Summary Report (August 2014), https://smd.iso-ne.com/committees/comm_wkgrps/relblty_comm/relblty/ceii/ceii_mtrls/2014/aug152014/a4_footprint_power_evaluation_of_need_report.pdf.

Advanced Greater Boston Solutions—Update, PAC presentation (June 19, 2014), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2014/jun192014/a7_greater_boston_north_cambridge_stuck_breaker.pdf.

NSTAR Underground Cable Ratings Update, PAC presentation (April 2013), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2013/apr242013/a10_nstar_greater_boston_cable_ratings.pdf.

Greater Boston Study Needs Assessment/Solution Study Status Update, PAC presentation (March 2012), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2012/mar142012/gbwg_update.pdf.

Pittsfield-Greenfield, MA, Area Transmission 2022 Needs Assessment (December 6, 2013), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/reports/2013/a_pittsfield_greenfield_2022_needs_assessment_final.pdf. Pittsfield-Greenfield 2022 Needs Assessment: N-1 and N-1-1 Results, PAC presentation (July 9, 2013), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2013/jul92013/a4_pittsfield_greenfield_needs_assessment_rev1.pdf.

Pittsfield-Greenfield MA, Area Transmission Solution Study (March 30, 2012), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/reports/2012/pitt_green_solution_report.pdf.

Pittsfield-Greenfield 2022 Solutions Study, PAC presentation (April 28, 2015), https://smd.iso-ne.com/planning/ceii/reports/2010s/archive/a8_pittsfield_greenfield_2022_solutions_study_rev2.pdf. RLC Engineering, Pittsfield-Greenfield Area 2022 Solutions Study, draft report prepared for ISO New England, Eversource Energy, and National Grid (September 11, 2015), https://smd.iso-ne.com/operations-services/ceii/pac/2015/09/draft_pga_2022_solutions_study_report.docx.

See the “Southeastern Massachusetts and Rhode Island Key Study Area” webpage; http://www.iso-ne.com/system-planning/key-study-areas/sema-ri.

National Grid, Newport, RI (Aquidneck Island) Transmission Area Improvements—Needs and Preferred Solution, PAC presentation (April 28, 2015), https://smd.iso-ne.com/operations-services/ceii/pac/2015/04/newport_aquidneck_island_transmission_area_improvements_presentation.pdf.

SWCT Area Transmission Needs Assessment (July 13, 2011), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/reports/2011/final_swct_needs_report.pdf.

SWCT Update on Continuing Alternatives Analyses (November 16, 2011), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2011/nov162011/swct_solution_study.pdf.

Southwest Connecticut Advanced Solutions Introduction (April 13, 2011), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2011/apr132011/swct_adv_sol_intro.pdf.

SWCT Advanced Solutions Mill River to Quinnipiac 8300 Line Reconfiguration Project (April 13, 2011), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2011/apr132011/8300_line.pdf.

SWCT Advanced Solutions Stamford Reliability Project (April 13, 2011), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2011/apr132011/stamford.pdf.

Southwest Connecticut 2022 Needs Assessment (May 23, 2013), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2013/may232013/a3_swct_needs_assessment_052313.pdf.

Southwest Connecticut 2022 Needs Assessment II (February 19, 2014), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2014/feb192014/a9_swct_needs_assessment_2.pdf. Southwest Connecticut Area Transmission 2022 Needs Assessment (June 2014), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/reports/2014/final_swct_2022_needs.pdf.

Southwest Connecticut 2022 Preferred Solution Selection (July 15, 2014), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2014/jul152014/a9_swct_2022_preferred_solutions.pdf. Southwest Connecticut Area Transmission 2022 Solutions Study (February 12, 2015), https://smd.iso-ne.com/planning/ceii/studies/ct/final_swct_2022_solutions_study.pdf.

The need for replacing the Freight 115 kV circuit breakers is conditional on QP 384 (i.e., the project in public queue position 384).

The work for the Baird 115 kV bus upgrade only includes the work identified through the SWCT study and does not include any of the work from the separate Baird Substation solutions study presented to the PAC. Baird 115/13.8 kV Substation Solutions Study (June 19, 2014), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2014/jun192014/a8_baird_substation_study.pdf.

As part of the development of solutions under the original solutions study in SWCT, the preferred solution for meeting short-circuit criteria at Pequonnock was to delay the circuit-breaker fault-clearing time to reduce the interrupt duty. The solution includes the complete replacement of the transmission control house and relays to incorporate the additional time delay in the tripping logic. With the retirement of Norwalk Harbor station and Bridgeport Harbor 2, the control house and new relays are no longer needed. However, the need persists to replace bus work and disconnects at the Pequonnock station to address short-circuit concerns.

Greater Hartford and Central Connecticut Working Group (ISO New England, Northeast Utilities, and United Illuminating), Greater Hartford and Central Connecticut Area Transmission 2022 Needs Assessment (April 2014), http://www.iso-ne.com/system-planning/key-study-areas/greater-hartford.

Greater Hartford and Central Connecticut Area (GHCC) Solutions Study II (July 15, 2014), http://www.iso-ne.com/system-planning/key-study-areas/greater-hartford. Greater Hartford and Central Connecticut (GHCC) Area Transmission 2022 Solutions Study (March 2015), https://smd.iso-ne.com/planning/ceii/reports/final_ghcc_solutions_study_report.pdf.

The SWCT Proposed Plan Application study identified low-voltage violations in the southern portion of the Middletown subarea due to a recent updated local-area load distribution forecast in the area. GHCC–Middletown Subarea 115 kV Capacitor Bank Modifications, PAC presentation (March 24, 2015), https://smd.iso-ne.com/operations-services/ceii/pac/2015/03/a3_ghcc_middletown_cap_banks_update.pdf.

Same as above note.

Eastern Connecticut Area Needs Assessment Updates, PAC presentation (July 9, 2013), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2013/jul92013/a3_eastern_ct_final_needs_assessment.pdf.

Eastern Connecticut Area Transmission 2022 Needs Assessment (June 2015), https://smd.iso-ne.com/planning/ceii/reports/2010s/final_eastern_ct_2022_needs_assessment_report.pdf.

Western Massachusetts Transmission Reinforcements 2007 to 2017 (September 2007), http://www.iso-ne.com/committees/comm_wkgrps/relblty_comm/relblty/mtrls/2007/oct102007/zip2_western_ma_ppa.zip.

National Grid, Auburn St. Substation Upgrades System Impact Study (November 2007) and Auburn St. Substation and Area Transmission System Reliability Study (July 2007), http://www.iso-ne.com/committees/comm_wkgrps/relblty_comm/relblty/mtrls/2007/dec192007/Zip%203%20auburn%20area.zip.

Greater Rhode Island Transmission Reinforcements (March 2008), http://www.iso-ne.com/committees/comm_wkgrps/relblty_comm/relblty/mtrls/2008/apr152008/zip1_gri-study-reports.zip.

National Grid, PPA withdrawal letter to the ISO (May 13, 2015), https://smd.iso-ne.com/operations-services/ceii/rc/2015/05/a3_7_greater_ri_ppa_withdrawal_letter.pdf.

Advanced Greater Boston Solutions, (December 2013), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2013/dec182013/a6_nu_advanced_greater_boston_solutions.ppt.

Advanced Greater Boston Solutions, see footnote 213.

Advanced Greater Boston Solutions—West Walpole to Holbrook N-1-1 Loss of Load, Needs and Preferred Solution (February 2014), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2014/feb192014/a4_advanced_greater_boston_west_walpole_to_holbrook_needs_and_solutions.pdf.

Advanced Greater Boston Solutions—Update, PAC presentation (June 19, 2014), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2014/jun192014/a7_greater_boston_north_cambridge_stuck_breaker.pdf.

PAC materials and meeting minutes are available at http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/index.html. The RSP Project List (XLS file) is available at http://www.iso-ne.com/system-planning/system-plans-studies/rsp.

Regional transmission service is comprised of regional network service (RNS) and through-or-out (TOUT) service. RNS is the transmission service the ISO provides over the PTFs, described in the OATT, Part II.B, that network customers use to serve load within the New England Control Area. The ISO’s TOUT service over the PTFs allows a real-time market transaction to be exported out of or “wheeled through” the New England area, including services used for network resources or regional network load not physically interconnected with a PTF. The PTO Administrative Committee is expected to make a supplemental filing on or before February 28, 2015, that will update New England Power Company’s transmission revenue requirement, which will revise the 2014 regional transmission service rates. See FERC, letter order to National Grid, Docket No. ER14-1686-000 (June 6, 2014), http://www.ferc.gov/CalendarFiles/20140606132455-ER14-1686-000.pdf.

NCPC is a payment to a supply resource that responded to the ISO’s dispatch instructions but did not fully recover its start-up and operating costs in either the Day-Ahead or Real-Time Energy Markets.

RSP15 2014 Historical Market Data: Locational Marginal Prices Interface MW Flows, PAC presentation, slide 7 (January 21, 2015), http://www.iso-ne.com/static-assets/documents/2015/01/a5_2014_lmps_interface_mw_flows.pdf.

ISO New England Inc. and New England Power Pool, Market Rule 1 Revisions to the NCPC Credit Rules; Docket No. ER14-___-000, FERC filing (January 24, 2014), http://www.iso-ne.com/static-assets/documents/regulatory/ferc/filings/2014/jan/er14_1147_1_24_2014_rev_ncpc_credit_rules.pdf.

This total includes seven projects in 2002, 26 projects in 2003, 30 projects in 2004, 51 projects in 2005, 55 projects in 2006, 36 projects in 2007, 64 projects in 2008, 38 projects in 2009, 37 projects in 2010, 44 projects in 2011, 61 projects in 2012, 91 projects in 2013, 66 projects in 2014, and 28 additional projects through June 2015. The June 2015 RSP Project List shows that 37 more projects are due in service by the end of 2015.

More information about NERC is available at http://www.nerc.com/.

Additional information on the EIPC is available at http://www.eipconline.com/.

EIPC, Steady State Modeling and Load Flow Working Group Report for 2018 and 2023 Roll-Up Integration Cases, Final Report (February 14, 2014), http://www.eipconline.com/uploads/FINAL_EIPC_Roll-up_Report_Feb14-2014.pdf.

Scenario information is available at the EIPC webpage, “Non-DOE Documents,” http://www.eipconline.com/Non-DOE_Documents.html. Information on stakeholder activities is available at http://www.eipconline.com/Stakeholder_Activities.html.

See NERC’s “Reliability Assessment and Performance Analysis,” webpage (2013), http://www.nerc.com/pa/RAPA/Pages/default.aspx.

NERC, 2014 Long-Term Reliability Assessment (November 2014), http://www.nerc.com/pa/RAPA/ra/Reliability%20Assessments%20DL/2014LTRA_ERATTA.pdf.

See NERC’s 2014 Probabilistic Assessment (April 2015), which examines resource adequacy from an unserved energy perspective; http://www.nerc.com/pa/RAPA/ra/Reliability%20Assessments%20DL/2014ProbA%20April%20Report%20Final_Final.pdf.

IRC, “Reports and Filings,” webpage (2014), http://www.isorto.org/Reports/default.

ISO/RTO Council, ISO Comments to FERC Regarding Coordination of Interstate Natural Gas Pipelines Scheduling Processes, FERC filing (November 25, 2014), http://www.isorto.org/ircreportsandfilings/iso-comments-to-ferc-regarding-coordination-of-interstate-natural-gas-pipelines-scheduling-processes (http://ircweb.businesscatalyst.com/Documents/Report/20141125_IRCComments-FERC-InterstateNaturalGasPipelineScheduling.pdf).

The NPCC region covers nearly 1.2 million square miles populated by more than 55 million people. NPCC in the United States includes the six New England states and the state of New York. NPCC Canada includes the provinces of Ontario, Québec, and the Maritime provinces of New Brunswick and Nova Scotia. As full members, New Brunswick and Nova Scotia also ensure that NPCC reliability issues are addressed for Prince Edward Island.

Northeastern ISO/RTO Planning Coordination Protocol (2004), http://www.iso-ne.com/static-assets/documents/committees/comm_wkgrps/othr/ipsac/rto_plan_prot/planning_protocol.pdf.

All IPSAC materials are available at http://www.iso-ne.com/committees/planning/ipsac.

ISO New England, New York ISO, and PJM, 2013 Northeast Coordinated System Plan (April 16, 2014), http://www.iso-ne.com/static-assets/documents/committees/comm_wkgrps/othr/ipsac/mtrls/2014/mar282014/2013_ncsp.pdf.

New England 2015 Regional System Plan Load, Energy, and Capacity Resource Overview, PAC presentation (April 28, 2015), http://www.iso-ne.com/static-assets/documents/2015/04/a3_rsp15_load_capacity_resource_overview.pdf.

Energy imports were 1,622 GWh over Highgate and 11,612 GWh over Phase II.

2013 ISO New England Electric Generator Air Emissions Report (December 2014), http://www.iso-ne.com/static-assets/documents/2014/12/2013_emissions_report_final.pdf.

ISO New England, “Strategic Planning Initiative,” webpage (2015), http://www.iso-ne.com/committees/key-projects/strategic-planning-initiative.

Approximately 838 MW of fossil-fired steam generating capacity at Mount Tom, Bridgeport Harbor, and Salem Harbor stations and the 641 MW Vermont Yankee nuclear unit retired during 2014. In addition, the approximately 1,535 MW Brayton Point Station is scheduled to retire by June 1, 2017.

“ISO New England Status of Non-Price Retirement Requests” (November 21, 2014), http://www.iso-ne.com/static-assets/documents/2014/09/npr_tracking_external.pdf.

Neptune LNG LLC’s request to the Maritime Administration to suspend its Deepwater Port License was approved as of June 26, 2013, for a five-year period. Neptune has the right to restart port operations before June 26, 2018, with six months’ prior notice to the Maritime Administration and if certain conditions established in Neptune’s Suspension Plan have been satisfied.

Marcellus shale gas is a recently developed source of natural gas located in central Pennsylvania.

LNG storage facilities can, on short notice, vaporize gas for injection into the New England pipelines and thus help the region meet peak demand. These facilities may require advance contracting, however, to assure adequate on-site liquid storage.

SNL Financial, Spot natural gas index average pricing for Algonquin City Gate (Boston); Tennessee Gas Pipeline, Dracut; and Tennessee Gas Pipeline, Zone 4. Marcellus pricing point from November 3, 2013, through March 31, 2015.

FERC, Communication of Operational Information between Natural Gas Pipelines and Electric Transmission Operators, Order No. 787, final rule (November 15, 2013), http://www.ferc.gov/CalendarFiles/20131115164637-RM13-17-000.pdf.

ISO New England, Pipeline Information-Sharing Changes, FERC filing (January 10, 2014), http://www.iso-ne.com/regulatory/ferc/filings/2014/jan/er14-970-000_1-10-2014_pipe_inf_sharing.pdf.

FERC, Coordination of the Scheduling Processes of Interstate Natural Gas Pipelines and Public Utilities, 151 FERC ¶ 61,049, final rule (April 16, 2015), http://www.ferc.gov/whats-new/comm-meet/2015/041615/M-1.pdf (Scheduling Coordination Final Rule).

FERC, Order Initiating Investigation into ISO and RTO Scheduling Practices and Establishing Paper Hearing Procedures (March 20, 2014), http://www.ferc.gov/whats-new/comm-meet/2014/032014/M-2.pdf.

“Winter 2013/2014 Reliability Solutions Key Project,” webpage (2015); http://www.iso-ne.com/committees/key-projects/winter-2013-2014-reliability-solutions, and “Winter 2014/2015 Reliability Solutions Key Project,” webpage (2015); http://www.iso-ne.com/committees/key-projects/implemented/winter-2014-2015-reliability-solutions.

”Bbls” refers to “blue barrels,” the traditional name of the units of oil purchased at 42 gallons/bbls.

The ISO performs the Reserve Adequacy Analysis at the close of the reoffer period for the Day-Ahead Energy Market to ensure that adequate resources are committed for meeting the forecasted load and operating-reserve requirements for the Real-Time Energy Market.

FERC, Coordination of the Scheduling Processes of Interstate Natural Gas Pipelines and Public Utilities, final rule, 151 FERC ¶ 61,049 (April 16, 2015), http://www.ferc.gov/whats-new/comm-meet/2015/041615/M-1.pdf.

DOE/Energy Information Administration (EIA), Annual Energy Outlook 2014 (AEO 2014), Table 132, “Lower 48 Natural Gas Production and Supply Prices by Supply Region—Reference Case.” The statistics are for dry gas production, which is natural gas that has been processed to remove heavier hydrocarbons (i.e., natural gas liquids—pentane, butane, ethane, and others).

ICF International (ICF), Gas-Fired Power Generation in Eastern New York and its Impact on New England’s Gas Supplies, white paper (November 18, 2013), http://www.iso-ne.com/static-assets/documents/committees/comm_wkgrps/prtcpnts_comm/pac/mtrls/2013/nov202013/icf_upstream_gen_impacts_white_paper_11_18_2013.pdf.

ICF, Assessment of New England’s Natural Gas Pipeline Capacity to Satisfy Short and Near-Term Electric Generation Needs: Phase II (December 16, 2013), http://www.iso-ne.com/static-assets/documents/2014/11/final_icf_phii_gas_study_report_with_appendices_112014.pdf. See additional scenarios in the ICF PAC presentation, Winter 2013/14 Benchmark and Revised Projections for New England Natural Gas Supplies and Demand (April 29, 2014), http://www.iso-ne.com/static-assets/documents/committees/comm_wkgrps/prtcpnts_comm/pac/mtrls/2014/apr292014/a3_icf_benchmarking_study.pdf.

EIPC, “Gas-Electric System Interface Study,” webpage (2014), http://www.eipconline.com/Gas-Electric.html. During 2013, the six EIPC participating planning authorities (ISO New England, NYISO, PJM, TVA, MISO, and the Independent Electricity System Operator [IESO] of Ontario), added natural gas-sector representation to the Stakeholder Steering Committee.

EIPC, “Gas-Electric Documents,” webpage (2015), http://www.eipconline.com/Gas-Electric_Documents.html.

The base case assumed sendout at the existing Canaport and Distrigas LNG storage facilities below their full capability.

Under an emissions trading program, an emissions allowance is the authorization for a source of a pollutant to emit one ton of the pollutant (e.g., SO2, nitrogen oxides [NOX,] or carbon dioxide [CO2]) during a specific compliance period.

RGGI is a mandatory, market-based effort to reduce greenhouse gas emissions in the Northeast and Mid-Atlantic states through a multistate CO2 emissions budget cap-and-trade program.

EPA, National Pollutant Discharge Elimination System—Final Regulations to Establish Requirements for Cooling Water Intake Structures at Existing Facilities and Amend Requirements at Phase I Facilities, final rulemaking, 79 FR 48299 (August 15, 2014); applies to existing and new cooling water intake structures at power plants and manufacturers. EPA, Effluent Limitation Guidelines and Standards for the Stream Electric Power Generating Point Source Category, proposed rule, 78 FR 34431 (June 7, 2013). The main pollutants of concern for these discharges include metals (mercury, arsenic, and selenium), nitrogen, and total dissolved solids generated by the operation of air pollution control devices (i.e., scrubbers). As of September 22, 2015, EPA has not finalized the latter rule.

Timothy H. Diehl and Mellissa A. Harris, Withdrawal and Consumption of Water by Thermoelectric Power Plants in the United States, 2010, US Geological Survey Scientific Investigations Report 2014–5184 (US Geological Survey, 2014), http://dx.doi.org/10.3133/sir20145184.

The requirement for reducing impingement mortality recognizes seven compliance alternatives that regulators may require: (1) operate a closed-cycle recirculating system; (2) operate a cooling water intake structure with a maximum through-screen design intake velocity of 0.5 feet per second (fps); (3) operate a cooling water intake structure with a maximum through-screen intake velocity of 0.5 fps; (4) operate an offshore velocity cap installed before the effective date of this rule; (5) operate a modified traveling screen that regulators determine is the best technology available for impingement reduction; (6) operate any other combination of technologies, management practices, and operational measures that regulators determine is the best technology available for impingement reduction; or (7) achieve the specified impingement mortality performance standard. EPA, NPDES— Final Cooling Water Intake Structures Regulations, 48299, see footnote 262.

US Department of the Interior, Endangered Species Act of 1973, as amended through the 108th Congress, http://www.fws.gov/endangered/esa-library/pdf/ESAall.pdf. EPA stated it will use the full extent of its Clean Water Act authority to object to a state permit it finds likely to jeopardize the continued existence of any listed species or destroy or adversely modify critical habitat. (79 FR at 48383). In New England, listed endangered species include the Atlantic salmon, Atlantic sturgeon, shortnose sturgeon, and dwarf wedgemussel; their critical habitats are found near several generators.

The calculation for affected capacity was based on the 2015 CELT Report summer SCC values for individual generators at affected facilities.

US EPA, CWA, final rule, 48372.

EPA, Effluent Limitation Guidelines and Standards for the Steam Electric Power Generating Point Source Category, prepublication final rule (September 30, 2015), http://www2.epa.gov/sites/production/files/2015-09/documents/steamelg_2040-af14_finalrule_preamble_2015-09-30_prepub.pdf. The final rule revises existing (circa 1982) wastewater effluent limitation guidelines for power plants to address the changing toxicity of power plant wastewater discharges from scrubbers and other air pollution control systems required by air quality regulations. Materials of concern include aluminum, arsenic, manganese, mercury, nitrogen, phosphorus, selenium, vanadium and zinc.

The calculation for affected capacity was based on 2015 CELT Report summer SCC values for individual generators at affected facilities.

Capital costs for an ELG-compliant wastewater discharge treatment system at a coal-fired facility in New England were reported to total $36.4 million (2011 dollars); annual overhead and maintenance costs are estimated at $1.52 million (2011 dollars).

US EPA, Clean Air Act, 42 USC §7401 et seq. (1970), http://www2.epa.gov/laws-regulations/summary-clean-air-act.

EPA, National Ambient Air Quality Standards for Ozone, final rule, 80 Fed. Reg. 65292 (October 26, 2015), https://www.federalregister.gov/articles/2015/10/26/2015-26594/national-ambient-air-quality-standards-for-ozone.

EPA, National Ambient Air Quality Standards for Ozone, proposed rule, 79 FR 75233 (December 17, 2014); National Ambient Air Quality Standards for Particulate Matter, final rule, 78 FR 3086 (January 15, 2013); National Ambient Air Quality Standards for Sulfur Dioxide, final rule, 75 FR 35520 (June 22, 2010).

Supreme Court of the United States, Michigan et al., v. EPA et al. 576 U. S. ____ (June 29, 2015), http://www.supremecourt.gov/opinions/14pdf/14-46_bqmc.pdf.

See footnote 271.

Dennis A. Wentz, Mark E. Brigham, et al., Mercury in the Nation’s Streams—Levels, Trends, and Implications, US Geological Survey Circular 1395, (USGS, 2014), http://pubs.usgs.gov/circ/1395/.

EPA, National Emission Standards for Hazardous Air Pollutants: Coal- and Oil-Fired Electric Utility Steam Generating Units, final rule, 77 FR 9304 (February 16, 2012). EPA developed standards under Section 112(d) to reduce hazardous air pollutant emissions from this source category. MATS was proposed on May 3, 2011 (76 FR 24976) and included proposed amendments to the criteria pollutant NSPS for utilities.

See footnote 271.

2013 ISO New England Electric Generator Air Emissions Report (December 2014), http://www.iso-ne.com/static-assets/documents/2014/12/2013_emissions_report_final.pdf.

RGGI, Inc., “Program Overview,” webpage (n.d.), http://www.rggi.org/design/overview. The RGGI CO2 budget (cap) is equal to the total number of CO2 allowances issued by RGGI states in a given year. A CO2 allowance represents a limited authorization to emit one short ton of CO2 from a regulated source, as issued by a participating state. During the current control period (2012–2014), the cap is 165 million short tons of CO2/yr for the nine-state region.

RGGI, Inc., “Updated Model Rule,” on 2012 Program Review webpage (February 7, 2013), http://www.rggi.org/design/program-review.

EIA, Regional Greenhouse Gas Initiative Auction Prices Continue to Rise (September 18, 2014), http://www.eia.gov/todayinenergy/detail.cfm?id=18031.

EPA, Carbon Pollution Emission Guidelines for Existing Stationary Sources: Electric Utility Generating Units, final rule 80 Fed. Reg. 64661–65120 (October 23, 2015), http://www.gpo.gov/fdsys/pkg/FR-2015-10-23/pdf/2015-22842.pdf.

EPA calculated the individual state Clean Power Plan mass-based (short tons) reduction goals by multiplying adjusted historical (2012) electric generation data (affected generator MWh) by the individual state-emission-rate goals and then adjusted the results by forecasted additional renewable energy generation (MWh). EPA Clean Power Plan Technical Support Document: Emissions Performance Rate and Goal Computation, appendix-1-5 (August 2015); http://www.epa.gov/airquality/cpp/tsd-cpp-emission-performance-rate-goal-computation-appendix-1-5.xlsx.

Clean Power Plan state plans must (1) a describe the plan approach and geographic scope; (2) state the applicability of state plans to affected generators; (3) demonstrate that the plan will achieve specified CO2 emissions reductions; (4) include monitoring, reporting, and recordkeeping requirements for generators; (5) include state reporting requirements to EPA; and (6) document public participation and legal authority for developing and submitting the plan. EPA, Carbon Pollution Emission Guidelines for Existing Stationary Sources: Electric Utility Generating Units, final rule (October 23, 2015). EPA, “Clean Power Plan Final Rule,” webpage (August 2015), http://www2.epa.gov/cleanpowerplan/clean-power-plan-final-rule and http://www.gpo.gov/fdsys/pkg/FR-2015-10-23/pdf/2015-22842.pdf.

“ISO New England Issues Statement on Entergy’s Announcement to Retire Vermont Yankee Nuclear Plant,” press release (August 27, 2013), http://www.iso-ne.com/nwsiss/pr/2013/iso_new_england_issues_statement_vy_retirement_final.pdf. The ISO studied the needs of the high-voltage power system serving Vermont and New Hampshire and concluded system reliability will be maintained.

Nuclear Regulatory Commission, Continued Storage of Spent Nuclear Fuel, final rule, 79 Fed. Reg. 56238 (September 19, 2014). The rulemaking replaces NRC’s Waste Confidence Rule (governing onsite storage of spent nuclear fuel) struck down in 2012 (New York v. NRC, 681 F.3d 471 (D.C. Cir. 2012).

FERC, Hydropower Licensing webpage (June 10, 2013), http://www.ferc.gov/industries/hydropower/gen-info/licensing.asp.

FERC, Modification to Integrated Licensing Process Schedule, Transcanada Hydro Northeast, Inc., and Firstlight Hydro Generating Company (December 21, 2012); Connecticut River Joint Commission, Relicensing of Connecticut River Dams (Accessed February 18, 2014).

NREL, The Western Wind and Solar Integration Study Phase 2, NREL/TP-5500-55588, technical report (DOE, September 2013), http://www1.eere.energy.gov/wind/pdfs/55588.pdf.

Note that the Aroostook, ME, region is considered to need major transmission line construction. ISO New England, Northern Maine System Performance, PAC presentation (September 21, 2010), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2010/sep212010/northern_maine.pdf.

Strategic Transmission Analysis: Wind Integration Study—Stage 1—Maine, Regional Constraints, PAC presentation (May 21, 2014), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2014/may212014/a4_strategic_transmission_analysis_wind_power_update.pdf.

TCSCs are series capacitors that can change their impedance within a fraction of a cycle. They are a type of flexible alternating-current transmission system (FACTS) device that uses a thyristor—a power electronics component that provides the ability to switch output. (See Section 11.3.1 for more on FACTS devices.)

Strategic Transmission Analysis: Wind Integration Study, PAC presentation (December 18, 2013), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2013/dec182013/a4_wind_study.pdf.

On December 27, 2012, the DOE Solar Program awarded funding to the IBM Thomas J. Watson Research Center (DOE Award No. DE-EE0006017). More information is available at DOE, “Improving the Accuracy of Solar Forecasting Funding Opportunity,” webpage (n.d.), http://energy.gov/eere/sunshot/improving-accuracy-solar-forecasting-funding-opportunity and DOE, “Watt-Sun: A Multiscale, Multimodel, Machine-Learning Solar Forecasting Methodology,“ web article (n.d.), http://energy.gov/eere/sunshot/watt-sun-multi-scale-multi-model-machine-learning-solar-forecasting-technology.

EPRI, Recommended Settings for Voltage and Frequency Ride-Through of Distributed Energy Resources (May 8, 2015), http://www.epri.com/abstracts/Pages/ProductAbstract.aspx?ProductId=000000003002006203.

Institute of Electrical and Electronics Engineers (IEEE) 1547 establishes criteria and requirements for the interconnection of distributed resources with electric power systems. This document provides a uniform standard for the performance, operation, testing, safety considerations, and maintenance of the interconnection. See “IEEE 1547 Standard for Interconnecting Distributed Resources with Electric Power Systems,” webpage (2014), http://grouper.ieee.org/groups/scc21/1547/1547_index.html.

IEEE 1547 and interconnection requirements for low/high-voltage ride through, low/high-frequency ride through, ramp rates, and others.

DG Interconnection Issues, PAC presentation (July 7, 2015), http://www.iso-ne.com/static-assets/documents/2015/07/a2_dg_interconnection_issues_update.pdf.

NREL, “Eastern Renewable Generation Integration Study,” webpage (2015), http://www.nrel.gov/electricity/transmission/eastern_renewable.html.

EnerNex, Eastern Wind Integration and Transmission Study (NREL, 2011), http://www.nrel.gov/docs/fy11osti/47078.pdf.

ISO New England, 2012 Economic Study, final report (April 30, 2014), http://www.iso-ne.com/static-assets/documents/committees/comm_wkgrps/prtcpnts_comm/pac/reports/2014/a9_2012_economic_study_final.pdf, and 2011 Economic Study, final report (March 31, 2014), http://www.iso-ne.com/static-assets/documents/committees/comm_wkgrps/prtcpnts_comm/pac/reports/2014/2011_eco_study_final.pdf. The 2013 Economic Study (October 30, 2014), http://www.iso-ne.com/static-assets/documents/2014/10/2013_economic_study_final.pdf.

2015 Economic Studies Keene Road Upgrades Scope of Work—Revised Draft, PAC presentation (June 17, 2015), http://www.iso-ne.com/static-assets/documents/2015/06/a9_2015_economic_studies_keene_rd_upgrades_scope_of_work_revised_draft.pdf. 2015 Economic Studies Strategic Transmission Analysis—On-Shore Wind Integration Scope of Work—Revised Draft, PAC presentation (June 17, 2015), http://www.iso-ne.com/static-assets/documents/2015/06/a9_2015_economic_studies_on_shore_wind_integration_scope_of_work_revised_draft.pdf. 2015 Economic Study—Off-Shore Wind Scope of Work—Revised Draft, PAC presentation (June 17, 2015), http://www.iso-ne.com/static-assets/documents/2015/06/a9_2015_economic_studies_off_shore_wind_scope_of_work_revised_draft.pdf.

ISO New England, Generic Capital Costs of Supply-Side Resources, PAC presentation (April 28, 2015), http://iso-ne.com/static-assets/documents/2015/04/a4_generic_costs_of_supply_resources.pdf.

EIA, Assumptions to the Annual Energy Outlook 2014, “Electricity Market Module” (2014), www.eia.gov/forecasts/aeo/assumptions/pdf/electricity.pdf, and Capital Cost for Electricity Plants (April 12, 2013), www.eia.gov/forecasts/capitalcost/.

EPRI, Program on Technology Innovation: Integrated Generation Technology Options 2012 (February 10, 2013), www.epri.com/abstracts/Pages/ProductAbstract.aspx?productId=000000000001026656.

ISO New England, "Net CONE Estimates for Potential Reference Technologies," Excel table (March 2014), www.iso-ne.com/static-assets/documents/committees/comm_wkgrps/mrkts_comm/mrkts/mtrls/2014/mar192014/a02_iso_net_cone_capital_budgeting_model_03_14_14.xlsx, and “Summary of Construction Cash Flows" Excel table (September 2013), www.iso-ne.com/static-assets/documents/committees/comm_wkgrps/mrkts_comm/mrkts/mtrls/2013/oct892013/a06_iso_ortp_analysis_final_results_10_02_13.xlsx.

WECC, Capital Cost Review of Power Generation Technologies (March 2014), www.wecc.biz/Reliability/2014_TEPPC_Generation_CapCost_Report_E3.pdf.

Energy Policy Act of 2005, Pub. L. 109-58, Title XII, Subtitle B, 119 Stat. 594 (2005) (amending the Federal Power Act to add a new § 216).

FERC, Order on Rehearing and Compliance, 150 FERC ¶ 61,209 (March 19, 2015), http://www.iso-ne.com/static-assets/documents/2015/03/er13-193_er13-193_order_on_rehearing_and_order_no_1000_compliance_filings.pdf.

See footnote 248 (http://www.ferc.gov/whats-new/comm-meet/2015/041615/M-1.pdf).

ISO-NE, et al., Docket No. EL14-23-000, Filing to Show Cause Why Tariff Changes to Adjust Timing of Day-Ahead Energy Market Results and Reliability Unit Commitment Process are Not Necessary, FERC filing (July 23, 2015), http://www.iso-ne.com/static-assets/documents/2015/07/el14-23-000.pdf.

CAISO, ISO-NE, MISO, NYISO, PJM, Southwest Power Pool, 2010 ISO/RTO Metric Report (December 6, 2010), http://www.iso-ne.com/static-assets/documents/regulatory/ferc/filings/2010/dec/ad10_5_000_12_6_10_metrics_report.pdf and 2011 ISO/RTO Metrics Report (August 31, 2011), http://www.iso-ne.com/static-assets/documents/regulatory/ferc/filings/2011/aug/ad10_5_00_8_31_11_joint_iso_rto_metrics_report.pdf. Also see FERC, “RTO/ISO Performance Metrics,” webpage (2015), http://www.ferc.gov/industries/electric/indus-act/rto/rto-iso-performance.asp.

FERC, Common Metrics (August 26, 2014), http://www.ferc.gov/legal/staff-reports/2014/AD14-15-performance-metrics.pdf.

FERC, Request for Information on Common Performance Metrics for RTOs and ISOs and Utilities Outside RTO and ISO Regions, 80 Fed. Reg. 50847–50848 (August 21, 2015), http://www.gpo.gov/fdsys/pkg/FR-2015-08-21/html/2015-20743.htm. PJM, Common Performance Metrics, Docket No. AD14-15-000, ISO/RTO Joint Common Performance Metrics Report (October 30, 2015),] FERC filing and report, http://www.iso-ne.com/static-assets/documents/2015/10/ad14-15-000_10-30-15_iso-rto_common_metric_rpt.pdf.

FERC, Physical Security Reliability Standard, final rule (November 20, 2014), http://www.ferc.gov/whats-new/comm-meet/2014/112014/E-4.pdf.

NERC, Physical Security, CIP-014-1 (April 4, 2014), http://www.nerc.com/pa/Stand/Prjct201404PhsclScrty/CIP-014-1_Physical_Sec_draft_2014_0409.pdf.

Piedmont Environmental Council v. FERC, 558 F.3d 304 (4th Cir. 2009).

DOE, National Electric Transmission Congestion Study (September 2015), http://www.energy.gov/sites/prod/files/2015/09/f26/2015%20National%20Electric%20Transmission%20Congestion%20Study_0.pdf, and Report Concerning Designation of National Interest Electric Transmission Corridors  (September 2015), http://energy.gov/sites/prod/files/2015/09/f26/2015%20Report%20on%20Designation%20of%20National%20Corridors.pdf.

DOE cited the development of coordinated transaction scheduling (i.e., allowing bidders to specify the price difference for which they are willing to schedule trades) between ISO New England and NYISO.

DOE, “The Quadrennial Energy Review,” webpage (2015), http://energy.gov/epsa/quadrennial-energy-review-qer.

DOE, QER, page 10-12 (335) provides a review of both meetings; http://energy.gov/sites/prod/files/2015/05/f22/QER%20Full%20Report_0.pdf.

More information about NESCOE is available at www.nescoe.com.

Northeast Forum on Regional Energy Solutions, Hartford, CT (April 23, 2015), http://events.r20.constantcontact.com/register/event?llr=lad5xpeab&oeidk=a07eaur0da6f444cf33.

“New England Governors’ Statement on Regional Cooperation for Energy Infrastructure,” press release (April 23, 2015), http://portal.ct.gov/Departments_and_Agencies/Office_of_the_Governor/Press_Room/Press_Releases/2015/04-2015/New_England_Governors__Statement_on_Regional_Cooperation_for_Energy_Infastructure/.

New England Governors’ Statement Regional Cooperation on Energy Infrastructure (April 23, 2015), http://nescoe.com/resources/govs-stmt-apr2015/. New England States, New England Energy Update: Actions for a Cleaner, More Reliable and More Affordable Energy Future, six-state action plan (July 2015), http://nescoe.com/resources/govs-actions-apr2015/. Note that the extent of authority to procure clean energy resources on transmission differs by state.

ISO New England, “Presentations, Speeches, and Other Materials,” webpage, “External Affairs Monthly Issues Memo” document type, http://www.iso-ne.com/about/government-industry-affairs/materials.

Eric Runge, “Sector Caucus Representatives for the EIPC,” memorandum (June 23, 2010), http://www.iso-ne.com/committees/comm_wkgrps/othr/eipc/eipc_caucus_reps.doc.

The end-user sector in the NEPOOL stakeholder process and the ISO stakeholder committees also convey consumer interests. Additional information on the CLG is available at http://www.iso-ne.com/committees/consumer-liaison.

ISO New England and Consumer Liaison Group Coordinating Committee, 2014 Report of the Consumer Liaison Group (March 10, 2015), http://www.iso-ne.com/static-assets/documents/2015/03/2014_clg_report_final.pdf.

CT DEEP, MA Department of Energy Resources, Eversource Energy, National Grid, and Unitil “New England Clean Energy RFP,” webpage (2015), http://cleanenergyrfp.com/2015/02/25/draft-rfp-released/.

The Institute of Electrical and Electronics Engineers (IEEE) describes the smart grid as a “next-generation” electrical power system that typically employs the increased use of communications and information technology for generating, delivering, and consuming electrical energy. See the IEEE’s Smart Grid Community webpage for a full discussion of smart grid technology: https://www.ieee.org/membership-catalog/productdetail/showProductDetailPage.html?product=CMYSG735.

PMUs use global positioning satellite technology to monitor the performance of the region’s electric power grid accurately and provide specific data, including synchrophasor power system measurements, for use in operating the grid and enhancing grid design. The IEEE defines FACTS as flexible alternating-current transmission systems that incorporate power-electronics-based controllers and other static controllers to enhance controllability and power-transfer capability. See the IEEE’s Power and Energy Society’s webpage: http://www.ieee-pes.org/nari-hingorani-facts-award.

For additional information on PSERC and EPRI, refer to http://www.pserc.wisc.edu/home/index.aspx and http://www.epri.com/.

EIA, ”Electric Power Sales, Revenue, and Energy Efficiency Form EIA-861, detailed data files,” webpage (April 22, 2015) http://www.eia.gov/electricity/data/eia861/.

Additional information on the Smart Grid Interoperability Panel is available at http://www.sgip.org/.

ISO/RTO Council, “2013 North American Demand-Response Characteristics Comparison” (February 28, 2014), http://www.isorto.org/ircreportsandfilings/2013-north-american-demand-response-characteristics-available.

For more information on IEEE, see http://www.ieee.org/index.html.

State of Connecticut, An Act Concerning Affordable and Reliable Energy, Public Act No. 15-107 (June 2015), http://www.cga.ct.gov/2015/ACT/PA/2015PA-00107-R00SB-01078-PA.htm.

For more information on Connecticut’s Class I renewable energy resources, see the DEEP website, “Connecticut Renewable Portfolio Standards Overview,” http://www.ct.gov/pura/cwp/view.asp?a=3354&q=415186.

Maine PUC, et al., A Review of Natural Gas Capacity Options (March 2014), http://www.sussex-advisors.com/wp-content/uploads/2014/03/Maine-PUC-Final-Report-February-26-2014.pdf.

State of Maine, An Act to Reduce Energy Costs, Increase Energy Efficiency, Promote Electric System Reliability and Protect the Environment, HP1128 (June 5, 2013), http://www.mainelegislature.org/legis/bills/getPDF.asp?paper=HP1128&item=1&snum=126.

London Economics, Maine Energy Cost Reduction Act: Cost Benefit Analysis of ECRC Proposals, Prepared for the Maine PUC (June 2015), https://mpuc-cms.maine.gov/CQM.Public.WebUI/Common/ViewDoc.aspx?DocRefId={3FF03959-6F22-496F-BFC5-FC38D2BB9336}&DocExt=pdf.

MPUC, Docket No, 2014-00048.

State of Maine, Resolve, To Study Options for a State Demand-Response Program (HP 244-LD 357, Chapter 14) (passed May 17, 2015), http://www.mainelegislature.org/legis/bills/display_ps.asp?paper=HP0244&snum=127.

MA DPU, Investigation by the Department of Public Utilities on Its Own Motion into Modernization of the Electric Grid (November 5, 2014), http://www.mass.gov/eea/docs/dpu/electric/grid-mod/dpu-12-76-c-order-11-5-2014.pdf.

Petitions for Approval of Grid-Modernization Plans, MA DPU Dockets 15-120, 15-121, 15-122, and 15-123 (2015); see the MA Executive Office of Energy and Environmental Affairs’ docket-listing webpage; http://web1.env.state.ma.us/DPU/FileRoom/dockets/recent.

MA DPU, Investigation by the Department of Public Utilities on Its Own Motion into Time-Varying Rates (June 12, 2014), http://www.mass.gov/eea/docs/dpu/orders/d-p-u-14-04-b-order-6-12-14.pdf.

MA DPU, Investigation into New, Incremental Natural Gas Delivery Capacity for Thermal Load and Electric Generation, Docket No. 15-37 (opened April 2, 2015), http://web1.env.state.ma.us/DPU/FileRoom/dockets/recent.

State of New Hampshire, An Act Relative to Electric Rate Reduction Financing, SB221 (June 5, 2015), http://www.gencourt.state.nh.us/house/committees/billtext.aspx?billnumber=SB0221.html.

NH OEP, New Hampshire 10-Year State Energy Strategy (September 2, 2014), http://www.nh.gov/oep/energy/programs/documents/energy-strategy.pdf.

State of New Hampshire, An Act Implementing Goals of the State 10-Year Energy Strategy, Modifying Uses of the Site Evaluation Committee Fund, Establishing Fees for Energy Facility Evaluation, and Relative to Public Information Sessions on Proposed Energy Siting, HB216 (June 15, 2015), http://www.gencourt.state.nh.us/legislation/2015/HB0614.html.

State of New Hampshire, An Act Relative to the Siting of Energy Facilities, SB245 (June 4, 2014), http://www.gencourt.state.nh.us/legislation/2014/SB0245.pdf. State of New Hampshire, An Act Relative to the Divestiture of PSNH Assets, HB1602 (June 4, 2014), http://www.gencourt.state.nh.us/legislation/2014/HB1602.pdf.

State of New Hampshire, An Act Relative to the Divestiture of PSNH Assets and Relative to the Siting of Wind Turbines, HB 1602 (June 4, 2014), http://www.gencourt.state.nh.us/legislation/2014/HB1602.html.

State of New Hampshire, “Gas and Electric Utilities Energy-Efficiency Resource Standard,” Docket No. DE 15-137NH, webpage (2015), http://puc.nh.gov/Regulatory/Docketbk/2015/15-137.html.

NH PUC, Report on Investigation into Potential Approaches to Mitigate Wholesale Electricity Prices, IR 15-124 (September 15, 2015), http://puc.state.nh.us/Electric/Wholesale%20Investigation/IR%2015-124%20Staff%20Report.pdf.

In accordance with RI Gen. Laws § 39-26-6(d), the Rhode Island PUC reviewed the state’s RES to determine the adequacy, or potential adequacy, of renewable energy supplies to meet the increase in the percentage of energy required from these supplies to go into effect in 2015.

RI PUC, Order No. 21353, Docket No. 4404, Commission’s Review into the Adequacy of Renewable Energy Supplies pursuant to R.I. Gen. Laws § 39-26-6(d), (February 10, 2014).

State of Rhode Island, Affordable Clean Energy Security Act, S 2439 Substitute A, as amended, and H 7991 Substitute A (June 2014), http://webserver.rilin.state.ri.us/BillText/BillText14/SenateText14/S2439Aaa.pdf and http://webserver.rilin.state.ri.us/BillText/BillText14/HouseText14/H7991A.pdf.

State of Vermont, An Act Relating to Establishing a Renewable Energy Standard, Act 56, Vt. Biennial Session (signed into law, June 11, 2015); http://legislature.vermont.gov/assets/Documents/2016/Docs/ACTS/ACT056/ACT056%20As%20Enacted.pdf.