## All Approved 18.4 & I.3.9
Application ID | Application Date | Facility/Station | General Description | Expected In Service Date | ISO Action | ISO Action Date
http://www.iso-ne.com/system-planning/transmission-planning/proposed-plan-applications
VELCO-16-GNF02 | 2016-03-11 | SUDBURY SOLAR PROJECT | Generator notification from Vermont Electric Power Company (VELCO) on behalf of Sudbury Solar LLC for the installation of a 2.0 MW solar array located in Sudbury, VT and interconnecting via Line 5 Pole 70-3 on the GMP Leicester Substation Circuit #LJ13 | 2016-04-06 | Notification | 2016-04-01
ES-16-G06 | 2016-03-08 | EMC BELLINGHAM SOLAR PROJECT | Generator notification from Eversource Energy (ES) on behalf of EMC for the installation of a 1.44 MW solar array located in Bellingham, MA and interconnecting via the 13.2 kV 65-H4 circuit to the 552L1 feeder to the Medway Station #65. | March 2016 | Notification | 2016-04-01
NEP-16-GNF07 | 2016-03-09 | FOSTER SOLAR NORTH SCITUATE SOLAR PROJECT | Generator notification from New England Power Company (NEP) for the installation of a 1.17 MW solar array located in North Scituate, RI and interconnecting via the 12.47 kV 34F3 feeder to the Chopmist 34 substation. | 2016-04-30 | Notification | 2016-04-01
NEP-16-GNF06 | 2016-03-09 | BLAIR ENTERPRISE RUTLAND SOLAR PROJECT | Generator notification from New England Power Company (NEP) for the installation of a 1.98 MW solar array located in Rutland, MA and interconnecting via the 13.2 kV 552L1 feeder to the Meadow St. 552 substation. | 2016-04-06 | Notification | 2016-04-01
NEP-16-GNF05 | 2016-03-09 | SUN EDISON ORIGINATION 1 FOXBORO SOLAR PROJECT | Generator notification from New England Power Company (NEP) for the installation of a 2 MW solar array located in Foxboro, MA and interconnecting via the 13.8 kV 3432W2 feeder to the Foxboro 3432 substation. | 2016-04-08 | Notification | 2016-04-01
NEP-16-T04 | 2016-02-05 | Replacement of 345-115 kV Autotransformer at Carpenter Hill Substation | Transmission notification from New England Power Company (NEP) for the replacement of the 345/115 kV Autotransformer (268/358/448 MVA) at the Carpenter Hill Substation in Charlton, MA. | June 2016 | Approved | 2016-02-23
NEP-15-T13 | 2016-01-21 | South Street Substation and T1, T2, T3 115 kV Supply Rebuild | Transmission notification from New England Power Company (NEP) on behalf of Narragansett Electric to replace the existing 115 kV overhead transmission lines (T1, T2, T3) from Franklin Square to the South Street Substation with three new 2000 kcmil Cu XLPE insulated underground cables, 0.3 miles each | May/June 2019 | Approved | 2016-02-23
NHT-16-T01 | 2016-01-22 | Seabrook 345kV Substation Breaker Removal and Bus Upgrade Project | Transmission notification from New Hampshire Transmission (NHT) to perform Bus upgrades and breaker removals at the Seabrook Switchyard. Project will consist of two phases. Phase I will remove the 345kV GIS Breaker 22. Bus 4 becomes part of Bus 2 and Remove Bus 4 CCVTs since removal of Bus 4 eliminates need for Bus 4 CCVTs. Upgrade remainder of Bus 2 from 1981 ITE 3000A GIB to new 4000A CGIT GIB. Phase II will remove the old 345kV GIS Breaker 11 that is no longer a functioning breaker and instead has been locked closed and converted to a Gas Zone. Upgrade remainder of Bus 1 from 1981vintage GIB to new 4000A CGIT GIB | Phase 1 - Nov. 2016 Phase 2 - Nov. 2017 | Notification | 2016-02-23
NEP-16-GNF01 | 2016-02-08 | Twin Rivers Quincy Gas Generator Project | Generator notification from New England Power Company (NEP) on behalf of Twin River Technologies for the installation of a 2.052 MW natural gas synchronous generator located in Quincy, MA and interconnecting to the Field Street Substation via the 1202 & 1203 13.8 kV Feeders | 2015-12-14 | Notification | 2016-02-23
NEP-16-GNF02 | 2016-02-08 | Peterson Road Palmer Solar Project | Generator notification from New England Power Company (NEP) for the installation of a 2.55 MW solar array located in Palmer, MA and interconnecting to the Palmer 503 Substation via the 13.2 kV 503L1 feeder. | 2016-02-17 | Notification | 2016-02-23
NEP-16-GNF03 | 2016-02-08 | Solar City Andover Solar Project | Generator notification from New England Power Company (NEP) for the installation of a 1.71 MW solar array located in Andover, MA and interconnecting to the East Tewksbury 59 Substation via the 13.2 kV 59L5 feeder | 2016-03-01 | Notification | 2016-02-23
NEP-16-GNF04 | 2016-02-08 | Brookfield Wire West Brookfield Solar Project | Generator notification from New England Power Company (NEP) for the installation of a 1.612 MW solar array located in West Brookfield, MA and interconnecting to the Lashway 525 Substation via the 13.2 kV 525L2 feeder. | 2016-03-15 | Notification | 2016-02-23
NEP-07-T47 Rev. 2 | 2016-02-01 | Upgrade Auburn Street Substation Rev. 2 | Transmission notification from New England Power Company (NEP) to revise the Auburn Street Substation Project to match the” as built” transformer positions. | May 2013 | Notification | 2016-02-23
VELCO-16-GNF01 | 2016-02-04 | Ball Mountain Jamaica Hydro Project | Generator notification from Vermont Electric Power Company (“VELCO”) on behalf of Blue Heron Hydro, LLC for the installation of a 2.196 MW run-of-river hydro generator located in Jamaica, VT and interconnecting at the GMP Line 5052, Pole 29. | 2016-02-05 | Notification | 2016-02-23
ES-16-T02 | 2016-01-07 | PITTSFIELD/GREENFIELD AREA – GROUP II TRANSMISSION UPGRADES PROJECT | Transmission notification from Eversource Energy (ES) for the installation of the 7T circuit breaker at Northfield Mountain 345-kV Substation and connect a new 75-150 MVAR Variable Shunt Reactor into the 7T/8T position using a live tank circuit breaker. | December 2017 | Approved | 2016-01-26
ES-16-T03 | 2016-01-07 | PITTSFIELD/GREENFIELD AREA – GROUP II TRANSMISSION UPGRADES PROJECT | Transmission notification from Eversource Energy (ES) for the installation of a new 75-150 MVAR Variable Shunt Reactor and connect it to the 345-kV Bus 3B using a circuit breaker at the Ludlow 19S Substation. | December 2017 | Approved | 2016-01-26
ES-16-T04 | 2016-01-07 | PITTSFIELD/GREENFIELD AREA – GROUP II TRANSMISSION UPGRADES PROJECT | Transmission notification from Eversource Energy (ES) for the installation of a 115-kV 20.6 MVAR Capacitor Bank and connect it into the 3T/4T ring-bus position using a 115-kV synchronous closing circuit breaker. Also the Doreen 13T circuit breaker will be operated normally open. | December 2017 | Approved | 2016-01-26
NU-12-T35-Rev.1 | 2016-01-07 | PITTSFIELD/GREENFIELD AREA – GROUP II TRANSMISSION UPGRADES PROJECT | Transmission notification revision from Eversource Energy (ES) for the rebuild of the 1361/1242 double-circuit tower line from Montague 21C Substation to Cumberland 22B Substation using 556 kcmil ACSS conductor for each circuit. The remainder of the 1242 line from Cumberland 22B Substation to Berkshire 18C Substation will not change. | December 2016 | Approved | 2016-01-26
NEP-16-T01 | 2016-01-06 | MEDWAY SUBSTATION BPS UPGRADE PROJECT | Transmission notification from Eversource Energy (ES) to upgrade the Medway Substation #65 to NPCC Bulk Power System (BPS) standards to include the construction of a new control house and installation of relaying and redundant control wiring. | June 2019 | Notification | 2016-01-26
PSEG-15-G01-Rev.1 | 2015-11-03 | PSEG BRIDGEPORT HARBOR GENERATOR MODIFICATION PROJECT | Generator notification from PSEG Power Connecticut LLC (PSEG) to modify the previously approved Bridgeport Harbor combined cycle generator output from 547.5 MWs to 532.6 MWs due to a change from a larger model generator size to a smaller model generator size. | 2019-05-31 | Approved | 2015-12-28
PSEG-15-T01-Rev.1 | 2015-11-03 | PSEG BRIDGEPORT HARBOR GENERATOR MODIFICATION PROJECT | Transmission notification from PSEG Power Connecticut LLC (PSEG) for the installation of a 264 MVA transformer (GSU-1) for the Bridgeport Harbor combined cycle generator | 2019-05-31 | Approved | 2015-12-28
PSEG-15-T02-Rev.1 | 2015-11-03 | PSEG BRIDGEPORT HARBOR GENERATOR MODIFICATION PROJECT | Transmission notification from PSEG Power Connecticut LLC (PSEG) for the installation of a 138 MVA transformer (GSU-2) for the Bridgeport Harbor combined cycle generator. Proposed in service date of the project is May 31, 2019. | 2019-05-31 | Approved | 2015-12-28
BE-15-G02 | 2015-11-16 | BRIDGEPORT ENERGY CAPACITY INCREASE PROJECT | Generator notification from Emera Energy Service Subsidiary #5 on behalf of Bridgeport Energy (BE) to increase the capacity of the Bridgeport Energy combined cycle generator located in Bridgeport, CT by 18MWs at 50 deg. F. | 4th Quarter of 2017 | Approved | 2015-12-28
NEP-15-GNF27 | 2015-12-04 | 510 PV PROJECT DEVELOPMENT BARRE SOLAR PROJECT | Generator notification from New England Power Company (NEP) on behalf of Massachusetts Electric Company for the installation of a 1.92 MW solar array located in Barre, MA and interconnecting via the 604W1 feeder out of the Barre Substation #604. | 2015-12-31 | Notification | 2015-12-28
NEP-15-GNF28 | 2015-12-04 | 510 PV PROJECT DEVELOPMENT SOUTHBRIDGE SOLAR PROJECT | Generator notification from New England Power Company (NEP) on behalf of Massachusetts Electric Company for the installation of a 1.92 MW solar array located in Southbridge, MA and interconnecting via the 413L4 feeder out of the Snow Street Substation #413. | 2016-01-18 | Notification | 2015-12-28
WED-15-T02 | 2015-12-01 | WALLINGFORD TRANSMISSION UPGRADE PROJECT | Transmission notification from Wallingford Department of Public Utilities Electric Division (WED) for the installation of a 0.1 mile overhead 115 kV line from Wallingford 13M – 1305 Line to Wallingford Energy 6G – 1305 Line to connect the new fourth transformer at Wallingford Energy 6G to 13M. | May 2018 | Notification | 2015-12-28
WED-15-T03 | 2015-12-01 | WALLINGFORD TRANSMISSION UPGRADE PROJECT | Transmission notification from Wallingford Department of Public Utilities Electric Division (WED) for the replacement of four existing 115 kV 25 kA circuit switchers, one on the high voltage side of each existing 115/13.8 kV power transformers at 13M, with 40 kA circuit switchers. | May 2018 | Notification | 2015-12-28
WED-15-T04 | 2015-12-01 | WALLINGFORD TRANSMISSION UPGRADE PROJECT | Transmission notification from Wallingford Department of Public Utilities Electric Division (WED) for revision of the 115 kV bus work to change the point where the existing 1640 Line attaches to the 13M ring bus. A new 115 kV/40 kA SF 6 circuit breaker will be installed between the existing 13M 2T and 13M 3T circuit breakers. This work addresses the contingency of any single breaker failure causing the loss of more than one 115 kV line out of 13M. | May 2018 | Notification | 2015-12-28
WED-15-T05 | 2015-12-01 | WALLINGFORD TRANSMISSION UPGRADE PROJECT | Transmission notification from Wallingford Department of Public Utilities Electric Division (WED) for the installation of seven new 115 kV poles and install and/or transfer 3000 feet of three phase line. This will place the 1630 and 1640 Lines from Wallingford 13M to the Pent Road Junction on separate structures. This address a double circuit contingency that limits the firm N-1 output of generation connected to 13M. | May 2018 | Notification | 2015-12-28
ES-15-G08 | 2015-11-19 | SOUTHERN SKY RENEWABLE ENERGY CARVER SOLAR PROJECT | Generator notification from Eversource Energy (ES) on behalf of Southern Sky Renewable Energy Carver LLC for the installation of a 1.5 MW solar array located in Carver, MA and interconnecting via the #10 feeder out of the .Eversource West Pond Substation #737. | 2015-11-15 | Notification | 2015-12-28
ES-15-G23 | 2015-11-30 | WILLOW HILL ROAD SOLAR PROJECT | Generator notification from Eversource Energy (ES) on behalf of Willow Hill Road Solar for the installation of a 1.904 MW solar array located in Lee, MA and interconnecting via the #17G7 feeder out of the Woodland 17G Substation. | April 2016 | Notification | 2015-12-28
ES-15-G13 | 2015-10-30 | Fusion Solar Project | Generator notification from Eversource Energy (“ES”) on behalf of Fusion Solar Center, LLC for the installation of a 20.0 MW solar array located in Sprague, CT and interconnected to the 23 kV distribution feeder to Tunnel 12S Substation in Preston, CT. | 2016-12-31 | Approved | 2015-12-01
NEP-15-T08 | 2015-11-04 | Kent County Substation Transformer Addition Project | Transmission notification from New England Power Company (“NEP”) for the installation of a new 115/13.2 kV, 24/32/40 MVA transformer T5 tapped off the G-185S line at the Kent County Substation #22. | January 2017 | Approved | 2015-12-01
EXE-15-X01 | 2015-11-05 | Mystic 7 AVR Replacement Project | Transmission notification from Exelon Generation Co. (“EXE”) for the replacement and installation of the Mystic 7 Automatic Voltage Regulator (AVR) with a new EX2100 voltage regulator for the GE Alterrex exciter. The module will also update the governor controller. | 2015-11-25 | Approved | 2015-12-01
ES-15-T94 | 2015-10-27 | Glenbrook 1K-3X Distribution Transformer Replacement Project | Transmission notification from Eversource Energy (“ES”) for the replacement of the Glenbrook 1K-3X 115/13.8 kV Distribution Transformer in Stamford, CT. The transformer rating is 36/48/670 MVA. | 2015-11-30 | Notification | 2015-12-01
NEP-15-GNF19 | 2015-11-06 | Erving Paper Mills Generator | Generator notification from New England Power Company (“NEP”) for the installation of a 3.3 MW synchronous generator located in Erving, MA and interconnecting at the Wendell Depot Substation #705 via the 13.8 kV 705W1 feeder. | 2015-11-20 | Notification | 2015-12-01
NEP-15-GNF20 | 2015-11-06 | Hollingsworth & Vose West Groton Generator | Generator notification from New England Power Company (“NEP”) for the installation of a 3.5 MW synchronous generator located in West Groton, MA and interconnecting at the Ayer Substation #201 via the 13.8 kV 201W4 feeder. | 2015-11-20 | Notification | 2015-12-01
NEP-15-GNF21 | 2015-11-06 | Ken’s Food Marlborough Generator | Generator notification from New England Power Company (“NEP”) for the installation of a 1.2 MW synchronous generator located in Marlborough, MA and interconnecting at the Northboro Road Substation #317 via the 13.8 kV 317W1 feeder. | 2015-11-20 | Notification | 2015-12-01
NEP-15-GNF22 | 2015-11-06 | WA MA West Warren Solar | Generator notification from New England Power Company (“NEP”) for the installation of a 2.0 MW solar array located in West Warren, MA and interconnecting at the Little Rest Road Substation #516 via the 13.2 kV 516L3 feeder. | 2015-12-07 | Notification | 2015-12-01
NEP-15-GNF23 | 2015-11-06 | Kearsarge Bellingham Solar | Generator notification from New England Power Company (“NEP”) for the installation of a 3.108 MW solar array located in Bellingham, MA and interconnecting at the Beaver Pond Substation #344 via the 13.8 kV 344W4 feeder. | 2015-12-14 | Notification | 2015-12-01
NEP-15-GNF24 | 2015-11-06 | Bluewave Capital Rehoboth Solar | Generator notification from New England Power Company (“NEP”) for the installation of a 1.67 MW solar array located in Rehoboth, MA and interconnecting at the Mink Street Substation #7 via the 13.2 kV 7L5 feeder. | 2015-12-15 | Notification | 2015-12-01
NEP-15-GNF25 | 2015-11-06 | Syncarpha Palmer Solar | Generator notification from New England Power Company (“NEP”) for the installation of a 4.995 MW solar array located in Palmer, MA and interconnecting at the Thorndike Substation #523 via the 13.2 kV 523L4 feeder. | 2015-12-21 | Notification | 2015-12-01
NEP-15-GNF26 | 2015-11-06 | RT MA Housatonic Solar | Generator notification from New England Power Company (“NEP”) for the installation of a 2.0 MW solar array located in Housatonic, MA and interconnecting at the Risingdale Substation #1109 via the 13.8 kV 1109W3 feeder. | 2015-12-31 | Notification | 2015-12-01
ES-15-G22 | 2015-11-04 | Church Street Weston Solar Project | Generator notification from Eversource Energy (“ES”) on behalf of Church Street Solar LLC for the installation of a 1.795 MW solar array located in Weston, MA and interconnecting to the Trapelo Road Waltham Station #450 13.8 kV circuit #450-H7. | 2015-12-15 | Notification | 2015-12-02
ES-15-T95 | 2015-10-31 | Speen Street Station #433 115 kV Line Disconnects | Transmission notification from Eversource Energy (“ES”) for the installation of two air break, motor-operated, 123 kV, 550 kV BIL and 2,000 amp continuous rated line disconnects at Speen St. Station 433 located in Framingham, MA. | 2016-03-01 | Notification | 2015-12-01
ES-15-G21 | 2015-11-05 | Brigham & Women’s Faulkner Hospital Generator Project | Generator notification from Eversource Energy (“ES”) on behalf of Brigham & Women’s Faulkner Hospital for the installation of two 800 kW CHP Synchronous Generators (1.6 MW Net Output) located in Jamaica Plain, MA and interconnecting to Hyde Park Station 496, 14 kV Bus Section(s) 3 and 4 via 14 kV lines 13-1416XY, 13-1417, 13-1418 and 13-1419. | 2016-02-01 | Notification | 2015-12-01
VELCO-15-GNF07 | 2015-11-09 | Waterhouse Hyde Park Solar Project | Generator notification from Vermont Electric Power Company on behalf of Village of Hyde Park Electric Department for the installation of 1.0 MW solar array located in Hyde Park, VT and interconnecting to the Hyde Park Substation | 2016-05-31 | Notification | 2015-12-01
ES-15-T82 | 2015-10-07 | Carver Street Breaker Addition Project | Transmission notification from Eversource Energy (“ES”) for the installation of six new 115 kV circuit breakers at Carver St. Station #71. Also install two high speed protection groups on 115 kV cables 329-512/513 between Carver St and Brighton Stations and 514/-512/513 cables between Carver St and Kingston Station. | Fall 2016 | Approved | 2015-11-05
ES-15-T75 | 2015-10-01 | Canal 15Q Substation Breaker and 115/23 kV Transformer Addition Project | Transmission notification from Eversource Energy (“ES”) for the installation of a new 115 kV circuit breaker and a second 36/48/60 MVA step down transformer at the Canal 15Q Substation in Southington, CT | May 2016 | Approved | 2015-11-05
ES-15-T84 | 2015-10-01 | North Keene Substation Project | Transmission notification from Eversource Energy (“ES”) for the construction of the North Keene 115 kV Substation. Loop in the 115-kV Line L163, utilizing two 115-kV circuit breakers. Also install one 115/12.47-kV 30 MVA transformer at North Keene Substation and modify the existing Keene Substation by replacing four of the five existing transformers at with one 115/12.47-kV 30 MVA transformer and replace the existing 12.47 kV switchgear. | June 2016 | Approved | 2015-11-05
NRG-15-G01 | 2015-10-09 | Canal Generator Addition and Transmission Project | Generator notification from NRG Energy Inc. (“NRG”) for the installation and interconnection of a 336 MW simple cycle combustion generator interconnected to the Canal 345 kV substation. | 2019-05-31 | Approved | 2015-11-05
NRG-15-T01 | 2015-10-09 | Canal Generator Addition and Transmission Project | Transmission notification from NRG Energy Inc. (“NRG”) for the installation of a 0.3 mile overhead 345 kV line from the Canal CT generator to the Canal Substation between breakers 812P and 812S. | 2019-05-31 | Approved | 2015-11-05
ES-15-T77 | 2015-10-07 | Canal Generator Addition and Transmission Project | Transmission notification from Eversource Energy (“ES”) for the installation of a 345 kV disconnect switch at the Canal 345 kV Substation and connection of Canal 3 to the Canal 345 kV Substation at the existing bus position between breakers 812P and 812S. | May 2019 | Approved | 2015-11-05
ES-15-T83 | 2015-10-01 | Rimmon Substation Project | Transmission notification from Eversource Energy (“ES”) for the construction of a new Rimmon substation and relocate the existing Rimmon Substation equipment to the new site. Add a second Rimmon 115/34.5-kV, 44.8 MVA transformer and associated equipment. Add two 115-kV terminals with two circuit breakers, associated disconnect switches, and protection and controls. Loop 115-kV Line J114 in and out of the Rimmon Substation. Also add new 115-kV capacitor banks (2x13.3 Mvar) and add a series 115-kV circuit breaker to the Greggs bus tie breaker BT30. | June 2016 | Approved | 2015-11-05
GDF-15-G01 | 2015-10-08 | Bethlehem Generator Replacement Project | Generator notification from GDF Suez Energy Marketing NA (“GDF”) for the installation of a replacement 17.1 MW synchronous generator located in Bethlehem, NH. | 2015-12-08 | Approved | 2015-11-05
ES-15-T80 | 2015-09-10 | Manchester 3A-2X 115/23 kV Distribution Transformer Replacement Project | Transmission notification from Eversource Energy (“ES”) for the replacement of the existing 3A-3X 115/23 kV distribution transformer due to asset conditions. | December 2016 | Notification | 2015-11-05
ES-15-G17 | 2015-10-05 | Solar City Needham Solar Project | Generator notification from Eversource Energy (“ES”) on behalf of Solar City Corporation for the installation of a 3.12 MW solar array located in Needham, MA and interconnecting at the Needham Station #148, 13.8 kV circuit 148-H1. | 2015-11-30 | Notification | 2015-11-05
ES-15-G18 | 2015-10-01 | Sunpin Pittsfield Solar Project | Generator notification from Eversource Energy (“ES”) on behalf of Sunpin Solar Development LLC for the installation of a 3.3 MW solar array located in Pittsfield, MA and interconnecting at the Partridge 15E 115 kV Substation via the Eversource 15E2 23 kV distribution circuit. | 2015-10-25 | Notification | 2015-11-05
VELCO-15-GNF06 | 2015-10-06 | Nebraska Valley Solar Project | Generator notification from Vermont Electric Company (“VELCO”) on behalf of Stowe Electric Department for the installation of a 1.0 MW solar array located in Stowe, VT and interconnecting at the 7.2/12.47 kV circuit #2 originating at the Stowe Wilkens Substation. | 2016-05-31 | Notification | 2015-11-05
NEP-15-GNF15 | 2015-10-05 | WGL Energy Systems Marlborough Solar Project | Generator notification from New England Power Company (“NEP”) on behalf of WGL Energy Systems LLC for the installation of a 1.073 MW solar array located in Marlborough, MA and interconnecting at the Marlborough 311 Substation via the #311W6 13.8 kV feeder. | 2015-11-01 | Notification | 2015-11-05
NEP-15-GNF16 | 2015-10-05 | Solar MA Project Management North Oxford Solar Project | Generator notification from New England Power Company (“NEP”) on behalf of Solar MA Project Management LLC for the installation of a 1.5 MW solar array located in Oxford, MA and interconnecting at the North Oxford 406 Substation via the #406L3 13.2 kV feeder. | 2015-11-23 | Notification | 2015-11-05
NEP-15-GNF17 | 2015-10-05 | Nextamp Peak Hancock Solar Project | Generator notification from New England Power Company (“NEP”) on behalf of Nextamp Peak LLC for the installation of a 2.0 MW solar array located in Hancock, MA and interconnecting at the Partridge 15E Substation via the #1018K1 23 kV feeder. | 2015-11-01 | Notification | 2015-11-05
NEP-15-GNF18 | 2015-10-05 | Altus Power America Great Barrington Solar Project | Generator notification from New England Power Company (“NEP”) on behalf of Altus Power America, Inc. for the installation of a 2.5 MW solar array located in Great Barrington, MA and interconnecting at the Risingdale 1109 Substation via the #1109W1 13.8 kV feeder. | 2015-12-01 | Notification | 2015-11-05
NU-14-G08-Rev.1 | 2015-10-09 | Nextamp Capital Dartmouth Solar Project Rev.1 | – Generator notification from Eversource Energy (“ES”) for the revision to the Nextamp Capital Dartmouth Solar Project downsizing the size of the project from 4.68 MWs to 2.25 MWs. The solar array will interconnect to the #543 13.2 kV distribution circuit out of the Cross Road Substation #651 off of the #111 transformer. | January 2016 | Notification | 2015-11-05
ES-15-T81 | 2015-10-05 | K Street Substation Breaker Addition Project | Transmission notification from Eversource Energy for the installation of a normally open 115 kV 63 kA IC 3000 amp breaker #33 between the existing breakers #12 and #15 at the K Street Substation in Boston, MA. | December 2016 | Notification | 2015-11-05
CMP-15-T03 | 2015-09-01 | New Gloucester Substation Project | Transmission notification from Central Maine Power Company (“CMP”) for the construction of a new 115/34.5 kV New Gloucester Substation that sectionalizes Section 208 by adding four 115 kV circuit breakers in a ring bus configuration with the installation of a new 115/34.5 kV 30/56 MVA transformer at a new green field site, construction of roughly 8 miles of new 115 kV (1192 kcmil 45/7 ACSR) conductor (Section 282) from the Surowiec Substation to the New Gloucester Substation,add a 115 kV circuit breaker and relocate Sections 166 and 69 into a different bay position at the Surowiec Substation, and partially re-build existing Section 208 to accommodate the new Section 282 in the ROW. | December 2021 | Approved | 2015-10-01
EP-15-G01 | 2015-09-03 | Newington Generator Uprate Project | Generator notification from Essential Power (“ES”) to install an Advanced Hot Gas Path Upgrade on Gas Turbines 1 & 2 at the Newington Station to increase summer incremental net capacity uprate of +27.9 MW (at ≥ 50° F). The combustion turbine generators (CTG1 and CTG2) will both be upgraded by 13.1 MW, and the steam turbine (STG) is being downgraded by 0.1 MW. The station service load has also reduced by 1.8 MW. The combined plant summer rated net output is 596.1 MW (at ≥ 50° F). The winter incremental net capacity uprate is 39.1 MW providing a net plant output of 634.9 MW (at ≥ 0°F).and improved efficiency. | September 2015 | Approved | 2015-10-01
ES-15-T61 | 2015-08-27 | North Cambridge Substation 115 kV Terminal Swaps Project | Transmission notification from Eversource Energy (“ES”) to swap the 115kV board positions for the Blair Pond-North Cambridge 115kV line 509-530 and the Alewife Station #828 Transformer #1 and the Brighton-North Cambridge 115kV line 329-531 and the Alewife Station #828 Transformer #4 at North Cambridge. The project addresses overloads for the loss of one of the North Cambridge 345/115kV Autotransformers followed by a stuck breaker of either the North Cambridge 115kV breakers #5 or #10. | December 2016 | Approved | 2015-10-01
ES-15-G12 | 2015-09-01 | Harvard DG Interconnection Project | Generator notification from Eversource Energy (“ES”) on behalf of President and Fellows of Harvard College for the installation of a 8 MW Combustion Turbine Generator located in Cambridge, MA and interconnected via the NSTAR owned 14 kV distribution lines 831-1111 and 831-1113 to Putnam Station 831. Both distribution lines will operate in parallel at Putnam Station 831 and the Harvard owned station. The connection to the transmission system will be through the NSTAR Electric and Gas Corp. owned 117.5/14.4 kV, 62.5 MVA distribution station transformers 110A and 110B located at Putnam Station 831. | 2015-10-01 | Approved | 2015-10-01
ES-15-X01 | 2015-09-02 | Line 326 SPS Setpoint Change Project | Transmission notification from Eversource Energy (“ES”) for the set point change to the 326 Line SPS (special protection system) installed on the 345-kV Line 326, at the Scobie Pond Substation. This SPS has three modes of operation ‘Disabled’, ‘Thermal’ (summer/winter), and ‘Stability’ and is classified as a NPCC Type I SPS. This change affects the thermal mode of the SPS and involves increasing the summer MVA set point from 1429 MVA to 1749 MVA and increasing the winter MVA set point from 1697 MVA to 1793 MVA. | March 2016 | Notification | 2015-10-01
ES-15-G14 | 2015-08-21 | Brass Mill Solar Project | Generator notification from Eversource Energy (“ES”) on behalf of Brass Mill Solar Center LLC for the installation of a 1.16 MW solar array located in Waterbury, CT and interconnecting at the 13F63 & 13F66 13.8 kV feeders from Eversouce CTs Baldwin 13F substation. | 2015-11-13 | Notification | 2015-10-01
IBR-15-G01 | 2015-08-04 | Deerfield Wind Generator Project | Generator notification from Iberdrola Renewables LLC (“IBR”) on behalf of Deerfield Wind LLC for the installation of 15 wind turbine generator rated at 2 MWs each (30 MWs net output) located in Bennington County, Vermont. | 2017-12-31 | Approved | 2015-08-25
IBR-15-T01 | 2015-08-04 | Deerfield Wind Generator Project | Transmission notification from Iberdrola Renewables LLC (“IBR”) on behalf of Deerfield Wind LLC for the installation of a 18/24/30 MVA 34.5/69 kV transformer at the to be constructed Putnam Road 69 kV Substation in Searsburg, VT. | 2017-10-01 | Approved | 2015-08-25
VELCO-15-T05 | 2015-07-27 | Deerfield Wind Generator Project | Transmission notification from Vermont Electric Power Company (“VELCO”) on behalf of Green Mountain Power for the construction of a new Putnam Road 3-breaker ring substation connecting to the Y-25 line, 0.5 mi west of route 8, between the Bennington 69 kV station and the Sleepy Hollow/Searsburg Wind tap. The substation will be the point of interconnection of a proposed wind generation project. | 2017-12-31 | Approved | 2015-08-25
NEP-15-T12 | 2015-08-05 | Deerfield Wind Generator Project | Transmission notification from New England Power Company (“NEP”) for the reconductoring of the seven mile overhead 69 kV J-10 line (Adams - Deerfield 5) with 477 ACSR to address the impact of interconnecting the 30 MW QP477 Deerfield Wind project as specified in IBR-15-G01. | 2017-10-01 | Approved | 2015-08-25
EXE-15-G01 | 2015-07-07 | Medway Generator and Transmission Project | Generator notification from Exelon West Medway II, LLC (“EXE”) for the installation of two 103.5 MW combustion turbine generators (207.0 MW net output) at the West Medway Generator Station in Medway, MA. | 2018-04-01 | Approved | 2015-08-25
EXE-15-T01 | 2015-07-07 | Medway Generator and Transmission Project | Transmission notification from Exelon West Medway II, LLC (“EXE”) for the installation of a three winding 13.8/13.8/115 kV Generator Step Up transformer (GSU) at the West Medway II Station to support the two new generators at Medway. This will be interconnected via a 0.25 mile, 1272 kcmil, 115 kV overhead line from the West Medway II Station to the Medway 115 kV Substation in Medway, MA. | April 2018 | Approved | 2015-08-25
ES-15-G11 | 2015-07-13 | CEC Kingston Solar Project | Generation notification from Eversource Energy (“ES”) on behalf of CEC Solar #1040 LLC and CEC Solar #1041 for the installation of a 1.57 MW solar array located in Kingston, MA and interconnecting to the Eversource Kingston Substation #735, #2 transformer, #909 23 kV circuit. | October 2015 | Notification | 2015-08-25
ES-15-G06 | 2015-07-14 | Ahold Stop & Shop Warehouse CoGen Project | Generation notification from Eversource Energy (“ES”) on behalf of Ahold for the installation of a 1.137 MW biodigester-fired cogeneration unit located in Freetown, MA and interconnecting #606 13.2 kV feeder out of the Assonet Substation #647, fed by the #635 34.5 kV line out of the Bell Rock Substation #661. | 2015-12-01 | Notification | 2015-08-25
NU-14-T11-Rev.1 | 2015-08-06 | Transmission Elements Upgrade due to CPV Towantic Generator | Transmission notification revision from Eversource Energy (formally “NU”) to rebuild the 6 mile overhead 15 kV 1585N Line from Towantic 115 kV Substation in Oxford, CT to the 115 kV Bunker Hill Substation in Waterbury, CT. | 2018-06-01 | Notification | 2015-08-25
NU-14-T12-Rev.1 | 2015-08-06 | Transmission Elements Upgrade due to CPV Towantic Generator | Transmission notification revision from Eversource Energy (“ES”) to reconductor the 1.2 mile overhead 115 kV 1575S Line from Towantic 115 kV Substation in Oxford, CT to the Oxford 115 kV Substation in Oxford, CT. | 2018-06-01 | Notification | 2015-08-25
ES-15-T72 | 2015-08-06 | Transmission Elements Upgrade due to CPV Towantic Generator | Transmission notification revision from Eversource Energy (“ES”) to rebuild the 3 mile overhead 115 kV 1575N-1 Line from Towantic 115 kV Substation in Oxford, CT to the 115 kV Baldwin Tap in Waterbury, CT. | 2018-06-01 | Notification | 2015-08-25
ES-15-T73 | 2015-08-06 | Transmission Elements Upgrade due to CPV Towantic Generator | Transmission notification revision from Eversource Energy (“ES”) to rebuild/reconductor the 4.4 mile overhead 115 kV 1710 Line from Devon 115 kV Substation in Milford, CT to the Trumbull Junction, CT. | 2018-06-01 | Notification | 2015-08-25
ES-15-T74 | 2015-08-06 | Transmission Elements Upgrade due to CPV Towantic Generator | Transmission notification revision from Eversource Energy (“ES”) to rebuild the 4.5 mile overhead 115 kV 1730 Line from Devon 115 kV Substation in Milford, CT to the UI Border/Trumbull 115 kV Substation in Trumbull, CT. | 2018-06-01 | Notification | 2015-08-25
WEII-15-G01 | 2015-06-29 | Wallingford Generator and Transmission Project | Generator notification from Wallingford Energy II, LLC (“WEII”) for the installation of two (Units 6 & 7) 50 MW natural gas turbine generators (100 MWs net output) located in Wallingford CT. | 2018-03-30 | Approved | 2015-07-23
WEII-15-T01 | 2015-06-29 | Wallingford Generator and Transmission Project | Transmission notification from Wallingford Energy II, LLC (“WEII”) for the installation of a 66 MVA 115/13.8 kV Generator Step Up Transformer interconnecting Unit #7 13.8 kV Bus to the Wallingford 115 kV Switchyard. | 2018-03-30 | Approved | 2015-07-23
WED-15-T01 | 2015-06-29 | Wallingford Generator and Transmission Project | Transmission Notification from Town of Wallingford, Department of Public Utilities (“WED”) for the replacement of the 795 kcml ACSR 115 kV transmission line from the Wallingford 13M 1305 Line to the Wallingford Energy 6G 1305 Line with 1590 kcml ACSR. | 2018-05-01 | Approved | 2015-07-23
NEP-12-G09-Rev.1 | 2015-06-22 | Harrington Street Vuelta Solar and Harrington Street Old Wardour Solar Generation and Transmission Project | Generator notifications from New England Power Company (“NEP”) on behalf of Vuelta Solar LLC and Old Wardour LLC for the installation of two 4.875 MW solar arrays (9.75 MW net output) located in East Brookfield, MA | 2015-10-31 | Approved | 2015-07-23
NEP-15-G10 | 2015-06-22 | Harrington Street Vuelta Solar and Harrington Street Old Wardour Solar Generation and Transmission Project | Generator notifications from New England Power Company (“NEP”) on behalf of Vuelta Solar LLC and Old Wardour LLC for the installation of two 4.875 MW solar arrays (9.75 MW net output) located in East Brookfield, MA | 2015-10-31 | Approved | 2015-07-23
NEP-15-G09 | 2015-06-22 | Harrington Street Vuelta Solar and Harrington Street Old Wardour Solar Generation and Transmission Project | Transmission notification from New England Power Company (“NEP”) for the installation of a 69/13.2 kV transformer rated 12/16/20 MVA and required switchgear at the proposed Harrington St PV Collector Substation to connect the Vuelta Solar and Old Wardour PV projects on the 69 kV E-5 line. | 2015-10-31 | Approved | 2015-07-23
ES-15-T76 | 2015-06-26 | Sudbury Substation Autotransformer and Ring Bus Installation Project | Transmission notification from Eversource Energy (“ES”) for the installation of a 230/115 kV Autotransformer and 230 kV Ring Bus at the Sudbury Substation located in Sudbury, MA. Also, an existing 230 kV line, 282-602, that currently runs between West Medway and Waltham, will be looped in and out of the new 230 kV ring at Sudbury. In addition, the termination of the existing 115 kV line, 342-507, will be relocated to a new breaker position at Sudbury, as a part of the Project. | 2015-12-01 | Approved | 2015-07-23
VELCO-15-GNF04 | 2015-06-12 | Bridport West Solar Project | Generator notification from Vermont Electric Company (VELCO) on behalf of VEEP Inc. for the installation of a 2.0 MW solar array located in Bridport, VT and interconnecting via the 12.47 kV feeder GMP line 36 on Circuit #WY81. | 2015-07-01 | Notification | 2015-07-23
VELCO-15-GNF05 | 2015-06-12 | Champlain Valley Solar Project | Generator notification from Vermont Electric Company (VELCO) on behalf of VEEP Inc. for the installation of a 2.0 MW solar array located in Middlebury, VT and interconnecting via the 12.47 kV feeder GMP line EM75 Extension on Pole #26.3 | 2015-07-01 | Notification | 2015-07-23
NEP-15-GNF08 | 2015-07-01 | Kent County Substation Transformer Addition Project | Transmission notification from New England Power Company (“NEP”) for the installation of a new 115/13.2 kV, 24/32/40 MVAR transformer T5 at the Kent County Substation #22 and tapped of the G-185S line. | 2017-01-01 | Notification
CMP-15-X01 | 2015-06-19 | Maine Capacitor Control Settings Project | Transmission notification from Central Maine Power Company (“CMP”) for changes to increase the overvoltage trip settings to the Orrington, Mason, Surowiec and South Gorham 115 kV connected capacitors to enhance system performance during power swing events through the Maine 345 kV transmission corridor. | 2015-06-15 | Notification | 2015-07-23
NEP-15-GNF13 | 2015-07-02 | BWC Fivemile River Solar Project | Generator notification from New England Power Company (“NEP”) on behalf of BWC Fivemile River LLC for the installation of a 1.5 MW solar array located in Oxford, MA and interconnecting by the 406L1 Feeder out of the North Oxford Substation #406. | 2015-08-31 | Notification | 2015-07-23
NEP-15-GNF14 | 2015-07-02 | Halifax Solar NG Solar Project | Generator notification from New England Power Company (“NEP”) on behalf of Halifax Solar NG LLC for the installation of a 2.5 MW solar array located in Halifax, MA and interconnecting by the 912W75 Feeder out of the Mill Street Substation #912. | 2015-08-13 | Notification | 2015-07-23
ES-15-T79 | 2015-07-02 | Orchard 27A Substation 3rd Distribution Transformer Project | Transmission notification from Eversource Energy (“ES”) for the installation of a 3rd 115/13.8 kV distribution transformer at the Orchard 27A Substation | 2015-10-31 | Notification | 2015-07-23
NEP-14-T07-Rev.1 | 2015-07-02 | North Oxford Substation Breaker and Transformer Addition Project | Transmission notification from New England Power Company (“NEP”) for the installation of an in-line breaker (V174) at the North Oxford Substation which will sectionalize the existing V-174 line into V-174W (Carpenter Hill – North Oxford) and V174 (North Oxford – Millbury 2). Also add a new 2nd 115/13.2 kV, 24/32/40 MVA transformer at the North Oxford Substation in Oxford, MA. | 2018-06-01 | Notification | 2015-07-23
CES-15-G01 | 2015-05-22 | Pioneer Valley Electric Center (PVEC) Generation and Transmission Uprate Project | Generator notification from Calpine Energy Services (“CES”) for the installation of 1 x 1 combined cycle generator (CTG - 292.2 MWs net output winter 20 deg F) (STG – 144.3 MWs net output winter 20 deg F) located in Westfield, MA. | 2018-06-01 | Approved | 2015-07-09
CES-15-T01 | 2015-05-22 | Pioneer Valley Electric Center (PVEC) Generation and Transmission Uprate Project | Transmission notification from Calpine Energy Services (“CES”) for the installation of a combustion turbine 115 kV generator step up transformer rated at 180/300 MVA. | 2018-03-01 | Approved | 2015-07-09
CES-15-T02 | 2015-05-22 | Pioneer Valley Electric Center (PVEC) Generation and Transmission Uprate Project | Transmission notification from Calpine Energy Services (“CES”) for the installation of a combustion turbine 115 kV generator step up transformer rated at 102/170 MVA. | 2018-03-01 | Approved | 2015-07-09
ES-15-T57 | 2015-05-22 | Pioneer Valley Electric Center (PVEC) Generation and Transmission Uprate Project | Transmission notification from Eversource Energy (“ES”) for the construction of a new 115-kV switching station in Westfield, MA in a ring bus configuration consisting of four (4) 115-kV circuit breakers with a minimum 40-kA short-circuit interrupting capability, associated breaker disconnects, control house, and protection and controls. Loop the existing line 1302 (between Buck Pond and Pochassic tap) into the new switching station and terminate to establish new lines from Buck Pond 34B Substation to PVEC Switching Station (length approximately 1.0 mile) and from Pochassic Substation tap to PVEC Switching Station (length approximately 2.12 miles). Also, terminate the leads for the steam turbine generator step-up transformer and the gas turbine generator step-up transformer into the new switching station. | 2018-03-01 | Approved Withdrawn | 7/9/2015 2/29/2016
ES-15-T58 | 2015-05-22 | Pioneer Valley Electric Center (PVEC) Generation and Transmission Uprate Project | Transmission notification from Eversource Energy (“ES”) for reconductoring of the 1657-3 line section (approximately 160 feet) from Southampton Junction to the Eversource / HG&E border using 795 kcmil ACSS conductor to match or exceed the ratings of the HG&E line section from the Eversource / HG&E border to Ingleside. | 2018-03-01 | Approved Withdrawn | 7/9/2015 2/29/2016
ES-15-T70 | 2015-05-22 | Pioneer Valley Electric Center (PVEC) Generation and Transmission Uprate Project | Transmission notification from Eversource Energy (“ES”) to upgrade the necessary terminal equipment at Agawam 16C Substation to match or exceed the 1302 line conductor ratings. | 2018-03-01 | Approved Withdrawn | 7/9/2015 2/29/2016
SE-15-G01 | 2015-05-27 | Hancock Wind Generation and Transmission Project | Generator notification from Emera Maine on behalf of Hancock Wind LLC for the installation of seventeen 3.0 MW wind turbine generators (51 MWs net output) located in Hancock County, ME. | 2016-12-31 | Approved | 2015-07-07
SE-15-T01 | 2015-05-27 | Hancock Wind Generation and Transmission Project | Transmission notification from Emera Maine on behalf of Hancock Wind LLC for the installation of the 115/34.5 kV Hancock Collector Substation new main power transformer, 16MVAR D-Var and associated breakers and protection. | 2015-12-31 | Approved | 2015-07-07
ES-15-G01 | 2015-05-28 | Acushnet Ball Plant CoGen Project | Generation notification from Eversource Energy (“ES”) on behalf of Acushnet Ball Plant #3 for the installation of a 2.001 MW natural gas cogeneration unit located in New Bedford, MA and interconnecting to the Industrial Park Substation #636 via 13.2 kV feeders #101 (normal) and #103 (Alternate). | 2015-08-01 | Notification | 2015-07-09
NEP-15-GNF11 | 2015-06-02 | Bluewave Capital Webster Solar Project | Generation notification from New England Power Company (“NEP”) on behalf of Bluewave Capital LLC for the installation of a 1.38 MW solar array located in Webster, MA and interconnecting via feeder #412L3 out of the East Webster Substation #412. | 2015-09-15 | Notification | 2015-07-09
NEP-15-GNF12 | 2015-06-02 | Castle Neck River Solar Project | Generator notification from New England Power Company (“NEP”) on behalf of BWC Castle Neck River LLC for the installation of 3.0 MW solar array located in Haverhill, MA and interconnecting via feeder 48L1 out of the North Haverhill Substation #48. | 2015-08-21 | Notification | 2015-07-09
ES-15-G02 | 2015-06-02 | SunEdison Plympton Solar Project | Generator notification from Eversource Energy (“ES”) on behalf of SunEdison LLC for the installation of a 4.0 MW solar array in Plympton, MA fed by the Brook Street Substation #727 23 kV feeder #51. | 2016-10-01 | Notification Withdrawn | 7/9/2015 8/27/2015
UI-15-G01 | 2015-05-14 | UIL Glastonbury Fuel Cell Project | Generator notification from United Illuminating Company (“UI”) on behalf of UIL Distributed Resources LLC for the installation of a 3.67 MW fuel cell generator in Glastonbury, CT and fed by the Hopewell Substation 22R5 feeder. | 2015-07-15 | Notification | 2015-07-09
ES-15-G07 | 2015-04-30 | Brigham & Woman’s Hospital CHP Synchronous Generator Project | Transmission notification from Eversource Energy (ES) to relocate termination for existing 36.7 MVAR 115kV Capacitor Bank at Chelsea Station #488 in Chelsea, MA | 2015-06-01 | Approved | 2015-05-26
ES-15-G05 | 2015-03-17 | Hadley 2 Solar Project | Generation notification from Eversource Energy (“ES”) on behalf of Hadley 2 Solar for the installation of a 1.95 MW solar array located in Hadley, MA and interconnecting via the 115 kV Amherst 17K substation through the 17K1 feeder at 13.8 kV. | 2015-04-30 | Approved | 2015-05-26
VELCO-15-X01 | 2015-04-24 | Disable Highgate HVDC Converter Runback Project | Transmission notification from Vermont Electric Power Company (“VELCO”) to permanently disable the Highgate HVDC Converter Runback schemes associated with the outage of PV 20, K21 or the K22 line. The Highgate runback schemes have been disabled since the refurbishment of the converter in November 2012 and the establishment of the export interface in October 2012 | 2015-04-24 | Notification | 2015-05-26
NEP-15-GNF18 | 2015-05-11 | NextAmp Capital Rutland Solar Project | Generator notification from New England Power Company (“NEP”) on behalf of NextAmp Capital LLC for the installation of a 4.999 MW solar array in Rutland, MA and customer fed by Feeder #55W3 out of the Treasure Valley Substation #55. | 2015-07-11 | Notification | 2015-05-26
NEP-11-T04-Rev.1 | 2015-05-08 | Chase Hill Substation Project – Rev.1 | Transmission notification from New England Power Company (“NEP”) for the revision to the Chase Hill Substation Project located in Hopkinton, RI. The initial scope of work included the installation of two (2) 24/32/40 MVA rated 115-13.2 kV transformers to serve the local distribution system in the Southern Rhode Island area; an in-line 2000A continuous, 40 kA interrupting circuit breaker to provide the necessary protection, and splitting the existing 1870S line into 1870S line from Wood River (National Grid) to Hopkinton (National Grid) and 1814 line from Hopkinton (National Grid) to Shunock (Northeast Utilities) substations. Since the initial project determination of “no adverse impacts” on June 7, 2011, the scope and name of the substation have changed and the in-line breaker and second transformer have been dropped | 2015-05-08 | Approved | 2015-05-26
NEP-15-GNF10 | 2015-05-08 | SunEdison Rutland Solar Project | Generator notification from New England Power Company (“NEP”) on behalf of SunEdison Origination 1 LLC for the installation of a 2.0 MW solar array in Rutland, MA and customer fed by Feeder #55W1 out of the Treasure Valley Substation #55 | 2015-08-26 | Notification | 2015-05-26
ES-15-T66 | 2015-03-27 | Chelsea Capacitor Bank Relocation Project | Transmission notification from Eversource Energy (ES) to relocate termination for existing 36.7 MVAR 115kV Capacitor Bank at Chelsea Station #488 in Chelsea, MA | 2015-12-31 | Approved | 2015-05-01
MIRA-15-X01 | 2015-04-02 | MIRA Exciter and Automatic Voltage Regulator Upgrade Project | Transmission notification from Materials Innovation Recycling Authority (MIRA) for the upgrade to the excitation and automatic voltage regulator (AVR) to existing generator #5 (Asset ID# 580) interconnected at the South Meadows 1A Substation with a GE EX2100E exciter. | 2015-05-07 | Approved | 2015-05-01
ES-15-T59 | 2015-03-17 | 211-503/504 Reconductor Project | Transmission notification from Eversource Energy (ES) to reconductor 2.08 miles of overhead 211-503/504 Lines from the North Woburn Tap to NSTAR/National Grid border at Burlington/Billerica. | 2017-05-01 | Notification | 2015-05-01
ES-15-T62 | 2015-03-27 | Greater Boston Circuit Breaker Project | Transmission notification from Eversource Energy (ES) for the installation of a 345kV 50 kA IC 3000 amp breaker in series with existing 345 kV breaker 104 at Stoughton Substation #330 in Stoughton, MA | 2016-12-01 | Notification | 2015-05-01
ES-15-T63 | 2015-03-27 | Greater Boston Circuit Breaker Project | Transmission notification from Eversource Energy (ES) for the installation of a new normally open 115kV 63 kA IC 3000 amp breaker in series with the existing normally open 115 kV breaker 29 at K St. Substation #385 in Boston, MA. | 2015-12-01 | Notification | 2015-05-01
ES-15-T64 | 2015-03-27 | Greater Boston Circuit Breaker Project | Transmission notification from Eversource Energy (ES) for the installation of a 345kV 50 kA IC 3000 amp breaker in series with the existing 345 kV breaker 104 at Woburn Substation #211 in Woburn, MA | 2016-12-01 | Notification | 2015-05-01
ES-15-T65 | 2015-03-27 | Greater Boston Circuit Breaker Project | Transmission notification from Eversource Energy (ES) for the installation of a new 115kV 63 kA IC 3000 amp breaker at Framingham Substation #240 in Framingham | 2017-06-01 | Notification | 2015-05-01
NEP-15-T03 | 2015-03-19 | Greater Boston Reconductor Project | Transmission notification from New England Power (NEP) to reconductor M-139/ N- 140 115 kV transmission lines, a total of 13.31 miles of overhead line. Proposed in-service dates: December 2016 for M-139 from Tewksbury Substation to Billerica Tap; December 2016 for M-139 from Billerica Tap to Pinehurst Tap; May 2017 for M-139 from Pinehurst Tap to Border; December 2016 for N-140 from Tewksbury Substation to Pinehurst Tap and; May 2017 for N-140 from Pinehurst Tap to Border. | 12/1/2016, 5/1/2017, 12/1/2016, 5/1/2017 | Notification | 2015-05-01
NEP-15-T04 | 2015-03-19 | Greater Boston Reconductor Project | Transmission notification from New England Power (NEP) to reconductor F-158N 115 kV overhead transmission line from Golden Hills Substation in Saugus, MA to Maplewood Substation in Malden, MA (4.28 miles), and separate F-158N and Q-169 lines (existing Double Circuit Tower (DCT) structures) between Golden Hills Substation and Maplewood Substation, into independent single circuit structures. Proposed in-service dates: June 2016 for reconductor of F-158N transmission line and December 2015 for the F-158N/Q-169 DCT separation. | 6/1/2016, 12/1/2015 | Notification | 2015-05-01
NEP-15-T05 | 2015-03-19 | Greater Boston Reconductor Project | Transmission notification from New England Power (NEP) to reconductor F-158S 115 kV overhead transmission line from Maplewood Substation in Malden, MA to Everett Substation in Everett, MA (2.48 miles). | 2016-06-01 | Notification | 2015-05-01
NEP-15-T06 | 2015-03-19 | Greater Boston Reconductor Project | Transmission notification from New England Power (NEP) to reconductor W-23W 69 kV overhead transmission line from Northborough Road Substation in Southborough, MA to Woodside Substation in Northborough, MA (3.67 miles). | 2016-06-01 | Notification | 2015-05-01
NEP-15-T07 | 2015-03-19 | Greater Boston Reconductor Project | Transmission notification from New England Power (NEP) to eliminate Double Circuit Tower structures on E-157 115 kV and X-24W 69 kV transmission lines. | 2015-12-01 | Notification | 2015-05-01
NEP-15-GNF07 | 2015-04-10 | SunE Solar New England I LLC Project | Generator notification from New England Power (NEP) on behalf of SunE Solar New England I LLC to interconnect a 3 MW solar generating system to National Grid’s 13.8 kV distribution system in Bridgewater, MA on the company’s 912W55 feeder out of the Mill Street Substation #912. | 2015-04-24 | Notification | 2015-05-01
NEP-15-GNF08 | 2015-04-10 | HA MA Solar LLC Project | Generator notification from New England Power (NEP) on behalf of HA MA Solar LLC to interconnect a 3.5 MW solar generating system to National Grid’s 13.2 kV distribution system in Hampden, MA on the company’s 139L1 feeder out of the West Hampden Substation #139. | 2015-07-16 | Notification | 2015-05-01
ES-15-T67 | 2015-04-01 | Bulls Bridge Substation Transformer Replacement Project | Transmission notification from Eversource Energy (ES) for replacement of 115/27.6 kV transformer with a rating of 28/37.3/46.7 MVA at the Bulls Bridge Substation in New Milford, CT. | 2015-03-01 | Notification | 2015-05-01
ES-15-G04 | 2015-03-31 | Holliston Solar Project | Generator notification from Eversource Energy (ES) on behalf of Marina Energy for the installation of a 1.3 MW PV facility in Holliston, MA and interconnecting on circuit 65-H7 via Medway Station #65, Bus Section #2. | 2015-05-01 | Notification | 2015-05-01
ES-15-T71 | 2015-04-21 | Manchester Substation Transformer Replacement Project | Transmission notification from Eversource Energy (ES) for replacement of Manchester 3A-2X 115/23 kV transformer with a rating of 36/48/60 MVA at the Manchester Substation in Manchester, CT. | 2015-12-01 | Notification | 2015-05-01
ES-15-T69 | 2015-03-30 | Line 372 Reconductor Project | Transmission notification from Eversource Energy (ES) to reconductor 4.2 miles of 345 kV underground cable Line 372 from Mystic to Kingston Street in Boston, MA. | 2015-12-01 | Notification | 2015-05-01
NU-13-T32 (Revision 1) | 2015-04-08 | Greenwich 115/13.2 kV Substation Project | Transmission notification from Connecticut Light and Power d.b.a. Eversource Energy (ES) of revisions to previously approved PPA NU-13-T32 that reflects changes to the radial circuits between existing Cos Cob Substation and previously approved Greenwich Substation and its configuration. | 2017-06-01 | Notification | 2015-05-01
GMP-15-G01 | 2015-04-08 | Proctor Hydroelectric Station Project | Generator notification from VELCO on behalf of Green Mountain Power Company for improvements to increase plant capacity from 6.65 MW to 10.2 MW which consists of five units connected via a 4.16/46 kV GSU to a radial 46 kV line supplied from VELCO Florence 115/46 kV Substation | 2015-05-03 | Notification | 2015-05-01
ES-15-T30 | 2015-02-17 | Southwest Connecticut – Greater Hartford/Central Connecticut Transmission Project | Transmission notification from Eversource Energy (“ES”) for the rebuild of the Bunker Hill Substation in Waterbury, CT by adding a new three bay, nine breaker/breaker and a half substation. | 2017-12-31 | Approved | 2015-04-16
ES-15-T31 | 2015-02-17 | Southwest Connecticut – Greater Hartford/Central Connecticut Transmission Project | Transmission notification from Eversource Energy (“ES”) for the looping the 115-kV 1990 Line in and out of Bunker Hill Substation in Waterbury, CT via termination on two new line terminal positions. This will create two lines, 1990N between Frost Bridge and Bunker Hill Substations and 1990S between Bunker Hill Substation, Baldwin Junction Substation, and Q384 Towantic Substation. | 2017-12-31 | Approved | 2015-04-16
ES-15-T32 | 2015-02-17 | Southwest Connecticut – Greater Hartford/Central Connecticut Transmission Project | Transmission notification from Eversource Energy (“ES”) for the replacement of 556 ACSR conductor with 556 ACSS conductor between Bunker Hill Substation in Waterbury, CT to Baldwin Junction in Middlebury CT. | 2017-12-31 | Approved | 2015-04-16
ES-15-T33 | 2015-02-17 | Southwest Connecticut – Greater Hartford/Central Connecticut Transmission Project | Transmission notification from Eversource Energy (“ES”) for closing the normally open 115-kV 2T circuit breaker at Baldwin 115-kV Substation in Waterbury, CT. | 2017-12-31 | Approved | 2015-04-16
ES-15-T34 | 2015-02-17 | Southwest Connecticut – Greater Hartford/Central Connecticut Transmission Project | Transmission notification from Eversource Energy (“ES”) for installation of a new 115-kV line from Plumtree Substation in Bethel, CT to Brookfield Junction in Brookfield, CT. | 2017-12-31 | Approved | 2015-04-16
ES-15-T35 | 2015-02-17 | Southwest Connecticut – Greater Hartford/Central Connecticut Transmission Project | Transmission notification from Eversource Energy (“ES”) for reconfiguring the 1887 line into a 3-terminal line between Plumtree, West Brookfield, and Shepaug Substations. The 1770 line will be reconfigured into a two 2-terminal lines so that 1770W Line will be from Plumtree Substation to Stony Hill Substation and 1770E Line will be from Stony Hill Substation to Bates Rock Substation. | 2017-12-31 | Approved | 2015-04-16
ES-15-T36 | 2015-02-17 | Southwest Connecticut – Greater Hartford/Central Connecticut Transmission Project | Transmission notification from Eversource Energy (“ES”) for reconductoring the 1887 line from 336 ACSR to 556 ACSS between West Brookfield Substation in Brookfield, CT and West Brookfield Junction in Brookfield, CT. | 2017-12-31 | Approved | 2015-04-16
ES-15-T37 | 2015-02-17 | Southwest Connecticut – Greater Hartford/Central Connecticut Transmission Project | Transmission notification from Eversource Energy (“ES”) for relocating the 22K 115-kV capacitor bank (37.8 MVAr) to the 1770E Line terminal at Stony Hill Substation in Brookfield, CT. Also install a synchronous condenser (+25/-12.5 MVAr) at Stony Hill Substation. | 2017-12-31 | Approved | 2015-04-16
ES-15-T38 | 2015-02-17 | Southwest Connecticut – Greater Hartford/Central Connecticut Transmission Project | Transmission notification from Eversource Energy (“ES”) for installation of a 115-kV circuit breaker in series with the existing 29T breaker. Also relocate the existing 37.8 MVAr capacitor bank from 115-kV “B” bus to “A” bus at Plumtree | 2017-12-31 | Approved | 2015-04-16
ES-15-T39 | 2015-02-17 | Southwest Connecticut – Greater Hartford/Central Connecticut Transmission Project | Transmission notification from Eversource Energy (“ES”) for installing two 14.4 MVAr capacitor banks and associated 115 kV circuit breakers at West Brookfield Substation in Brookfield, CT. | 2017-12-31 | Approved | 2015-04-16
ES-15-T40 | 2015-02-17 | Southwest Connecticut – Greater Hartford/Central Connecticut Transmission Project | Transmission notification from Eversource Energy (“ES”) for reducing the 25.2 MVAr capacitor at Rocky River 115-kV Substation in New Milford, CT to 14.4 MVAr. | 2017-12-31 | Approved | 2015-04-16
ES-15-T41 | 2015-02-17 | Southwest Connecticut – Greater Hartford/Central Connecticut Transmission Project | Transmission notification from Eversource Energy (“ES”) for replacing two Freight Substation 115-kV circuit breakers in Waterbury, CT. The circuit breaker replacements are required if ISO-NE Queue position #384 project is completed. | 2017-12-31 | Approved | 2015-04-16
ES-15-T42 | 2015-02-17 | Southwest Connecticut – Greater Hartford/Central Connecticut Transmission Project | Transmission notification from Eversource Energy (“ES”) for installing a 25.2 MVAr 115 kV capacitor bank at Oxford Substation, in Oxford, CT. | 2017-12-31 | Approved | 2015-04-16
ES-15-T43 | 2015-02-17 | Southwest Connecticut – Greater Hartford/Central Connecticut Transmission Project | Transmission notification from Eversource Energy (“ES”) for rebuilding a portion of 115-kV 1682 line from Wilton 115-kV Substation in Wilton, CT to Norwalk 115-kV Substationin Norwalk, CT and upgrading Wilton Substation terminal equipment. | 2017-12-31 | Approved | 2015-04-16
ES-15-T44 | 2015-02-17 | Southwest Connecticut – Greater Hartford/Central Connecticut Transmission Project | Transmission notification from Eversource Energy (“ES”) for reconductoring the 115-kV 1470-1 and 1470-3 lines from Wilton 115-kV Substation in Wilton, CT to Ridgefield Junction in Ridgefield, CT and from Ridgefield Junction to Peaceable 115-kV Substation in Redding, CT | 2017-12-31 | Approved | 2015-04-16
ES-15-T45 | 2015-02-17 | Southwest Connecticut – Greater Hartford/Central Connecticut Transmission Project | Transmission notification from Eversource Energy (“ES”) for looping the 1570 line in and out of the United Illuminating Pootatuck 115-kV Substation in Shelton, CT. | 2017-12-31 | Approved | 2015-04-16
ES-15-T46 | 2015-02-17 | Southwest Connecticut – Greater Hartford/Central Connecticut Transmission Project | Transmission notification from Eversource Energy (“ES”) for separating the 3827 Line and the 1610 Line between Cook Hill Junction in Cheshire, CT and the Cheshire Hamden town line. | 2017-12-31 | Approved | 2015-04-16
ES-15-T47 | 2015-02-17 | Southwest Connecticut – Greater Hartford/Central Connecticut Transmission Project | Transmission notification from Eversource Energy (“ES”) for retirement of the two +/- 8 MVAr Stony Hill DVARs as part of the Southwest Connecticut (SWCT) Solutions. | 2017-12-31 | Approved | 2015-04-16
ES-15-T48 | 2015-02-17 | Southwest Connecticut – Greater Hartford/Central Connecticut Transmission Project | Transmission notification from Eversource Energy (“ES”) for retirement of the +/- 8 MVAr Bates Rock DVAR and a 13.8-kV capacitor bank as part of the Southwest Connecticut (SWCT) Solutions. | 2017-12-31 | Approved | 2015-04-16
UI-12-T15-Rev.1 | 2015-02-17 | Southwest Connecticut – Greater Hartford/Central Connecticut Transmission Project | Transmission notification from United Illuminating Company (“UI”) for the installation of a 115 kV series reactor (7.5 ohm) at Mix Avenue Substation in Hamden, CT located on the 1610-2 terminal. | 2017-12-31 | Approved | 2015-04-16
UI-15-T02 | 2015-02-17 | Southwest Connecticut – Greater Hartford/Central Connecticut Transmission Project | Transmission notification from United Illuminating Company (“UI”) for the re-conductor/rebuild the 2.26 mile overhead 88006A 115kV line to 1590 kcmil ACSS (or equivalent rated) from the Baird 115 kV Substation in Stratford, CT to the Devon Tie 115 kV Switching Station in Milford CT. | 2017-12-31 | Approved | 2015-04-16
UI-15-T03 | 2015-02-17 | Southwest Connecticut – Greater Hartford/Central Connecticut Transmission Project | Transmission notification from United Illuminating Company (“UI”) for the re-conductor/rebuild the 2.26 mile overhead 89006B 115kV line to 1590 kcmil ACSS (or equivalent rated) from the Baird 115 kV Substation in Stratford, CT to the Devon Tie 115 kV Switching Station in Milford CT. | 2017-12-31 | Approved | 2015-04-16
UI-15-T04 | 2015-02-17 | Southwest Connecticut – Greater Hartford/Central Connecticut Transmission Project | Transmission notification from United Illuminating Company (“UI”) for reconfiguring the Pootatuck 115 kV Substation in Shelton, CT into a 4 breaker ring bus and the addition of 115 kV capacitor bank (30 MVAR). | 2017-12-31 | Approved | 2015-04-16
UI-15-T05 | 2015-02-17 | Southwest Connecticut – Greater Hartford/Central Connecticut Transmission Project | Transmission notification from United Illuminating Company (“UI”) for the installation of two 25 MVAr 115 kV capacitor banks at the Ansonia Substation in Ansonia, CT (1 on 1560 terminal, 1 on 1594 terminal). | 2017-12-31 | Approved | 2015-04-16
ES-15-T01 | 2015-02-17 | Greater Hartford/Central Connecticut (GHCC) Transmission Project | Transmission notification from Eversource Energy (“ES”) for adding a new 345/115-kV autotransformer at Barbour Hill Substation in South Windsor, CT. The project requires reconfiguration of the existing substation and consists of installing one 345-kV to be designated 2T at the Barbour Hill 345-kV Substation and re-terminate the 3557 Line between the Barbour Hill 2T and 3T 345-kV circuit breakers. Install two 115-kV circuit breakers designated as the 2X3-A1 and 2X3-B1 at the Barbour Hill 115-kV Substation. Also add a second 345/115-kV autotransformer at the Barbour Hill Substation. The second 345/115-kV autotransformer at the Barbour Hill Substation shall have the same electrical impedances (R, X, and B) on a 100-MVA base as the existing Barbour Hill 1X autotransformer. | 2017-12-31 | Approved | 2015-04-16
ES-15-T02 | 2015-02-17 | Greater Hartford/Central Connecticut (GHCC) Transmission Project | Transmission notification from Eversource Energy (“ES”) for installation of a new 345-kV 24TA circuit breaker in series with the existing 345-kV 24T circuit breaker at Manchester Substation in Manchester, CT. | 2017-12-31 | Approved | 2015-04-16
ES-15-T03 | 2015-02-17 | Greater Hartford/Central Connecticut (GHCC) Transmission Project | Transmission notification from Eversource Energy (“ES”) for reconductoring the 115-kV 1763 Line between Manchester 115-kV Substation in Manchester, CT and CT Barbour Hill 115-kV Substation in South Windsor, CT with a 795 ACSS conductor. | 2017-12-31 | Approved | 2015-04-16
ES-15-T04 | 2015-02-17 | Greater Hartford/Central Connecticut (GHCC) Transmission Project | Transmission notification from Eversource Energy (“ES”) for constructing a new 115-kV line between Frost Bridge Substation in Watertown, CT and Campville Substation in Harwinton, CT. In addition to the proposed 115-kV line, there are substation modifications that are required to accommodate the new line and eliminate specific stuck breaker contingencies. These modifications are installation of three 115 kV circuit breakers (BTA, BT and 3TA) at Campville Substation and terminate the proposed line between the new BT and 3TA circuit breakers. Install the 2TA 115-kV circuit breaker in series with the 2T circuit breaker at Campville Substation. Install the AT 115-kV circuit breaker and terminate the proposed line in the bus section between the existing 24T circuit breaker and the proposed AT circuit breaker at Frost Bridge. | 2017-12-31 | Approved | 2015-04-16
ES-15-T05 | 2015-02-17 | Greater Hartford/Central Connecticut (GHCC) Transmission Project | Transmission notification from Eversource Energy (“ES”) for separating the 115-kV double circuit tower (DCT) configuration corresponding to the 115-kV1191 Line from Frost Bridge Substation in Watertown, CT to Campville Substation inHarwinton, CT and the 1921 Line from Thomaston Substation in Thomaston, CT toCampville Substation. | 2017-12-31 | Approved | 2015-04-16
ES-15-T06 | 2015-02-17 | Greater Hartford/Central Connecticut (GHCC) Transmission Project | Transmission notification from Eversource Energy (“ES”) for reconductoring the 115-kV 1810-1 Line from Southington Substation in Southington, CT to Lake Avenue Junction in Bristol, CT with 795 ACSS conductor | 2017-12-31 | Approved | 2015-04-16
ES-15-T07 | 2015-02-17 | Greater Hartford/Central Connecticut (GHCC) Transmission Project | Transmission notification from Eversource Energy (“ES”) for replacing the existing 115-kV 3% series reactors on the 1910 and 1950 Lines with 5% seriesreactors at Southington 115-kV Substation in Southington, CT | 2017-12-31 | Approved | 2015-04-16
ES-15-T08 | 2015-02-17 | Greater Hartford/Central Connecticut (GHCC) Transmission Project | Transmission notification from Eversource Energy (“ES”) for replacing the normally open 115-kV 19T circuit breaker with a 115-kV 3% series reactor at Southington Substation in Southington, CT. The 19T circuit breaker will be relocated to Ring Bus #1 and the proposed 21TA 115-kV circuit breaker will also be installed on Ring Bus #1 to establish the terminal position for the proposed series reactor. Additionally, the proposed 5TA 345-kV circuit breaker will be installed in series with the existing 5T circuit breaker in the Southington 345-kV Substation. | 2017-12-31 | Approved | 2015-04-16
ES-15-T09 | 2015-02-17 | Greater Hartford/Central Connecticut (GHCC) Transmission Project | Transmission notification from Eversource Energy (“ES”) for converting the Newington 115-kV Substation in Newington, CT into a ring bus. The project consists of installing two 115-kV circuit breakers AT and BT. Reterminating the 1785 Line into the terminal position between the existing 2T and proposed AT circuit breakers. Also reterminating the 1783 Line into position between the existing 1T and 2T circuit breakers. | 2017-12-31 | Approved | 2015-04-16
ES-15-T10 | 2015-02-17 | Greater Hartford/Central Connecticut (GHCC) Transmission Project | Transmission notification from Eversource Energy (“ES”) for reconductoring the 115-kV 1783-2 Line from Newington 115-kV Substation in Newington, CT to Newington Tap in Newington, CT, with 1590 ACSS conductor. 1783 line relocated to the ring bus position between the existing 1T and 2T breakers. | 2017-12-31 | Approved | 2015-04-16
ES-15-T11 | 2015-02-17 | Greater Hartford/Central Connecticut (GHCC) Transmission Project | Transmission notification from Eversource Energy (“ES”) for installing a new 5000 kcmil XLPE 115-kV underground cable between Newington 115-kV Substation in Newington, CT and Southwest Hartford Substation in Hartford, CT. The line will be terminated at Newington Substation to the position between the existing 2T and the proposed AT 115-kV circuit breakers. The line will connect to a new 2% series reactor with a parallel bypass switch. The series reactor and bypass switch will terminate between the new AT and BT circuit breakers at Southwest Harford Substation. Also installing two 115-kV, 63-kA, 3000A circuit breakers (AT and BT) at the Southwest Hartford Substation. | 2017-12-31 | Approved | 2015-04-16
ES-15-T12 | 2015-02-17 | Greater Hartford/Central Connecticut (GHCC) Transmission Project | Transmission notification from Eversource Energy (“ES”) for installing the two 115-kV circuit breaker (AT and BT) at the Southwest Hartford Substation and converting the Southwest Hartford Substation into a ring bus. | 2017-12-31 | Approved | 2015-04-16
ES-15-T13 | 2015-02-17 | Greater Hartford/Central Connecticut (GHCC) Transmission Project | Transmission notification from Eversource Energy (“ES”) for installing a 26 TA 115-kV circuit breaker in series with the existing 26T circuit breaker at the Berlin Substation in Berlin CT. Also relocate the existing 115 kV 50.5 MVAR capacitor bank from 115 kV B bus to the 115 kV A bus. | 2017-12-31 | Approved | 2015-04-16
ES-15-T14 | 2015-02-17 | Greater Hartford/Central Connecticut (GHCC) Transmission Project | Transmission notification from Eversource Energy (“ES”) for installing a 115-kV 3% series reactor in series with the 1704 Line at Southwest Hartford 115-kV Substation in Hartford, CT | 2017-12-31 | Approved | 2015-04-16
ES-15-T15 | 2015-02-17 | Greater Hartford/Central Connecticut (GHCC) Transmission Project | Transmission notification from Eversource Energy (“ES”) for reconfiguring the 115-kV Rood Avenue 115-kV Substation in Windsor, CT to a ring bus by installing four new 115-kV circuit breakers in the AT, BT, CT and DT positions. Also loop the 115-kV 1779 Line in and out of Rood Avenue 115-kV Substation to create two 2-terminal lines between South Meadow 115-kV Substation in Hartford, CT to Rood Avenue Substation and Rood Avenue Substation to Bloomfield Substation in Bloomfield, CT. | 2017-12-31 | Approved | 2015-04-16
ES-15-T16 | 2015-02-17 | Greater Hartford/Central Connecticut (GHCC) Transmission Project | Transmission notification from Eversource Energy (“ES”) for upgrading the1779 line between Rood Avenue 115-kV Substation in Windsor, CT and Bloomfield 115-kV Substation in Bloomfield, CT and separating the 1777/1779 DCT. In addition, the proposed 2TA 115-kV circuit breaker will be installed at Bloomfield Substation in Bloomfield, CT. The reconfigured 1779 Line will be terminated between the proposed 2TA and existing 3T circuit breakers at Bloomfield Substation. | 2017-12-31 | Approved | 2015-04-16
ES-15-T17 | 2015-02-17 | Greater Hartford/Central Connecticut (GHCC) Transmission Project | Transmission notification from Eversource Energy (“ES”) for separating the 1751/1777 DCT between Bloomfield 115-kV Substation in Bloomfield, CT and Bloomfield Junction in Bloomfield, CT and installing the 13TA 115-kV circuit breaker in series with the existing 13T circuit breaker at North Bloomfield 115-kV Substation in Bloomfield, CT. | 2017-12-31 | Approved | 2015-04-16
ES-15-T18 | 2015-02-17 | Greater Hartford/Central Connecticut (GHCC) Transmission Project | Transmission notification from Eversource Energy (“ES”) for installing three new single phase 200-MVA rated 345/115-kV autotransformers at Haddam 11C Substation in Haddam, CT with same electrical impedances (R, X, and B), ratings (Normal, STE, LTE) and the same LTC tap size and range as the existing Haddam autotransformer. Install four 345 kV circuit breaker and reconfigure the Haddam 345‐kV Substation into a breaker-and-half configuration. Also split the 345 kV 348 Line into two 2‐terminal lines 348E ‐ Millstone to Haddam, and 348W - Haddam to Beseck. Reconfigure the Haddam Substation. | 2017-12-31 | Approved | 2015-04-16
ES-15-T19 | 2015-02-17 | Greater Hartford/Central Connecticut (GHCC) Transmission Project | Transmission notification from Eversource Energy (“ES”) for installing six new 115-kV circuit breakers in Green Hill Substation in Madison, CT, and reconfiguring the substation into a ring bus, and installing two 25.2 MVAr capacitor banks. | 2017-12-31 | Approved | 2015-04-16
ES-15-T20 | 2015-02-17 | Greater Hartford/Central Connecticut (GHCC) Transmission Project | Transmission notification from Eversource Energy (“ES”) for adding one 115-kV circuit breaker and installing one 37.8 MVAr capacitor bank at the Hopewell Substation in Glastonbury, CT. | 2017-12-31 | Approved | 2015-04-16
ES-15-T21 | 2015-02-17 | Greater Hartford/Central Connecticut (GHCC) Transmission Project | Transmission notification from Eversource Energy (“ES”) for installing one 25.2 MVAr capacitor bank and 115-kV circuit breaker on the 1766 line terminal at the West Side Substation in Middletown, CT | 2017-12-31 | Approved | 2015-04-16
ES-15-T22 | 2015-02-17 | Greater Hartford/Central Connecticut (GHCC) Transmission Project | Transmission notification from Eversource Energy (“ES”) for separating the existing 1572-1620 DCT configuration between Middletown and Pratt and Whitney Substations between Middletown and Haddam Substations. | 2017-12-31 | Approved | 2015-04-16
ES-15-T23 | 2015-02-17 | Greater Hartford/Central Connecticut (GHCC) Transmission Project | Transmission notification from Eversource Energy (“ES”) for separating the existing 1537-1655 DCT configuration between Branford and Branford Railroad Substations and between Branford and North Haven Substations. It also consists of installing one new 115-kV circuit breaker adjacent to the 2T circuit breaker at the Branford 115-kV Substation in Branford, CT. | 2017-12-31 | Approved | 2015-04-16
ES-15-T24 | 2015-02-17 | Greater Hartford/Central Connecticut (GHCC) Transmission Project | Transmission notification from Eversource Energy (“ES”) for increasing the 37.8 MVAr capacitor at Branford 115-kV Substation in Branford, CT to 50.4 MVAr. | 2017-12-31 | Approved | 2015-04-16
NU-08-T61-Rev.1 | 2015-02-17 | Greater Hartford/Central Connecticut (GHCC) Transmission Project | PPA Withdrawal Notification from Eversource Energy (formally NU) for the Frost Bridge 18R Substation expansion by adding a 345/115 kV autotransformer. | 2017-12-31 | Withdrawn | 2015-04-16
NU-12-T15 | 2015-02-17 | Greater Hartford/Central Connecticut (GHCC) Transmission Project | PPA Withdrawal Notification from Eversource Energy (formally NU) for the North Bloomfield 2A Substation expansion. | 2017-12-31 | Approved | 2015-04-16
NU-12-T16-Rev.1 | 2015-02-17 | Greater Hartford/Central Connecticut (GHCC) Transmission Project | PPA Withdrawal Notification from Eversource Energy (formally NU) for the addition of a 2nd Beseck 9F Substation variable shunt reactor (75-150 MVAr). | 2017-12-31 | Approved | 2015-04-16
ES-15-T53 | 2015-02-25 | Blair Pond Substation Project | Transmission notification from Eversource Energy (“ES”) for the construction of a new Blair Pond 115/13.8 kV substation in Belmont, MA. The substation will have a 115 kV ring bus and will be supplied by existing 329-530115 kV line between the North Cambridge and Brighton substations (to be re-numbered as 509-530). | 2016-06-30 | Approved | 2015-04-16
VELCO-15-T01 | 2015-02-27 | Connecticut River Corridor Transmission Project | Transmission Application from Vermont Electric Power Company (“VELCO”) to upgrade the existing K31 Coolidge to Ascutney 115 kV Line with 1351 ACSS conductor. | 2017-10-30 | Approved | 2015-04-16
VELCO-15-T02 | 2015-02-27 | Connecticut River Corridor Transmission Project | Transmission Application from Vermont Electric Power Company (“VELCO”) to install a 50/-25 MVAr Static VAR Compensator (SVC) at the Ascutney Substation and add a third bay to the Ascutney Substation. | 2017-10-30 | Approved | 2015-04-16
VELCO-15-T03 | 2015-02-27 | Connecticut River Corridor Transmission Project | Transmission Application from Vermont Electric Power Company (“VELCO”) to split the Harford 25 MVAr capacitor bank into two 12.5 MVAr capacitor banks. | 2017-10-30 | Approved | 2015-04-16
VELCO-15-T04 | 2015-02-27 | Connecticut River Corridor Transmission Project | Transmission Application from Vermont Electric Power Company (“VELCO”) to reconfigure the Chelsea 115 kV Substation from a straight bus to a 3 breaker ring substation. | 2017-10-30 | Approved | 2015-04-16
NEP-15-T02 | 2015-03-06 | Ipswich River/Peabody Substation Project | Transmission notification from New England Power Company “NEP”) for the removal of the existing single transformer Ipswich River 115–23 kV substation currently tapped from B-154N line and installation of a new two transformer Ipswich River 115–23 kV substation which will tap both the B-154N and the C-155N lines. | 2016-05-30 | Approved | 2015-04-16
NEP-15-G01 | 2015-03-03 | Spruce Ridge Wind Generation and Transmission Project | Generator Notification from New England Power Company (“NEP”) on behalf of Spruce Ridge Wind Farm LLC for the installation of 28 1.815 Vestas V1000 wind turbine generators (50.82 MWs net output) located in Groton, NH. Construction of two 34.5 kV collector circuits with 14 wind turbines per circuit. Also install a 230/34.5/13.8 kV main transformer with 40/53/66 MVA rating and switchgear to interconnect the wind power facility. | 2017-09-15 | Approved | 2015-04-16
NEP-15-T01 | 2015-03-03 | Spruce Ridge Wind Generation and Transmission Project | Transmission notification from New England Power Company (“NEP”) for the construction of a 230 kV interconnection substation in Groton, NH, which includes three 230kV, 3000A, 40kA, non-IPT breakers and nine (9) 230kV, 3000A three phase motor operated disconnects. Construct a 0.05 mile long, 230 kV tap line connecting the interconnection substation to the 230 kV A-201 transmission line. Connect the interconnection substation to the proposed wind power facility as specified in NEP-15-G01. | 2017-09-15 | Approved | 2015-04-16
ES-15-T55 | 2015-03-03 | Spruce Ridge Wind Generation and Transmission Project | Transmission notification from Eversource Energy (“ES”) for the thermal upgrade of the 11 mile 115 kV A111 Line from Webster Substation in Webster, NH to Pemigewassett Substation in Littleton, NH from 135 MVA to 138 MVA in support of the Spruce Ridge Wind Generator Project. | 2017-09-15 | Approved | 2015-04-16
ES-15-T56 | 2015-03-03 | Spruce Ridge Wind Generation and Transmission Project | Transmission notification from Eversource Energy (“ES”) for the thermal upgrade of the 8 mile 115 kV E115-2 Line from Ashland Tap in Ashland, NH to the Pemigewassett Substation in Littleton, NH from 135 MVA to 138 MVA in support of the Spruce Ridge Wind Project. | 2017-09-15 | Approved | 2015-04-16
GRE-15-G01 | 2015-03-10 | Granite Ridge Generator Uprate Project | Generator notification from Granite Ridge Energy LLC (“GRE”) for the summer incremental net capacity uprate of +40 MW (at ≥ 50° F) of an existing 2x1 combined cycle facility. The steam turbine generator (STG) will be connected at PSNH’s 115 kV Watts Brook station and the combustion turbine generators (CTG1 and CTG2) will be connected at National Grid’s 230 kV North Litchfield station. CTG1 and CTG2 will both be upgraded by approximately 17.5 MW, and STG will be upgraded by 5 MW (at ≥ 50° F). The combined plant summer rated net output is 761 MW (at ≥ 50° F). The winter incremental net capacity uprate is +8 MW for a combined net plant output of 814 MW (at ≥ 0° F). | 2015-03-17 | Approved | 2015-04-16
VELCO-15-GNF03 | 2015-02-20 | Stafford Hill Solar Project | Generation notification from Vermont Electric Power Company (“VELCO”) for the installation of a 2.0 MW solar array interconnecting at the East Rutland Substation via the 12.47 kV Circuit #51, Line 222, Pole 2-5 in Rutland, VT. | 2015-04-30 | Notification | 2015-04-16
ES-15-T60 | 2015-03-02 | 533-508 Line Upgrade Project | Transmission notification from Eversource Energy (“ES”) for upgrading the 533-508 Line from Hartwell Avenue Substation in Lexington, MA to Lexington Substation in Lexington, MA by removing sag limitation, replacing cable risers and control and protection changes including installing new meter and CTs. Once the upgrade is complete, the line will be rated to the full conductor rating of 282/359/400 MVA Summer. Existing ratings are 279/279/279 MVA Summer | 2015-05-30 | Notification | 2015-04-16
NEP-15-GNF06 | 2015-03-06 | TJA Bridgewater Solar Project | Generator notification from New England Power Company (“NEP”) on behalf of TJA Solar LLC, PV Project for the installation of a 2.967 MW solar array in Bridgewater, MA and customer fed by Feeder #797W1 out of the East Bridgewater Substation #797. | 2015-05-22 | Notification | 2015-04-16
NEP-15-GNF05 | 2015-03-06 | Bluewave Capital Sturbridge Solar Project | Generator notification from New England Power Company (“NEP”) on behalf of Bluewave Capital LLC, PV Project for the installation of a 2 MW solar array in Sturbridge, MA and customer fed by Feeder #415L3 out of the West Charlton Substation #415. | 2015-05-24 | Notification | 2015-04-16
ES-15-G03 | 2015-03-03 | Wind Colebrook South Project | Generator notification from Eversource Energy (“ES”) on behalf of Wind Colebrook South LLC for the installation of a 4.98 MW wind turbine generator located in Colebrook, CT and interconnecting to the 27 kV Canton 5R Substation circuit 5R80. | 2015-06-01 | Notification | 2015-04-16
NEP-15-GNF04 | 2015-01-30 | Johnston Solar Project | Generator notification from New England Power Company (“NEP”) on behalf of Johnston Solar I LLC for the installation of a 1.375 MW solar array located in Johnston, RI and interconnecting via the Feeder #21F2 out of the West Cranston Substation #21 | 2015-04-01 | Approved | 2015-02-25
NEP-15-GNF03 | 2015-01-30 | Synacarpha Leominster Solar Project | Generator notification from New England Power Company (“NEP”) on behalf of Syncarpha Massachusetts LLC for the installation of a 2.0 MW solar array located in Leominster, MA and interconnecting via the Feeder #219W2 out of the Prospect Street Substation #219. | 2015-02-28 | Approved | 2015-02-25
NEP-15-GNF02 | 2015-01-30 | Solar City Swansea Solar Project | Generator notification from New England Power Company (“NEP”) on behalf of Solar City Corporation for the installation of a 2.0 MW solar array located in Swansea, MA and interconnecting via the Feeder #11W84 out of the Swansea Substation #11. | 2015-04-24 | Approved | 2015-02-25
NEP-15-GNF01 | 2015-01-30 | North Adams Solar Project | Generator notification from New England Power Company (“NEP”) for the installation of a 2.25 MW solar array located in North Adams, MA and interconnecting via the Feeder #1015W01 out of the Walker Street Substation #1015. | 2015-04-06 | Approved | 2015-02-25
ES-15-T52 | 2015-01-29 | Valley Substation Transformer Replacement Project | Transmission notification from Eversource Energy Service Company (“ES”) for the replacement of the Valley #2 15/20/25 MVA Transformer bank with a new 30/40/50 MVA 115/23kV transformer bank, 23kV secondary breaker, and 23kV breaker disconnect switches located in Plymouth, MA. | 2015-06-01 | Approved | 2015-02-25
NMLD-15-T01 | 2015-01-21 | Norwood Line 447-508 and 447-509 Line Rehabilitation Project | Transmission notification from Norwood Municipal Light Department (“NMLD”) for the rehabilitation of 115 kV lines 447-508 and 447-509 from the NSTAR tap in Sharon to the Dean St. #495 substation in Norwood, MA | 2016-11-30 | Approved | 2015-02-25
UI-15-G01 | 2015-01-20 | University of Bridgeport Fuel Cell Project | Generator notification from United Illuminating Company (“UI) on behalf of UB Fuel Cell for the installation of a 1.389 MW (net output) fuel cell generator in Bridgeport, CT and interconnecting to the Pequonnock Substation Feeder #2507. | 2015-02-11 | Approved | 2015-02-25
ES-15-T25 | 2015-02-10 | 1779 Line Upgrade Project | Transmission notification from Eversource Energy Service Company (“ES”) for the rebuilding of 1779 115-kV Line from South Meadow Substation to Bloomfield Substation in Bloomfield, CT due to asset conditions. | 2017-12-31 | Approved | 2015-02-25
FW-15-G01 | 2015-01-01 | Blue Sky Wind Generation and Transmission Project | Generation notification from First Wind Energy Marketing (“FW”) on behalf of Blue Sky West LLC for the construction of 56 Vestas 3.3 MW wind turbine generators (184.8 MWs net output) and a 60 MVA synchronous condenser and an associated collector system, located in Piscataquis County, ME. | 2016-12-31 | Approved | 2015-03-02
FW-15-T01 | 2015-01-01 | Blue Sky Wind Generation and Transmission Project | Transmission notification from First Wind Energy Marketing (“FW”) on behalf of Blue Sky West LLC for the construction of a new 34.5/115 kV Substation (Blue Sky West Substation) located in Bingham, ME, and 17 miles of overhead 795 KCM ACSR 2 conductor, bundle 115 kV transmission line between the Blue Sky West Substation and the Guilford Substation. | 2016-12-31 | Approved | 2015-03-02
CMP-15-T01 | 2015-01-01 | Blue Sky Wind Generation and Transmission Project | Transmission notification from Central Maine Power Company (“CMP”) for the installation of a 0/+70 MVAR SVC at the Detroit Substation located in Detroit, ME, in association with the Blue Sky West Wind Farm. | 2017-05-01 | Approved | 2015-03-02
CMP-15-T02 | 2015-01-01 | Blue Sky Wind Generation and Transmission Project | Transmission notification from Central Maine Power Company (“CMP”) for the rerate of Section 85 115 kV line from Detroit to Guilford Substations and add a three breaker ring bus to the Guilford Substation located in Parkman, ME, in association with the Blue Sky West Wind Farm. | 2016-08-01 | Approved | 2015-03-02
EM-15-T01 | 2015-01-01 | Blue Sky Wind Generation and Transmission Project | Transmission notification from Emera Maine (“EM”) for the reinstallation of the existing Orrington series capacitor (originally S388, now S3023 due to a line reconfiguration change), reducing its size from 25 ohms to 22.32 ohms. Also install a second series capacitor in S388 to compensate 42% of the Orrington toCoopers Mills line section. | 2016-12-31 | Approved | 2015-03-02
PSEG-15-G01 (Revision available) | 2015-01-07 | Bridgeport Harbor Combined Cycle Generator and Transmission Project | Generator notification from PSEG Energy Resources & Trade LLC (“PSEG”) for the construction of a 517.5 MW (Summer Net Output)/542.5 MW (Winter Net Output) 1x1 Combined Cycle Gas & Steam Turbine generator located in Bridgeport, CT. | 2018-05-31 | Approved | 2015-02-10
PSEG-15-T01 (Revision available) | 2015-01-07 | Bridgeport Harbor Combined Cycle Generator and Transmission Project | Transmission notification from PSEG Energy Resources & Trade LLC (“PSEG”) for the installation of a 430 MVA transformer for the CT GSU-1 interconnecting the Bridgeport Harbor CCGT generator at the Singer 345 kV Substation. | 2018-05-31 | Approved | 2015-02-10
PSEG-15-T02 (Revision available) | 2015-01-07 | Bridgeport Harbor Combined Cycle Generator and Transmission Project | Transmission notification from PSEG Energy Resources & Trade LLC (“PSEG”) for the installation of a 430 MVA transformer for the ST GSU-2 interconnecting the Bridgeport Harbor CCGT generator at the Singer 345 kV Substation. | 2018-05-31 | Approved | 2015-02-10
UI-15-T01 | 2015-01-07 | Bridgeport Harbor Combined Cycle Generator and Transmission Project | Transmission notification from United Illuminating Company (“UI”) to terminate and connect the 345 kV underground line from the Bridgeport Harbor Combined Cycle Generator to the Singer 345 kV Substation. | 2018-05-31 | Approved | 2015-02-10
BE-15-G01 | 2015-01-02 | Bridgeport Energy Generator Uprate | Generator notification from Emera Energy Service Subsidiary #5/Bridgeport Energy (“BE”) to increase the net output of the Bridgeport Energy combined cycle generator (BE ST10, CT 11, CT 12) located in Bridgeport, CT by 47.8 MWs at 50 degrees. | 2015-03-01 | Approved | 2015-02-10
NU-14-G11 | 2015-01-09 | TJA Carver Solar Project | Generator notification from Northeast Utilities Service Company (“NU”) on behalf of TJA Solar Inc. for the installation of a 4.99 MW solar array located in Carver, MA and interconnecting to the NU Brook Street Substation #727, 23 kV feeder #51, 23 kV circuit #980. | 2015-03-01 | Notification | 2015-02-10
VELCO-15-GNF01 | 2015-01-05 | Whitcomb Solar Project | Generator notification from Vermont Electric Power Company (“VELCO) on behalf of Chester Power Partners for the installation of a 2.175 MW solar array and interconnecting to the 19G5 feeder to the Essex Substation in Essex Junction, VT. | 2014-10-30 | Notification | 2015-02-10
VELCO-15-GNF02 | 2015-01-05 | Chester Solar Project | Generator notification from Vermont Electric Power Company (“VELCO) on behalf of ER WR Whitcomb Farm Solar, LLC for the installation of a 2.2 MW solar array and interconnecting Substation #11, Circuit #03, Poll 1-3-2 in Chester, VT. | 2014-11-03 | Notification | 2015-02-10
EXE-14-X01 | 2014-12-11 | Framingham and Mystic AVR Replacement Project | Transmission notification from Exelon Generation Company LLC (“EXE”) for the replacement of the excitation controller and AVRs at Framingham Station (Jets 1, 2 and 3). The upgrade will install a new Allen Bradley Combination Generation Control Module with Series Boost Unit at each jet, which will provide excitation current to the existing brushless exciters and replace the existing AVRs. | 2014-12-19 | Approved | 2014-12-29
EXE-14-X02 | 2014-12-11 | Framingham and Mystic AVR Replacement Project | Transmission notification from Exelon Generation Company LLC (“EXE”) for the replacement of the excitation controller and AVR at the Mystic Jet. The upgrade will install a new Allen Bradley Combination Generation Control Module with Series Boost Unit, which will provide excitation current to the existing brushless exciter and replace the existing AVR. Proposed in service date of the project is | 2014-12-19 | Approved | 2014-12-29
VELCO-14-GNF10 | 2014-11-14 | Barton Solar Project | Generator notification from Vermont Electric Company (“VELCO”) on behalf of Barton Solar. LLC for the installation of a 1.89 MW solar array located in Barton, VT and interconnecting to the 3A feeder origination from the Burton Hill Substation via the 3A5 pad-mounted recloser located at the Barton Solar project. | 2014-11-14 | Notification | 2015-01-13
NEP-14-GNF21 | 2014-12-05 | SEC CRSD Solar One Solar Project | Generator notification from New England Power Company (“NEP”) on behalf of SEC CRSD Solar One, LLC for the installation of a 2.89 MW solar array located in Hardwick, MA and interconnecting via Feeder #501L2 out of the Ware Substation #501. | 2014-12-31 | Notification | 2015-01-13
NEP-14-GNF22 | 2014-12-05 | Solar City Williamsburg Solar Project | Generator notification from New England Power Company (“NEP”) on behalf of Solar City Corp. for the installation of a 2.266 MW solar array located in Williamsburg, MA and interconnecting via Feeder #909W3 out of the Florence Junction Substation #909. | 2014-12-22 | Notification | 2015-01-13
CMP-14-X01 | 2014-12-11 | Eliminate 3rd Path of Section 396 SPS Project | Transmission notification from Central Maine Power Company (“CMP”) for the elimination of the 3rd Path of Section 396 SPS because of over-redundancy | 2015-01-01 | Notification | 2015-01-13
WBLTN-14-G01 | 2014-10-03 | Borrego West Boylston Solar | Generator notification from West Boylston Municipal Lighting Plant (“WBLTN”) on behalf of Borrego Solar Systems Inc. for the installation of a 3.0 MW solar array located in West Boylston, MA and interconnecting to the 13.8 kV Hartwell Street feeder via the West Boylston Substation P142W. |  | Notification | 2014-09-09
PWF-14-G01 | 2014-10-29 | Passadumkeag Wind Restudy Project | Wind Generation project with total output 39.975MW, connecting to Emera Maine Line 64 by means of a new collector substation |  | Approved | 2014-09-09
PWF-14-T01 | 2014-10-29 | Passadumkeag Wind Restudy Project | Q357 Collector substation 115/34.5 kV under load tap changing transformer located at the collector substation and point of interconnection with Emera Maine. |  | Approved | 2014-09-09
EM-14-T02 | 2014-10-29 | Passadumkeag Wind Restudy Project | Ring bus tap of existing Line 64 and renumber of southern portion of that line |  | Approved | 2014-09-09
DEM-14-G01 | 2014-11-05 | Manchester Street Generator Uprate Project | Generator notification from Dominion Energy, Manchester St, Inc. (“DEM”) for the increased MW output of Manchester St generators 9/9A, 10/10A, and 11/11A based on upgrades performed to the combustion turbines. As a result, the station’s summer NCR will increase from 483 MWs to 510 MWs and the CNRC will increase from 447 MWs to 477 MWs. | 2015-03-02 | Approved | 2014-12-01
NU-14-T21 | 2014-10-01 | Sudbury Station 115 kV Shunt Reactor Installation Project | Transmission notification from Northeast Utilities Service Company (“NU”) for the installation of two new 115 kV, 20 MVAR shunt reactors at Sudbury Substation. The new reactors are needed to lower transmission voltages in the Sudbury - Maynard load area under light load conditions. The main project components consist of the 115 kV, 20 MVAR reactors and associated 115 kV circuit breakers with a synchronous switching controller. | 2014-12-01 | Approved | 2014-11-20
NU-13-T31-Rev.1 | 2014-11-06 | Peaslee Substation Modification Project | Transmission notification from Northeast Utilities Service Company (“NU”) for the Peaslee Substation project to alleviate breaker failure contingencies through a change in the line termination points at the Peaslee Substation | 2016-06-01 | Approved | 2014-12-01
NEP-14-GNF17 | 2014-11-07 | Clinton Solar Project | Generator notification from New England Power Company (“NEP”) on behalf of Solar MA Project Management LLC for the installation of a 2.0 MW solar array located in Clinton, MA and interconnecting to the Fitch Road 216 Substation via the 13.8 kV 216W5 feeder. | 2014-12-01 | Notification | 2014-12-01
NEP-14-GNF18 | 2014-11-07 | RIN Logistics Fall River Solar Project | Generator notification from New England Power Company (“NEP”) on behalf of RIN Logistics Inc. for the installation of a 1.5 MW solar array located in Fall River, MA and interconnecting to the Sykes Road 28 Substation via the 13.8 kV 28W51 feeder. | 2014-11-15 | Notification | 2014-12-01
NEP-14-GNF19 | 2014-11-07 | Independence Stoughton Solar Project | Generator notification from New England Power Company (“NEP”) on behalf of Independence Solar VII LLC for the installation of a 1.725 MW solar array located in Stoughton, MA and interconnecting to the Parkview 94 Substation via the 13.8 kV 94W42 feeder. | 2014-11-14 | Notification | 2014-12-01
NEP-14-GNF20 | 2014-11-07 | Sune Solar Norton Solar Project | Generator notification from New England Power Company (“NEP”) on behalf of Sune Solar Norton 1 LLC for the installation of a 3.0 MW solar array located in Norton, MA and interconnecting to the Easton 92 Substation via the 13.8 kV 92W79 feeder. | 2014-12-31 | Notification | 2014-12-01
NEP-14-T12 | 2014-11-07 | Webster Street Tap #1 Reconductor Project | Transmission notification from New England Power Company (“NEP”) for the reconductor of 2.2 miles of overhead transmission of the 115 kV A-127 line. | 2017-05-01 | Notification | 2014-12-01
NU-12-T44-Rev.1 | 2014-10-29 | Littleton Substation Autotransformer Revision Project | Transmission notification from Northeast Utilities Service Company (“NU”) for the installation of a 230 kV circuit breaker versus the initial design of a circuit switcher on the second 230/115 kV Littleton Autotransformer TB138 located in Littleton, NH to enable future improvements in area fault isolation. | 2014-11-04 | Notification | 2014-12-01
NU-14-G02 | 2014-10-23 | Novartis Synchronous Generator Project | Generator notification from Northeast Utilities Service Company (“NU”) on behalf of Novartis for the installation of two 1.4 MW synchronous generators in Cambridge, MA. Generator one will interconnect to the Putnam Station #831, Bus Section A via 14 kV distribution line 831-1301. Generator 2 will interconnect to the Putnam Station #831, Bus Section B via 14 kV distribution line 831-1324. | 2014-12-31 | Notification | 2014-12-01
VELCO-14-GNF09 | 2014-11-05 | GMP Park Street Rutland Solar Project | Generator notification from Vermont Electric Company (“VELCO”) on behalf of Park Street Solar for the installation of a 1.833 MW solar array located in Rutland, VT and interconnecting to the South Rutland Substation 12.47 kV circuit 70. | 2014-11-30 | Notification | 2014-12-01
VELCO-14-GNF08 | 2014-11-05 | Route 7 Rutland Solar Project | Generator notification from Vermont Electric Company (“VELCO”) on behalf of NextSun Energy Rutland for the installation of a 1.5 MW solar array located in Rutland, VT and interconnecting to the North Rutland Substation 12.47 kV circuit 34. | 2014-11-30 | Notification | 2014-12-01
BRP-14-X01 | 2014-10-08 | Cataract Hydro AVR Replacement Project | Transmission notification from Brookfield Renewable Energy (“BRP”) for the replacement of the Automatic Voltage Regulator (“AVR”) at the Cataract Hydro Unit 1 located near the Louden 115 kV Substation. | 2015-10-16 | Approved | 2014-11-20
BRP-14-G01 | 2014-10-03 | Wyman Hydro Upgrade Project | Generator notification from Brookfield Renewable Power (BRP) for the upgrade of the Wyman Hydro Units 1 & 3. Unit 1 will perform a turbine runner replacement, GSU transformer replacement and excitation system replacement. Unit 3 will perform a turbine runner replacement, stator rewinding and excitation system replacement. Upgrades will result in a 7.1 MW net output increase for the units to 30 MWs (total net output) and increased reactive capability. | 2015-03-31 | Approved | 2014-11-20
BELD-14-G01 | 2014-10-06 | Watson 3 (Potter Repowering) Generator Project | Generator notification from Braintree Electric Light Department (“BELD”) for the installation of a combustion turbine generator with a maximum summer net output of 63.3 MW (at 50° F and higher). The Project will be interconnected at the same point as the existing Potter II combined cycle plant. The existing Potter II plant and associated generator step-up transformer (GSU) will be retired prior to QP438 being placed into service. The Project will result in a MW capacity reduction of approximately 22 MW (summer, ≥ 50° F) and 32 MW (winter, ≥ 0° F) at the Potter 115kV station. | 2018-11-22 | Approved | 2014-11-20
BELD-14-T01 | 2014-10-06 | Watson 3 (Potter Repowering) Generator Project | Transmission notification from Braintree Electric Light Department (“BELD”) for the interconnection of the Watson 3 generator to the 115 kV Switchyard Station 16 via a 636 KCMIL Aluminum 0.03 mile overhead 115 kV line. | 2018-11-22 | Approved | 2014-11-20
NU-14-G09 | 2014-10-07 | Freetown Braley 2 Solar Project | Generator notification from Northeast Utilities Service Company (“NU”) On behalf of Braley Rd II LLC, c/o Rockland Capital for the installation of a 2.948 MW solar array located in East Freetown, MA and interconnecting to the NU Industrial Park Substation #636 via the 13.2 kV feeder #108. | 2014-10-01 | Notification | 2014-11-20
NU-14-G10 | 2014-10-07 | Freetown Chace Road Solar Project | Generator notification from Northeast Utilities Service Company (“NU”) on behalf of Braley Rd II LLC, c/o Rockland Capital for the installation of a 4.5 MW solar array located in East Freetown, MA and interconnecting to the NU Industrial Park Substation #636 via the 13.2 kV feeder #108. | 2014-10-01 | Notification | 2014-11-20
NU-14-G08 (Revision available) | 2014-10-07 | NextAmp Dartmouth Solar Project | Generator notification from Northeast Utilities Service Company (“NU”) on behalf of NextAmp Capital, LLC for the installation of a 4.68 MW solar array located in Dartmouth, MA and interconnecting to the NU Cross Road Substation #651 via the 13.2 kV feeder #543. | 2016-01-01 | Notification | 2014-11-20
NU-14-T71 | 2014-10-07 | Bloomfield 3X 115/23 kV Distribution Transformer Replacement Project | Transmission notification from Northeast Utilities Service Company (“NU”) for the replacement of the existing Bloomfield 3X 115/23 kV distribution transformer at the Bloomfield 3B 115/23 kV substation in Bloomfield CT. The new transformer will be rated at 60MVA, 115/23 kV. | 2014-11-30 | Notification | 2014-11-20
WGE-14-G01 | 2014-10-08 | Twiss Street Solar Project | Generator notification from Westfield Gas & Electric Department (“WGE”) for the installation of a 1.5 MW solar array in Westfield, MA and interconnecting to the WGE Buck Pond 34B substation via the 23 kV Feeder #34B7. | 2014-12-31 | Notification | 2014-11-20
VELCO-14-GNF07 | 2014-09-29 | Boltonville Hydro Project | Generator notification from Vermont Electric Power Company (“VELCO”) for the interconnection of a 1.318 MW run of river hydro generator in Boltonville, VT and interconnecting to the Ryegate Power Substation #85 via the 85G2 circuit. Proposed in service date of the project will be upon completion of the project interconnection agreement if required. |  | Notification | 2014-11-20
NU-14-G16 | 2014-09-02 | Jericho Wind Farm Expansion Project | Generator notification from Northeast Utilities Service Company (“NU”) on behalf of Queue Position #437 for the installation of two 2.85 MW wind turbine generators at the Jericho Wind Farm. Project will interconnect to the PSNH Jericho Road 34/.5 kV Substation in Berlin, NH. Unit name plate capability is 5.7 MWs but due to distribution system limitations, the combined total output of the project and QP #415 will be limited by a wind farm controller 10 12.05 MWs, a 3.5 MW increase from the original QP #415 project | 2014-11-01 | Approved | 2014-10-21
NEP-14-T10 | 2014-09-02 | Southeast Substation Project | Transmission notification from New England Power Company (“NEP”) for the construction of a new Southeast Substation located in Pawtucket, RI. Project will consist of two 115/13.8 kV 33/44/55 MVA LTC transformer supplied via taps off the X3 and T7 Lines. In addition, at Pawtucket No. 1 substation, move the T74 115/13.8 kV transformer to the T71 transformer position and retire existing T71 115/13.8 kV transformer and associated 13.8 kV indoor bus. | 2014-12-01 | Approved | 2014-10-21
NU-14-G17 | 2014-09-09 | Brewster Landfill Solar Project | Generator notification from Northeast Utilities Service Company (“NU”) on behalf of CF CVEC Owner One LLC the installation of a 1.083 MW solar array located in Brewster, MA and interconnecting to the NU Harwich Substation #968, #118 transformer via the 23 kV feeder #89A. | 2014-09-05 | Notification | 2014-10-21
NEP-14-T11 | 2014-09-09 | Ward Hill Transformer Replacement Project | Transmission Notification from New England Power Company (“NEP”) for the replacement of the existing 48/64/80 MVA 115/24 kV T1 transformer with a new 45/60/75 MVA 115/24 kV transformer due to unit conditions at the Ward Hill substation located in Haverhill, MA. | 2014-06-01 | Notification | 2014-10-21
NEP-14-T05 | 2014-08-25 | East Beverly Substation Transformer Replacement Project | Transmission notification from New England Power Company (“NEP”) for the replacement of two existing 115/34.5 kV 24/32/40 MVA transformers with115/34.5 kV 33/44/55 MVA transformers at the East Beverly Substation located in Beverly, MA. | 2016-11-01 | Notification | 2014-10-21
UI-14-G03 | 2014-08-28 | UI Seaside Renewable Solar Project | Generator notification from United Illuminating Company (“UI”) for the installation of a 2.2 MW solar array fuel cell generator located in Bridgeport CT and interconnecting to the Pequonnock 115/13.8 KV Substation 13.8 kV bus #1, position #8, circuit #2501. | 2015-07-01 | Notification | 2014-10-21
VELCO-14-T01 | 2014-07-14 | PV 20 Cable Line Replacement Project | Transmission notification from Vermont Electric Company (“VELCO”) for replacement of the submarine cables along the PV 20 115 kV line connecting Plattsburgh, NY substation and the Sand Bar VT substation. | 2017-12-01 | Notification | 2014-10-21
VELCO-14-GNF03 | 2014-07-14 | Coventry Solar Project | Generator notification from Vermont Electric Company (“VELCO”) on behalf of Coventry Photovoltaic LLC for the construction of a 2.2 MW solar array located in Coventry, VT and interconnecting to the H17 45 kV line out of the Irasburg substation. | 2014-07-09 | Notification | 2014-10-21
VELCO-14-GNF04 | 2014-07-14 | North Clarendon Solar Project | Generator notification from Vermont Electric Company (“VELCO”) on behalf of Clarendon Solar Farm LLC for the construction of a 2.0 MW solar array located in North Clarendon, VT and interconnecting to the 12.5 kV feeder out of North Brattleboro supplied from the Vernon Road substation. | 2014-08-01 | Notification | 2014-10-21
VELCO-14-GNF05 | 2014-07-14 | Technology Drive Solar Project | Generator notification from Vermont Electric Company (“VELCO”) on behalf of WE 90 Technology Drive, LLC for the construction of a 2.0 MW solar array located in Brattleboro, VT and interconnecting to the 12.5 kV feeder out of South Rutland supplied from the Cold River substation. | 2014-07-01 | Notification | 2014-10-21
VELCO-14-GNF06 | 2014-07-14 | Charlotte Solar Project | Generator notification from Vermont Electric Company (“VELCO”) on behalf of Charlotte Solar, LLC for the installation of a 2.0 MW solar array located in Charlotte, VT and interconnecting to the Green Mountain Power pole #129 to a 12.47 kV distribution circuit. |  | Notification | 2014-10-21
PWF-14-G01 | 2014-06-06 | Passadumkeag Wind Generation and Transmission Project | Generator notification from Passadumkeag Windpark LLC (“PWF”) for the installation of thirteen 3.075MW wind turbine generators (39.975 MW net output) located in Passadumkeag, ME and interconnecting to the Emera Maine Line 64 by means of a new collector substation. | 2015-12-31 | Approved | 2014-09-09
PWF-14-T01 | 2014-06-06 | Passadumkeag Wind Generation and Transmission Project | Transmission notification from Passadumkeag Windpark LLC (“PWF”) for the construction of a new 115/34.5 kV collector substation under load tap changing transformer located at the collector substation and point of interconnection with Emera Maine | 2015-12-31 | Approved | 2014-09-09
EM-14-T02 | 2014-06-06 | Passadumkeag Wind Generation and Transmission Project | Transmission notification from Emera Maine (“EM”) for a ring bus tap of the existing Line 64 aprox. 22.5 miles north of Graham and aprox. 10 miles south of Enfield and renumber of the southern portion of the line | 2015-12-31 | Approved | 2014-09-09
NU-14-G12 | 2014-07-29 | Borrego Federal Road Solar Project | Generator notification from Northeast Utilities Service Company (“NU”) for the installation of a 4.5 MW solar array located in Carver, MA and interconnecting via the NU #83 23 kV distribution feeder out of the Wareham Substation #714 | 2014-12-31 | Notification | 2014-09-09
NU-14-G07 | 2014-07-29 | Mattapoisett Crystal Spring Road Project | Generator notification from Northeast Utilities Service Company (“NU”) on behalf of BlueWave Capital, LLC for the installation of a 4.5 MW solar array located in Mattapoisett, MA and interconnecting via the NU #302 13.2 kV distribution feeder out of the Crystal Spring Substation #646. | 2015-03-01 | Notification | 2014-09-09
NU-14-G15 | 2014-07-29 | Plymouth Cedarville Phase II Solar | Generator notification from Northeast Utilities Service Company (“NU”) on behalf of Renewable Energy Development Partners, LLC for the installation of a 2.0 MW solar array located in Plymouth, MA and interconnecting via the NU #89 23 kV distribution feeder out of the Valley Substation #715. | 2014-10-01 | Notification | 2014-09-09
NU-14-G13 | 2014-07-29 | Tihonet Park East Solar | Generator notification from Northeast Utilities Service Company (“NU”) on behalf of 510 PV Project Development, LLC for the installation of a 2.0 MW solar array located in Wareham, MA and interconnecting via the NU #83 23 kV distribution feeder out of the Wareham Substation #714. | 2014-12-31 | Notification | 2014-09-09
NU-14-G14 | 2014-07-29 | Onset Water District Solar Project | Generator notification from Northeast Utilities Service Company (“NU”) on behalf of 510 PV Project Development, LLC for the installation of a 2.0 MW solar array located in Wareham, MA and interconnecting via the NU #84 23 kV distribution feeder and #961 23 kV distribution circuit out of the Wareham Substation #714 | 2014-12-31 | Notification | 2014-09-09
NEP-14-GNF14 | 2014-08-01 | SunEdison Origination I Fall River Solar Project | Generator notification from New England Power Company (“NEP”) on behalf of SunEdison Origination I, LLC for the installation of a 2.0 MW solar array located in Fall River, MA and interconnecting via the 28W50 13.8 kV distribution feeder to the Sykes Road Substation #28. |  | Notification | 2014-09-09
NEP-14-GNF15 | 2014-08-01 | SunEdison Origination I Grafton Solar | Generator notification from New England Power Company (“NEP”) on behalf of SunEdison Origination I, LLC for the installation of a 2.0 MW solar array located in Grafton, MA and interconnecting via the 304W1 13.8 kV distribution feeder to the Millbury Substation #304. |  | Notification | 2014-09-09
NEP-14-GNF16 | 2014-08-01 | Bluewave Capital Palmer Solar Project | Generator notification from New England Power Company (“NEP”) on behalf of Bluewave Capital, LLC for the installation of a 3.8 MW solar array located in Palmer, MA and interconnecting via the 0504 23 kV distribution feeder to the Palmer Substation #514. |  | Notification | 2014-09-09
NEP-14-T09 | 2014-07-24 | V-148N 115 kV Line Reconductoring | Transmission notification from New England Power Company (“NEP”) on behalf of Narragansett Electric for the reconductoring of the 4.2 mile overhead V-148N 115 kV transmission line from Woonsocket Substation, RI to Washington Substation, RI. | 2017-06-01 | Notification | 2014-09-09
UI-14-T03 | 2014-07-29 | Old Town 115/13.8 kV Substation Rebuild Project | Transmission notification from United Illuminating Company (“UI”) For the reconstruction of the Old Town Substation located in Bridgeport, CT. Project will consist of installation of nine new monopoles to allow for re-routing of the 1222 and 1710 115 kV lines in and out of the substation, including the addition of a new 115 kV gas circuit breaker and disconnect switches and modification of the 115 kV bus. The installation of two new 30/40/50 MVA, 118/14.9 kV power transformers, with load tap changers(LTCs). The installation of a new Power Delivery Center (PDC) for interconnecting the existing distribution circuits and the removal of the existing distribution substation | 2017-12-01 | Notification | 2014-09-09
UI-14-T04 | 2014-07-29 | Baird 115/13.8 kV Substation Rebuild Project | Transmission notification from United Illuminating Company (“UI”) for the reconstruction of the Baird Substation located in Stratford, CT. Project will consist of the installation of two new monopoles to allow for re-routing of the 88006A and 89006B 115 kV line taps into the substation, including the addition of two new 115 kV gas circuit breakers, associated disconnect switches and modification of the 115 kV bus. The installation of two new 30/40/50 MVA, 118/14.9 kV power transformers, with load tap changers (LTCs. The installation of a new Power Delivery Center (PDC) for interconnecting the existing distribution circuits and the removal of the existing distribution substation. | 2018-12-31 | Notification | 2014-09-09
UI-14-G01 | 2014-07-30 | East Shore Renewable Fuel Cell Project | Generator notification from United Illuminating Company (“UI”) for the installation of a 2.8 MW fuel cell generator located in New Haven, CT and interconnecting to the East Shore 115/13.8 kV Substation 13.8 kV bus #2, position #26. | 2015-01-15 | Notification | 2014-09-09
UI-14-G02 | 2014-07-30 | Seaside Renewable Fuel Cell Project | Generator notification from United Illuminating Company (“UI”) for the installation of a 2.8 MW fuel cell generator located in Bridgeport, CT and interconnecting to the Pequonnock 115/13.8 kV Substation 13.8 kV bus #1, position #8, circuit #2501. | 2015-04-15 | Notification | 2014-09-09
NU-14-T19 | 2014-07-28 | Summerville Substation Transformer Replacement Project | Transmission notification from Northeast Utilities Service Company (“NU”) to upgrade the Somerville Station #402 in Somerville, Massachusetts to replace Transformer 110A and its associated circuit switcher. The new transformer will be rated 117/15kV 37/50/65.4 MVA. Relays will be upgraded but relay schemes will not be changed | 2015-06-01 | Notification | 2014-09-09
NU-14-T20 | 2014-07-28 | Wing Lane Substation Upgrades Project | Transmission notification from Northeast Utilities Service Company (“NU”) for the upgrades to the Wing Lane Substation #624 in Acushnet, Massachusetts. Replace three automatic sectionalizing switches for primary / alternate supply from 115kV lines #112 and #114 to Wing Lane and Arsene substations with a two-breaker switching module; install a 115/13.2 kV, 24/32/40 MVA transformer and associated equipment to double end the substation; install line metering on the 112 and 114 lines to enhance system operations. | 2015-08-01 | Notification | 2014-09-09
NU-14-T17 | 2014-06-25 | K Street to Dewar & Andrew Square Cable Project | Transmission notification from Northeast Utilities Service Company (“NU”) for the installation of two 115 kV HPFF 2250 kcmil CU cables from K St Substation to a wye-splice manhole on Day Blvd for a distance of approximately 5,000’. Split the wye-splices on the 483-524/525 lines and reconnect the sections to Andrew Sq creating circuits 106-526/527. Connect these new circuits to K St bus positions formerly connected to generators. At K St install a new circuit breaker in the west 115 kV bus to create separate positions for autotransformer 345A and line 483-525. | 2015-06-01 | Approved | 2014-08-08
NEP-14-T07 | 2014-07-16 | North Oxford Substation Project | Transmission notification from New England Power Company (“NEP”) for the installation of 115 kV inline breaker and a new 2nd 24/32/40 MVA, 115/13.2 kV transformer at the North Oxford Substation located in Oxford, MA. Proposed in service | 2018-06-01 | Approved | 2014-08-08
NEP-14-T06 | 2004-06-30 | North Grafton Substation Project | Transmission notification from New England Power Company (“NEP”) for the replacement of the existing 69/4.16 kV, 3.75MVA transformer with a 69/13.8 kV, 24/32/40 MVA transformer at the North Grafton Substation #328 located in North Grafton, MA. | 2016-06-01 | Approved | 2014-08-08
CPV-14-G01 | 2014-06-05 | Towantic Combined Cycle Generator and Transmission Project | Generator notification from CPV Towantic LLC (“CVP”) for the construction of a 745MW (net output) (CT1 265 MWs net, CT2 265 MWs net, ST1 245 MWs net), 2 x 1 combined-cycle generation plant in Oxford, CT. | 2018-06-01 | Approved | 2014-08-08
CPV-14-T01 | 2014-06-05 | Towantic Combined Cycle Generator and Transmission Project | Transmission notification from CPV Towantic LLC (“CVP”) for the installation of two 200/330 MVAR transformers for CTs 1 & 2. | 2018-06-01 | Approved | 2014-08-08
CPV-14-T02 | 2014-06-05 | Towantic Combined Cycle Generator and Transmission Project | Transmission notification from CPV Towantic LLC (“CVP”) for the installation of a 200/330 MVA transformers for ST 1. | 2018-06-01 | Approved | 2014-08-08
NU-14-T10 | 2014-06-05 | Towantic Combined Cycle Generator and Transmission Project | Transmission notification from Northeast Utilities Service Company (“NU”) for the construction of Towantic 115-kV Substation and Termination of 1575, 1585, and 1990 115-kV Lines into Towantic 115-kV Substation | 2018-06-01 | Approved | 2014-08-08
NU-14-T11 (Revision available) | 2014-06-05 | Towantic Combined Cycle Generator and Transmission Project | Transmission notification from Northeast Utilities Service Company (“NU”) for the upgrade of the 115-kV 1585N Line section between Towantic and Bunker Hill Substations. | 2018-06-01 | Approved | 2014-08-08
NU-14-T12 (Revision available) | 2014-06-05 | Towantic Combined Cycle Generator and Transmission Project | Transmission notification from Northeast Utilities Service Company (“NU”) for the For the upgrade 115-kV 1575S Line section between Towantic and Oxford Substations | 2018-06-01 | Approved | 2014-08-08
NEP-14-T08 | 7/16/204 | East Webster Substation Project | Transmission notification from New England Power Company (“NEP”) for the replacement of the existing 69/13.2kV 30MVA transformer T1 with a 24/32/40 MVA 69/13.2kV transformer | 2018-06-01 | Notification | 2014-08-08
NU-14-T18 | 2014-08-11 | Montville Autotransformer Replacement Project | Transmission notification from Northeast Utilities service Company (“NU”) for the replacement of existing 18x and 19x 345/115-kV Autotransformers at Montville Substation with similar rated transformers. | 12/31/20104 | Notification | 2014-08-08
EM-14-X01 | 2014-07-09 | New Brunswick Direct Path Logic Special Protection System Modification | Transmission notification from Emera Maine (“EM”) on behalf of the New Brunswick Power System Operator for the modification of the New Brunswick Direct Path Logic (DPL) Special Protection System (SPS – NPCC SPP #176) to include the Madawaska HVDC facility. | 2014-07-17 | Notification | 2014-07-18
NU-14-T15 | 2014-06-02 | Acushnet/Pine Street Cable Project | Transmission notification from Northeast Utilities Service Company (“NU”) for the Relocation of two 115 kV pipe-type cables from the present Acushnet River crossing to a new river crossing. Reconfiguration of the Acushnet #612 substation to effectively parallel underground cables #112 and #114 (to be renamed #142 and #143); installation of a series breaker with Acushnet breaker #EW22. At Pine St Substation # 611 install series breakers with circuit breaker 11212 and 11412; Remove two former GSU transformers from service. Also install two 10 MVAr switched shunt reactors with isolation circuit breakers. Make condition based upgrades to miscellaneous equipment at both substation as well as upgrade relays and control equipment. | 2016-06-01 | Approved | 2014-07-18
NEP-14-T03 | 2014-05-28 | Pelham Transformer and Breaker Project | Transmission notification from New England Power Company (“NEP”) for the installation of an in-line 115 kV circuit breaker. Loop the 115 kV Y-151 line through the substation via a section of new 115 kV overhead line. Replace the existing 115/13.2, 12/16/20 MVA transformer with a 115/13.2 kV, 24/32/40 MVA transformer. Install a second 115/13.2 kV, 24/32/40 MVA transformer. | 2017-06-01 | Approved | 2014-07-18
CPV-14-G01 | 2014-03-28 | Towantic Combined Cycle Generator Project | Generator notification from CPV Towantic LLC (“CVP”) for the construction of a 745MW (net output) (CT1 265 MWs net, CT2 265 MWs net, ST1 245 MWs net), 2 x 1 combined-cycle generation plant in Oxford, CT. | 2018-06-01 | Approved | 2014-08-08
CPV-14-T01 | 2014-03-28 | Towantic Combined Cycle Generator Project | Transmission notification from CPV Towantic LLC (“CVP”) for the installation of two 200/330 MVAR transformers for CTs 1 & 2. | 2018-06-01 | Approved | 2014-08-08
CPV-14-T02 | 2014-03-28 | Towantic Combined Cycle Generator Project | Transmission notification from CPV Towantic LLC (“CVP”) for the installation of a 200/330 MVA transformers for ST 1. | 2018-06-01 | Approved | 2014-08-08
NU-14-T10 | 2014-03-28 | Towantic Combined Cycle Generator Project | Transmission notification from Northeast Utilities Service Company (“NU”) for the construction of Towantic 115-kV Substation and Termination of 1575, 1585, and 1990 115-kV Lines into Towantic 115-kV Substation. | 2018-06-01 | Approved | 2014-08-08
NU-14-T11 | 2014-03-28 | Towantic Combined Cycle Generator Project | Transmission notification from Northeast Utilities Service Company (“NU”) for the upgrade of the 115-kV 1585N Line section between Towantic and Bunker Hill Substations. | 2018-06-01 | Approved | 2014-08-08
NU-14-T12 | 2014-03-28 | Towantic Combined Cycle Generator Project | Transmission notification from Northeast Utilities Service Company (“NU”) for the For the upgrade 115-kV 1575S Line section between Towantic and Oxford Substations | 2018-06-01 | Approved | 2014-08-08
FGE-14-G01 | 2014-05-29 | Chase Road Solar Project | Generator notification from Unitil-Fitchburg Gas & Electric Company (“FGE”) for the installation of a 2.49 MW solar array located in Lunenburg, MA and interconnecting via the 13.8 kV 30W31 circuit to the Lunenburg substation #30. | 2014-06-30 | Notification | 2014-07-18
UI-14-T01 | 2014-05-29 | Housatonic River Crossing 115 kV Line Rebuild Project | Transmission notification from United Illuminating Company (“UI”) for the 0.47 mile overhead 88006A 115 kV Line Rebuild, Milford-Stratford, Connecticut. | 2015-12-01 | Notification | 2014-07-18
UI-14-T02 | 2014-05-29 | Housatonic River Crossing 115 kV Line Rebuild Project | Transmission notification from United Illuminating Company (“UI”) for the 0.47 mile overhead 89006B 115 kV Line Rebuild, Milford-Stratford, Connecticut. | 2015-12-01 | Notification | 2014-07-18
NU-14-T16 | 2014-06-12 | Barnstable/Harwich Tap 115 kV Line Project | Transmission notification from Northeast Utilities Service Company (“NU”) for the construction of a 7.8 mile 115 kV overhead transmission line from the Barnstable 115 kV Substation to Harwich Tap. This new line will mitigate the loss of load resulting from the simultaneous loss of double circuit tower (DCT) lines 118 and 119. | 2018-06-01 | Notification | 2014-07-18
NU-14-X02 | 2014-06-12 | Barnstable/Harwich Tap 115 kV Line Project | Transmission notification from Northeast Utilities Service Company (“NU”) for the modification of the existing Barnstable Type 1 SPS. The modification is needed in order to keep the function of the existing SPS unchanged after the completion of the project. | 2018-06-01 | Notification | 2014-07-18
NU-14-T06-Rev.1 and NU-14-X01-Rev.1 | 2014-05-13 | UMA Tillson Substation Project Rev.1 | Transmission notifications from Northeast Utilities Service Company (“NU”) for the revision to the UMA Tillson Substation Project to document the correction in the Winter STE rating of line 1113 from the Five Corners Substation tap point to the UMA Tillson Substation in Amherst, MA tap point from 90 MVA to 91 MVA. | 2015-09-01 | Notification | 2014-07-18
NEP-14-GNF13 | 2014-06-06 | NexAmp Belchertown Solar Project | Generator notification from New England Power Company (“NEP”) on behalf of NexAmp Belchertown Solar LLC for the construction of a 1.3 MW solar array located in Belchertown, MA and interconnecting to the National Grid 13.2 kV distribution system on the 509L2 feeder out of the Belchertown 509 substation. | 2014-06-17 | Notification | 2014-07-18
NEP-14-T04 | 2014-06-05 | Tewksbury 22A 345 kV GIS Substation Rebuild Project | Transmission notification from New England Power Company (“NEP”) in kind replacement of the Tewksbury 22A GIS Substation Rebuild Project due to asset conditions, reliability and environment issues. | 2014-12-01 | Notification | 2014-07-18
CEL-14-G02 | 2014-06-05 | CRBP Solar Project | Generator notification from Chicopee Electric Light Department on behalf of Chicopee Granby Road Solar LLC for the construction of a 1.6 MW solar array located in Chicopee, MA and interconnecting via the 18L13 feeder out of the Chicopee 18L substation | 2014-12-01 | Notification | 2014-07-18
CEL-14-G01 | 2014-06-05 | CRBP Solar Project | Generator notification from Chicopee Electric Light Department on behalf of Chicopee River Business Park Solar LLC for the construction of a 2.0 MW solar array located in Chicopee, MA and interconnecting via the 18L12 feeder out of the Chicopee 18L substation. | 2014-12-01 | Notification | 2014-07-18
FW-12-T02-Rev.2 | 2014-05-01 | Oakfield Wind Project Rev. 2 | Transmission notification revision from First Wind Energy Marketing (“FW”) on behalf of Evergreen Wind Power II LLC for the Addition of a new Keene Rd 115/345kV autotransformer dedicated to the project, two 115kV 25MVAR capacitor banks, associated circuit breakers and switchgear, 115kV transmission line between Keene Rd and the new Oakfield collector substation, 115/34.5/12.5kV three winding transformer located at the collector substation, and one 60MVA synchronous condenser located on collector substation transformer tertiary winding. The change that is reflected in Rev. 2 is going from two transformers in the collector substation to a single larger transformer with the same effective impedance as the original configuration. | 2015-12-01 | Approved | 2014-05-29
FW-12-G02-Rev.2 | 2014-05-01 | Oakfield Wind Project Rev. 2 | Generator notification revision from First Wind Energy Marketing (“FW”) on behalf of Evergreen Wind Power II LLC for the modification of the 147.6 MW Oakfield Wind Farm collector substation to show updated 34.5 kV breaker arrangement, transformer changes and turbine count installation interconnecting to the Emera Maine Keene Road 345 kV | 2015-12-01 | Approved | 2014-05-29
NEP-14-GNF10 | 2014-05-09 | UGT Renewable Energy 7 Billerica Solar Project | Generator notification from New England Power Company (“NEP”) on behalf of UGT Renewable Energy 7 LLC for the installation of a 4.99 MW solar array located in Billrica, MA and interconnecting to the 13.2 kV 70L8 feeder out of the Billerica Substation #70. | 2014-06-01 | Notification | 2014-05-29
NEP-14-GNF11 | 2014-05-09 | Bluewave Capital Uxbridge Solar Project | Generator notification from New England Power Company (“NEP”) on behalf of BlueWave Capital LLC for the installation of a 3.0 MW solar array located in Uxbridge, MA and interconnecting to the 13.8 kV 321W9 feeder out of the Uxbridge Substation #321. | 2014-06-01 | Notification | 2014-05-29
NEP-14-GNF12 | 2014-05-09 | SunEdison Origination 3 Rehoboth Solar Project | Generator notification from New England Power Company (“NEP”) on behalf of SunEdison Origination 3 LLC for the installation of a 4.0 MW solar array located in Rehoboth, MA and interconnecting to the 23 kV 2284 feeder out of the West Street Substation. | 2014-06-01 | Notification | 2014-05-29
NU-14-G06 | 2014-04-14 | Norwalk Hospital Gas Generator Project | Generator notification from Northeast Utilities Service Company (“NU”) on behalf of Norwalk Hospital for the installation of a 3.0 MW gas turbine generator located in Norwalk, CT and interconnecting to the 9S4 feeder out of the Norwalk Substation. | 2014-05-30 | Notification | 2014-05-29
NEP-14-G03 | 2014-03-21 | Block Island Wind Farm Project | Generator notification from New England Power Company (“NEP”) on behalf of Deep Water Wind, LLC for the installation of five 6.0 MW wind turbine generators (30 MW net output) located on a off shore wind farm 3 miles SE of Block Island, RI and interconnecting to a new 34.5 kV substation in the town of New Shoreham in Block Island, RI. The project will be connected to Narragansett’s 34.5kV sub-transmission system at Wakefield substation via the to-be-constructed Block Island Transmission System (BITS) which includes two new 34.5 kV substations, one on Block Island and the other on the main land in Narragansett, RI, and 34.5 kV sub-submarine, underground and overhead lines | 2016-06-01 | Approved | 2014-04-28
NU-14-T06 | 2013-03-17 | UMA Tillson Substation Project | Transmission notification from Northeast Utilities Service Company (“NU”) for the construction of a 115/13.8 kV substation located in Amherst, MA. to serve the increased load at the University of Massachusetts (UMA). The new Tillson substation will be connected to the WMECO transmission system by tapping existing lines 1113 and 1044, and building two single circuit lines from the tap points to the substation. A 115-kV bus tie-breaker with 40-kA interrupting capability will be installed at Tillson substation and operated normally open (N.O.). Also, 115-kV line circuit switchers with 40 kA interrupting capability will be installed on the two lines (1044 and 1113) coming into the substation and on the 1044 line at Amherst substation.Two (2) 115/13.8 kV distribution transformers will be installed at Tillson substation, each with a high-side (115-kV) circuit switcher. The capacity of existing lines 1113 and 1044 will be upgraded as follows: • Increase clearances on the 1113 line from the Five Corners substation tap point to the UMA Tillson substation tap point to obtain summer ratings of at least 68/68/68/73 MVA (normal/LTE/STE/DAL), and winter ratings of at least 91/91/90/99 MVA. • Increase clearances on the 1113 line from Fairmont 16H Substation to the Five Corners substation tap point to obtain summer ratings of at least 76/76/76/86 MVA (normal/LTE/STE/DAL), and winter ratings of at least 120/120/121/139 MVA. • Increase clearances on the 1044 line from Montague 21G Substation to the Tillson/Amherst tap point to obtain summer ratings of at least 58/58/58/62 MVA (normal/LTE/STE/DAL), and winter ratings of at least 84/84/84/91 MVA. | 2015-09-01 | Approved | 2014-04-28
NU-14-X01 | 2013-03-17 | UMA Tillson Substation Project | Transmission notification from Northeast Utilities Service Company (“NU”) to install a Type 3 Special Protection System (SPS) to avoid loading lines 1113 and 1044 above the STE/DAL ratings during switching operations necessary for load transfers at Tillson, Podick and Amherst substations following the 1113, 1044, 1632 and 1134 line outages. The SPS will be facilitated by communication links between the area substations | 2015-09-01 | Approved | 2014-04-28
NU-14-T09 | 2014-03-21 | Mill Pond Substation Project | Transmission notification from Northeast Utilities Service Company (“NU”) for the construction of a new 115/12.5 kV Mill Pond substation located in Portsmouth, NH.The transformer loadings at Jackson, Lafayette and ISLG 559 distribution 34.5 kV and 12.5kV substations in the Portsmouth area of New Hampshire are projected to exceed their emergency limits in 2015. These distribution substations are fed from the 115-kV transmission system out of the Resistance and Ocean Road substations. The new substation will be fed from a new half mile radial 115-kV line. The new line will be tapping the existing 115-kV U181 Line from Ocean Road to Schiller Substation. | 6/1/20105 | Approved | 2014-04-28
NU-14-G05 | 2014-03-26 | SunDurance CFS I Solar Project | Generator notification from Northeast Utilities Service Company (“NU”) on behalf of SunDurance-CFS I, LLC for the installation of a two 1.67 MW solar arrays (3.30 MW net output) in Southwick, MA and interconnecting to the Southwick 29A 115 kV substation via the WMECO 29A1 13.8 kV distribution circuit. | 2014-05-30 | Notification | 2014-04-28
NEP-14-GNF05 | 2014-04-04 | UGT Renewable Energy 13 Oxford Solar Project | Generator notification from New England Power Company (“NEP”) on behalf of UGT Renewable Energy 13 LLC for the installation of a 2.75 MW solar array located in Oxford, MA and interconnecting to the 406L4 feeder out of the North Oxford Substation #406. | 2014-06-01 | Notification | 2014-04-28
NEP-14-GNF06 | 2014-04-04 | CES Massachusetts Easton Solar Project | Generator notification from New England Power Company (“NEP”) on behalf of CES Massachusetts Solar LLC for the installation of a 2 MW solar array located in Easton, MA and interconnecting to the 98W46 feeder out of the Belmont St. Substation #98. | 2014-06-01 | Notification | 2014-04-28
NEP-14-GNF07 | 2014-04-04 | Bluewave Capital Haverhill Solar Project | Generator notification from New England Power Company (“NEP”) on behalf of BlueWave Capital LLC for the installation of a 1.43 MW solar array located in Haverhill, MA and interconnecting to the 47L1 feeder out of the West Newbury Substation #47. | 2014-06-01 | Notification | 2014-04-28
NEP-14-GNF08 | 2014-04-04 | Mass PV 7 Leicester Solar Project | Generator notification from New England Power Company (“NEP”) on behalf of Mass PV 7 LLC for the installation of a 4.833 MW solar array located in Leicester, MA and interconnecting to the 21W2 feeder out of the Leicester Substation #21. | 2014-06-01 | Notification | 2014-04-28
NEP-14-GNF09 | 2014-04-04 | 205 Sturbridge Solar Brimfield Solar Project | Generator notification from New England Power Company (“NEP”) on behalf of 205 Sturbridge Solar, LLC for the installation of a 2.0 MW solar array located in Brimfield, MA and interconnecting to the 516L1 feeder out of the Little Rest Road Substation. | 2014-04-15 | Notification | 2014-04-28
NU-13-T04 | 2014-03-03 | Mashpee Substation Upgrade Project | Transmission notification from Northeast Utilities Service Company (“NU”) for the addition of a second 30/40/50 MVA 115/23 kV transformer and 23kV bus section, and provide for two additional 23kV feeders and a 4.8 MVAR station capacitor bank. As part of the project to increase station capacity, a 2-breaker 115kV breaker arrangement with associated equipment will be installed at Mashpee Substation in #136 Falmouth Tap to Barnstable 115kV line. | 2015-12-31 | Approved | 2014-03-20
EP-14-G01 | 2014-03-10 | Newington Generator Uprate Project | Generator notification from Essential Power Newington, LLC (“EP”) for the uprate of the Newington Energy combined cycle generator located in Newington, NH from 561.5 MWs to 594.8 MWs net output degrees F and 547.5 MWs to 568.2 MWs net output at 50 degrees F as a result of an air permitting correction that allows supplementary firing of the plant’s heat recovery steam generator duct burners during temperatures below 60 degrees F. | 2014-03-01 | Approved | 2014-03-20
NU-14-G03 | 2014-02-12 | Jericho Mountain Wind Project | Generator notification from Northeast Utilities Service Company (“NU”) for the construction of three 2.85 MW (8.55 MWs net output) in Berlin, NH and interconnect to the Jericho Road 34.5 kV substation also in Berlin, NH. | 2014-10-01 | Approved | 2014-03-20
CMP-14-T01 | 2014-03-03 | County Road Substation Project | Transmission notification from Central Maine Power Company (“CMP”) for the construction of a new County Road (Rice Rips) substation that sectionalizes Section 241 by adding four 115 kV circuit breakers in a ring bus configuration and install two 115/34.5 kV 30/56 MVA transformers at a new green field site. The new substation will replace the existing Rice Rips substation. Also construct 6.5 miles of new 115 kV (1192 kcmil 45/7 ACSR) conductor from the Section 241A tap point to the new Country Road Substation | 2017-09-01 | Approved | 2014-03-20
NU-14-T07 | 2014-03-18 | Saxonville Temporary Mobile Station #278 Project | Transmission notification from Northeast Utilities Service Company (“NU”) to establish a new temporary 115/14 kV at the retired 14/4 kV Station #278 located in Framingham, MA. Tap 115 kV line 342-507. Install mobile station equipment including a 20 MVA, 117/15.12 kV transformer, a 123 kV, 1,200 amp, 31.5 kAmp interrupting rated circuit switcher and 2 - 1,200 amp, 15 kV vacuum circuit breakers. Tie into existing 13.8 kV distribution circuit infrastructure at ROW 8-1 and Lake Rd. The new temporary station provides additional distribution system supply in time for summer peak 2014. | 2014-06-01 | Notification | 2014-03-20
NU-14-G04 | 2014-02-28 | Hartford Hospital Fuel Cell Project | Generator notification from Northeast Utilities Service Company (“NU”) for the installation of a 1.5 MW fuel cell in Hartford, CT and interconnecting to South Meadows Feeder 109 and Feeder 151 | 2014-03-21 | Notification | 2014-03-20
VELCO-14-GNF02 | 2014-02-28 | WMA Chester Solar I Project | Generator notification from Vermont Electric Company (“VELCO”) on behalf of Vermont Public Power Supply Authority for the construction of a 4.8 MW solar array located in Chester, MA and interconnecting to the Blandford 19J 115 kV substation via WMECO’s 19J3 23kV distribution circuit via the Town of Chester Municipal Electric Light Department’s “extension of the WMECO 19J3” 23 kV distribution circuit. | 2014-03-19 | Notification | 2014-03-20
UI-09-T01-Rev.1 | 2014-03-10 | Shelton Substation Name Change to Pootatuck Substation | Transmission notification from United Illuminating Company (“UI”) to change the name of the existing Shelton 115/13.8 kV substation located in Shelton, CT to Pootatuck 115/13.8 kV substation. | 2014-03-18 | Notification | 2014-03-20
UI-12-T20-Rev.1 | 2014-01-28 | Hawthorne 115 kV Capacitor Bank Addition Project Rev.1 | Transmission notification from United Illuminating Company (“UI”) for the reduction of the previously proposed two capacitor banks from 30 MVAR each to 20 MVAR each (40 MVAR total) located at the Hawthorne 115 kV Substation in Fairfield, CT | 2015-12-01 | Approved | 2014-02-27
FW-14-G01 | 2014-01-15 | Bowers Wind Generation and Transmission Project | Generation notification from First Wind Energy Marketing (“FW”) on behalf of Champlain Wind LLC for the construction of sixteen 3 MW wind turbine generators (total output 48 MWs) located in Penobscot and Washington Counties, ME. | 2015-08-31 | Approved Withdrawn | 2/24/2014 2/17/2015
FW-14-T01 | 2014-01-15 | Bowers Wind Generation and Transmission Project | Transmission Notification from First Wind Energy Marketing (“FW”) on behalf of Champlain Wind LLC for the construction of a new 115/34.5 kV substation in Penobscot County, ME. Install two 34.5 kV circuit breaker and a new 115/34.5 kV interconnection transformer (30/40/50 MVA). | 2015-08-31 | Approved Withdrawn | 2/24/2014 2/17/2015
EM-14-T01 | 2014-01-15 | Bowers Wind Generation and Transmission Project | Transmission notification from Emera Maine (“EM”) for the installation of a 20 MVAR DVAR at the Chester 115 kV Substation located in Chester, ME to mitigate voltage performance issues. | 2015-08-31 | Approved | 2014-02-24
FW-12-G02-Rev.1 | 2013-12-16 | Oakfield Wind Generation and Transmission Project Rev.1 | Generator notification revision from First Wind Energy Marketing (“FW”) on behalf of Evergreen Wind Power II LLC for the removal of the normally open bus tie breaker and the elimination of the 40.5 MVAR variable capacitor bank as part of the 147.6 MW Oakfield Wind Farm. | 2014-08-31 | Approved | 2014-02-24
FW-12-T02-Rev.1 | 2013-12-16 | Oakfield Wind Generation and Transmission Project Rev.1 | Transmission notification revision from First Wind Energy Marketing (“FW”) on behalf of Evergreen Wind Power II LLC for the addition of a 60 MVA synchronous condenser and related transformer changes at the Oakfield collector substation. | 2015-12-31 | Approved | 2014-02-24
NEP-14-T01 | 2014-01-24 | Mid-Weymouth Substation Transformer Project | Transmission notification from New England Power Company (“NEP”) for the addition of a 115 kV transformer at the Mid-Weymouth Substation located in Weymouth, MA to mitigate anticipated load growth in the area. | 2015-06-01 | Notification | 2014-02-27
NEP-14-GNF02 | 2014-02-07 | 205 Sturbridge Solar Project | Generator notification from New England Power Company (“NEP”) on behalf of 205 Sturbridge Solar LLC for the installation of a 3 MW solar array located in Brimfield, MA and interconnect to the NGrid 13.2 kV distribution system on the 516L1 feeder out of the Little Rest Road #516 substation. | 2014-04-15 | Notification | 2014-02-27
NEP-14-GNF03 | 2014-02-07 | Bluewave Capital Grafton Solar Project | Generator notification from New England Power Company (“NEP”) on behalf of Bluewave Capital LLC for the installation of a 2 MW solar array located in Grafton, MA and interconnecting to the NGrid 13.8 kV distribution system on the 304W1 feeder out of the Millbury 4 substation. | 2014-04-14 | Notification | 2014-02-27
NEP-14-GNF04 | 2014-02-07 | Bluewave Capital Berlin Solar Project | Generator notification from New England Power Company (“NEP”) on behalf of Bluewave Capital LLC for the installation of a 3 MW solar array located in Berlin, MA and interconnecting to the NGrid 13.8 kV distribution system on the 318W3 feeder out of the North Marlborough substation. | 2014-05-30 | Notification | 2014-02-27
NEP-13-GNF44-Rev.1 | 2014-02-07 | Gardner Solar 1 Project Revision | Generator notification revision from New England Power Company (“NEP”) on behalf of Massachusetts Electric Company for the Gardner Solar I Project to change the size of the solar array to 1.98 MWs and interconnect to the NGrid 13.8 kV distribution system in Gardner, MA on the 601W1 feeder out of the Park St. 601 substation. | 2014-02-14 | Notification | 2014-02-27
NU-13-T24-Rev.1 | 2014-01-15 | Northern Pass – Scobie Pond Substation Project Revision | Transmission notification revision from Northeast Utilities Service Company (“NU”) for revisions to the Scobie Pond Substation drawing to reflect the addition of the 802S circuit breaker. | 2017-06-01 | Notification | 2014-02-27
NU-14-T02 | 1/29/20104 | Norwalk Substation 115/13.8 kV Transformer Addition Project | Transmission notification revision from Northeast Utilities Service Company (“NU”) for installation of a 115/13.8 kV transformer and one 115 kV circuit breaker at the Norwalk Substation located in Norwalk, CT. | 2014-06-01 | Notification | 2014-02-27
NEP-13-G04 | 2014-01-10 | Toray Plastics Gas Generator Project | Generator notification from New England Power Company (“NEP”) for two gas fired generator (12.5 MWs total net output) located in Davisville, MA and interconnecting to the NGrid 84T4 34.5 kV feeder out of the Davisville substation. | 2013-12-01 | Approved | 2014-02-24
NEP-12-G04-Rev.1 | 2014-01-09 | Warren Solar Project Revision | Generator notification revision from New England Power Company (“NEP”) on behalf of First Wind for the construction of a 14 MW solar generator located in Warren, MA and interconnecting via the NGrid 516L4 13.2 kV feeder out of the Little Rest Road substation. Project revisions include a change to the previous owner (Mass PV 3 LLC) to First Wind, station capacity change from 9 MWs to 14 MWs and the SMA inverter models were included, as documented in the supporting revised study report. | 2014-03-01 | Approved | 2014-02-11
EMI-05-G01-Rev.1 | 2014-01-15 | Cape Wind Project Revisions | Generator notification revision from Energy Management Inc. for the installation of 130 wind turbines each rated at 3.6 MWs (454 MWs total net output, 468 MWs total gross output) located in Nantucket Sound, MA and interconnecting to the NSTAR 115 kV Barnstable Substation. Application revised to reflect a change to the wind turbine type from GE 3.6 MW Type 3 to Seimens SWT-4.0-107 (firmware limited to 3.6 MWs) wind turbines. | 2016-12-01 | Approved | 2014-02-11
EMI-14-T01 | 2014-01-15 | Cape Wind Project Revisions | Transmission Notification from Energy Management Inc. for the construction of two 115kV submarine/underground cable circuits and a 33:115kV offshore electric service platform (ESP) connecting the offshore wind farm to the 115kV Barnstable Substation. The electric service platform will consist of three 114/152/190MVA 33:115kV transformers and a five breaker GIS ring bus. Each cable circuit will be 18.4 miles in length and consist of two 800 mm solid dielectric cables with 12.6 miles being submarine cable and 5.8 miles being underground upland cable. | 2016-05-01 | Approved | 2014-02-11
NU-14-T04 | 2014-01-15 | Cape Wind Project Revisions | Transmission notification from Northeast Utilities Service Company (“NU”) for the expansion of the Barnstable 115 kV substation to include a circuit breaker in the fourth bay and a circuit breaker in the fifth bay. Due to modifications at the Barnstable 115 kV substation since the approval of the NSTAR-05-T07 PPA, the requirement to expand the Barnstable 115 kV substation to include a fifth bay with two circuit breakers and add a third circuit breaker in the planned fourth bay has been reduced. Installation of four 35 MVAR shunt reactors at the Barnstable 115 kV substation to compensate for 115 kV and 33 kV cable charging. Each shunt reactor shall have a dedicated synchronous closing circuit breaker in order to avoid any transient over-voltages during switching. The modification to this requirement from the original NSTAR-05-T07 PPA is the change in location of two of the four 35 MVAR shunt reactors from the Cape Wind Electric Service Platform to the Barnstable 115 kV substation. Installation of a redundant circuit breaker in series with the existing #312 circuit breaker at the Canal 345 kV substation. Replacement of the Bourne 115 kV #12272 circuit breakers with breakers having independent poletripping (IPT). Addition of two harmonic filter banks to the Barnstable 115 kV substation with each having 35 MVAR of net charging. Each filter bank shall have a dedicated closing circuit breaker. The need for the filter capacitor banks was determined through detailed design studies of the Cape Wind project. The compensation of the net charging from these additional filter capacitor banks resulted in the following two required upgrades: Modification of the Barnstable SVC to result in having a net inductive operating capability of 70.5 MVAR and the addition of a 40 MVAR shunt reactor at the West Barnstable 115 kV substation that shall have a dedicated closing circuit breaker. | 2016-05-01 | Approved | 2014-02-11
NU-13-G28 | 2014-01-09 | Barnstable Airport Solar Project | Generator notification from Northeast Utilities Service Company (“NU”) for the installation of a 4.5 MW solar array located in Barnstable, MA and interconnecting to the Hyannis Junction Substation #961 via the NU #92A 23 kV distribution feeder. | 2014-06-01 | Notification | 2014-02-24
NU-14-T01 | 2014-01-06 | Dover Transformer Replacement Project | Transmission notification from Northeast Utilities Service Company (“NU”) for the replacement of the 110/13.8 kV, 18/24 MVA transformer 110B at Dover Station #456. The existing transformer is vintage 1953, and has reached the end of its useful life. The outdated transformer is in poor condition and limits the capacity of the station to levels below the 2014 forecasted load. | 2014-06-01 | Notification | 2014-02-24
NU-13-T34 | 2013-12-18 | Harwich Tap Reconductoring Project | Transmission notification from Northeast Utilities Service Company (“NU”) to reconductor the 4.4 mile Harwich #119 Tap line from Harwich Tap (Dennis, MA) to Harwich Bulk (Harwich, MA) from 4/0 ACSR 6/1 to 795 ACSS 54/7. This line section will also be brought up to present state code and hardened with the installation of steel structure at line angles. | 2014-03-01 | Notification | 2014-02-24
NU-14-G01 | 2014-01-09 | Lahey Clinic Hospital CHP Generator Project | Generator Notification from Northeast Utilities Service Company (“NU”) for the construction of a load reducing 2.93 MW (net output) CHP synchronous generatorm in Burlington, MA and interconnecting to the NSTAR Burlington #391 substation via the 541-1377H feeder. | 2014-01-01 | Notification | 2014-02-24
NU-13-G27 | 2014-01-13 | New Bedford Solar Project | Generator notification from Northeast Utilities Service Company (“NU”) on behalf of TJA Solar, LLC for the construction of a 3 MW solar array located in New Bedford, MA and interconnecting to the Northeast Utilities Industrial Park Substation #636 via the 13.2 kV feeder #103. | 2014-03-01 | Notification Withdrawn | 1/21/2014 6/12/2014
VELCO-13-GNF06 | 2014-01-07 | Sheldon Springs Solar Project | Generator Notification from Vermont Electric Company (“VELCO”) for the construction of a 2.2 MW solar array located in Sheldon, VT and interconnecting via the VEC Sheldon Springs Hydro 46 kV supplied by the Highgate 15 kV substation. | 2013-08-11 | Notification | 2014-02-24
VELCO-13-GNF07 | 2014-01-07 | St. Albans Solar Project | Generator Notification from Vermont Electric Company (“VELCO”) for the construction of a 2.0 MW solar array located in St. Albans, VT and interconnecting via the 12.5 kV #52 circuit at the GMP East St. Albans 34.5 kV substation. | 2013-11-07 | Notification | 2014-02-24
VELCO-13-GNF08 | 2014-01-07 | Cross Pollination Solar Project | Generator Notification from Vermont Electric Company (“VELCO”) for the construction of a 1.96 MW solar array in New Haven, VT and interconnecting via the 9G4 12.5 kV circuit at the Vergennes 34.5 kV substation. | 2013-09-04 | Notification | 2014-02-24
VELCO-14-GNF01 | 2014-01-07 | Limerick Solar Project | Generator Notification from Vermont Electric Company (“VELCO”) for the construction of a installation of a 2.12 MW solar array located in Shelburne, VT and interconnecting via the GMP 53G1 12.47 kV circuit at the Shelburne substation. | 2014-01-17 | Notification | 2014-02-24
NEP-14-GNF01 | 2014-01-10 | North Brookfield Solar Project | Generator notification from New England Power Company (“NEP”) on behalf of North Brookfield Solar LLC for the installation of a 3.0 MW solar array located in North Brookfield, MA and interconnecting via the #525L1 feeder out of the Lashaway substation #525. | 2014-03-17 | Notification | 2014-02-24
NU-13-T20 | 2013-12-01 | Northern Pass Transmission Project | Transmission notification from Northeast Utilities Service Company (“NU”) on behalf of Northern Pass Transmission LLC. for the construction of a 345 kV air insulated substation with a eight circuit breaker ring bus. in Franklin, NH, a 1200 MW bi-directional, bi-polar, and a HVDC line commutated converter station 0/100 Mvar Static VAR Compensator (SVC). The 345-kV Franklin substation will interconnect to Public Service of New Hampshire’s 345-kV Deerfield substation (POI), located in Deerfield, New Hampshire, via a 345-kV ac overhead transmission line, and to the Des Canton substation in Quebec, Canada, via an HVDC link. The HVDC link will be a 1200 MW bi-directional HVdc line commutated converter, operating at ±300 kV. The Franklin HVdc link will have two 600 MW, 12-pulse line commutated converters with the following reactive compensation: 400 Mvar (2x100 Mvar per pole) of harmonic filters; 350 Mvar (175 Mvar per pole) of thyristor switched capacitors (1x25 Mvar TSC brank, 1x50 Mvar TSC branch, and 1x100 Mvar TSC branch);120 Mvar (2x60 Mvar) of mechanically switched reactors (MSR). | 2017-12-01 | Approved | 2013-12-31
NU-13-T21 | 2013-12-01 | Northern Pass Transmission Project | Transmission notification from Northeast Utilities Service Company (“NU”) on behalf of Northern Pass Transmission LLC. for the construction of a 153 mile dc transmission line, which includes 8 miles of underground cable, from the Franklin Converter Terminal Substation located in Franklin, New Hampshire, to the US / Canadian border. The distance from the US / Canadian border in Quebec to the Des Canton Substation, which is where the dc line will terminate, is approximately 48 miles. The proposed dc transmission line is a bipolar, ± 300-kV, constructed of 2x2933 AAAC conductors per pole. A dedicated metallic return circuit will be of a single 2933 AAAC conductor. The underground portion of the dc line will be constructed of 2000 (mm)2 copper conductor. | 2017-12-01 | Approved | 2013-12-31
NU-13-T22 | 2013-12-01 | Northern Pass Transmission Project | Transmission notification from Northeast Utilities Service Company (“NU”) on behalf of Northern Pass Transmission LLC. for the construction of a new 345-kV ac transmission line, 3132, will be constructed from the Franklin Converter Terminal Substation to the Deerfield 345-kV Substation. Fiber optic cable will be installed on the new transmission line. To accommodate termination of line 3132 at Deerfield, and to prevent transmission line crossings, the existing 345-kV Line 373 (Deerfield Substation to Scobie Pond Substation) will be re-positioned at the 345-kV Deerfield Substation to its own new bay position. Line 3132 will be constructed with two (2) 1590 ACSR, 45/7 stranding, conductors per phase having 18 inch conductor spacers. The transmission towers will be a combination of H-frame, delta, and vertical structures. | 2017-12-01 | Approved | 2013-12-31
NU-13-T23 | 2013-12-01 | Northern Pass Transmission Project | Transmission notification from Northeast Utilities Service Company (“NU”) on behalf of Northern Pass Transmission LLC. for the construction of the 345-kV Deerfield Substation. The Deerfield 345-kV Substation will be reconfigured to accommodate the new Northern Pass Transmission Project ac transmission line 3132 interconnection, the re-termination of the 345-kV Buxton to Scobie Pond transmission line 391, and the addition of shunt capacitor banks. Four 345-kV shunt capacitor banks, 50 Mvar each, will be installed with four new 345-kV existing Deerfield 345-kV series circuit breakers, (7310 & 7310S, and 851 & 851S), will remain in place. To accommodate termination of the new 345-kV Franklin to Deerfield line, and to prevent transmission line crossings, the existing 373 line (Deerfield Substation to Scobie Pond Substation) will be re-positioned to its own new bay position. The new transmission line 3132 will terminate at the vacated 373 line position. The existing bus protection scheme will be retained and reconfigured to accommodatethe new line terminations. | 2017-12-01 | Approved | 2013-12-31
NU-13-T24 | 2013-12-01 | Northern Pass Transmission Project | Transmission notification from Northeast Utilities Service Company (“NU”) on behalf of Northern Pass Transmission LLC. for the installation of a 210 Mvar of 345-kV capacitor banks at the 345-kV Scobie Pond Substation. The capacitor banks will be connected to 345-kV Scobie Pond Bus #2 via a five 345-kV, 50 kA circuit breaker. The capacitor banks will be divided into four separate banks, three (3) 60 Mvar banks and one (1) 30 Mvar bank with each bank having its own dedicated circuit breaker. The capacitor banks will be equipped with voltage protection. In addition to the capacitor banks, two 345-kV, 50 kA circuit breakers will be installed. One circuit breaker is to be installed in series with the existing 9126 circuit breaker, and the other circuit breaker installed in series with the 262 circuit breaker. | 2017-12-01 | Approved | 2013-12-31
NU-13-T25 | 2013-12-01 | Northern Pass Transmission Project | Transmission notification from Northeast Utilities Service Company (“NU”) on behalf of Northern Pass Transmission LLC. for the termination of the 345-kV ac transmission line 391, 345-kV Buxton Substation to 345-kV Scobie Pond Substation at the 345-kV Deerfield Substation. Terminating line 391 at the 345-kV Deerfield Substation creates two separate transmission line circuits; line 391N from 345-kV Buxton Substation to 345-kV Deerfield Substation, and line 391S from 345-kV Deerfield Substation to 345-kVScobie Pond Substation. The 391N line will terminate in its own new bay position at the 345-kV Deerfield Substation. The 391S line will terminate between the existing series circuit breakers 7332 and 3220. New primary and backup transmission line protection schemes will be installed for line 391N and line 391S. In addition to terminating transmission line 391 at the 345-kV Deerfield Substation, the Project requires that the new 391S line section be upgraded to a minimum Long Time Emergency thermal rating of 1470 MVA. To achieve this thermal rating, conductor sag limitations will be removed and the line’s connecting hardware will be replaced so that the line can be operated to 140 degrees C. The existing 345-kw transmission line 391, Buxton Substation to Scobie Pond Substation, is approximately 68 mileslong, (Buxton to ME/NH border ~31 miles, ME/NH border to Scobie Pond ~37 miles). The proposed 345-kV transmission line 391N, 345-kV Buxton Substation to 345-kV Deerfield Substation, will be approximately 50 miles long, (Buxton to ME/NH border ~31 miles, ME/NH border to Deerfield ~19 miles). The proposed 345-kv transmission line 391S, 345-kV Deerfield Substation to 345-kV Scobie Pond Substation, will be approximately 19 miles long. | 2017-12-01 | Approved | 2013-12-31
NU-13-T26 | 2013-12-01 | Northern Pass Transmission Project | Transmission notification from Northeast Utilities Service Company (“NU”) on behalf of Northern Pass Transmission LLC. for the 345-kV ac transmission line 373, 345-kV Deerfield Substation to 345-kV Scobie Pond Substation, be thermally up-rated to a minimum Long Time Emergency thermal rating of 1435 MVA. To achieve this thermal rating, conductor sag limitations will be removed and the line’s connecting hardware will be replaced so that the line can be operated to 140 degrees C | 2017-12-01 | Approved | 2013-12-31
NU-13-X03 | 2013-12-01 | Northern Pass Transmission Project | Transmission notification from Northeast Utilities Service Company (“NU”) on behalf of Northern Pass Transmission LLC to increase the 326 Line SPS summer thermal mode setpoint to 1515 MVA. The 326 Line SPS is a NPCC #26 Type 1 SPS. The 326 line summer thermal rating, N/LTE/STE, will be 1358/1515/1515 MVA. The Northern Pass Transmission (NPT) Project SIS determined that the Northeast Utilities’ portion of the 345-kV ac transmission line 326, 345-kV Scobie Pond Substation to the PSNH/NEP border, be thermally upgraded to a minimum summer Long Time Emergency (LTE) thermal rating of 1515 MVA. To achieve this thermal rating, conductor sag limitations would be removed and the conductor’s connecting hardware would be replaced, from the 345-kV Scobie Pond Substation through to the New Hampshire (PSNH)/Massachusetts (NEP) border, so that the line can be operated to 140 degrees C. The 326 Line SPS would require a thermal mode setpoint change from 1430 MVA to 1515 MVA. The 326 transmission line has been upgraded as part of the New Hampshire / Vermont 10 Year Study Plan while the NPT study was nearingcompletion. The present 326 transmission line summer thermal rating (N/LTE/STE) is 1358/1429/1429 MVA. The 326 line’s summer thermal LTE rating is limited by the 326 Line SPS thermal mode set point of 1429 MVA. The present 326 transmission line conductor summer thermal rating, N/LTE/STE, is 1358/1747/1906 MVA. The 345-kV 326 transmissionline distances are Scobie Pond to Lawrence Road ~11 miles and Lawrence to New Hampshire/Massachusetts Border ~7 miles. | 2017-12-01 | Approved | 2013-12-31
FP-13-G01 | 2013-12-11 | Footprint Generator and Salem Harbor Transmission Project | Generator notification from Footprint Power Salem Harbor Development LP (“FP”) for the construction of two combined cycle (1 gas turbine, one steam turbine) generating units, each with a combined net output of 337.0 MWs (647.0 MWs total net output) at the existing Salem Harbor generation site located in Salem, MA. | 2016-05-31 | Approved | 2014-02-03
NEP-13-T12 | 2013-12-11 | Footprint Generator and Salem Harbor Transmission Project | Transmission notification from New England Power Company (“NEP”)for the construction of a single new 115 kV bay with two circuit breakers at the existing Salem Harbor Substation in support of the Footprint Generator project. | 2016-05-31 | Approved | 2014-02-03
NU-13-T17 | 2013-11-13 | Newtown Substation Circuit Breaker Project | Transmission notification from Northeast Utilities Service Company (“NU”) for the installation of a new 115 kV circuit breaker at the Newtown Substation located in Newtown, CT. splitting the 1760 and 1876 lines into two independent line to provide optimization of the line relay settings for the most reliable operation. Also, tripping and reclosing selectivity will be improved. | 2014-12-31 | Approved | 2014-02-11
NU-13-T31 | 2013-12-03 | Peaslee Substation/Kingston Substation Project | Transmission notification from Northeast Utilities Service Company (“NU”) for the construction of the 115 kV Peaslee Switching Station consisting of a five circuit breakers in a ring bus configuration (PTF). Construction of a 115-kV overhead circuit, approximately 5.5 miles (PTF). Protection and Control additionsand changes at remote terminals, including Scobie Pond, Chester (Pulpit Rock), Brentwood, Great Bay, Kingston (PTF and Non-PTF). Construction of two 115-kV radial overhead circuits, each approximately 1500 feet, to supply a new Unitil 115/34.5-kV Substation (Non-PTF). | 2016-06-01 | Approved | 2014-02-11
UES-13-T01 | 2013-12-03 | Peaslee Substation/Kingston Substation Project | Transmission notification from Unitil Energy Systems (“UES”) for the construction of the 115kV – 34.5kV Kingston distribution stepdown substation, consisting of a two 60MVA stepdown transformers, 115kV circuit breakers, 34.5kV capacitor banks and 34.5kV circuit breakers for transformer and distribution line protection (non-PTF) along with protection and control additions/changes at Kingston (Non-PTF). | 2016-06-01 | Approved | 2014-02-11
NU-13-G33 | 2013-11-12 | Sudbury Landfill Solar Project | Generator notification from Northeast Utilities Service Company (“NU”) on behalf of Solar Sudbury One LF, LLC for a 1.33 MW solar array located in Sudbury MA and interconnect to the Sudbury Station #342, transformer 110A via the 14 kV distribution circuit 342-H3. | 2014-12-01 | Notification | 2014-02-11
NSTAR-11-T08-Rev.1 | 2013-12-06 | West Barnstable Substation Project Revision | Transmission notification from Northeast Utilities Service Company (“NU”) for the construction of an Construct an eight circuit breaker 115 kV substation at the West Barnstable location and install a new nominally 550 MVA 345/115kV auto-transformer at the new substation. The high side of the auto-transformer will be supplied with a 345 kV line from Carver 345 kV. Also, Line #115 will be brought in and out of the new substation. The name of the substation has been changed from Service Road to West Barnstable and the number of circuit breakers has been increased from 6 to 8. | 2013-09-01 | Notification | 2014-02-11
NSTAR-11-X01-Rev.1 | 2013-12-06 | West Barnstable Substation Project Revision | Transmission notification from Northeast Utilities Service Company (“NU”) to disable the existing Special Protection System (SPS) at the Barnstable 115 kV Substation will be disabled. The SPS will be enabled whenever the new 345 kV line from Carver to the West Barnstable Substation is out of service. Also updating the station name from Service Road to West Barnstable and update the one line diagrams to reflect the additional circuit breakers. | 2012-06-01 | Notification | 2014-02-11
NEP-13-GNF58 | 2013-12-09 | 100 Dupont Solar Project | Generator Notification from New England Power Company (“NEP”) for the installation of a 1.225 MW solar array located in Providence, RI and interconnecting to the Elmwood Substation via the 23 kV, 2228 Feeder. |  | Notification | 2014-02-11
NEP-13-GNF59 | 2013-12-09 | Synagro Woonsocket Solar Project | Generator Notification from New England Power Company (“NEP”) for the installation of a 2.0 MW solar array located in Woonsocket, RI and interconnecting to the Riverside 108 Substation via the 13.8 kV, 108W55 Feeder. |  | Notification | 2014-02-11
PLMP-13-13-G01 | 2013-12-04 | Waters River Jet Capacity Revision Project | Generator notification from Massachusetts Municipal Wholesale Electric Company on behalf of Peabody Municipal Light Plant (“PMLP”) for the generation true up of the Waters River Jet generator located in Peabody, MA. Revised unit rating is 47.050 MWs net output. P | 2013-12-31 | Notification | 2014-02-11
NU-13-T33 | 2013-12-05 | Holbrook Autotransformer Project | Transmission notification from Northeast Utilities Service Company (“NU”) to replace the existing 345/115 kV, 490 MVA autotransformer at Holbrook Station #478. The existing autotransformer was installed in June 2013 (NU-13-T08). The autotransformer was taken out of service in November 2013 due to high noise and vibration believed to be caused by high harmonics on the 345 kV system. NSTAR plansto temporarily reinstall the “old” Holbrook autotransformer. The temporary replacementautotransformer is rated 400 MVA Summer Normal. | 2013-12-31 | Notification | 2014-02-11
NU-13-G34 | 2013-11-14 | Waltham High School Solar Project | Generator notification from Northeast Utilities Service Company (“NU”) to install a 1.1 MW solar array located in Waltham, MA and interconnecting to the Waltham Station #450, transformer 110A via the 14 kV distribution circuit 363-1369YH1. | 2012-10-18 | Notification | 2014-02-11
NEP-13-T11 | 2013-12-09 | Salem Harbor Cable Replacement Project | Transmission notification from New England Power Company (“NEP”) for the replacement of the S-145E/T-146E underground cables from Salem Harbor to Canal Street with 5000 kcmil Cu. The expected summer LTE rating is 400 MVA per circuit. | 2016-06-01 | Notification | 2014-02-11
NU-13-T32 | 2013-12-03 | Greenwich 115/13.2 kV Substation Project | Transmission notification from Northeast Utilities Service Company (“NU”) for the construction of a new 115/13.2 kV substation located in Greenwich, CT. The GIS substation will include two 115/13.2-kV 60-MVA bulk power transformers, two 115-kV circuit breakers. Two new 115-kV 5000 kcmil XPLE Underground cables from Greenwich to Cos Cob Substation approximately 3.0 miles each. In addition, supporting modifications will be made to the Cos Cob substation will include one new 115 kV circuit breaker and repositioning of the 1750 line termination | 2017-06-01 | Notification | 2014-02-11
NU-13-G35 | 2013-12-12 | Acton Landfill Solar Project | Generator notification from Northeast Utilities Service Company (“NU”) for the construction of a 1.5 MW solar array located in Acton, MA and interconnecting to Maynard Station #416, Bus Section 1 via a 14 kV distribution circuit 416-H4. | 2013-12-18 | Notification | 2014-02-11
MATEP-13-G01 | 2013-10-21 | MATEP Generator Addition Project | Generator notification from MATEP LLC for the installation of a third gas turbine (14.9 MW net output) at the existing MATEP generating plant in Boston, MA. The generator will interconnect through the existing MATEP interconnection with NSTAR via three 13.8 kV tie lines from the NStar Brighton Station #329. | 2017-06-01 | Approved | 2014-01-09
NU-13-G30 | 2013-11-01 | Antares Solar Project | Generator Notification from Northeast Utilities Service Company (“NU”) for the installation of a 4.0 MW solar array located in East Lyme, CT and interconnecting to the Flanders 11Y Substation, 23 kV feeder 11Y1-2. | 2013-12-30 | Notification | 2014-01-09
NU-13-G24 | 2013-11-05 | Bluewave Dartmouth Solar Project | Generator Notification from Northeast Utilities Service Company (“NU”) on behalf of Bluewave Capital LLC for the installation of a 3.5 MW solar array in Dartmouth, MA and interconnecting to the NU Industrial Park Substation #636, #112 Transformer 13.2 kV feeder #103. | 2013-11-05 | Notification | 2014-01-09
NU-13-G23 | 2013-11-05 | Bluewave Mattapoisett Solar Project | Generator Notification from Northeast Utilities Service Company (“NU”) on behalf of Bluewave Capital LLC for the installation of a 1.5 MW solar array in Mattapoisett, MA and interconnecting to the NU Crystal Springs Substation #646, 13.2 kV feeder #301. | 2014-03-01 | Notification | 2014-01-09
NU-13-G22 | 2013-11-05 | Bluewave Plymouth Solar Project | Generator Notification from Northeast Utilities Service Company (“NU”) on behalf of Bluewave Capital LLC for the installation of a 4.26 MW solar array in Plymouth, MA and interconnecting to the Manomet Substation #721, 23 kV feeder #71. | 2014-03-01 | Notification | 2014-01-09
NU-13-G18 | 2013-11-05 | Bluewave Holliston Solar Project | Generator Notification from Northeast Utilities Service Company (“NU”) on behalf of Bluewave Capital LLC for the installation of a 3.0 MW solar array in Holliston, MA and interconnecting to the Medway Station 65, 13.8 kV circuit 65-H6. | 2014-06-30 | Notification | 2014-01-09
NU-13-T18 | 2013-11-01 | Torrington Autotransformer Replacement Project | Transmission Notification from Northeast Utilities Service Company (“NU”) for the replacement of the 40/53/67 MVA 115/69kV Autotransformer at the Torrington Terminal Substation located in Torrington, CT. | 2013-12-01 | Notification | 2014-01-09
NU-13-G29 | 2013-11-13 | Southern Sky Ravenbrook Landfill Solar Project | Generator Notification from Northeast Utilities Service Company (“NU”) for the installation of a 5.0 MW solar array in Carver, MA and interconnecting to the Northeast Utilities #10 23 kV distribution supply line and #930 23 kV distribution circuit out of the West Pond Substation #737. | 2013-12-30 | Notification | 2013-12-10
CED-13-G04 | 2013-10-10 | Merrimack Solar Project | Generator Notification from Con Edison Development (“CED”) on behalf of Merrimac Solar, LLC for the installation of a 1.5 MW solar array located in Merrimac, MA and interconnecting to the Mill Street Substation via the 13.8 kV distribution feeder #3. | 2013-12-01 | Notification | 2014-01-09
NEP-13-GNF38 | 2013-11-08 | Smith College Steam Turbine Project | Generator notification from New England Power Company (“NEP”) for the installation of a 3.5 MW gas fueled steam turbine generator located in Northampton, MA and interconnecting to the West Street #901 Substation via the 13.8 kV S100feeder. | 2013-10-15 | Notification | 2014-01-09
NEP-13-GNF48 | 2013-11-08 | Forbes Street Solar Project | Generator notification from New England Power Company (“NEP”) for the installation of a 3 MW solar array located in East Providence, RI and interconnecting to the Mink Street #7 Substation via the 23 kV 2267feeder. | 2013-11-22 | Notification | 2013-11-21
NEP-13-GNF49 | 2013-11-08 | Solventerra Palmer Project | Generator notification from New England Power Company (“NEP”) for the installation of a 3.5 MW solar array located in Palmer, MA and interconnecting to the Thorndike #523 Substation via the 13.2 kV 523L2feeder. | 2013-12-01 | Notification | 2014-01-09
NEP-13-GNF50 | 2013-11-08 | Solventerra Warren Solar Project | Generator notification from New England Power Company (“NEP”) for the installation of a 3 MW solar array located in Warren, MA and interconnecting to the Little Rest Road #516 Substation via the 13.2 kV 516L3feeder. | 2013-12-05 | Notification | 2014-01-09
NEP-13-GNF51 | 2013-11-08 | Lowell Landfill Solar Project | Generator notification from New England Power Company (“NEP”) for the installation of a 1.333 MW solar array located in Lowell, MA and interconnectingto the North Chelmsford #2 Substation via the 13.2 kV 2L4feeder. | 2013-12-27 | Notification | 2014-01-09
NEP-13-GNF52 | 2013-11-08 | EPG Solar Barre I Project | Generator notification from New England Power Company (“NEP”) for the installation of a 2 MW solar array located in Barre, MA and interconnecting to the Barre #604 Substation via the 13.8 kV 604W1feeder. Marvelous | 2013-12-31 | Notification | 2014-01-09
NEP-13-GNF53 | 2013-11-08 | EPG Solar Barre II Project | Generator notification from New England Power Company (“NEP”) for the installation of a 1.5MW solar array located in Barre, MA and interconnecting to the Barre #604 Substation via the 13.8 kV 604W3feeder. | 2013-12-31 | Notification | 2014-01-09
NEP-13-GNF54 | 2013-11-08 | Cabot Beverly Solar Project | Generator notification from New England Power Company (“NEP”) for the installation of a 2 MW solar array located in Beverly, MA and interconnecting to the North Beverly #18 Substation via the 23 kV 2365feeder. | 2013-12-31 | Notification | 2014-01-09
NEP-13-GNF55 | 2013-11-08 | UGT Renewable Energy Lancaster I Solar Project | Generator notification from New England Power Company (“NEP”) for the installation of a 2.5 MW solar array located in Lancaster, MA and interconnecting to the Laurel Circle #227 Substation via the 13.8 kV 227W1feeder. | 2013-12-31 | Notification | 2014-01-09
NEP-13-GNF56 | 2013-11-08 | UGT Renewable Energy Lancaster II Solar Project | Generator notification from New England Power Company (“NEP”) for the installation of a 2.499 MW solar array located in Lancaster, MA and interconnecting to the Laurel Circle #227 Substation via the 13.8 kV 227W3feeder. | 2013-12-31 | Notification | 2014-01-09
NEP-13-GNF57 | 2013-11-08 | Old Wardour Holdings Spencer Solar Project | Generator notification from New England Power Company (“NEP”) for the installation of a 4 MW solar array located in Spencer, MA and interconnecting to the E5 transmission line via the 69 kV E5feeder. | 2013-12-01 | Notification | 2014-01-09
NEP-13-T10 | 2013-11-12 | East Longmeadow Transformer Replacement | Transmission notification from New England Power Company (“NEP”) for the replacement of the existing T1 69/13.2 kV 6.25 MVA transformer with a 69/13.2 kV 24/32/40 MVA transformer at the East Longmeadow Substation in East Longmeadow, MA. | 2015-02-01 | Notification | 2014-01-09
CMEEC-13-G01 | 2013-09-30 | Backus Hospital Diesel Generator Project | Generator notification from Connecticut Municipal Electric Energy Cooperative (“CMEEC”) for the installation of four 2.49 MW (9.96 MW total net output) diesel generators located in Norwich, CT and interconnecting to the 13.8 kV Dudley Street Substation. | 2014-06-01 | Approved | 2013-10-23
NU-13-G16 | 2013-10-01 | Dartmouth Solar Project | Generator notification from Northeast Utilities Service Company (“NU”) for the installation of two solar farms with two separate points of interconnection to one 13.2kV distribution feeder, with a combined output of 6.75 MW located in Dartmouth, MA. The project will interconnect to the NU Utilities’ #541 13.2kV distribution feeder out of Cross Road Substation #651. | 2013-06-01 | Approved | 2013-10-23
NU-13-G19 | 2013-10-01 | Plymouth Wind Project | Generator notification from Northeast Utilities Service Company (“NU”) on behalf of Future Generation Wind, LLC for the installation of three 2 MW wind turbines (5.927 MW net output) located in Buzzard’s Bay, MA. Project will interconnect to a new 22.8 kV feeder that will connect to Bus #2 at the Valley Substation #715. | 2014-04-01 | Approved | 2013-10-23
GMP-11-G01-Rev1 | 2013-10-01 | Kingdom Wind/Jay Tap Synchronous Condenser Project | Generator Notification revision from Green Mountain Power Company (“GMP”) for a wind farm power plant controller (“PPC”) that manages wind farm turbines’ collective reactive capability to control the wind farm’s 46kV collector bus voltage has been introduced to replace the need for the 34.5kV collector-installed +/-2MVAr STATCOM and reduce the Jay Tap 46kV station-installed dynamic reactive requirement from +35MVAr to +25MVAr | 2013-11-01 | Approved | 2013-10-23
BRE-13-X01 | 2013-10-05 | Fife Brook AVR Project | Transmission notification from Brookfield Renewable Energy Group (“BRE”) for the replacement of the existing Automatic Voltage Regulator (AVR) with a Basler DECS-250 model to the Fife Brook Generator (Asset ID#413). The upgrade will not change the voltage capability of the generation output of the unit. | 2013-11-01 | Approved | 2013-10-23
NU-13-G21 | 2013-10-07 | Pave Paws Wind Project | Generator Notification from Northeast Utilities Service Company (“NU”) for the installation of two 1.5 MW (3 MWs net output) wind turbine generators located in Bourne, MA. The units will interconnect to a privately-owned 115/23kV distribution substation owned by the U.S. Air Force, which is interconnected to NU's #122 115kV transmission line between Bourne Switching Station #917 and Sandwich Substation #916. The interconnection of the two new 1.6 MW wind turbines bring the total connected generation at this point of interconnection to 6.2 MW, above the 5 MW threshold in PP5-1 whereby a Level 2 PPA is required. | 2013-10-21 | Approved | 2013-10-23
NEP-13-T09 | 2013-09-12 | Cooks Pond Transformer Replacement Project | Transmission notification from New England Power Company (“NEP”) for the replacement of the T1 and T2 69/13.8 kV 10/12.5 MVA transformers with 69/13.8 24/32/40 MVA transformers and replace the 1T54 and 2T53 69 kV airbreaks with 1200A 69 kV circuit switchers at the Cooks Pond #23 Substation located in Worcester, MA. | 2013-09-01 | Notification | 2013-10-23
NEP-13-GNF24 | 2013-10-04 | NextSun Energy Douglas Solar Project | Generator notification from New England Power Company (“NEP”) for the installation of a 3.0 MW solar array in Douglas, MA and interconnecting to the Uxbridge #321 Substation via the 13.8 kV 321W1 feeder. | 2013-10-01 | Notification | 2013-10-23
NEP-13-GNF39 | 2013-10-04 | Solventerra North Brookfield Solar Project | Generator notification from New England Power Company (“NEP”) for the installation of a 2.0 MW solar array located in North Brookfield, MA and interconnecting to the Lashway #525 Substation via the 23 kV 0012 feeder |  | Notification | 2013-10-23
NEP-13-GNF40 | 2013-10-04 | NextAmp Hubbardson Solar Project | Generator notification from New England Power Company (“NEP”) for the installation of a 2.8 MW solar array located in Hubbardson, MA and interconnecting to the Westminster #602 Substation via the 13.8 kV 602W2 feeder. |  | Notification | 2013-10-23
NEP-13-GNF41 | 2013-10-04 | Syncarpha Bolton Solar Project | Generator notification from New England Power Company (“NEP”) for the installation of a 4.95 MW solar array located in Bolton, MA and interconnecting to the Pratt’s Junction #225 Substation via the 13.8 kV 225W1 feeder. |  | Notification | 2013-10-23
NEP-13-GNF42 | 2013-10-04 | NextAmp Winchendon Solar Project | Generator notification from New England Power Company (“NEP”) for the installation of a 1.9 MW solar array located in Winchendon, MA and interconnecting to the East Winchendon #612 Substation via the 13.8 kV 612W3 feeder. |  | Notification | 2013-10-23
NEP-13-GNF43 | 2013-10-04 | NextAmp Ayers Village Solar Project | Generator notification from New England Power Company (“NEP”) for the installation of 2.0 MW solar array located in Methuen, MA and interconnecting to the Ward Hill #43 Substation via the 23 kV 2376 feeder. |  | Notification | 2013-10-23
NEP-13-GNF44 | 2013-10-04 | Gardner Solar I Project | Generator notification from New England Power Company (“NEP”) for the installation of a 2.0 MW solar array located in Gardner, MA and interconnecting to the Park Street #601 Substation via the 13.8 kV 601W1feeder. |  | Notification | 2013-10-23
NEP-13-GNF45 | 2013-10-04 | Fall River Innovation Solar Project | Generator notification from New England Power Company (“NEP”) for the installation of a 2.85 MW solar array located in Fall River, MA and interconnecting to the Sykes Road #28 Substation via the 13.8 kV 28W50 feeder. |  | Notification | 2013-10-23
NEP-13-GNF46 | 2013-10-04 | Geospeak Energy Charlton I Solar Project | Generator notification from New England Power Company (“NEP”) for the installation of a 2.0 MW solar array located in Charlton, MA and interconnecting to the West Charlton #415 Substation via the 13.2 kV 415L1 feeder. |  | Notification | 2013-10-23
NEP-13-GNF47 | 2013-10-04 | Geospeak Energy Charlton II Solar Project | Generator notification from New England Power Company (“NEP”) for the installation of a 2.0 MW solar array located in Charlton, MA and interconnecting to the West Charlton #415 Substation via the 13.2 kV 415L2 feeder |  | Notification | 2013-10-23
NU-13-G26 | 2013-09-30 | Cottage Street Solar Project | Generator notification from Northeast Utilities Service Company (“NU”) on behalf of Western Massachusetts Electric Company for the for the installation of a 3.25 MW solar array located in Springfield, MA and interconnecting to the East Springfield 5J Substation via the 13.8 kV 5J13 feeder. | 2013-10-16 | Notification | 2013-10-23
NU-13-T15 | 2013-09-03 | Newtown Substation Project | Transmission notification from Northeast Utilities Service Company (“NU”) for the expansion of the 12 M 115/13.8 kV Newtown Substation located in Newtown, CT to support added load growth in the area. | 2012-05-01 | Notification | 2013-10-23
NU-13-G25 | 2013-09-23 | Hudson Energy Solar Project | Generator notification from Northeast Utilities Service Company (“NU”) on ehalf of Hudson Energy Solar Corp. for the installation of three 500 kW solar arrays (1.5 MWs net output) in Southwick, MA and interconnecting to the Southwick 29A 115 kV Substation via the WEMECO 29A1 13.8 distribution circuit. | 2014-03-01 | Notification | 2013-10-23
CMP-13-T01 | 2013-09-09 | Kimball Road Transformer Project | Transmission notification from Central Maine Power Company (”CMP”) For the installation of a second 120/36 kV 30/56 MVA transformer at the Kimball Road Substation and relocate one of the 115 kV 30 MVAR capacitor banks from Bus 4 to Bus 3. | 2014-12-01 | Approved | 2013-10-02
NU-13-T16 | 2013-08-06 | Reeds Ferry 115 kV Circuit Breaker Addition Project | Transmission notification from Northeast Utilities Service Company (“NU”) for the installation of a 115 kV circuit breaker at the Reeds Ferry Substation located in Merrimack, NH | 2014-01-01 | Approved | 2013-10-02
AMLP-13-G01 | 2013-08-20 | Ashburnham Solar Project | Generator notification from Massachusetts Municipal Wholesale Electric Company (MMWEC) on behalf of Ashburnham Municipal Light Plant for the installation of a 3 MW solar project located in Ashburnham, MA and interconnecting to Ashburnham Substation 610 via circuit feeder W2. | 2013-10-01 | Notification | 2013-10-02
NU-13-G20 | 2014-09-18 | Future Generation Wind Project | Generator Notification from Northeast Utilities Service Company (“NU”) on behalf of Future Generation Wind LLC for the installation of a 1.976 net MW solar project located in Buzzard’s Bay, MA and interconnecting to the Valley Substation #715 via the 22.8 kV distribution feeder circuit #88. | 2014-04-01 | Notification | 2013-10-02
CMP-13-T02 | 2014-09-18 | Section 242 Line Rebuild Project | Transmission notification from Central Maine Power Company (“CMP”) for the 1.1 mile rebuild of the 115 kV transmission line Section 242 from 477 ACSR to single pole 1192 ACSR conductor from Haywood Road Substion in Benton, ME to Winslow Substation in Winslow, ME. | 2014-12-01 | Notification | 2013-10-02
NU-13-G04 | 2014-09-09 | Sullivan Ledge New Bedford Solar Project | – Generator notification from NSTAR Electric & Gas Company (“NSTAR) on behalf of Blueware Capital and RGS Energy for the installation of a 1.75 MW solar array located in New Bedford, MA and interconnecting to the Highland Avenue Substation #688 via the 13.2 kV distribution feeder #403 | 2014-04-01 | Notification | 2013-10-02
NEP-13-GNF32 | 2014-09-09 | Integrys Lancaster Solar Project | Generator notification from New England Power Company (“NEP”) on behalf of Integrys MA Solar LLC for the installation of a 3 MW solar array located in Lancaster, MA and fed by feeder #225W3 out of the Pratt’s Junction Substation #225 | 2013-10-10 | Notification | 2013-10-02
NEP-13-GNF33 | 2014-09-09 | NextSun Energy Rockland Solar Project | Generator notification from New England Power Company (“NEP”) on behalf of NextSun Energy Rockland LLC for the installation of a 2 MW solar array located in Rockland, MA and fed by feeder #93W40 out of the Plymouth Street Substation #90. | 2013-12-04 | Notification | 2013-10-02
NEP-13-GNF34 | 2014-09-09 | Millbury Solar Project | Generator notification from New England Power Company (“NEP”) on behalf of Millbury Solar LLC for the installation of a 3 MW solar array located in Millbury, MA and fed by feeder #304W5 out of the Millbury Substation #304. | 2013-12-27 | Notification | 2013-10-02
NEP-13-GNF35 | 2014-09-09 | A Plus International Westborough Solar Project | Generator notification from New England Power Company (“NEP”) on behalf of A Plus International for the installation of a 1.82 MW solar array located in Westborough, MA and fed by feeder #312W4 out of the Westborough Substation #312. | 2013-10-08 | Notification | 2013-10-02
NEP-13-GNF36 | 2013-09-09 | Outland Renewable Energy Spencer Solar Project | Generator notification from New England Power Company (“NEP”) on behalf of Outland Renewable Energy LLC for the installation of a 3 MW solar array located in Spencer, MA and fed by feeder #552L1 out of the Meadow Street Substation #552. | 2013-11-13 | Notification | 2013-10-02
NEP-13-GNF37 | 2013-09-09 | Tecta Solar West Bridgewater Solar Project | Generator notification from New England Power Company (“NEP”) on behalf of Tecta Solar West Bridgewater LLC for the installation of a 1.5 MW solar array located in West Bridgewater, MA and fed by feeder #797W19 out of the East Bridgewater Substation #797. | 2013-08-15 | Notification | 2013-10-02
NU-13-T14 | 2013-09-12 | Line Z177 Circuit Breaker Addition Project | Transmission notification from Northeast Utilities Service Company (“NU”) for the installation of a 115 kV Circuit Breaker on Line Z177with disconnect switches at the Berlin Substation in Berlin, NH. | 2013-09-01 | Notification | 2013-10-02
NU-13-T13 | 2013-08-09 | Pochassic Transformer Replacement Project | Transmission Notification from Northeast Utilities Service Company (“NU”) for the replacement of 115/69 kV transformer at the Pochassic 37R Substation in Westfield, | 2013-09-01 | Approved | 2013-08-28
ERM-13-G01 | 2013-08-09 | Dighton Power Uprate and AVR Project | Generator notification from EquiPower Resources Management (“ERM”) for the capacity increase of Dighton Power from 185.0MWs to 195.0 MWs (Winter Net) and 160.0 MWs to 167.0 MWs (Summer Net). | 2013-10-01 | Approved | 2013-08-28
ERM-13-X01 | 2013-08-09 | Dighton Power Uprate and AVR Project | Transmission notification from EquiPower Resources Management (“ERM”) for the replacement of the existing Dighton Power Automatic Voltage Regulator with newer model. | 2013-10-01 | Approved | 2013-08-28
NEP-13-T08 | 2013-07-31 | Reed Street Transformer Replacement Project | Transmission notification revision from New England Power Company (“NEP”) to replace the existing T4 115-13.2 kV 12/16/20 MVA transformer with one 115-13.2 kV 24/32/40 MVA transformer, replace the 148T4- 115 kV airbreak with one 1200A 115 kV circuit switcher. |  | Notification | 2013-08-28
NEP-13-GNF18 | 2013-08-09 | NextAmp Capital Rutland Solar Project | Generator notification from New England Power Company (“NEP) for the installation of a of a 4.999 MW solar generator and interconnecting to the National Grid 13.8 kV distribution system in Rutland, MA via the 55W1feeder out of the Treasure Valley 55 substation. |  | Notification | 2013-08-28
NEP-13-GNF26 | 2013-08-09 | Citizens Enterprises Rehoboth Solar Project | Generator Notification from New England Power Company (“NEP) for the installation of a of a 2.0 MW solar array in Rehoboth, MA and interconnecting to the National Grid 13.2 kV distribution system in Rehoboth via the 8L4feeder out of the Chartley Pond 8 substation. |  | Notification | 2013-08-28
NEP-13-GNF27 | 2013-08-09 | Soltas Energy Franklin Solar Project | Generator Notification from New England Power Company (“NEP) for the installation of a of a 1.725 MW solar array in Franklin, MA and interconnecting to the National Grid 13.8 kV distribution system in Franklin via the 344W3feeder out of the Beaver Pond 344 substation. |  | Notification | 2013-08-28
NEP-13-GNF28 | 2013-08-09 | One United West Bridgewater Solar Project | Generator Notification from New England Power Company (“NEP) for the installation of a of a 1.75 MW solar array in West Bridgewater, MA and interconnecting to the National Grid 13.8 kV distribution system in West Bridgewater via the 98W44 feeder out of the Belmont St. 98 substation |  | Notification | 2013-08-28
NEP-13-GNF29 | 2013-08-09 | NextAmp Capital North Kingstown Solar Project | Generator Notification from New England Power Company (“NEP) for the installation of a of a 2.0 MW solar array in North Kingstown, RI and interconnecting to the National Grid 12.47 kV distribution system in North Kingstown via the 46F4 feeder out of the Old Baptist Rd. 46 Substation |  | Notification | 2013-08-28
NEP-13-GNF30 | 2013-08-09 | GLC Development South Easton Solar Project | Generator Notification from New England Power Company (“NEP) for the installation of a of a 1.5 MW solar array in South Easton, MA and interconnecting to the National Grid 13.8 kV distribution system in South Easton via the 92W54 feeder out of the Easton 92 substation. |  | Notification | 2013-08-28
VELCO-13-GNF01 | 2013-07-24 | Williamstown Solar Project | Generator notification from Vermont Electric Company (“VELCO”) on behalf of Gasna 14P, LLC for the installation of a 2.0 MW solar generator and interconnecting to the GMP 70 G4 Circuit in White River Junction, VT. | 2012-12-01 | Notification | 2013-08-28
VELCO-13-GNF02 | 2013-07-24 | South Burlington Solar Project | Generator notification from Vermont Electric Company (“VELCO”) on behalf of SunGen Sharon I, LLC for the installation of a 1.805 MW solar generator and interconnecting to the Line 2904 Pole 1-2 PT in Sharon, VT. | 2012-08-01 | Notification | 2013-08-28
VELCO-13-GNF03 | 2013-07-24 | SunGen Solar I Project | Generator notification from Vermont Electric Company (“VELCO”) on behalf of SunGen Sharon I, LLC for the installation of a 1.805 MW solar generator and interconnecting to the Line 2904 Pole 1-2 PT in Sharon, VT. | 2012-08-01 | Notification | 2013-08-28
VELCO-13-GNF04 | 2013-07-24 | White River Junction Solar Project | Generator notification from Vermont Electric Company (“VELCO”) on behalf of CRL Solar, LLC for the installation of a 2.166 MW solar generator and interconnecting to the GMP 70 G4 Circuit in White River Junction, VT. | 2012-10-19 | Notification | 2013-08-28
VELCO-13-GNF05 | 2013-07-24 | Southern Vermont Energy Park Solar Project | Generator notification from Vermont Electric Company (“VELCO”) on behalf of SVEP Solar Project Company, LLC for the installation of a 2.0 MW solar generator and interconnecting at the Washington Electric Cooperative/Jackson Corners Circuit 3 in Williamstown, VT. | 2012-12-01 | Notification | 2013-08-28
NU-13-T10 | 2013-06-03 | Holliston Temporary Transformer Project | Transmission notification from Northeast Utilities Service Company (“NU”) for the installation of a 115/14.4 kV mobile station transformer and two distribution circuits to establish a new supply in the Western region of NSTAR. The need for this installation is driven by the high annual load growth rate at Purchase Street Station #126. The Project will establish a temporary distribution system supply at transmission ROW 7 and Fiske Street in Holliston. The transformer will be connected to 115 kV line 274-509 which extends from Medway Station 65 to Sherborn Station 274. The temporary transformer will be connected to the 115 kV line with a circuit switcher. | 2013-06-01 | Approved | 2013-07-25
NEP-13-GNF25 | 2013-06-01 | Cornerstone Power Monson Solar Project | Generator Notification from New England Power Company (NEP) for the installation of a 3.0 MW solar array in Monson, MA and interconnecting to the Palmer #503 substation via the 13.2 kV 503L2 feeder. | 2013-10-31 | Approved | 2013-08-07
CPEM-12-X01 | 2013-06-06 | Rumford Power System Stabilizer (PSS) Project | System Stabilizer (PSS) Project – Level III (Vote) CPEM-12-X01 – Transmission Notification from CP Energy Marketing (“CPEM”) topermanently install the previously commissioned Power System Stabilizer EX2000 software at the Rumford Power facility. This equipment is currently installed at the Rumford Facility pursuant to a Proposed Plan Application for the temporary installation of the PSS during transmission construction. The PPA for temporary construction was approved by ISO New England on March 30, 2012. Under PPA#CPEM -12-X01, the PSS entered into service in November 2012. This application provides for the permanent installation of the PSS upon the completion of certain area transmission construction in May 2014. | 2014-05-01 | Approved | 2013-07-25
CMP-12-X01-Rev.1 | 2013-06-05 | Rumford Area Temporary SPS Modification Project | Transmission notification from Central Maine Power Company (“CMP”) For the installation of a temporary Rumford Area SPS (NPCC Type III SPS) to reject generation at Rumford Power Associates (RPA) for faults on Sections: 210, 211, 217, 221, 228, 243, 229, various Rumford Area buses, and breaker failure conditions at Kimball Road during the construction of Section 243A as part of the Maine Power Reliability Program (MPRP). This change is required to maintain system stability during the construction period. (This modification adds a fault on the 229 line as a trigger of SPS action.). | 2013-09-29 | Approved | 2013-07-25
NEP-13-T05 | 2013-05-10 | Wakefield Substation Project | Transmission notification from New England Power Company (“NEP”) for the construction of a new 115/13.8 kV substation to be named Wallace Substation in Wakefield, MA supplied via taps off of the S-145 & T-146 lines from Tewksbury 22 to Wakefield Junction. | 2014-06-01 | Approved | 2013-07-25
NEP-13-T06 | 2013-05-10 | Wakefield Substation Project | Transmission notification from New England Power Company (“NEP”) for the reconductoring of the 115 kV lines S-145 & T-146 between Wakefield Junctionand the new Wallace Substation in Wakefield, MA. | 2014-06-01 | Approved | 2013-07-25
NU-13-T08 | 2013-06-03 | Holbrook Autotransformer Replacement Project | Transmission Notification from Northeast Utilities Service Company (“NU”) to replace the existing 345/115 kV, 400 MVA Autotransformer at Holbrook Station #478.The existing autotransformer is being replaced based on age and operating condition issues. The new autotransformer is rated 490 MVA Summer Normal. | 2013-06-01 | Approved | 2013-06-18
NU-12-T14-Rev.1 | 2013-05-29 | Beseck Substation Variable Shunt Reactor Project | Transmission notification revision from Northeast Utilities Service Company (“NU”) due to a change in the reactor connection at the existing Beseck 9F Substation as part of the GSRP project. Connect a variable 75-150 MVAR shunt reactor to Bus B with a 500-kV 63 kA live tank circuit breaker at Beseck 9F 345-kV switching station | 2013-12-01 | Notification | 2013-07-25
NU-12-T16-Rev.1 | 2013-05-29 | Beseck Substation Variable Shunt Reactor Project | Transmission notification revision from Northeast Utilities Service Company (“NU”) due to a change in the reactor connection at the existing Beseck 9F Substation as part of the NEEWS/CCRP project. Connect a second variable 75-150 MVAR shunt reactor to Bus A with a 500-kV 63 kA live tank circuit breaker at the Beseck 9F 345-kV switching station. | 2017-12-01 | Notification | 2013-07-25
PMLP-13-T01 | 2013-05-09 | Peabody Bus Links Project | Transmission notification from Peabody Municipal Light Plant (“PMLP”) for the installation of a permanent set of bus links into the CS3 115 kV circuit switcher at the Waters River Substation. Installation will allow the Waters River Jet 2 generation asset to be connected to the B154 South 115 kV transmission Line | 2013-06-20 | Notification | 2013-07-25
NU-13-G17 | 2013-06-03 | Somers Solar Center Project | Generator Notification from Northeast Utilities Service Company (“NU”) for the installation of a 4.99 MW solar array in Somers, CT and interconnecting at at the Scitico 27H Substation 23 kV distribution feeder on South Rd. Somers, CT. | 2013-09-30 | Notification | 2013-07-25
NU-13-T09 | 2013-05-31 | Somersville Substation Transformer Replacement Project | Transmission notification from Northeast Utilities Service Company (“NU”) to replace the existing 115/14 kV, 65 MVA transformer at Somerville Station #402. The existing transformer failed on May 6, 2013 after experiencing an internal fault. A new 65 MVA transformer was installed and placed in-service May 31, 2013 | 2013-05-31 | Notification | 2014-09-09
NEP-13-GNF-16 | 2013-06-07 | Berkeley Real Estate Solar Project | Generator notification from New England Power Company (“NEP) on behalf of Berkeley Real Estate Management LLC for the installation of a 2 MW solar generator and interconnecting to the National Grid 13.2 distribution system in Methuen, MA via the 63L2 feeder out of the West Methuen 63 substation | 2013-10-01 | Notification | 2013-07-25
NEP-13-GNF-17 | 2013-06-07 | OSG Solar Project | Generator notification from New England Power Company (“NEP) On behalf of OSG Solar I-III LLC for the installation of a 2.5 MW solar generator and Interconnecting to the National Grid 13.8 kV distribution system in Orange, MA via the 702W2 feeder out of the Chestnut Hill 702 substation | 2012-07-06 | Notification | 2013-07-25
NEP-13-GNF-19 | 2013-06-07 | Sungen Orange Solar Project | Generator notification from New England Power Company (“NEP) on behalf of SunGen Orange LLC for the installation of a 2 MW solar generator and interconnecting to the National Grid 705W2 feeder via the Wendell Depot 705 substation | 2013-06-07 | Notification | 2013-07-25
NEP-13-GNF-20 | 2013-06-07 | Wilson Ground Mount Solar Generator Project | Generator notification from New England Power Company (“NEP) on behalf of GLC-(MA) Wilson LLC for the installation of a 2 MW solar generator and interconnecting to the National Grid 13.2 kV distribution system in Spencer, MA via the 552L1 feeder out of the Meadow St. 552 substation. | 2013-06-20 | Notification | 2013-07-25
NEP-13-GNF-21 | 2013-06-07 | Scituate Wind Project | Generator notification from New England Power Company (“NEP)on behalf of Scituate Wind LLC for the installation of a 1.5 MW wind turbine generator and interconnecting to the National Grid 13.8 distribution system in Scituate, MA via the 915W36 feeder out of the Scituate 915 substation. | 2013-03-29 | Notification | 2013-07-25
MMWEC-12-G01-Rev.1 | 2013-06-06 | Chicopee Citizens Enterprise Solar Project | Generation Notification revision from Massachusetts Municipal Wholesale Electric Company (“MMWEC”) for the increase in output power from 2.5 MW to 3.0 MWs for the solar array generator located in Chicopee, MA. Project will interconnect to the 24B1 Feeder out of Prospect Street Substation. | 2013-12-01 | Notification | 2013-07-25
UI-13-G01 | 2013-05-07 | Bridgeport Fuel Cell Project | Generator notification from United Illuminating Company (“UI”) on behalf of Bridgeport Fuel Cell Park, LLC for the installation of two 2.8 MW (5.6 MWs net output) fuel cells in Bridgeport, CT and a 13.8 kV interconnection to the Ash Creek Substation. | 2013-12-24 | Approved | 2013-07-02
UI-13-G02 | 2013-05-07 | Bridgeport Fuel Cell Project | Generator notification from United Illuminating Company (“UI”) on behalf of Bridgeport Fuel Cell Park, LLC for the installation of two 2.8 MW (5.6 MWs net output) fuel cells in Bridgeport, CT and a 13.8 kV interconnection to the New Congress I Substation | 2013-12-24 | Approved | 2013-07-02
UI-13-G03 | 2013-05-07 | Bridgeport Fuel Cell Project | Generator notification from United Illuminating Company (“UI”) on behalf of Bridgeport Fuel Cell Park, LLC for the installation of one 2.8 MW fuel cell and one 1.35 MW induction generator in Bridgeport, CT and a 13.8 kV interconnection to the New Congress II Substation. | 2013-12-24 | Approved | 2013-07-02
NU-13-T07 | 2013-05-07 | Haddam Neck 345 kV Variable Shunt Reactor Project | Transmission notification from Northeast Utilities Service Company (“NU”) for the installation of one 75-150 MVAr 345 kV variable shunt reactor at the Haddam Neck 14B Switching Station. Also install a 345-kV circuit breaker (14B-3T-2) at the Haddam Neck 14B Switching Station in the existing spare position between the 14B-2T-2 and 14B-4T-2 circuit breakers, and replace the existing 345-kV circuit breaker (14B-4T-2). | 2014-06-01 | Approved | 2013-07-02
NU-13-G15 | 2013-05-07 | Acushnet RGHRT Braley 1 Solar Project | Generator Notification from Northeast Utilities Service Company (“NU”) for the installation of a 1.5 MW solar array in Freetown, MA and interconnecting at 13.3 kV to the #604 distribution circuit and the #102 13.2 kV feeder out of the Industrial Park Substation #636. | 2012-06-15 | Notification | 2013-07-25
NU-13-G12 | 2013-05-07 | Plymouth Solar Project | Generator Notification from Northeast Utilities Service Company (“NU”) for the installation of a 4.75 MW solar array in Plymouth, MA and interconnecting at the #73 23 kV distribution feeder out of the Manomet Substation #721. | 2013-05-01 | Notification | 2013-07-02
NU-13-G11 | 2013-05-07 | Plympton Solar Project | Generator Notification from Northeast Utilities Service Company (“NU”) for the installation of a 4.0 MW solar array in Plympton, MA and interconnecting at the #51 23kV distribution supply line out of the Brook Street Substation #727. Brook Street Substation #727 is a new 115/23kV bulk distribution station that is currently under construction, with an expected in-service date of June 2013. The new substation was approved under I.3.9 application NSTAR-12-T02. The PV array will not be permitted to interconnect until the new substation is in-service | 2013-06-01 | Notification | 2013-07-02
NEP-13-GNF07 | 2013-05-10 | Boston Scientific Quincy Solar Project | Generator notification from New England Power Company (“NEP”) on behalf of Boston Scientific for the installation of a 1.1 MW solar generator located in Quincy, MA and interconnecting to the #11W3 feeder out of the North Quincy Substation # 11. | 2013-11-01 | Notification | 2013-07-02
NEP-13-GNF08 | 2013-05-10 | Narragansett Bay Commission Wind Project | Generator notification from New England Power Company (“NEP”) on behalf of Narragansett Bay Commission for the installation of a 4.5 MW wind turbine generator located in Providence, RI and interconnecting to the #76F8 feeder out of the Point Street Substation # 76. | 2012-10-16 | Notification | 2013-07-02
NEP-13-GNF10 | 2013-05-10 | Soltas Athol Solar Project | Generator notification from New England Power Company (“NEP”) on behalf of Soltas Athol for the installation of a 3.0 MW solar generator located in Athol, MA and interconnecting to the #702W1 feeder out of the Chestnut Hill Substation # 702. | 2013-07-01 | Notification | 2013-07-02
NEP-13-GNF09 | 2013-05-10 | Soltas Orange Solar Project | Generator notification from New England Power Company (“NEP”) on behalf of Soltas Orange for the installation of a 3.0 MW solar generator located in Orange, MA and interconnecting to the #702W3 feeder out of the Chestnut Hill Substation # 702. | 2013-07-01 | Notification | 2013-07-02
NEP-13-GNF11 | 2013-05-10 | Scituate Solar Project | Generator notification from New England Power Company (“NEP”) on behalf of the Town of Scituate for the installation of a 3.0 MW solar generator located in Scituate, MA and interconnecting to the #915W36 feeder out of the Scituate Substation # 915. | 2013-11-01 | Notification | 2013-07-02
NEP-13-GNF12 | 2013-05-10 | Winchendon Solar Project | Generator notification from New England Power Company (“NEP”) on behalf of Town of Winchendon for the installation of a 2.0 MW solar generator located in Winchendon, MA and interconnecting to the #612W1feeder out of the East Winchendon Substation # 612. | 2013-12-01 | Notification Withdrawn | 7/2/2013 11//19/2013
NEP-13-GNF13 | 2013-05-10 | Kearsarge Franklin Solar Project | Generator notification from New England Power Company (“NEP”) on behalf of Kearsarge Franklin LLC for the installation of a 3.0 MW solar generator located in Franklin, MA and interconnecting to the #3422W1feeder out of the South Wrentham Substation # 3422. | 2013-08-01 | Notification | 2013-07-02
NEP-13-GNF15 | 2013-05-10 | Hubbardston Solar Project | Generator notification from New England Power Company (“NEP”) on behalf of Hubbardson Solar LLC for the installation of a 2.0 MW solar generator located in Hubbardson, MA and interconnecting to the #604W4 feeder out of the Barre Substation # 604 | 2013-08-01 | Notification | 2013-07-02
NEP-13-GNF14 | 2013-05-10 | KS Solar Five Solar Project | Generator notification from New England Power Company (“NEP”) on behalf of KS Solar Five LLC for the installation of a 4.0 MW solar generator located in Franklin, MA and interconnecting to the #2284 feeder out of the South Wrentham Substation # 2284. | 2013-12-01 | Notification | 2013-07-02
CED-13-G02 | 2013-05-10 | West Greenwich Solar Project | Generator notification from Con Edison Development (“CED”) for the installation of a 1.75 MW solar array in West Greenwich, RI and interconnecting to the Hopkins Hill Substation via the Narragansett 63F6 12.47 kV distribution circuit. | 2013-05-27 | Notification | 2013-07-02
NEP-13-G02 | 2013-04-11 | Monson Solar Project | Generator notification from New England Power Company (“NEP”) for the installation of ten 0.5 MW (5 MWs net output) solar plant in Monson, MA and install a 69/13.2 kV, 5 MVA transformer and switchgear interconnecting to the plant. | 2014-06-01 | Approved Withdrawn | 5/14/2013 10/28/2014
NEP-13-G03 | 2013-04-11 | Monson Solar Project | Generator notification from New England Power Company (“NEP”) for the installation of ten 0.5 MW (5 MWs net output) solar plant in Monson, MA and install a 69/13.2 kV, 5 MVA transformer and switchgear interconnecting to the plant. | 2014-06-01 | Approved Withdrawn | 5/14/2013 10/28/2014
NEP-13-T07 | 2013-04-11 | Monson Solar Project | Transmission notification from New England Power Company (“NEP”) for the construction of a new interconnection substation with a single (1) 69 kV, 2000A, 31.5kA breaker and two (2) 2000A load-break switches in Monson, MA. Construct a 0.1 mile long, 69 kV tap line connecting the interconnection substation to the 69 kV N-14 transmission line. Connect the interconnection substation to the proposed PV plants as specified in NEP-13-G02 and NEP-13-G03. | 2014-06-01 | Approved Withdrawn | 5/14/2013 10/28/2014
NU-13-G13 | 2013-04-08 | Velcro Generator Project | Generator Notification from Northeast Utilities Service Company (“NU”) on behalf of Velcro USA, Inc for the construction of a 5.3 MW gas turbine generator and interconnecting to the PSNH 370X2 circuit that taps into the 370X line which is fed by the 3142 circuit out of PSNH’s Bedford Substation | 2013-05-31 | Approved | 2013-05-14
NU-13-X01 | 2013-03-19 | Lake Road Type III SPS Generation Rejection Retirement Project | Transmission Notification from Northeast Utilities Service Company (“NU”) for the Lake Road Type III SPS Generation Rejection Retirement. In 2016, the Interstate Reliability Project of the New England East-West Solution will be installed. This project includes a second Card to Lake Road transmission line and a Lake Road to West Farnum. The NEEWS 2012 Proposed Plan Application (PPA) studies included delta P calculations for the Lake Road plant. These calculations indicated that with these additional system modifications that under all lines in-service that potential excessive shaft torques was no longer a concern. This was the sole need for the Type III SPS. The other power flow, short circuit and stability simulations performed as part of the NEEWS PPA did not indicate any other need for this SPS. | 121/2016 | Notification | 2013-05-14
NU-13-G14 | 2013-04-10 | NextAmp Hadley Solar Project | Generator Notification from Northeast Utilities Service Company (“NU”) for the installation of five 0.50 MW (2.5 MWs net output) solar generator on Hadley, MA and interconnecting to the Amherst 17K 115 kV substation via the WEMECO 17K1 13.8 kV distribution circuit. | 2013-09-01 | Notification | 2013-05-14
NEP-13-GNF01 | 2013-04-10 | Berkshire School Solar Project | Generator Notification from New England Power Company (“NEP”) for the installation of a 1.75 MW solar generator in Sheffield, MA and interconnecting to the 1108W1 feeder out of the Sheffield #8 substation. | 2011-12-10 | Notification | 2013-05-14
NEP-13-GNF02 | 2013-04-10 | Douglas Solar Project | Generator Notification from New England Power Company (“NEP”) for the installation of a 2.0 MW solar generator in Douglas, MA and interconnecting to the 320W2 feeder out of the Whitins Pond Substation #320 in Northbridge, MA | 2012-12-28 | Notification | 2013-05-14
NEP-13-GNF03 | 2013-04-10 | NCCI Gardner Prison Wind Project | Generator Notification from New England Power Company (“NEP”) for the installation of a 3.3 MW wind turbine generator in Gardner, MA and interconnecting to the 601W4 feeder out of the Park Street substation # 601. | 2013-04-03 | Notification | 2013-05-14
NEP-13_GNF04 | 2013-04-10 | Sungen Uxbridge Solar Project | Generator Notification from New England Power Company (“NEP”) for the ninstallation of a 2.85 MW solar generator in Uxbridge, MA and interconnecting to the 321W4 feeder out of the Uxbridge substation #321. Proposed in service date of the project is May 1, 2013. | 2013-05-01 | Notification | 2013-05-14
NEP-13-GNF05 | 2013-04-10 | Sungen Mark Andover Solar Project | Generator Notification from New England Power Company (“NEP”) for the installation of a 2.85 MW solar generator in Andover, MA and interconnecting to the 59L1 feeder out of the East Tewksbury Substation #59 | 2013-05-01 | Notification | 2013-05-14
NEP-13-GNF06 | 2013-04-10 | East Bridgewater Solar Project | Generator Notification from New England Power Company (“NEP”) for the installation of a 2.0 MW solar generator in East Bridgewater, MA and interconnecting to the 797W42 feeder out of the East Bridgewater substation #797. | 2013-05-01 | Notification | 2013-05-14
CED-13-G01 | 2013-04-10 | UMass Amherst Solar Project | Generator notification from Con Edison Development Inc. (“CED”) for the installation of four 0.50 MW (2.0 MWs net output) solar generator located in Hadley, MA and interconnecting to the Podick 18G 115 kV substation via WEMECO 18G4 13.8 distribution circuit. | 2013-05-01 | Notification | 2013-05-14
NEP-13-T02 | 2013-03-06 | Mt. Support/Slayton Hill/Michael Ave. Substation Project | Transmission Notification from New England Power Company (“NEP”) to loop the 115 kV W-149N line into the Mount Support Substation in Lebanon, NH by building a 2.1-mile tap line from Wilder Switching Junction to Mount Support. Install one 115 kV, 40 kA in-line breaker at Mount Support, creating two separate lines, W-149N between Wilder and Mount Support and W-149 between Mount Support and Slayton Hill. Install equipment for one high speed protection system on W-149N between Wilder and Mount Support and one high speed protection system on resulting W-149 between Mount Support and Slayton Hill. Install a 2nd 24/30/40 MVA, 115/13.8 kV transformer. | 2017-06-01 | Approved | 2013-04-04
NEP-13-T03 | 2013-03-06 | Mt. Support/Slayton Hill/Michael Ave. Substation Project | Transmission Notification from New England Power Company (“NEP”) to replace the existing 12/16/20 MVA, 115/13.8 kV transformer T1 at the Slayton Hill Substation in Lebanon, NH with a 33/44/55 MVA unit. Install equipment for one high speed protection system on the W-149 line between Mount Support and Slayton Hill. | 2017-06-01 | Approved | 2013-04-04
NEP-13-T04 | 2013-03-06 | Mt. Support/Slayton Hill/Michael Ave. Substation Project | Transmission Notification from New England Power Company (“NEP”) to construct a new Michael Ave Substation in Charlestown, NH by tapping the W-149S line. Install one 15/20/25 MVA, 115/13.2 kV transformer at Michael Ave | 2013-06-01 | Approved | 2013-04-04
NU-13-G06 | 2013-03-11 | Barnstable Landfill Solar Project | Generator Notification from Northeast Utilities Service Company (“NU”) on behalf of American Capital Energy for the installation of a 1.416 MW PV array, consisting of a AE Solaron 250 kW and a AE Solaron 500 kW inverter interconnected to a 750 kVA 480Y/277 volt to 23kV padmount step-up transformer, and two AE Solaron 333 kW inverters connected to a 2nd 750 kVA 480Y/277 volt to 23kV padmount stepup transformer. Both padmount step-up transformers will connect via 23kV 1/0 AL URD cable through a recloser to NSTAR’s #88 23kV feeder out of Mashpee Substation #946. | 2013-04-01 | Notification | 2013-04-15
NU-13-G07 | 2013-03-11 | Barnstable Landfill Solar Project | Generator Notification from Northeast Utilities Service Company (“NU”) on behalf of American Capital Energy for the installation of a2.0 MW PV array, consisting four (4) AE Solaron 500 kW inverters interconnected to a 2000 kVA 480Y/277 volt to 23kV padmount stepup transformer. The padmount step-up transformer will connect via 23kV 1/0 AL URD cable through a recloser to NSTAR’s #80A 23kV feeder out of Oak Street | 2013-04-01 | Notification | 2013-04-15
NU-13-T05 | 2013-02-15 | Canton Transformer Replacement Project | Transmission Notification from Northeast Utilities Service Company (“NU”) to replace the existing transformer 110B at Canton Station 470 with a new 117/15.12, 37/50/62.5 MVA, OA/FA/FA LTC unit. | 2013-06-01 | Notification | 2013-04-04
NU-13-T06 | 2013-02-15 | Canton Transformer Replacement Project | Transmission Notification from Northeast Utilities Service Company (“NU”) to replace the existing transformer 110A at Canton Station 470 with a new 117/15.12, 37/50/62.5 MVA, OA/FA/FA LTC unit. | 2013-06-01 | Notification | 2013-04-04
NU-13-G03 | 2013-03-11 | Dennis Landfill Solar Project | Generator Notification from NSTAR Electric and Gas Company (“NSTAR”) on behalf of American Capital Energy for the installation of two (2) separate PV array interconnections of 1.25 MW each, with each 1.25 MW array consisting of two 500 kW Solaron Inverters connected through 500 kVA 480V to 23kV padmount step-up transformers, and a 250 kW Solaron Inverter connected through a 250 kVA 480V to 23kV padmount step-up transformer. Interconnection will be made to the NSTAR’s #92B 23kV distribution feeder out of NSTAR’s Harwich Substation #968 | 2013-03-01 | Notification | 2013-04-15
BHE-13-T01 | 2013-03-05 | Keene Road Transformer Project | Transmission Notification from Bangor Hydro Electric Company (“BHE”) for the installation of a new load serving transformer and related facilities at Keene Rd 115kV substation. Transformer is intended to operate in parallel with existing transformer(s) serving the BHE 46kV subtransmission system. | 2014-07-01 | Notification | 2013-04-15
NU-08-T13-Rev. | 2013-02-06 | NEEWS/GSRP Project Revisions | Transmission Notification revision from Northeast Utilities Service Company (“NU”) for the Breckwood 115-kV circuit 1322 Reactor Bypass and Open Breckwood Substation 1T Breaker and Maintain Breaker in the Normally Open Position. | 2013-12-01 | Notification | 2013-04-04
NU-08-T35-Rev.1 | 2013-02-06 | NEEWS/GSRP Project Revisions | Transmission Notification revision from Northeast Utilities Service Company (“NU”) to add a 2nd High Speed Protection System to the 115 kV Line 1311, Agawam to West Springfield. | 2013-12-01 | Notification | 2013-04-04
NU-08-T36-Rev.1 | 2013-02-06 | NEEWS/GSRP Project Revisions | Transmission Notification revision from Northeast Utilities Service Company (“NU”) to add a 2nd High Speed Protection System to the 115 kV Line 1412, Agawam to West Springfield. | 2013-12-01 | Notification | 2013-04-04
NU-13-T01 | 2013-02-26 | Scotia Street Circuit Breaker Project | Transmission Notification from Northeast Utilities Service Company (“NU”) for the installation of three new indoor 115 kV gas insulated circuit breakers at the Scotia Street Substation #492 in Boston, MA. One of the new circuit breakers will replace 115/14 kV transformer 110B circuit switcher CS770. The second new breaker will replace 115 kV switch S790 on Brighton Station #329 side of cable 329-513. The third breaker will be added on the Kingston Street Station #514 side of cable 329-513. The Scotia Street 110B transformer protection will be tied into the new 115 kV transformer breaker. The two new circuit breakers on cable 329-513 will initially be used to provide sectionalizing capability and will not be part of 329-513 transmission line protection. A proposed future project will split line 329-513 into two independently relayed lines. | 2013-05-01 | Notification | 2013-04-04
NU-13-G02 | 2013-03-11 | Mashpee Landfill Solar Project | Generator Notification from NSTAR Electric and Gas Company (“NSTAR”) on behalf of American Capital Energy for the interconnection of three (3) AE Solaron 500 kW inverters, all connected to a common 1500 kVA 480Y/277 Volt to 23kV padmount step-up transformer. The padmount transformer connects back via 23kV 1/0 AL URD cable and overhead tap through recloser to an existing NSTAR overhead 23kV distribution circuit on Asher’s Path. The point of interconnection will be made to NSTAR’s #88 23kV distribution supply line and #455 circuit out of NSTAR’s Mashpee Substation #946 | 2013-03-01 | Notification | 2013-04-15
NU-13-G08 | 2013-03-01 | Tolland Solar Project | Generator Notification from Northeast Utilities Service Company (“NU”) for the installation of seven 500 kW solar generators (3.5 MW net output) located in Tolland, MA and interconnecting to the Blanford 19J 115 kV Substation via WEMECO’s 9J4 23 kV distribution circuit. | 2013-03-26 | Notification | 2013-04-12
FPLE-13-G01 | 2013-01-29 | Weston Hydro Upgrade Project | Generator Notification from NextEra Energy Resources (“NextEra”) for the change in net station output at the Weston Hydro Electric Station. Project will uprate Unit 4 by installing a new runner and rehabilitate the generator components. A new AVR will be installed on all 4 units. A new generator step up transformer will be installed and changed to a Wye configuration on the system side (34.5 kV). The units will be connected to the CMP Weston Hydro Solon Substation #5, 34.5 kV. The result of the project upgrade will increase the current claimed capability from 13.2 MWs to 14.8 MWs. | 2014-12-01 | Notification | 2013-04-12
NU-12-T23 | 2013-01-31 | New Hampshire Transmission Upgrades Project | Transmission Notification from Northeast Utilities Service Company (“NU”) to eliminate the conductor clearance limitations on the 18 mile 345 kV overhead line from Scobie Pond to Lawrence Road NH/MA border. | 2016-12-01 | Approved | 2013-03-07
NU-12-T44 | 2013-01-31 | New Hampshire Transmission Upgrades Project | Transmission Notification from Northeast Utilities Service Company (“NU”) to install a 2nd 230/115 kV autotransformer at the Littleton Substation. Tap the existing National Grid 230-kV Comerford- Moore C203 line into the Littleton Substation. Build a new 1/2 mile 230-kV transmission line between the C203 tap point and the Littleton Substation and connect it to the new 230/115-kV autotransformer. Install a 230-kV circuit switcher and two 115-kV circuit breakers at Littleton Substation. | 2016-12-01 | Approved | 3/7/2013 12/1/14
NU-12-T45 | 2013-01-31 | New Hampshire Transmission Upgrades Project | Transmission Notification from Northeast Utilities Service Company (“NU”) to install two +25/-12.5 MVAR 115-kV dynamic devices and two 115-kV circuit breaker at the Saco Valley Substation. Two 115/13.8-kV transformers will also be installed to accommodate the dynamic devices. | 2016-12-01 | Approved | 2013-03-07
NU-12-T46 | 2013-01-31 | New Hampshire Transmission Upgrades Project | Transmission Notification from Northeast Utilities Service Company (“NU”) to install four 26.6 MVAR 115-kV capacitor banks and two 115-kV circuit breakers at the Webster Substation. | 2016-12-01 | Approved | 2013-03-07
NU-12-T47 | 2013-01-31 | New Hampshire Transmission Upgrades Project | Transmission Notification from Northeast Utilities Service Company (“NU”) to tap the existing 345-kV Scobie Pond to Amherst 380 line and build a new three circuit breaker 345-kV ring bus. Install a single 345/115-kV autotransformer at the Eagle Substation. Install four 115-kV circuit breakers and four 26.6 MVAR capacitor banks at the Eagle Substation. | 2016-12-01 | Approved | 2013-03-07
NU-12-T48 | 2013-01-31 | New Hampshire Transmission Upgrades Project | Transmission Notification from Northeast Utilities Service Company (“NU”) to install a new 345-kV series circuit breaker next to the existing 802 circuit breaker for the 380E line at the Scobie Pond Substation | 2016-12-01 | Approved | 2013-03-07
NU-12-T49 | 2013-01-31 | New Hampshire Transmission Upgrades Project | Transmission Notification from Northeast Utilities Service Company (“NU”) to build a new 6 mile 115-kV transmission line between the Scobie Pond and Huse Road Substations in parallel to the existing I158 Line. Install two 115-kV circuit breakers at the Huse Rd Substation and one circuit breaker at the Scobie Pond Substation. | 2016-12-01 | Approved | 2013-03-07
NU-12-T50 | 2013-01-31 | New Hampshire Transmission Upgrades Project | Transmission Notification from Northeast Utilities Service Company (“NU”) to eliminate terminal equipment and conductor clearance limitations on the 18 mile 115-kV Deerfield to Garvins G146 line. | 2016-12-01 | Approved | 2013-03-07
NU-12-T51 | 2013-01-31 | New Hampshire Transmission Upgrades Project | Transmission Notification from Northeast Utilities Service Company (“NU”) to eliminate terminal equipment and conductor clearance limitations on the 12 mile 115-kV Merrimack to Oak Hill P145 line. | 2016-12-01 | Approved | 2013-03-07
NU-12-T52 | 2013-01-31 | New Hampshire Transmission Upgrades Project | Transmission Notification from Northeast Utilities Service Company (“NU”) to rebuild the existing 15 mile 115-kV Deerfield to Pine Hill D118 line. | 2016-12-01 | Approved | 2013-03-07
NU-12-T53 | 2013-01-31 | New Hampshire Transmission Upgrades Project | Transmission Notification from Northeast Utilities Service Company (“NU”) to rebuild the existing 3 mile 115-kV Merrimack to Garvins H137 line. | 2016-12-01 | Approved | 2013-03-07
NU-12-T54 | 2013-01-31 | New Hampshire Transmission Upgrades Project | Transmission Notification from Northeast Utilities Service Company (“NU” to eliminate terminal equipment and conductor clearance limitations on the existing 115-kV Greggs-Rimmon-Eddy J114 line. | 2016-12-01 | Approved | 2013-03-07
NU-12-T55 | 2013-01-31 | New Hampshire Transmission Upgrades Project | Transmission Notification from Northeast Utilities Service Company (“NU”) to tap the existing 115-kV Garvins-Webster V182 line into the Oak Hill Substation and build a new six 115-kV circuit breaker substation in a “breaker & half” configuration. | 2016-12-01 | Approved | 2013-03-07
NU-12-T56 | 2013-01-31 | New Hampshire Transmission Upgrades Project | Transmission Notification from Northeast Utilities Service Company (“NU”) to relocate the existing two 36.7 MVAR 115-kV capacitor banks from Bus 2, installing one bank on Bus 1 and the other bank on Bus 3 at the Merrimack Substation. Replace the existing Q171 circuit breaker at the Merrimack Substation. | 2016-12-01 | Approved | 2013-03-07
NU-12-T57 | 2013-01-31 | New Hampshire Transmission Upgrades Project | Transmission Notification from Northeast Utilities Service Company (“NU”) to rebuild the existing 5 mile 115-kV Eagle – Bridge Street – Power Street K165 Line. | 2016-12-01 | Approved | 2013-03-07
NU-12-T58 | 2013-01-31 | New Hampshire Transmission Upgrades Project | Transmission Notification from Northeast Utilities Service Company (“NU”) to build a new 13 mile 115-kV transmission line between the Madbury and Portsmouth Substations. Install one 115-kV circuit breaker at both the Madbury and Portsmouth Substations. | 2016-12-01 | Approved | 2013-03-07
NU-12-T59 | 2013-01-31 | New Hampshire Transmission Upgrades Project | Transmission Notification from Northeast Utilities Service Company (“NU”) to build a new 6 mile 115-kV transmission line between the Scobie Pond and Chester Substations. Build a new five 115-kV circuit breaker substation in a “breaker & half” configuration at the Chester Substation and install one 115-kV circuit breaker at the Scobie Pond Substation. Proposed | 2016-12-01 | Approved | 2013-03-07
NU-12-T60 | 2013-01-31 | New Hampshire Transmission Upgrades Project | Transmission Notification from Northeast Utilities Service Company (“NU”) to install six 13.3 MVAR capacitor banks and two 115-kV circuit breakers at the Schiller Substation. Install a new 115-kV circuit breaker in series with the existing BT10 circuit breaker. Relocate the existing 115-kV Schiller – Portsmouth Z156 line from Bus A to Bus B | 2016-12-01 | Approved | 2013-03-07
NU-12-T61 | 2013-01-31 | New Hampshire Transmission Upgrades Project | Transmission Notification from Northeast Utilities Service Company (“NU”) to eliminate terminal equipment and conductor clearance limitations on the 19 mile 115-kV Chester to Great Bay H141 line. | 2016-12-01 | Approved | 2013-03-07
NU-12-T62 | 2013-01-31 | New Hampshire Transmission Upgrades Project | Transmission Notification from Northeast Utilities Service Company (“NU”) to eliminate terminal equipment and conductor clearance limitations on the 11 mile portion of the 115-kV Scobie Pond to Kingston Tap R193 line. | 2016-12-01 | Approved | 2013-03-07
NU-12-T63 | 2013-01-31 | New Hampshire Transmission Upgrades Project | Transmission Notification from Northeast Utilities Service Company (“NU”) to install a new 115-kV circuit breaker in series with the R1690 circuit breaker at the Three Rivers Switching Station. | 2016-12-01 | Approved | 2013-03-07
NU-12-T64 | 2013-01-31 | New Hampshire Transmission Upgrades Project | Transmission Notification from Northeast Utilities Service Company (“NU”) to build a new 2 mile 115-kV transmission line between the Fitzwilliam and Monadnock Substations. Install two 115-kV circuit breakers at the Fitzwilliam Substation and one 115-kV circuit breaker at the Monadnock Substation. | 2016-12-01 | Approved | 2013-03-07
NU-12-T65 | 2013-01-31 | New Hampshire Transmission Upgrades Project | Transmission Notification from Northeast Utilities Service Company (“NU”) to install two 345-kV 26.6 MVAR capacitor banks and one 345-kV circuit breaker at the Amherst Substation. | 2016-12-01 | Approved | 2013-03-07
NU-12-T66 | 2013-01-31 | New Hampshire Transmission Upgrades Project | Transmission Notification from Northeast Utilities Service Company (“NU”) to eliminate terminal equipment and conductor clearance limitations on the 11 mile 115-kV Keene to Monadnock T198 line. | 2016-12-01 | Approved | 2013-03-07
NU-12-T67 | 2013-01-31 | New Hampshire Transmission Upgrades Project | Transmission Notification from Northeast Utilities Service Company (“NU”) to install two 115-kV 13.3 MVAR capacitor banks and one 115-kV circuit breaker at the Weare Substation. | 2016-12-01 | Approved | 2013-03-07
NU-12-T68 | 2013-01-31 | New Hampshire Transmission Upgrades Project | Transmission Notification from Northeast Utilities Service Company (“NU”) to rebuild the existing 13 mile 115-kV Chestnut Hill to Westport to Swanzey A152 Line. | 2016-12-01 | Approved | 2013-03-07
NU-12-T69 | 2013-01-31 | New Hampshire Transmission Upgrades Project | Transmission Notification from Northeast Utilities Service Company (“NU”) to rebuild the existing 1 mile 115-kV Chestnut Hill to NH/VT border N186 Line. | 2016-12-01 | Approved | 2013-03-07
NU-12-X02 | 2013-01-31 | New Hampshire Transmission Upgrades Project | Transmission Notification from Northeast Utilities Service Company (“NU”) to retire the Saco Valley Under Voltage Load Shedding (UVLS) scheme. | 2016-12-01 | Approved | 2013-03-07
NU-12-X03 | 2013-01-31 | New Hampshire Transmission Upgrades Project | Transmission Notification from Northeast Utilities Service Company (“NU”) to retire the Beebe River Under Voltage Load Shedding (UVLS) scheme. | 2016-12-01 | Approved | 2013-03-07
NU-13-T02 | 2013-01-31 | New Hampshire Transmission Upgrades Project | Transmission Notification from Northeast Utilities Service Company (“NU”) to upgrade the Power Street Substation in Hudson, NH to NPCC BPS standards. | 2016-12-01 | Approved | 2013-03-07
NEP-12-T19 | 2013-01-31 | New Hampshire Transmission Upgrades Project | Transmission Notification from New England Power Company (“NEP”) to reconductor the 345 kV 326 line section between Sandy Pond in Ayer, MA and MA/NH state border with 2-1113 ACSR. Replace five (5) 345 kV 2000A disconnects with 3000A disconnects | 2016-12-01 | Approved Withdrawn | 3/7/2013 1/13/2015
NEP-12-T20 | 2013-01-31 | New Hampshire Transmission Upgrades Project | Transmission Notification from New England Power Company (“NEP”) to build a new 0.2-mile 230 kV C-203 tap line into the Littleton Substation (NU). | 2016-12-01 | Approved | 2013-03-07
NEP-13-T01 | 2013-01-02 | Shrewsbury Centech Substation Project | Transmission Notification from New England Power Company (“NEP”) on behalf of Shrewsbury Electric and Cable Operations (“SELCO”) for the construction of a new 115/13.8 kV substation to be named “Centech” supplied via a loop of the NEP Line E-157 which will contain an inline circuit breaker to sectionalize the existing E-157 line into E-157W (Millbury – Centech) and E-157 (Centech – E Main St), with one transformer on each resulting line. (The third section of E-157 from E Main St to Northboro Rd will be renamed E-157E as part of a separate, previously processed application). | 2014-06-01 | Approved | 2013-03-07
SELCO-13-T01 | 2013-01-02 | Shrewsbury Centech Substation Project | Transmission Notification from Shrewsbury Electric and Cable Operations (“SELCO”) for the construction of a new 115/13.8 kV distribution substation with its 115 kV In-line breaker as a looped interconnection into the existing NGRID circuit E-157 which NGRID will split with one segment terminating at the Millbury Substation being designated as 157W, and the segment terminating at the N. Main Street Substation will retain the prior E-157 designation. | 2014-06-01 | Approved | 2013-03-07
NU-13-T02 | 2013-02-04 | Doubling Carver Breaker 862 Project | Transmission Notification from NSTAR Electric and Gas Company (“NSTAR”) for the installation of a circuit breaker in series with the Carver 345 kV circuit breaker #862 at the Carver 345 kV Substation. | 2013-12-01 | Notification | 2013-03-07
NEP-11-T07-Rev.1 | 2013-01-22 | Reconductor S-145/T-147 Line Project | Transmission Notification revision from New England Power Company (“NEP”) for the reconductor S-145/T-146 115 kV transmission lines from Tewksbury #22 Substation to North Reading Tap. | 2014-06-01 | Notification | 2013-03-07
NU-12-T23 | 2012-11-30 | New Hampshire Transmission Upgrades Project | Transmission Notification from Northeast Utilities Service Company (“NU”) to eliminate the conductor clearance limitations on the 18 mile 345 kV overhead line from Scobie Pond to Lawrence Road NH/MA border. | 2016-12-01 | Approved | 2013-03-07
NU-12-T44 | 2012-11-30 | New Hampshire Transmission Upgrades Project | Transmission Notification from Northeast Utilities Service Company (“NU”) to install a 2nd 230/115 kV autotransformer at the Littleton Substation. Tap the existing National Grid 230-kV Comerford- Moore C203 line into the Littleton Substation. Build a new 1/2 mile 230-kV transmission line between the C203 tap point and the Littleton Substation and connect it to the new 230/115-kV autotransformer. Install a 230-kV circuit switcher and two 115-kV circuit breakers at Littleton Substation. | 2016-12-01 | Approved | 2013-03-07
NU-12-T45 | 2012-11-30 | New Hampshire Transmission Upgrades Project | Transmission Notification from Northeast Utilities Service Company (“NU”) to install two +25/-12.5 MVAR 115-kV dynamic devices and two 115-kV circuit breaker at the Saco Valley Substation. Two 115/13.8-kV transformers will also be installed to accommodate the dynamic devices. | 2016-12-01 | Approved | 2013-03-07
NU-12-T46 | 2012-11-30 | New Hampshire Transmission Upgrades Project | Transmission Notification from Northeast Utilities Service Company (“NU”) to install four 26.6 MVAR 115-kV capacitor banks and two 115-kV circuit breakers at the Webster Substation. | 2016-12-01 | Approved | 2013-03-07
NU-12-T47 | 2012-11-30 | New Hampshire Transmission Upgrades Project | Transmission Notification from Northeast Utilities Service Company (“NU”) to tap the existing 345-kV Scobie Pond to Amherst 380 line and build a new three circuit breaker 345-kV ring bus. Install a single 345/115-kV autotransformer at the Eagle Substation. Install four 115-kV circuit breakers and four 26.6 MVAR capacitor banks at the Eagle Substation. | 2016-12-01 | Approved | 2013-03-07
NU-12-T48 | 2012-11-30 | New Hampshire Transmission Upgrades Project | Transmission Notification from Northeast Utilities Service Company (“NU”) to install a new 345-kV series circuit breaker next to the existing 802 circuit breaker for the 380E line at the Scobie Pond Substation. | 2016-12-01 | Approved | 2013-03-07
NU-12-T49 | 2012-11-30 | New Hampshire Transmission Upgrades Project | Transmission Notification from Northeast Utilities Service Company (“NU”) to build a new 6 mile 115-kV transmission line between the Scobie Pond and Huse Road Substations in parallel to the existing I158 Line. Install two 115-kV circuit breakers at the Huse Rd Substation and one circuit breaker at the Scobie Pond Substation. | 2016-12-01 | Approved | 2013-03-07
NU-12-T50 | 2012-11-30 | New Hampshire Transmission Upgrades Project | Transmission Notification from Northeast Utilities Service Company (“NU”) to eliminate terminal equipment and conductor clearance limitations on the 18 mile 115-kV Deerfield to Garvins G146 line. | 2016-12-01 | Approved | 2013-03-07
NU-12-T51 | 2012-11-30 | New Hampshire Transmission Upgrades Project | Transmission Notification from Northeast Utilities Service Company (“NU”) to eliminate terminal equipment and conductor clearance limitations on the 12 mile 115-kV Merrimack to Oak Hill P145 line. | 2016-12-01 | Approved | 2013-03-07
NU-12-T52 | 2012-11-30 | New Hampshire Transmission Upgrades Project | Transmission Notification from Northeast Utilities Service Company (“NU”) to rebuild the existing 15 mile 115-kV Deerfield to Pine Hill D118 line. | 2016-12-01 | Approved | 2013-03-07
NU-12-T53 | 2012-11-30 | New Hampshire Transmission Upgrades Project | Transmission Notification from Northeast Utilities Service Company (“NU”) to rebuild the existing 3 mile 115-kV Merrimack to Garvins H137 line | 2016-12-01 | Approved | 2013-03-07
NU-12-T54 | 2012-11-30 | New Hampshire Transmission Upgrades Project | Transmission Notification from Northeast Utilities Service Company (“NU”) to eliminate terminal equipment and conductor clearance limitations on the existing 115-kV Greggs-Rimmon-Eddy J114 line. | 2016-12-01 | Approved | 2013-03-07
NU-12-T55 | 2012-11-30 | New Hampshire Transmission Upgrades Project | Transmission Notification from Northeast Utilities Service Company (“NU”) to tap the existing 115-kV Garvins-Webster V182 line into the Oak Hill Substation and build a new six 115-kV circuit breaker substation in a “breaker & half” configuration. | 2016-12-01 | Approved | 2013-03-07
NU-12-T56 | 2012-11-30 | New Hampshire Transmission Upgrades Project | Transmission Notification from Northeast Utilities Service Company (“NU”) to relocate the existing two 36.7 MVAR 115-kV capacitor banks from Bus 2, installing one bank on Bus 1 and the other bank on Bus 3 at the Merrimack Substation. Replace the existing Q171 circuit breaker at the Merrimack Substation. | 2016-12-01 | Approved | 2013-03-07
NU-12-T57 | 2012-11-30 | New Hampshire Transmission Upgrades Project | Transmission Notification from Northeast Utilities Service Company (“NU”) to rebuild the existing 5 mile 115-kV Eagle – Bridge Street – Power Street K165 Line. | 2016-12-01 | Approved | 2013-03-07
NU-12-T58 | 2012-11-30 | New Hampshire Transmission Upgrades Project | Transmission Notification from Northeast Utilities Service Company (“NU”) to build a new 13 mile 115-kV transmission line between the Madbury and Portsmouth Substations. Install one 115-kV circuit breaker at both the Madbury and Portsmouth Substations | 2016-12-01 | Approved | 2013-03-07
NU-12-T59 | 2012-11-30 | New Hampshire Transmission Upgrades Project | Transmission Notification from Northeast Utilities Service Company (“NU”) to build a new 6 mile 115-kV transmission line between the Scobie Pond and Chester Substations. Build a new five 115-kV circuit breaker substation in a “breaker & half” configuration at the Chester Substation and install one 115-kV circuit breaker at the Scobie Pond Substation. | 2016-12-01 | Approved | 2013-03-07
NU-12-T60 | 2012-11-30 | New Hampshire Transmission Upgrades Project | Transmission Notification from Northeast Utilities Service Company (“NU”) to install six 13.3 MVAR capacitor banks and two 115-kV circuit breakers at the Schiller Substation. Install a new 115-kV circuit breaker in series with the existing BT10 circuit breaker. Relocate the existing 115-kV Schiller – Portsmouth Z156 line from Bus A to Bus B. | 2016-12-01 | Approved | 2013-03-07
NU-12-T61 | 2012-11-30 | New Hampshire Transmission Upgrades Project | Transmission Notification from Northeast Utilities Service Company (“NU”) to eliminate terminal equipment and conductor clearance limitations on the 19 mile 115-kV Chester to Great Bay H141 line. | 2016-12-01 | Approved | 2013-03-07
NU-12-T62 | 2012-11-30 | New Hampshire Transmission Upgrades Project | Transmission Notification from Northeast Utilities Service Company (“NU”) to eliminate terminal equipment and conductor clearance limitations on the 11 mile portion of the 115-kV Scobie Pond to Kingston Tap R193 line. | 2016-12-01 | Approved | 2013-03-07
NU-12-T63 | 2012-11-30 | New Hampshire Transmission Upgrades Project | Transmission Notification from Northeast Utilities Service Company (“NU”) to install a new 115-kV circuit breaker in series with the R1690 circuit breaker at the Three Rivers Switching Station. | 2016-12-01 | Approved | 2013-03-07
NU-12-T64 | 2012-11-30 | New Hampshire Transmission Upgrades Project | Transmission Notification from Northeast Utilities Service Company (“NU”) to build a new 2 mile 115-kV transmission line between the Fitzwilliam and Monadnock Substations. Install two 115-kV circuit breakers at the Fitzwilliam Substation and one 115-kV circuit breaker at the Monadnock Substation. | 2016-12-01 | Approved | 2013-03-07
NU-12-T65 | 2012-11-30 | New Hampshire Transmission Upgrades Project | Transmission Notification from Northeast Utilities Service Company (“NU”) to install two 345-kV 26.6 MVAR capacitor banks and one 345-kV circuit breaker at the Amherst Substation. | 2016-12-01 | Approved | 2013-03-07
NU-12-T66 | 2012-11-30 | New Hampshire Transmission Upgrades Project | Transmission Notification from Northeast Utilities Service Company (“NU”) to eliminate terminal equipment and conductor clearance limitations on the 11 mile 115-kV Keene to Monadnock T198 line. | 2016-12-01 | Approved | 2013-03-07
NU-12-T67 | 2012-11-30 | New Hampshire Transmission Upgrades Project | Transmission Notification from Northeast Utilities Service Company (“NU”) to install two 115-kV 13.3 MVAR capacitor banks and one 115-kV circuit breaker at the Weare Substation. | 2016-12-01 | Approved | 2013-03-07
NU-12-T68 | 2012-11-30 | New Hampshire Transmission Upgrades Project | Transmission Notification from Northeast Utilities Service Company (“NU”) to rebuild the existing 13 mile 115-kV Chestnut Hill to Westport to Swanzey A152 Line. | 2016-12-01 | Approved | 2013-03-07
NU-12-T69 | 2012-11-30 | New Hampshire Transmission Upgrades Project | Transmission Notification from Northeast Utilities Service Company (“NU”) to rebuild the existing 1 mile 115-kV Chestnut Hill to NH/VT border N186 Line. | 2016-12-01 | Approved | 2013-03-07
NU-12-X02 | 2012-11-30 | New Hampshire Transmission Upgrades Project | Transmission Notification from Northeast Utilities Service Company (“NU”) to retire the Saco Valley Under Voltage Load Shedding (UVLS) scheme. | 2016-12-01 | Approved | 2013-03-07
NU-12-X03 | 2012-11-30 | New Hampshire Transmission Upgrades Project | Transmission Notification from Northeast Utilities Service Company (“NU”) to retire the Beebe River Under Voltage Load Shedding (UVLS) scheme. | 2016-12-01 | Approved | 2013-03-07
NEP-12-T19 | 2012-11-30 | New Hampshire Transmission Upgrades Project | Transmission Notification from New England Power Company (“NEP”) to reconductor the 345 kV 326 line section between Sandy Pond in Ayer, MA and MA/NH state border with 2-1113 ACSR. Replace five (5) 345 kV 2000A disconnects with 3000A disconnectsat the Sandy Pond Substation. | 2016-12-01 | Approved | 2013-03-07
NEP-12-T20 | 2012-11-30 | New Hampshire Transmission Upgrades Project | Transmission Notification from New England Power Company (“NEP”) to build a new 0.2-mile 230 kV C-203 tap line into the Littleton Substation (NU). | 2016-06-15 | Approved | 2013-03-07
NU-13-G01 | 2013-01-04 | UMass/Dartmouth Gas Turbine Project | Generator Notification from Northeast Utilities Service Company (“NU”) for the construction of a 2.015 MW gas turbine synchronous generator in Dartmouth, MA and interconnecting at the 13.2 kV distribution level to NSTAR #531 13.2 kV feeder out of the Cross Road Substation #651 and under N-1 conditions for loss of that feeder, after actuation of an autothrowover scheme, to the #525 feeder out of Fisher Road Substation #657. | 2013-01-15 | Notification | 2013-01-18
NU-12-T42 | 2012-11-28 | 1990 Line Structure Replacement Project | Transmission Notification from Northeast Utilities Service Company (“NU”) for the 20 mile overhead modifications to the 1990 line relaying from Frost Bridge 115 kV Substation in Watertown, CT to Baldwin 115 kV in Waterbury, CT and Stevenson 115 kV Substation in Monroe, CT in order to account for the proposed conductor changes. OPGW fiber will be added between all 3 terminals, the backup relay scheme will be changed to line current differential and the relay settings will be changed. | 2014-12-01 | Approved | 2013-01-18
NU-12-G03 | 2012-12-03 | Antrim Wind Generator and Transmission Project | Generator Notification from Northeast Utilities Service Company (“NU”) on behalf of Antrim Wind Energy, LLC for the construction of eleven 3 MW wind turbine generators (33 MWs total) located in Antrim, NH | 2013-12-01 | Approved Withdrawn | 1/18/2013 8/15/2013
NU-12-T43 | 2012-12-03 | Antrim Wind Generator and Transmission Project | Transmission Notification from Northeast Utilities Service Company (“NU”) on behalf of Antrim Wind Energy, LLC for the construction of a new 115-kV switching station in Antrim, New Hampshire in a ring bus configuration consisting of three 115-kV circuit breakers, associated breaker disconnects, control house, and protection and controls. Split 115 kV Line L163 (between Jackman and Keene Substations) into the new switching station to establish new lines from Jackman Substation to the new Tuttle Hill Switching Station (Line X104, approximate length of 6.5 miles) and from Keene Substation to the new Tuttle Hill Switching Station (Line L163, approximate length of 19.4 miles). | 2013-12-01 | Approved Withdrawn | 1/18/2013 8/15/2013
NEP-12-T15 | 2012-12-05 | Highland Drive Substation Project | Transmission Notification from New England Power Company (“NEP”) for the construction of a new Highland Drive 115/13.8kV substation with a single (1) breaker and two (2) 115/13.8kV, 33/44/55 MVA transformers in Cumberland, RI. Loop the new substation into the J16 line by constructing two new 115kV taps each 0.045 miles in length. Reconductor approximately 2.24 miles of the J16 overhead line between Riverside and the new Highland Drive substation. Upgrade the relaying for the J16 at Riverside substation and J16 at Staples substation. | 2014-06-01 | Approved | 2013-01-18
NEP-12-T16 | 2012-12-05 | Highland Drive Substation Project | Transmission Notification from New England Power Company (“NEP”) for the upgrade of the 344 and 333 oil circuit breakers to SF6 insulated breakers, aluminum bus conductor and all associated equipment for the V-148S circuit at Robinson Ave. Reconductor the V-148S overhead conductor (approximately 0.02 miles) between the bus and the V-148 tap. | 2014-06-01 | Approved | 2013-01-18
NEP-12-G04 | 2012-11-29 | Little Rest Road Solar Project | Generator Notification from New England Power Company (“NEP”) on behalf of Mass PV3 LLC for the construction of eighteen 0.5 solar arrays (9 MWs total) located in Warren, MA and interconnecting to the 516L4 13.2 kV feeder out of the Little Rest Road Substation | 2012-12-01 | Approved | 2013-01-18
NU-12-G06 | 2012-12-03 | Timbertop Wind Project | Generator Notification from Northeast Utilities Service Company (“NU”) on behalf of Timbertop Wind I, LLC for construction and interconnection of seven 2.3 MW wind turbine generators (16.1 MWs net output) located in New Ipswich and Temple Township, NH and interconnecting via a 8.5 mile overhead 34.5 feeder at the project bus on the PSNH 3235 Line and terminating at the Monadnock 34.5 kV Substation | 2014-10-01 | Approved Withdrawn | 1/18/2013 8/15/2013
CPN-12-G01 | 2012-12-04 | Westbrook Energy Center Uprate Project | Generator Notification from Calpine Corporation (“CPN”) for a 10 MW uprate at the Westbrook Energy Center turbine generator from 528 MWs to 538 MWs (net output). | 2012-10-20 | Approved | 2013-01-18
UI-12-T01-Rev.1 | 2012-12-06 | 8300 Line Reconfiguration Project | Transmission Notification from United Illuminating Company (“UI”) for the reconfiguration of the overhead 115 kV lines, Quinnipiac – Grand Avenue 8300 and Mill River - Grand Avenue 9550 will not be terminated at the Grand Avenue 115 kV Switching Station as proposed in Figure 1: 8300 Line Reconfiguration Project - Grand Avenue Switching Station Configuration as proposed in UI-12-T01. Instead, due to physical construction reasons, the 8300 and 9505 115 kV lines will have their terminations at Grand Avenue Switching Station swapped. | 2012-11-28 | Notification | 2013-01-18
UI-12-T02-Rev.1 | 2012-12-06 | 8300 Line Reconfiguration Project | Transmission Notification from United Illuminating Company (“UI”) for the reconfiguration the overhead 115 kV lines, Quinnipiac – Grand Avenue8300 and Mill River - Grand Avenue 9550 will not be terminated at the Grand Avenue 115 kV Switching Station as proposed in Figure 1: 8300 Line Reconfiguration Project –Grand Avenue Switching Station Configuration as proposed in UI-12-T02. Instead, due to physical construction reasons, the 8300 and 9505 115 kV lines will have their terminations at Grand Avenue Switching Station swapped. | 2012-11-28 | Notification | 2013-01-18
UI-12-T03-Rev.1 | 2012-12-06 | 8300 Line Reconfiguration Project | Transmission Notification from United Illuminating Company (“UI”) for the reconfiguration the overhead 115 kV lines, Quinnipiac – Grand Avenue 8300 and Mill River - Grand Avenue 9550 will not be terminated at the Grand Avenue 115 kV Switching Station as proposed in Figure 1: 8300 Line Reconfiguration Project –Grand Avenue Switching Station Configuration as proposed in UI-12-T03. Instead, due to physical construction reasons, the 8300 and 9505 115 kV lines will have their terminations at Grand Avenue Switching Station swapped. | 2012-11-28 | Notification | 2013-01-18
NEP-12-GNF08 | 2012-11-29 | Westford Solar Project | Generator Notification from New England Power Company (“NEP”) for the construction of four (4) photovoltaic generator units, rated with a total of 4 MW, is proposed to be interconnected into National Grid’s 23 kV distribution system through 23 kV Feeder #2387 in Chelmsford, MA. National Grid’s 23 kV Feeder #2387 is supplied from National Grid North Chelmsford No. 2 Substation located in Chelmsford, MA. The generator will export onto the 23kV distribution system. | 2012-04-05 | Notification | 2013-01-18
NEP-12-GNF13 | 2012-11-13 | 433 Purchase Solar Project | Purchase Solar NG, LLC (NuGen capital Management LLC) for the construction and interconnection of a photovoltaic generating facility, rated 2.5 MW, to National Grid’s distribution system by a single phase lateral off the 19W73 feeder. The 19W73 feeder is a 13.8 kV, 3 phase, 4 wire multi grounded wye circuit supplied by the Dighton substation located in Dighton, MA. | 2012-11-17 | Notification | 2013-01-18
NEP-12-GNF14 | 2012-11-19 | South Barre Solar Project | Generator Notification from New England Power Company (“NEP”) on behalf of South Barre Solar LLC for the construction and interconnection of a 1.6 MW photovoltaic generating facility at a ‘greenfield’ stand-alone site at 750 South Barre Rd (Rt 32), Barre, MA. The area where the generator is situated is supplied by the 13.2kV 604W3 feeder from the nearby Barre substation approximately 1,600 circuit feet away. | 2012-11-29 | Notification | 2013-01-18
NEP-12-GNF15 | 2012-11-19 | EPG Solar Project | Generator Notification from New England Power Company (“NEP”) on behalf of EPG Solar LLC for the construction and interconnection of a 3 MW PV generation system located near 236 Blackmer Road Southbridge MA. The proposed area for the PV system is served by National Grid’s 13.2kV three-phase, grounded radial feeder 413L3 from Snow Street Substation. | 2012-12-06 | Notification | 2013-01-18
NEP-12-GNF16 | 2012-11-29 | Equity Industrial Wind Project | Generator Notification from New England Power Company (“NEP”) on behalf of Equity Industrial Turbines LLC for the construction and interconnection of two wind turbine generator units each rated at 2 MW for a total of 4 MW to National Grid’s 23 kV subtransmission system onto the Company’s #2364 feeder out of the Gloucester Substation. | 2012-12-18 | Notification | 2013-01-18
NEP-12-GNF11 | 2012-12-05 | Constellation Solar Project | Generator Notification from New England Power Company (“NEP”) on behalf of Constellation Energy for the construction and interconnection of a 2 MW solar array in Uxbridge, MA and customer fed through two 1000 KVA transformers fed by Feeder 321W2 out of the Uxbridge Substation #321 | 2012-08-06 | Notification | 2013-01-18
NEP-12-GNF17 | 2012-12-05 | Wind Energy Development Wind Turbine Project | Generator Notification from New England Power Company (“NEP”) on behalf of Wind Energy Development for construction and interconnection of a 1.5 MW wind turbine generator located in North Kingstown, RI and customer fed through NGRID’s 12.47 KV feeder out of the Lafayette Substation #30. | 2012-11-26 | Notification | 2013-01-18
NU-12-G04 | 2012-12-03 | Ludlow Landfill Solar Project | Generator Notification from Northeast Utilities Service Company (“NU”) for the construction of four 0.5 MW solar arrays (2 MWs total) located in Ludlow, MA and interconnecting to the Orchard 27A 115 kV Substation via WMECO 27A5 distribution circuit. | 2013-03-01 | Notification | 2013-01-18
NU-12-G05 | 2012-12-03 | NextAmp Capital Solar Project | Generator Notification from Northeast Utilities Service Company (“NU”) for the construction of a 2MW solar array located in Whately, MA and interconnecting to the Podick 18G 115 kV Substation via the WMECO 18G8 13.8 distribution circuit. | 2013-05-01 | Notification | 2013-01-18
NSTAR-12-G15 | 2012-12-06 | No Fossil Fuel II Solar Project | Generator Notification from NSTAR Electric and Gas Company (“NSTAR”) for the construction of a 4.56 MW solar array located in Dartmouth, MA and interconnecting to the Fisher Road Substation #657 13.2 kV circuit #525. | 2012-12-01 | Notification | 2013-01-18
BHE-08-T08-Rev.1 | 2012-12-05 | Line 66 Rerate Revision Project | Transmission Notification revision from Bangor Hydro Electric Company (“BHE”) to rerate the 25 mile overhead 115 kV Line 66 between Rebel Hill Switching Station and the Deblois Switching Station due to an impedance change created by a conductor replacement. | 2013-12-01 | Notification | 2013-01-18
NEP-12-T13 | 2012-10-26 | Pittsfield/Greenfield Area Upgrade Project | Transmission notification from New England Power Company (“NEP”) at the Harriman Substation to install a 115 kV tie breaker and reconductor both 115 kV main busses. Upgrade the 115 kV terminal equipment for E-131 circuit and replace five 115 kV breakers at the substation due to asset condition. Also construct a new 115 kV control house in the 115 kV yard and migrate the 115 kV controls and protection from the existing power house to the new control house. | 2017-06-01 | Approved | 2012-12-07
NEP-12-T14 | 2012-10-26 | Pittsfield/Greenfield Area Upgrade Project | Transmission notification from New England Power Company (“NEP”) to Reconductor the A-127 115 kV line with 2-477 ACCR between the new substation in Erving, MA and Montague Tap. Swap the existing tap to Montague from B-128 Line to the A-127 Line. Reconductor A-127 Tap to Montague with 1590 ACSS. Separate the A-127 and Y-177 lines (existing Double Circuit Tower structures) between Montague and Montague Tap onto independent single circuit structures. | 2017-06-01 | Approved | 2012-12-07
NU-12-T29 | 2012-10-26 | Pittsfield/Greenfield Area Upgrade Project | Transmission notification from Northeast Utilities Service Company (“NU”) for the installation of a 14.4 MVAR 115 kV capacitor bank and 115 kV circuit breaker at the Podick 18G substation located in Amherst, MA | 2016-06-01 | Approved | 2012-12-07
NU-12-T30 | 2012-10-26 | Pittsfield/Greenfield Area Upgrade Project | Transmission notification from Northeast Utilities Service Company (“NU”) for the installation of a 14.4 MVAR 115 kV capacitor bank and 115 kV circuit breaker at the Amherst 17K substation located in Amherst, MA | 2016-06-01 | Approved | 2012-12-07
NU-12-T31 | 2012-10-26 | Pittsfield/Greenfield Area Upgrade Project | Transmission notification from Northeast Utilities Service Company (“NU”) for the installation of a 14.4 MVAR 115 kV capacitor bank and 115 kV circuit breaker at the Cumberland 22B substation located in Greenfield, MA. | 2016-06-01 | Approved | 2012-12-07
NU-12-T32 | 2012-10-26 | Pittsfield/Greenfield Area Upgrade Project | Transmission notification from Northeast Utilities Service Company (“NU”) for the expansion of the Northfield Mountain 16R substation into a breaker-and-a-half arrangement. The 345-kV 6T circuit breaker will be added to complete the existing partial breaker-and-a-half bay, and four additional 345-kV circuit breakers will be installed to form two new bays (one on the east side of the substation and one on the west side). A 345/115-kV autotransformer rated 632/730/862 MVA (normal/LTE/STE) will be installed with a new 115-kV circuit breaker on the low-side. Lines 354, 312 and 381 will be re-terminated into different bay positions. The five new 345-kV circuit breakers will have a nameplate rating of 3000 A and an interrupting capability of 50 kA. The new 115-kV circuit breaker will have a nameplate rating of 4000 A and an interrupting capability of at least 40 kA. | 2016-06-01 | Approved | 2012-12-07
NU-12-T33 | 2012-10-26 | Pittsfield/Greenfield Area Upgrade Project | Transmission notification from Northeast Utilities Service Company (“NU”) for the construction of a new 115-kV station name Erving 38F Switching Station located in Erving, MA, in a ring bus configuration consisting of three (3) 115-kV circuit breakers with a nameplate rating of 3000A and a short-circuit interrupting capability of at least 40 kA. Loop the existing A127 line into the new Erving switching station. | 2016-06-01 | Approved | 2012-12-07
NU-12-T34 | 2012-10-26 | Pittsfield/Greenfield Area Upgrade Project | Transmission notification from Northeast Utilities Service Company (“NU”) for the construction of a new 115-kV line 1604 from Northfield Mountain Substation to the new Erving Switching Station located in Erving, MA.. | 2016-06-01 | Approved | 2012-12-07
NU-12-T35 (Revision available) | 2012-10-26 | Pittsfield/Greenfield Area Upgrade Project | Transmission notification from Northeast Utilities Service Company (“NU”) to rebuild the 1361 line from Montague 21C substation to Cumberland 22B substation on separate single-circuit structures. | 2016-06-01 | Approved | 2012-12-07
NU-12-T36 | 2012-10-26 | Pittsfield/Greenfield Area Upgrade Project | Transmission notification from Northeast Utilities Service Company (“NU”) to disconnect the Montague 5T circuit breaker for line Y177 from the 11T/4T position and reconnect it into the 3T/4T position via a 115-kV underground cable. Install a 115-kV 40 kA circuit switcher on the high side of distribution transformer 3X. Provide high speed primary protection for the A127W line (Harriman-Montague-Erving). | 2016-06-01 | Approved | 2012-12-07
NU-12-T37 | 2012-10-26 | Pittsfield/Greenfield Area Upgrade Project | Transmission notification from Northeast Utilities Service Company (“NU”) to remove the sag limitation on the 1512 line from Blandford 19J substation to Granville Junction. | 2016-06-01 | Approved | 2012-12-07
NU-12-T38 | 2012-10-26 | Pittsfield/Greenfield Area Upgrade Project | Transmission notification from Northeast Utilities Service Company (“NU”) to remove the sag limitation on the 1421 line from Pleasant 16B substation to Blandford 19J substation. | 2016-06-01 | Approved | 2012-12-07
NU-12-T39 | 2012-10-26 | Pittsfield/Greenfield Area Upgrade Project | Transmission notification from Northeast Utilities Service Company (“NU”) to reconductor the 1371 line from Woodland 17G substation to Pleasant 16B substation. | 2016-06-01 | Approved Withdrawn | 12/7/2012 1/7/2016
NU-12-T41 | 2012-10-26 | Pittsfield/Greenfield Area Upgrade Project | Transmission notification from Northeast Utilities Service Company (“NU”) to upgrade the thermal rating of the 345 kV Line 381 from the MA/NH border to NH/VT border. The upgrade will result in summer thermal ratings of at least 1358/1626/1760 MVA (normal/LTE/STE). The upgrade is to be achieved by increasing the maximum allowable conductor temperature to 140°C, which involves replacing connectors and raising structures | 2016-06-01 | Approved | 2012-12-07
NU-12-T27 | 2012-10-25 | South Norwalk Substation Project | Transmission notification from Northeast Utility Service Company (“NU”) to split the 1890E Line from South Norwalk 115 kV Substation to the Sherwood 115 kV Substation and the 1890W Line from South Norwalk 115 kV Substation to the Ely Avenue 115 kV Junction as required to interconnect the CTMEEC South Norwalk 115/13.8 kV Substation Project (CTMEEC-11-T01). | 2013-06-01 | Approved | 2012-12-07
CTMEEC-11-T01 CTMEEC-11-T01-Rev.1 | 12/22/2011 10/25/2012 | South Norwalk Substation Project | CTMEEC-11-T01-Rev.1 – Transmission Notification from Connecticut Transmission Municipal Electric Energy Cooperative (“CTMEEC”) on behalf of South Norwalk Electric and Water District for the construction of a new 115/13.8-kV substation located in South Norwalk, CT and NU will interconnect the project to the existing 115-kV system via the 1890 line between CL&P’s Sherwood Substation and the Ely Avenue Tap. | 2013-06-01 | Approved | 1/17/2012 12/7/2012
TERM-12-G01 | 2012-10-16 | Wallingford Capacity Increase Project | Generator notification from Twin Eagle Resource Management (“TERM”) for a 2.7 MW increase in the capacity rating for each of the Wallingford 1-5 gas generators (13.5 MW net increase) located in Wallingford, CT. | 2012-12-31 | Approved | 2012-12-07
NSTAR-12-T16 | 2012-10-16 | 107 Line Reconductor Project | Transmission notification from NSTAR Electric and Gas Company (“NSTAR”) to Reconductor 5.2 miles of overhead 115 kV transmission Line 107 from 4/0 ACSR conductor to 795 kcmil ACSS 54/7 Condor conductor and rebuild/replace ~ 35 wood H- Frame tangent structures, increasing height as necessary for adequate ground clearance and rebuild/replace ~ 11 wood angle or Dead-End structures with three-pole steel structures. | 2013-12-31 | Notification | 2012-12-07
NSTAR-12-T14 | 2012-10-15 | Baker Street/Newton Oil Line and Substation Upgrade Project | Transmission notification from NSTAR Electric and Gas Company (“NSTAR”) for the addition of a dielectric fluid (“oil”) circulation underground pipe for the Baker Street – Newton 292-522 and 292-523 115kV cables with heat exchangers at both Baker St and Newton Highlands substations; At Newton Highland Substation- Install two new 115kV breakers to complete the 115kV ring bus and replace the existing 115/14kV transformers 110A, 110B and 110C with three new 117/15.12kV 37/50/62.5 MVA transformers (75 MVA LTE) | 2013-12-31 | Notification | 2012-12-07
NSTAR-12-T17 | 2012-11-02 | Line 115 Upgrade Project | Transmission notification from NSTAR Electric and Gas Company (“NSTAR”) to upgrade 3.7 miles of existing 115 kV Line #115 from Oak Street area to Barnstable 115 kV substation. to 1113 ACSS conductor resulting in a new LTE rating of 448 MVA. The upgrade is required to mitigate an overload of the Line #115 section following the loss of the 122/120 DCT lines. This upgrade will allow the de-activation of the Barnstable SPS in 2013 following the completion of the Long Term Lower SEMA project. | 2013-12-31 | Notification | 2012-12-07
NSTAR-12-G16 | 2012-11-05 | No Fossil Fuel Solar Project | Generator notification from NSTAR Electric and Gas Company (“NSTAR”) on behalf of No Fossil Fuel for the installation of a 3.04 MW solar array in Marshfield, MA and interconnecting at the 23 kV distribution level to the #21 23 kV feeder out of the NSTAR Marshfield Substation #739 | 2012-11-01 | Notification | 2012-12-07
NSTAR-12-T18 | 2012-10-23 | Hyannis Junction Substation Transformer Project | Transmission notification from NSTAR Electric and Gas Company (“NSTAR”) for the installation of a 3rd 30/40/50 MVA transformer bank at Hyannis Junction, with two 115kV ABB Pass MO circuit breakers with an auto-throw-over scheme. It is further proposed to eliminate the capacity constraint on the #123 line by reconductoring one-mile of 4/0 ACSR with 795 ACSS conductor. | 2014-06-30 | Notification | 2012-12-07
NSTAR-12-T19 | 2012-10-23 | Putnam Station #831 Bus Improvement Project | Transmission notification from NSTAR Electric and Gas Company (“NSTAR”) for replacement of 115 kV load break switch LBS6A at Putnam Station #831 with a normally closed breaker and the swapping the bus positions between the 831-540 line and transformer 110B. | 2013-05-31 | Notification | 2012-12-07
NSTAR-12-T13 | 2012-11-08 | Crystal Springs Substation Transformer Replacement Project | Transmission notification from NSTAR Electric and Gas Company (“NSTAR”) for replacement of an existing 12/16/20 MVA 115/13.2kV bulk distribution transformer with a larger spare 24/32/40 MVA 117/14.4kV bank at Crystal Spring Substation #646. The transformer replacement is required to resolve all facilities in (N-0) capacity | 2012-12-31 | Notification | 2012-12-07
NEP-07-T26 Rev.1 | 2012-10-25 | Adams Substation Project | Transmission notification revision from New England Power Company (“NEP”) for the installation of two new 115 kV, 3000 A, 40 kA breakers to complete the 4-breaker ring bus configuration at the Adams substation. Relocate the E-131 and Q-117 115 kV line terminations at Adams. Swap the positions of the 115/69 kV autotransformer T3 and the 115/23 kV transformer T4. | 2014-12-31 | Notification | 2012-12-07
NEP-12-GNF12 | 2012-10-08 | Varian Semiconductor Wind Project | Generator notification from New England Power Company (“NEP”) on behalf of Varian Semiconductor Equipment Associates for the construction of a 2.5 MW wind turbine generator located in Gloucester, MA and interconnecting to the NGRID 23 kV Feeder #2364 supplied from Gloucester #24 substation. |  | Notification | 2012-12-07
VELCO-12-T09 | 2012-10-31 | Bennington Line Change Project | Transmission notification from Vermont Electric Company (“VELCO”) to increase the transmission length of the overhead 115 kV K4 Line from Bennington to Adams by approximately one mile (19.51 miles total length). Project is associated with the Bennington Substation relocation (VELCO-10-T06). | 2013-10-31 | Notification | 2012-12-07
VELCO-12-T10 | 2012-10-31 | Bennington Line Change Project | Transmission notification from Vermont Electric Company (“VELCO”) to increase the transmission length of the overhead 115 kV K6 Line from Bennington to Hoosick by approximately one half mile (27.76 miles total length). Project is associated with the Bennington Substation relocation (VELCO-10-T06). | 2013-10-31 | Notification | 2012-12-07
VELCO-12-T11 | 2012-10-31 | Bennington Line Change Project | Transmission notification from Vermont Electric Company (“VELCO”) to reduce the transmission length of the overhead 115 kV Y25 Line from Bennington to Deerfield by approximately one mile (10.19 miles total length). Project is associated with the Bennington Substation relocation (VELCO-10-T06). | 2013-10-31 | Notification | 2012-12-07
NU-12-T40 | 2012-10-25 | East Devon Substation Circuit Breaker Project | Transmission notification from Northeast Utilities Service Company (“NU”) for the installation of a 345 kV circuit breaker at the East Devon 345 kV substation located in Milford, CT. | 2014-06-01 | Notification | 2012-12-07
NU-12-G02 | 2012-10-17 | Hatfield Solar Project | Generator notification from Northeast Utilities Service Company (“NU”) on behalf of Western Massachusetts Electric Company for the construction of four 0.50 MW solar array (2.0 MWs new output) located in Hatfield, MA and interconnecting to the Podick 18G 115 kV substation via the WMECO 18G6 13.8 kV distribution circuit. | 2012-12-01 | Notification | 2012-12-07
NU-12-X01 | 2012-10-04 | Merrimack AVR Replacement Project | Transmission notification from Northeast Utilities Service Company (“NU”) to retrofit the existing Automatic Voltage Regulators (AVR) at the Merrimack Generating Station CT1 and CT2 with identical Basler DECS-200 digital excitation controllers. | 2012-11-01 | Approved | 2012-11-08
UI-12-T21 | 2012-10-04 | 2015-12-01 | Transmission notification from United Illuminating Company (“UI”) for the control house rebuild at the Pequonnock 115 kV Substation to allow for relay upgrades and the addition of a one cycle protection clearing time delay. | 2015-12-01 | Approved Withdrawn | 11/8/12 9/25/2014
UI-12-T14 | 2012-10-04 | 115 kV Phase Angle Regulator Removal and Mix Avenue Series Reactor Addition Project | Transmission notification from United Illuminating Company (“UI”) for the Sacket 115 kV Phase Angle Regulator (PAR) removal from the Sackett 115 kV Substation in North Haven, CT. | 2015-12-01 | Approved | 2012-11-08
UI-12-T15 | 2012-10-04 | 115 kV Phase Angle Regulator Removal and Mix Avenue Series Reactor Addition Project | Transmission notification from United Illuminating Company (“UI”) for the Mix Avenue 115 kV Series Reactor Addition located at the Mix Avenue 115 kV Substation in Hamden, CT | 2015-12-01 | Approved | 2012-11-08
NEP-12-T06 | 2012-10-04 | Shun Pike Substation Project | Transmission notification from New England Power Company (“NEP”) on behalf of Narragansett Electric Company for the construction of a new Shun Pike Substation that will tap the T-172S line to supply local area load requirements with one dedicated 12/16/20 MVA-rated 115/13.2 kV transformer, and use a 40 kA-rated circuit switcher for transformer protection. In addition, Shun Pike substation will be built to enable future expansion for two115/12.47 kV transformers and an in-line 115 kV circuit breaker. | 2013-12-01 | Approved | 2012-11-08
NEP-12-T07 | 2012-10-04 | Wamesit Substation Project | Transmission notification from New England Power Company (“NEP”) for the construction of a new Wamesit Substation #20 with two 115/13.2 kV 33/44/55 MVA transformers on existing National Grid owned land in Tewksbury, build 115 kV tap lines to the K-137E and J-162 lines and install SCADA-capable, in-line disconnect switches, one on each line, for sectionalizing the 115 kV lines. Primary protection for all transmission line elements, including the tap lines, will be the circuit breakers at remote substations. Circuit switchers rated for 40 kA will be used for local transformer protection. | 2016-12-01 | Approved | 2012-11-08
VELCO-12-T05 | 2012-10-03 | Ascutney Line Change Project | Transmission Notification from Vermont Electric Company (“VELCO”) to increase the length of the overhead 115 kV K15 Line from Ascutney to Windsor by one mile increasing total line length to 7.93 miles. Project is associated with the Ascutney Substation Relocation project. | 2013-03-01 | Notification | 2012-11-08
VELCO-12-T06 | 2012-10-03 | Ascutney Line Change Project | Transmission Notification from Vermont Electric Company (“VELCO”) to increase the length of the overhead 115 kV K31 Line from Ascutney to Coolidge by one mile increasing total line length to 13.92 miles. Project is associated with the Ascutney Substation Relocation project. | 2013-03-01 | Notification | 2012-11-08
VELCO-12-T07 | 2012-10-03 | Ascutney Line Change Project | Transmission Notification from Vermont Electric Company (“VELCO”) to reduce the length of the overhead tap into the 115 kV K149 Line from Bellows Falls to Slayton Hill by one mile reducing total line length to 38.39 miles. Project is associated with the Ascutney Substation Relocation project. | 2013-03-01 | Notification | 2012-11-08
VELCO-12-T08 | 2012-10-03 | Ascutney Line Change Project | Transmission Notification from Vermont Electric Company (“VELCO”) to reduce the length of the overhead tap into the 115 kV K174 Line from Ascutney to Webster by one mile reducing total line length to 17.18 miles. Project is associated with the Ascutney Substation Relocation project. | 2013-03-01 | Notification | 2012-11-08
NSTAR-12-G14 | 2012-10-03 | Farmview Estates Solar Project | Generator notification from NSTAR Electric and Gas Company (“NSTAR”) for the installation of a 3.5 MW solar array in Sandwich, MA. Generator will interconnect at the 23 kV distribution level to the #443 distribution circuit and the #81B 23 kV feeder out of the NSATR Sandwich Substation # 916. | 2012-11-30 | Notification | 2012-11-08
NSTAR-12-G12 | 2012-10-03 | Tisbury Landfill Solar Project | Generator notification from NSTAR Electric and Gas Company (“NSTAR”) for the installation of a 1.083 MW solar array in Tisbury, MA. Generator will interconnect at the 23 kV distribution level to the #228 distribution circuit and the #97 23 kV feeder out of the NSTAR Falmouth Substation # 933. | 2013-06-01 | Notification | 2012-11-08
NEP-12-T12 | 2012-10-04 | Line L-164 Derate Project | Transmission notification from New England Power Company (“NEP”) To de-rate the 115 kV L-164 Line sections at the East Dracut Tap (Tewksbury Jct. to East Dracut – 1.9 miles overhead) and North Dracut Tap (East Dracut to North Dracut- 3.8 miles overhead). | 2012-11-05 | Notification | 2012-11-08
VELCO-12-T04 | 2012-09-07 | Bennington 115 kV Capacitor Addition Project | Transmission notification from Vermont Electric Company (“VELCO”) for the installation of two 12.5 MVAR capacitor banks at the Bennington 115 kV Substation located in Bennington, VT. | 2013-10-01 | Approved | 2012-10-09
UI-12-T16 | 2012-08-29 | Bridgeport/New Haven Area Voltage Upgrade Project | Transmission Notification from United Illuminating Company (“UI”) for the installation of two 20 MVAR 115 kV capacitor banks at the Mix Avenue 115 kV Substation located in Hamden, CT. | 2015-12-01 | Approved | 2012-10-05
UI-12-T17 | 2012-08-29 | Bridgeport/New Haven Area Voltage Upgrade Project | Transmission Notification from United Illuminating Company (“UI”) for the installation of a 42 MVAR 115 kV capacitor bank at the Grand Avenue 115 kV Substation located in New Haven, CT. | 2015-12-01 | Approved Withdrawn | 10/5/2012 3/6/2014
UI-12-T18 | 2012-08-29 | Bridgeport/New Haven Area Voltage Upgrade Project | Transmission Notification from United Illuminating Company (“UI”) for the removal of a 42 MVAR 115 kV capacitor bank at the Sackett 115 kV Substation in North Haven, CT. | 2015-12-01 | Approved | 2012-10-05
UI-12-T19 | 2012-08-29 | Bridgeport/New Haven Area Voltage Upgrade Project | Transmission Notification from United Illuminating Company (“UI”) for the installation of a 20 MVAR 115 kV capacitor bank at the Sackett 115 kV Substation in North Haven, CT. | 2015-12-01 | Approved Withdrawn | 10/5/2012 3/6/2014
UI-12-T20 | 2012-08-29 | Bridgeport/New Haven Area Voltage Upgrade Project | Transmission Notification from United Illuminating Company (“UI”) for the installation of two 30 MVAR 115 kV capacitor banks at the Hawthorne115 kV Substation located in Fairfield, CT. | 2015-12-01 | Approved | 2012-10-05
BRP-12-G02 | 2012-09-06 | Granite Reliable Wind Control System Revision Project | Generation Notification from Brookfield Renewable Energy Group (“BRP”) on behalf of Granite Reliable Power, LLC for the change in unit leading MVAr capability from 0.0 MVAr to -0.301 MVAr for each of the 33 Granite Reliable Wind Park turbines located in Coos County, NH. in order to improve unit performance and minimize voltage stability concerns. | 2012-12-01 | Approved | 2012-10-09
BRP-12-X01 | 2012-09-06 | Granite Reliable Wind Control System Revision Project | Transmission Notification from Brookfield Renewable Energy Group (“BRP”) on behalf of Granite Reliable Power, LLC for the addition of a Power Plant Controller (PPC) to allow the reactive output of the Granite Reliable Wind Farm to respond and control voltage by varying real and reactive power output, frequency and voltage for each of the wind turbine generators. | 2012-12-01 | Approved | 2012-10-09
NU-12-T28 | 2012-09-07 | Memorial Drive 115 kV Cable Project | Transmission Notification from Northeast Utilities Service Company (“NU”) on behalf of Chicopee Electric Light Department for the installation of a 0.08 mile underground cable for a section of each of the two circuits (1638 and 1904) to Memorial Drive substation to avoid crossing overhead lines 1702, 1803 and 1601. | 2013-12-01 | Approved | 2012-10-09
CEL-12-T01 | 2012-09-07 | Memorial Drive 115 kV Cable Project | Transmission Notification from Chicopee Electric Light (“CEL”) for the construction of a new Chicopee Memorial Drive 115/13.8 kV Substation fed from a loop of planned 115 kV Line No. 1904 (Piper to new Fairmont Substation) and the construction of 0.75 mile of overhead 115kV line for a section of each of the two circuits (1638 and 1904). | 2013-12-01 | Approved | 2012-10-09
NSTAR-12-G09 | 2012-09-05 | Harwich Landfill Solar Project | Generator Notification from NSTAR Electric and Gas Company (“NSTAR”) on behalf of American Capital Energy Inc. for the installation of two 2 MW solar arrays (4.0 MWs net output) located in Harwich, MA and interconnecting to the NSTAR Harwich Substation #968, 23 kV feeder #89A. | 2013-06-01 | Notifcation | 2012-10-09
NSTAR-12-G10 | 2012-09-05 | Chatham Landfill Solar Project | Generator Notification from NSTAR Electric and Gas Company (“NSTAR”) on behalf of American Capital Energy Inc. for the installation of a 1.5 MW solar array located in Chatham, MA and interconnecting to the NSTAR 23 kV distribution circuit #606, fed by #95B 23 kV distribution supply feeder from Orleans Substation #975. | 2013-06-01 | Notifcation | 2012-10-09
NSTAR-12-G11 | 2012-09-05 | Katama Farm Solar Project | Generator Notification from NSTAR Electric and Gas Company (“NSTAR”) on behalf of American Capital Energy Inc. for the installation of a 1.083 MW solar array located in Edgartown, MA and interconnecting to the NSTAR Falmouth Substation #933, 23 kV distribution supply feeder #97 | 2013-06-01 | Notifcation | 2012-10-09
NSTAR-12-T10 | 2012-09-05 | Mashpee Substation Transformer Replacement Project | Transmission Notification from NSTAR Electric and Gas Company (“NSTAR”) for the replacement of the existing 20/26/33 MVA 115/23 kV distribution transformer with a new 30/40/50 MVA transformer at the Mashpee Substation #946 located in Mashpee, MA. | 2013-06-01 | Notifcation | 2012-10-09
NEP-12-G09 | 2012-07-26 | East Brookfield Solar Project | Generator notification from New England Power Company (“NEP”) for the installation of twelve 0.5 MW photovoltaic generators (6.0 MWs net output) and installation of a 69/13.2 kV, 7.5 MVA transformer and switchgear interconnecting to the photovoltaic plant located in East Brookfield, MA. | 2012-12-01 | Approved | 2012-08-27
NEP-12-T09 | 2012-07-26 | East Brookfield Solar Project | Transmission notification from New England Power Company for the construction and interconnection of a new substation with a 69 kV, 2000A, 31.5 kA breaker and two 2000 A load break switches located in East Brookfield, MA. Also construct a new 69 kV tap line connecting the substation to the 69 kV E-5 transmission line and interconnect the substation to the East Brookfield photovoltaic plant. | 2012-12-01 | Approved | 2012-08-27
NEP-12-T05 | 2012-07-25 | Kilvert Street Substation Transformer Installation Project | Transmission notification from New England Power Company (“NEP”) for the installation of a new 115/12.47 kV 33/44/55 MVA transformer at the Kilvert Street Substation located in Warwick, RI. Also install a new circuit switcher inside the substation for T1 protection and a new load break disconnect switch on J-188 Line, to sectionalize the radial line during outages. | 2014-12-01 | Notification | 2012-08-27
NEP-12-T10 | 2012-07-25 | Reconductor L-164 115 kV Line Project | Transmission notification from New England Power Company (“NEP) for the reconductoring of Line L-164 from Tewksbury Junction to West Andover, MA to relieve potential line loading under contingency conditions. | 2012-12-31 | Notification | 2012-08-27
UI-12-T05 | 2012-07-11 | New Haven/Bridgeport Area Thermal Upgrades Project | Transmission notification from United Illuminating Company (“UI”) for the Reconductor/Rebuild of the 2.4 mile overhead 8809A 115 kV Line from the Baird 115 kV Substation in Stratford, CT to the Congress 115 kV Substation in Bridgeport, CT. | 2015-12-01 | Notification | 2012-08-27
UI-12-T06 | 2012-07-11 | New Haven/Bridgeport Area Thermal Upgrades Project | Transmission notification from United Illuminating Company (“UI”) for the Reconductor/Rebuild of the 2.4 mile overhead 8909B 115 kV Line from the Baird 115 kV Substation in Stratford, CT to the Congress 115 kV Substation in Bridgeport, CT. | 2015-12-01 | Notification | 2012-08-27
UI-12-T07 | 2012-07-11 | New Haven/Bridgeport Area Thermal Upgrades Project | Transmission notification from United Illuminating Company (“UI”) for the Baird 115 kV A & B Bus Upgrade at the Baird 115 kV Substation in Stratford, CT. | 2015-12-01 | Notification | 2012-08-27
UI-12-T08 | 2012-07-11 | New Haven/Bridgeport Area Thermal Upgrades Project | Transmission notification from United Illuminating Company (“UI”) for the Reconductor/Rebuild of the 2.9 mile overhead 1610-2 115 kV Line from Glen Lake junction 115 kV in Woodbridge, CT to the Mix Avenue 115 kV Substation in Hamden, CT. | 2015-12-01 | Notification Withdrawn | 2012-08-27
UI-12-T09 | 2012-07-11 | New Haven/Bridgeport Area Thermal Upgrades Project | Transmission notification from United Illuminating Company (“UI”) for the upgrade of the 1685 and 1610 115 kV relaying at the June Street 115 kV substation in Woodbridge, CT. | 2015-12-01 | Notification | 2012-08-27
UI-12-T10 | 2012-07-11 | New Haven/Bridgeport Area Thermal Upgrades Project | Transmission notification from United Illuminating Company (“UI”) for the upgrade of the 1630-3 115 kV relaying at the North Haven 115 kV substation in North Haven, CT. | 2015-12-01 | Notification | 2012-08-27
UI-12-T11 | 2012-07-11 | New Haven/Bridgeport Area Thermal Upgrades Project | Transmission notification from United Illuminating Company (“UI”) for the Reconductor/Rebuild of the 1.67 mile overhead 1630-3 115 kV Line from the North Haven 115 kV substation in North Haven, CT to the Walrec 115 kV substation in Wallingford, CT | 2015-12-01 | Notification Withdrawn | 8/27/2012 3/6/2014
UI-12-T12 | 2012-07-11 | New Haven/Bridgeport Area Thermal Upgrades Project | Transmission notification from United Illuminating Company (“UI”) for the Reconductor/Rebuild of the 1.4 mile overhead 88005A 115 kV Line from the Milvon 115 kV substation in Milford, CT to the Devon Tie 115 kV Switching Station in Milford, CT. | 2015-12-01 | Notification | 2012-08-27
UI-12-T13 | 2012-07-11 | New Haven/Bridgeport Area Thermal Upgrades Project | Transmission notification from United Illuminating Company (“UI”) for the Reconductor/Rebuild of the 1.4 mile overhead 89005B 115 kV Line from the Milvon 115 kV substation in Milford, CT to the Devon Tie 115 kV Switching Station in Milford, CT. | 2015-12-01 | Notification | 2012-08-27
BRP-12-G01 | 2012-07-03 | Granite Reliable Wind Farm Revisions | Generator notification from Brookfield Renewable Power Inc. (“BRP”) to revise the limit of the leading MVar capability of the Granite Reliable Wind Farm for each turbine from 0.0875 MVar to 0.0 MVar for an overall reduction of 28.9 MVar change to the generating resource. The 99 MW Granite Reliable Wind farm is interconnected to the PSNH Coos 115 kV transmission loop located in Drummer, NH | 2012-07-20 | Approved | 7/252012
NSTAR-12-T06 | 2012-06-04 | Hartwell 115 kV Shunt Capacitor Installation Project | Transmission notification from NSTAR Electric and Gas Company (“NSTAR”) for the installation of a new 115 kV, 36.7 MVAR shunt capacitor at Hartwell Substation. The new capacitor bank is needed to support sagging transmission voltages in the Burlington - Hartwell load area for contingencies that result in the loss of 115 kV line 533-508 between Lexington and Hartwell. The main project components consist of the 115 kV, 36.7 MVAR mobile capacitor and a 115 kV circuit breaker with a Synchronous Switching Controller. | 2012-11-01 | Approved | 2012-08-06
BHE-12-G01 | 2012-05-29 | Pisgah Wind Farm Generation and Transmission Project | Generation notification from Bangor Hydro Electric Company (“BHE”) for the construction of five 1.815 MW wind turbine generators (9.075 MWs net) on Pisgah Mountain, Clifton, ME and interconnecting via the BHE 115 kV Line 66 as a tap. | 2013-07-01 | Approved | 2012-08-06
BHE-12-T04 | 2012-05-29 | Pisgah Wind Farm Generation and Transmission Project | Transmission notification from Bangor Hydro Electric Company (“BHE”) To interconnect the Pisgah Wind Farm via a 0.04 mile overhead tap to Line 66 to the Pisgah collector substation high side breaker. | 2013-09-01 | Approved | 2012-08-06
NSTAR-12-G07 | 2012-07-06 | Canton Landfill Solar Project | Generator Notification from NSTAR Electric and Gas Company (“NSTAR”) for the construction of three 1 MW (3 MWs net) solar generators interconnecting to the Canton Station #470, Transformer 110A via distribution circuit 470-H4 located in Canton, MA | 2012-07-18 | Notification | 2012-08-06
NSTAR-12-G08 | 2012-07-06 | Canton Landfill Solar Project | Generator Notification from NSTAR Electric and Gas Company (“NSTAR”) for the construction of two 1 MW (2 MWs net) solar generators interconnecting to the Canton Station #470, Transformer 110C via distribution circuit 470-H8 located in Canton, MA. | 2012-07-18 | Notification | 2012-08-06
MMWEC-12-G03 | 2012-06-14 | Ipswich Wind II Project | Generator notification from Massachusetts Municipal Wholesale Electric Company (“MMWEC”) for the construction of a 2.0 MW wind turbine generator located in Ipswich, MA and interconnecting to the Fowlers Lane Substation #5 supplied from the High Street Substation #4 supplied by a 23 kV Line 2372 or Line 2394 feed from the National Grid 115 kV King Street Substation in Groveland, MA. | 2012-09-30 | Notification | 2012-08-06
FPLE-12-G01 | 2012-07-05 | Skelton Hydro Capacity Increase Project | Generator notification from FPL Maine Hydro (“FPLE”) for 2.4 MW capacity increase to the Skelton Hydro generating station (Asset #569) by replacement of the two generator turbines, control switchgear, and station service wiring. The units will be interconnected to the CMP Louden Substation 34.5 kV bus in York County, ME through a 34.5 kV generator lead. | 8/12/2013 12/26/2013 | Notification | 2012-08-06
FW-12-G02 | 2012-06-18 | Oakfield Wind Farm and Transmission Project | Generator notification from First Wind (“FW”) on behalf of Evergreen Wind Power II, LLC for construction of forty eight 3.075 MW wind turbine generators (147.6 MWs Net) located in Oakfield, ME. And interconnecting to the BHE Keene Road 345 kV Substation. | 2014-08-31 | Approved | 2012-07-17
FW-12-T02 | 2012-06-18 | Oakfield Wind Farm and Transmission Project | Transmission notification from First Wind (“FW”) on behalf of Evergreen Wind Power II, LLC for the construction of a Oakfield collector substation, Keene Rd 115/345kV new autotransformer , 59 mile overhead 115 kV transmission line between Keene Rd and the new Oakfield collector substation, two 115 kV 25 MVAR capacitor banks, associated circuit breakers and switchgear, and two 115/34.5 kV under load tap changing transformers located at the collector substation. | 2014-08-31 | Approved | 2012-07-17
BHE-12-T03 | 2012-06-18 | Oakfield Wind Farm and Transmission Project | Transmission notification from Bangor Hydro Electric Company (“BHE”) for bus expansion, protection updates and new 345 kV breaker to accommodate new generator transformer and lead interconnection | 2014-08-31 | Approved | 2012-07-17
NU-12-T25 | 2012-06-04 | South End 115 kV Cable Project | Transmission notification from Northeast Utilities Service Company for the installation of a 1.5 mile underground 115 kV cable from the Glenbrook 115 kV substation to the South End 115 kV substation located in Stamford, CT. | 2014-12-31 | Approved | 2012-07-17
CTMEEC-12-T01 | 2012-06-13 | Fitch Street Substation Project | Transmission notification from Connecticut Transmission Municipal Electric Energy Cooperative (“CTMEEC”) for the construction of a new 115 kV to 27.6 kV Substation on behalf of Third Taxing District (TTD) Electric Department. The substation will be energized via the CL&P 1416 Line between Compo and Darien 115 kV Substations. The new substation will include two 115/27.6 kV transformers along with protective devices and systems. | 2013-12-31 | Approved | 2012-07-17
NU-12-T26 | 2012-06-13 | Fitch Street Substation Project | Transmission notification from Northeast Utilities Service Company (“NU”) modification to the exiting 115-kV 1416 line between CL&P’s Darien and Compo Substations. The modification is in support of the Connecticut Transmission Municipal Electric Energy Cooperative (dba TRANSCO), proposed installation of a new 115/27.6 kV substation that TRANSCO is proposing on behalf of the Third Taxing District (TTD) in Norwalk, CT. | 2013-12-31 | Approved | 2012-07-17
MMED-03-T01-Rev.1 | 2012-06-05 | East Mansfield Substation and Transformer Project Revision 1 | Transmission Notification from Mansfield Municipal Electric Department (“MMED”) for the construction of a new 115/13.8 kV substation located in Mansfield, MA. The station was to consist of one 115/13.8 kV, 24/32/40 MVA transformer. The substation transformer was to be connected to the 115 kV system via a circuit switcher to a single circuit extension of Line E1. The design has been modified to incorporate two 115/13.8 kV, 24/32/40 MVA transformers. Also the single phase line extension to the East Mansfield substation from Easton Station #92 is now labeled as the A24 Line. | 2012-07-01 | Notification | 2012-07-17
NSTAR-12-T09 | 2012-05-21 | Reconductor 211-508 115 kV Line Project | Transmission notification from NSTAR Electric and Gas Company (“NSTAR”) for the reconductoring of the 211-508 115 kV Line from Woburn to Burlington. | 2013-01-31 | Notification | 2012-07-17
VELCO-12-T03 | 2012-05-30 | Vernon Road Breaker Addition Project | Transmission notification from Vermont Electric Company (“VELCO”) on behalf of Central Vermont Public Service for the installation of three new 115 kV circuit breakers at the Vernon Road Substation | 2013-06-01 | Notification | 2012-07-17
NSTAR-12-T08 | 2012-06-04 | West Medway Breaker Addition | Transmission notification from NSTAR Electric and Gas Company (“NSTAR”) for the addition of a new 345 kV 63 kA IC 3000 amp breaker in series with the existing 345 kV breaker #106 at West Medway. |  | Notification | 2012-07-17
VELCO-12-G01 | 2012-04-18 | Grandpa’s Knob Wind Farm and Transmission Project | Generator notification from Vermont Electric Power Company (“VELCO”) on behalf of Grandpa’s Knob Windpark, LLC,for construction of twenty 2.5 MW Nordex N100 wind turbine generators (50 MWs Net) located in West Rutland, VT and interconnecting to the West Rutland 115 kV Substation.. | 2013-12-31 | Approved Withdrawn | 5/29/2012 5/23/2014
VELCO-12-T01 | 2012-04-18 | Grandpa’s Knob Wind Farm and Transmission Project | Transmission notification from Vermont Electric Power Company (“VELCO”) for the construction of two miles of overhead 115 kV line from the Grandpa’s Knob wind farm to the West Rutland Substation. | 2013-12-31 | Approved Withdrawn | 5/29/2012 5/23/2014
VELCO-12-T02 | 2012-04-18 | Grandpa’s Knob Wind Farm and Transmission Project | Transmission notification from Vermont Electric Power Company (“VELCO”) for the construction of a new 115 kV substation connecting the Grandpa’s nob wind farm to the 115 kV system via a 115/34.5 kV step up transformer. | 2013-12-31 | Approved Withdrawn | 5/29/2012 5/23/2014
NEP-07-T23 Rev. 1 | 2012-04-25 | A-127W 115 kV Line Reconductor Rev. 1 | Transmission notification from New England Power Company (“NEP”) to reconductor portions of the A-127W line with 477 ACCR conductor (instead of 795 ACSS as in the original application) for 7 miles from Tower 510 to Paxton and 10 miles from Wendell Depot to the Cabot Taps. Additionally, due to the reconductoring on both the A-127W and B-128W lines as described in NEP-11-T01 the proposed swapping of the Cabot/Montague tap from the B-128 Line to the A-127 Line is no longer required, and switch 2713 will be replaced with a 2000A switch rather than being removed from the A-127W line. | 2014-11-01 | Approved | 2012-05-30
MMWEC-12-T01 | 2012-04-10 | Denton-Lovell Substation Project | Transmission Notification from Massachusetts Municipal Wholesale Electric Company (“MMWEC”) to upgrade the Denton-Lovell Substation by replacing the existing 15 kV distribution switchgear with new 15 kV switchgear. Replacement of both power transformers (115 kV/13.8 kV with new units rated at 24/32/40 MVA. Removal of the existing 115 kV bus tie disconnect switches and replacement of the existing circuit switchers with new 115 kV disconnect switches and circuit breakers | 2012-12-01 | Notification | 2012-05-29
MMWEC-12-G01 | 2012-04-10 | Chicopee Citizens Enterprise Solar Project | Generation Notification from Massachusetts Municipal Wholesale Electric Company (“MMWEC”) for the construction of a 2.5 MW solar array generator located in Chicopee, MA. Project will interconnect to the 24B1 Feeder out of Prospect Street Substation. | 2012-05-01 | Notification | 2012-05-30
MMWEC-12-G02 | 2012-04-10 | Shrewsbury-Cherry Street Solar Project | Generation Notification from Massachusetts Municipal Wholesale Electric Company (“MMWEC”) for the construction of a 2.5 MW solar array generator located in Shrewsbury, MA. Project will interconnect to the SELCO Feeder Circuit R13-1 from Rolf Avenue Substation connected to the NGrid P142 Line. | 2012-07-01 | Notification | 2012-05-30
MMED-03-T01-Rev.1 | 2012-05-07 | East Mansfield Substation and Transformer Project Revision 1 | Transmission Notification from Mansfield Municipal Electric Department (“MMED”) for the construction of a new 115/13.8 kV substation located in Mansfield, MA. The station was to consist of one 115/13.8 kV, 24/32/40 MVA transformer. The substation transformer was to be connected to the 115 kV system via a circuit switcher to a single circuit extension of Line E1. The design has been modified to incorporate two 115/13.8 kV, 24/32/40 MVA transformers. Also the single phase line extension to the East Mansfield substation from Easton Station #92 is now labeled as the A24 Line. | 2012-07-01 | Notification | 2012-07-17
NSTAR-12-T05 | 2012-04-25 | Scotia Street Station 115 kV Upgrade Project | Transmission Notification from NSTAR Electric and Gas Company (“NSTAR”) for the installation of three new indoor 115 kV gas insulated circuit breakers at Scotia Street substation #492 in Boston MA. The project is presently under construction due to the need to repair station damage resulting from the Scotia Street station fire that occurred on 3/13/2012. One of the new circuit breakers will replace 115/14 kV transformer 110A circuit switcher CS771. The second new breaker will replace 115 kV switch S791on Brighton Station #329 side of cable 329-512. The third breaker will be added on the Kingston Street Station #514 side of cable 329-512. The Scotia Street 110A transformer protection will be tied into the new 115 kV transformer breaker. The two new circuit breakers on cable 329-512 will initially be used to provide sectionalizing capability and will not be part of 329-512 transmission line protection. A proposed future project will split line 329-512 into two independently relayed lines. The main project component is the Gas Insulated Switchgear consisting of three 115 kV breakers and associated vdisconnects and grounding switches. | 2012-06-01 | Notification | 2012-05-30
NEP-08-T44-Rev-1 | 2012-04-03 | NEEWS Interstate Analysis Project | Transmission notification from New England Power Company (“NEP”) to install a new 341 West Farnum to Connecticut/Rhode Island Border 345 kV Line. PPA | 2015-12-01 | Approved | 2012-05-04
NEP-08-T45-Rev.1 | 2012-04-03 | NEEWS Interstate Analysis Project | Transmission notification from New England Power Company (“NEP”) to install a new 366 Millbury to West Farnum 345 kV Line. | 2015-12-01 | Approved | 2012-05-04
NEP-08-T48-Rev.1 | 2012-04-03 | NEEWS Interstate Analysis Project | Transmission notification from New England Power Company (“NEP”) to expand, reconfigure and upgrade the 345 kV Millbury Substation and upgrade the 1402, 302 and 314 breakers with new 4000A 50 kA breakers. | 2015-12-01 | Approved | 2012-05-04
NEP-12-T01 | 2012-04-03 | NEEWS Interstate Analysis Project | Transmission notification from New England Power Company (“NEP”) to rebuild and reconductor the 345 kV 328 Line from Sherman Road Switching Station in Burrillville, RI to West Farnum Substation in Smithfield, RI. | 2015-12-01 | Approved | 2012-05-04
NEP-12-T02 | 2012-04-03 | NEEWS Interstate Analysis Project | Transmission notification from New England Power Company (“NEP”) to construct a new Sherman Road Air Insulated Substation and replace the existing ring bus with a new two bay breaker and half open air switching station with a double tie breaker in one of the bays, with breakers rated at 4000A continuous and 50kA interrupting capability. This construction is required as Sherman Road requires substantial upgrades due to changes in the thermal loadings, short circuit fault duty duties. | 2015-12-01 | Approved | 2012-05-04
NEP-12-T03 | 2012-04-03 | NEEWS Interstate Analysis Project | Transmission notification from New England Power Company (“NEP”) to upgrade the West Farnum 115 kV Substation and double the 1713 tie breaker and upgrade the 115kV station to comply with current BPS standards. The addition of this new breaker constitutes “significant work” and therefore will require the station be brought to current BPS standards. | 2015-12-01 | Approved | 2012-05-04
NEP-08-T52-Rev-1 | 2012-04-03 | Rhode Island Reliability Projects | Transmission notification from New England Power Company (“NEP”) to expand and reconfigure the 345 kV West Farnum Substation. This includes the expansion required for all three of the new 345 kV lines terminating at the substation. Revision is due to change in final configuration of 345kV station changed to facilitate line crossings and entry points. | 2012-05-20 | Approved | 2012-05-04
NEP-08-T53-Rev-1 | 2012-04-03 | Rhode Island Reliability Projects | Transmission notification from New England Power Company (“NEP”) to install a third 345/115kV auto transformer at Kent County and expand and reconfigure 345/115 kV Substation and build to BPS standards. Transformer nameplate rating 269/358/448 MVA, make new 345 kV breakers 3000A, 50 kA breakers and new 115 kV breakers 3000A, 63 kA breakers. Revision is due to additional 115kV breaker added on 115kV side of existing T3 transformer to mitigate an N-1-1 contingency voltage concern. | 2011-11-20 | Approved | 2012-05-04
NEP-08-T56-Rev-1 | 2012-04-03 | Rhode Island Reliability Projects | Transmission notification from New England Power Company (“NEP”) to upgrade 115 kV Franklin Square terminal equipment. Discussions with breaker manufacturer revealed that by adding breaker capacitors at various locations on the bus work the breaker short circuit capacity would be increased from 40kA to 50 kA instead of the original plan of upgrading the 115 kV Franklin Square terminal equipment (including all 115 kV breakers to 3000A, 63 kA). | 2012-05-20 | Approved | 2012-05-04
NU-08-T11-Rev. 01 | 2012-04-03 | Greater Springfield Reliability Project | Transmission notification from Northeast Utilities Service Company (“NU”) to rebuild the 115-kV Line 1230 from Agawam16C Substation to Piper 21N Substation. Revision is because the conductor is being revised from 1590 kcmil ACSR to 1272 kcmil ACSS based on the new NU standard. The ratings of both conductors are comparable. | 2013-12-01 | Approved | 2012-05-04
NU-08-T12-Rev. 01 | 2012-04-03 | Greater Springfield Reliability Project | Transmission notification from Northeast Utilities Service Company (“NU”) to rebuild the 115-kV Line 1314 from Agawam 16C Substation to Chicopee 18L Substation. Revision is because the conductor is being revised from 1272 kcmil ACSR to 1272 kcmil ACSS based on the new NU standard | 2013-12-01 | Approved | 2012-05-04
NU-08-T13-Rev. 01 | 2012-04-03 | Greater Springfield Reliability Project | Transmission notification from Northeast Utilities Service Company (“NU”) for the 115-kV circuit 1322 from East Springfield 5J Substation to Breckwood 20A Substation to have the existing series reactors bypassed. Revision is the bypass switch will be a circuit switcher. | 2013-12-01 | Approved | 2012-05-04
NU-08-T14-Rev. 01 | 2012-04-03 | Greater Springfield Reliability Project | Transmission notification from Northeast Utilities Service Company (“NU”) to rebuild the 115-kV Line 1426 from Cadwell 50F Switching Station to Orchard 27A Substation. Revision is because the conductor is being revised from 1272 kcmil ACSR to 1272 kcmil ACSS based on the new NU standard | 2013-12-01 | Approved | 2012-05-04
NU-08-T15-Rev. 01 | 2012-04-03 | Greater Springfield Reliability Project | Transmission notification from Northeast Utilities Service Company (“NU”) to reconductor / rebuild the 115-kV Line 1481 from Ludlow19S Substation to Cadwell 50F Switching Station. Revision is because the conductor is being revised from 2x795 kcmil ACSR to 1590 kcmil ACSS to allow existing structures to be used. The two conductor sizes have comparable ratings. | 2013-12-01 | Approved | 2012-05-04
NU-08-T16-Rev. 01 | 2012-04-03 | Greater Springfield Reliability Project | Transmission notification from Northeast Utilities Service Company (“NU”) to reconductor the 115-kV Line 1552 from Ludlow 19S Substation to Orchard 27A Substation. Revision is because the conductor is being revised from 1590 kcmil ACSR to 1272 kcmil ACSS based on the new NU standard. The ratings of both conductors are comparable and the ACSS conductor can be placed on the existing structures. | 2013-12-01 | Approved | 2012-05-04
NU-08-T17-Rev. 01 | 2012-04-03 | Greater Springfield Reliability Project | Transmission notification from Northeast Utilities Service Company (“NU”) to separate the 115-kV three terminal line 1723 (Fairmont-Piper-East Springfield), and rebuild/construct a two terminal line #1904, from Fairmont 16H switching station to Piper 21N substation. Revision is because the conductor is being revised from 1590 kcmil ACSR to 1272 kcmil ACSS based on the new NU standard. The ratings of both conductors are comparable. Also, the line number changed from 1601 to 1904. | 2013-12-01 | Approved | 2012-05-04
NU-08-T18-Rev. 01 | 2012-04-03 | Greater Springfield Reliability Project | Transmission notification from Northeast Utilities Service Company (“NU”) to separate the 115-kV three terminal line 1254 (Fairmont-Chicopee-Shawinigan), and rebuild/construct a two terminal line #1702 from Fairmont 16H switching station to Chicopee 18L substation. Revision is because the conductor is being revised from 1272 kcmil ACSR to 1272 kcmil ACSS based on the new NU standard. Also, the line number changed from 1602 to 1702. | 2013-12-01 | Approved | 2012-05-04
NU-08-T19-Rev. 01 | 2012-04-03 | Greater Springfield Reliability Project | Transmission notification from Northeast Utilities Service Company (“NU”) to separate the 115-kV three terminal line 1723 (Fairmont-Piper-East Springfield), and rebuild/construct a two terminal line #1803 from Fairmont 16H switching station to Cadwell 50F switching station. Revision is because the conductor is being revised from 2x1272 kcmil ACSR to 2x1272 kcmil ACSS based on the new NU standard. The stability requirement for the 2nd high speed protection scheme has been eliminated since both Fairmont and Cadwell switching stations are not BPS facilities. Also, the line number changed from 1603 to1803. | 2013-12-01 | Approved | 2012-05-04
NU-08-T20-Rev.01 | 2012-04-03 | Greater Springfield Reliability Project | Transmission notification from Northeast Utilities Service Company (“NU”) to separate the 115-kV three terminal line 1254 (Fairmont-Chicopee-Shawinigan), and rebuild/construct a two terminal line 1601 from Fairmont 16H switching station to Shawinigan 55E substation. Add a 2nd high-speed protection scheme. Revision is because the conductor is being revised from 2x1590 kcmil ACSR to 2x1272 kcmil ACSS based on the new NU standard. The two conductor sizes have comparable ratings. Also, the line number changed from 1604 to 1601. | 2013-12-01 | Approved | 2012-05-04
NU-08-T21-Rev. 01 | 2012-04-03 | Greater Springfield Reliability Project | Transmission notification from Northeast Utilities Service Company (“NU”) for the Southwick – North Bloomfield 115 kV line 1768 and South Agawam – North Bloomfield double-circuit 115-kV line 1821/1836 to be disconnected at North Bloomfield. Line 1836 will also be disconnected at South Agawam. Lines 1768 and 1821 will be connected (joined) at Granby Junction (approximately 5 miles north of North Bloomfield) to form a new Southwick to South Agawam 115 kV line. The line portion from South Agawam to the CT/MA border will utilize 1272 kcmil ACSS conductor and will be placed on the same structures as the new Agawam to North Bloomfield 345-kV line 3216. The portion from the CT/MA border to Granby Junction will cross bundle the existing circuits 1821/1836. The other portion from Granby Junction to Southwick will utilize the same conductors on the existing structures. Also, the reactors at South Agawam in series with lines 1821 and 1836 will be disconnected and removed. Revision is because based on the new NU standard, the conductor is being revised from 1590 kcmil ACSR to 1272 kcmil ACSS for the line portion from South Agawam to the CT/MA border. The two conductor sizes havecomparable ratings. | 2013-12-01 | Approved | 2012-05-04
NU-08-T22-Rev. 01 | 2012-04-03 | Greater Springfield Reliability Project | Transmission notification from Northeast Utilities Service Company (“NU”) to rebuild the 115-kV line 1781 from Agawam 16C substation to South Agawam 42E substation. Line 1781 will share some transmission structures with the new 345-kV Agawam to North Bloomfield line 3216. Add a 2nd high-speed protection scheme. Revision is because the conductor is being revised from 1272 kcmil ACSR to 1272 kcmil ACSS based on the new NU standard. | 2013-12-01 | Approved | 2012-05-04
NU-08-T23-Rev. 01 | 2012-04-03 | Greater Springfield Reliability Project | Transmission notification from Northeast Utilities Service Company (“NU”) to rebuild the 115-kV line 1782 from Agawam 16C substation to South Agawam 42E substation. Add a 2nd high-speed protection scheme. Revision is because the conductor is being revised from 1272 kcmil ACSR to 1272 kcmil ACSS based on the new NU standard | 2013-12-01 | Approved | 2012-05-04
NU-08-T24-Rev. 01 | 2012-04-03 | Greater Springfield Reliability Project | Transmission notification from Northeast Utilities Service Company (“NU”) to rebuild the 115-kV line 1845 from Ludlow 19S substation to Shawinigan 55E substation. Add a 2nd high-speed protection scheme. Revision is because the conductor is being revised from 2x1272 kcmil ACSR to 2x1272 kcmil ACSS based on the new NU standard. | 2013-12-01 | Approved | 2012-05-04
NU-08-T25-Rev. 01 | 2012-04-03 | Greater Springfield Reliability Project | Transmission notification from Northeast Utilities Service Company (“NU”) to construct a new 345-kV line from Ludlow 19S substation to Agawam 16C substation. Revision is because the conductor is being revised from 2x1590 kcmil ACSR to 2x1590 kcmil ACSS based on the new NU standard. | 2013-12-01 | Approved | 2012-05-04
NU-08-T26-Rev. 01 | 2012-04-03 | Greater Springfield Reliability Project | Transmission notification from Northeast Utilities Service Company (“NU”) to construct a new 345-kV line from Agawam 16C substation to North Bloomfield 2A substation. Revision is because the conductor is being revised from 2x1590 kcmil ACSR to 2x1590 kcmil ACSS based on the new NU standard | 2013-12-01 | Approved | 2012-05-04
NU-08-T27-Rev. 01 | 2012-04-03 | Greater Springfield Reliability Project | Transmission notification from Northeast Utilities Service Company (“NU”) to establish a 0.44 mile 115-kV line 1556 between the East Springfield 5J substation and the new Cadwell 50F switching station, utilizing the existing 1723 line section between these two substations on the ROW. Install a 1250A, 3% (on 100 MVA base) reactor in series with the new 1556 line. Revision is because of the need to install a 1250A, 3% (on 100 MVA base) reactor in series with the new 1556 line to resolve short-circuit issues at East Springfield 5J substation. The line number changed from 5001 to 1556. | 2013-12-01 | Approved | 2012-05-04
NU-08-T28-Rev. 01 | 2012-04-03 | Greater Springfield Reliability Project | Transmission notification from Northeast Utilities Service Company (“NU”) to establish a 0.44 mile 115-kV line 1645 between the East Springfield 5J substation and the new Cadwell 50F switching station, utilizing the existing 1481 line section between these two substations on the ROW. Install a 1250A, 3% (on 100 MVA base) reactor in series with the new 1645 line. Revision is because of the need to install a 1250A, 3% (on 100 MVA base) reactor in series with the new 1645 line to resolve short-circuit issues at East Springfield 5J substation. The line number changed from 5002 to 1645. | 2013-12-01 | Approved | 2012-05-04
NU-08-T29-Rev.01 | 2012-04-03 | Greater Springfield Reliability Project | Transmission notification from Northeast Utilities Service Company (“NU”) to expand Ludlow 19S 345-kV substation by adding one complete breaker and a half bay. Replace the existing two 345/115-kV autotransformers with the new standard higher impedance autotransformers (3 single phase units) due to short-circuit issues. Terminate line 3196, and re-terminate lines 3419, 301, and the 3X autotransformer. Replace 115-kV circuit breakers 44T and 46T with breakers having 3000A ratings. Replace bus connected circuit breakers 1X3 and 3X3 with breakers having 4000A ratings. Revision is because two 120 MVAR 345-kV capacitor banks are being eliminated. Four (4) 115-kV circuit breakers are being replaced instead of five. Circuit breakers 44T and 46T will have a nameplate rating of 3000A insteadof 4000A. | 2013-12-01 | Approved | 2012-05-04
NU-08-T30-Rev. 01 | 2012-04-03 | Greater Springfield Reliability Project | Transmission notification from Northeast Utilities Service Company (“NU”) to build a new 345-kV substation at the existing 115-kV Agawam 16C substation site with two breaker and a half bays, and install two 345/115 kV standard autotransformers. Terminate lines 3196 (Agawam to Ludlow) and 3216 (Agawam to North Bloomfield). Add a complete 115-kV breaker and a half bay. Re-terminate line 1781 into a new 115-kV bay position. Replace 115-kV circuit breakers 24T, 25T, and 26T with new breakers having a 4000A nameplate rating and a 63 kA interrupting capability. Replace 115-kV circuit breaker 10K associated with the capacitor banks with a 63 kA breaker. The Agawam 16C Substation 345-kV and 115-kV voltage classes are to be classified as NPCC Bulk Power System (BPS) facilities. Revision is because Agawam Autotransformers #1 and #2 swapped positions | 2013-12-01 | Approved | 2012-05-04
NU-08-T31-Rev. 01 | 2012-04-03 | Greater Springfield Reliability Project | Transmission notification from Northeast Utilities Service Company (“NU”) to construct a new 115-kV station name Cadwell 50F Switching Station located in Springfield, MA, in a ring bus configuration consisting of five (5) 115-kV circuit breakers with a nameplate rating of 3000A and an interrupting capability of 63 kA. Install a 1250A, 3% (on 100 MVA base) reactor in series with each line 1556 and 1645. Revision is because of the need to install a 1250A, 3% (on 100 MVA base) reactor in series with each line 1556 and 1645 to resolve short-circuit issues at East Springfield 5J substation. The Cadwell circuit breaker numbers have changed. | 2013-12-01 | Approved | 2012-05-04
NU-08-T32-Rev. 01 | 2012-04-03 | Greater Springfield Reliability Project | Transmission notification from Northeast Utilities Service Company (“NU”) to build a new Fairmont 16H Switching Station using a breaker and a half arrangement. Install fifteen (15) new 115-kV circuit breakers to form five (5) complete breaker and a half bays. Also add new circuit breaker 20T at the end of the south bus. All new 115-kV circuit breakers will have an interrupting capability of 63 kA. Circuit breakers 13T, 14T, and 15T are to have a 4000 A nameplate rating. All the other circuit breakers will have a nameplate rating of 3000 A. Revision is because a new Fairmont switching station will be built instead of expanding and reconfiguring the existing one. The existing seven (7) circuit breakers are being replaced to minimize outages during construction and for short-circuit considerations. The Fairmont circuit breaker numbers have changed. | 2013-12-01 | Approved | 2012-05-04
NU-08-T33-Rev. 01 | 2012-04-03 | Greater Springfield Reliability Project | Transmission notification from Northeast Utilities Service Company (“NU”) to modify South Agawam 42E Substation to accommodate the newly formed 115-kV line 1768, South Agawam to Southwick. The reactor at South Agawam substation in series with line 1821 will be disconnected. Revision is because the reactor at South Agawam substation in series with line 1821 will be disconnected instead of being bypassed. A typo was also corrected noting that the line portion from South Agawam substation to the CT/MA border will share the same structures as the Agawam (not Ludlow) to North Bloomfield 345-kV line. | 2013-12-01 | Approved | 2012-05-04
NU-08-T39-Rev. 01 | 2012-04-03 | Greater Springfield Reliability Project | Transmission notification from Northeast Utilities Service Company (“NU”) for the Shawinigan 55E Substation, to replace the 115-kV circuit breakers 4T and 6T with new circuit breakers having a 4000 A nameplate rating, and replace circuit breakers 1T and 2T with new circuit breakers having a 3000 A nameplate rating. All the new 115-kV circuit breakers will have an interrupting capability of 63 kA. Revision is because of the need to replace circuit breakers 1T and 2T with new circuit breakers having a 3000 A nameplate rating. | 2013-12-01 | Approved | 2012-05-04
NU-08-T60-Rev. 01 | 2012-04-03 | Greater Springfield Reliability Project | Transmission notification from Northeast Utilities Service Company (“NU”) to build a new Bulk Power System 345-kV transmission substation at the existing 115-kV North Bloomfield 2A Substation site. The New 345-kV substation will have two (2) breakers and a half bays consisting of six (6) 345-kV circuit breakers rated at 3000 A nameplate, 50 kA interrupting capability. Add a second 345/115-kV autotransformer. Terminate the 3216 (Agawam to North Bloomfield) and 3642 (Manchester to North Bloomfield) lines. Disconnect 115-kV lines 1768, 1821, and 1836 from this substation, which opens the 115-kV tie-lines to Massachusetts. Replace 115-kV circuit breakers 10K, 20K and 3X1 with new circuit breakers having an interrupting capability of 63 kA. Revision is because a 3rd 345-kV bay was eliminated (due to CCRP being deferred) and the 345-kV lines and autotransformers are connected into different bay positions. | 2013-12-01 | Approved | 2012-05-04
NU-12-T10 | 2012-04-03 | Greater Springfield Reliability Project | Transmission notification from Northeast Utilities Service Company (“NU”) for the Chicopee 18L Substation, to replace circuit breakers 1T and 2T with new circuit breakers having a nameplate rating of 3000 A and an interrupting capability of 63 kA. Proposed in-service date is December 2013. | 2013-12-01 | Approved | 2012-05-04
NU-12-T11 | 2012-04-03 | Greater Springfield Reliability Project | Transmission notification from Northeast Utilities Service Company (“NU”) to separate the 3-terminal 395 line at Meekville Junction. The existing Barbour Hill portion will remain connected to the Manchester portion and re-numbered as the 3557 line. A new 345-kV line from Manchester to Meekville Junction will be built using 2-1590 kcmil ACSS conductor and connected to the existing line to North Bloomfield to form a new 3642 line. | 2013-12-01 | Approved | 2012-05-04
NU-12-T12 | 2012-04-03 | Greater Springfield Reliability Project | Transmission notification from Northeast Utilities Service Company (“NU”) for the Manchester 345-kV 3A substation to add circuit breaker 24T with a nameplate rating of 3000 A and an interrupting capability of 50 kA. Re-terminate line 3557 (Barbour Hill to Manchester) and terminate line 3642 (North Bloomfield to Manchester). | 2013-12-01 | Approved | 2012-05-04
NU-12-T13 | 2012-04-03 | Greater Springfield Reliability Project | Transmission notification from Northeast Utilities Service Company (“NU”) to reconductor the 1784 line using 1590 kcmil ACSS conductor. Replace the existing series reactor at North Bloomfield 2A substation with a 2% (on 100 MVA base) reactor having ratings that match (or exceed) the new conductor ratings. | 2013-12-01 | Approved | 2012-05-04
NU-12-T14 | 2012-04-03 | Greater Springfield Reliability Project | Transmission notification from Northeast Utilities Service Company (“NU”) to install a 345-kV variable 75-150 MVAR reactor and one 345-kV circuit breaker at the Beseck 9F Substation. | 2013-12-01 | Approved | 2012-05-04
NU-08-T52-Rev. 01 | 2012-04-03 | Interstate Reliability Project | Transmission notification from Northeast Utilities Service Company (“NU”) to construct a new 345-kV transmission line from the Card 11F Substation to the Lake Road 27E Substation. Revision is because the conductor is being revised from 2x1590 kcmil ACSR to 2x1590 kcmil ACSS based on the new NU standard. | 2013-12-01 | Approved | 2012-05-04
NU-08-T54-Rev. 01 | 2012-04-03 | Interstate Reliability Project | Transmission notification from Northeast Utilities Service Company (“NU”) to construct a new 345-kV transmission line from Lake Road 27E Substation to the Connecticut/Rhode Island state border, which will be the NU section of the new line connecting to the National Grid USA, West Farnum Substation. Revision is because the conductor is being revised from 2x1590 kcmil ACSR to 2x1590 kcmil ACSS based on the new NU standard. | 2013-12-01 | Approved | 2012-05-04
NU-08-T59-Rev. 01 | 2012-04-03 | Interstate Reliability Project | Transmission notification from Northeast Utilities Service Company (“NU”) for Card 11F Substation, to expand the existing 345-kV ring bus by adding three (3) new 345-kV circuit breakers rated at 3000A nameplate, 50 kA interrupting capability. Terminate transmission line 3271. Revision is because Card 11F 345-kV substation is being revised not to be reconfigured into a breaker and a half arrangement. The requirement for Card 11F 115-kV substation to become a BPS facility has been eliminated since it is already classified as part of the NPCC Bulk Power System (BPS). | 2013-12-01 | Approved | 2012-05-04
NU-08-T51-Rev. 01 | 2012-04-03 | Central Connecticut Reliability Project | Transmission notification from Northeast Utilities Service Company (“NU”) to build a new 345-kV transmission line from North Bloomfield 2A Substation to the Frost Bridge 8R Substation. Revision is because the conductor is being revised from 2x1590 kcmil ACSR to 2x1590 kcmil ACSS based on the new NU standard. | 2017-12-01 | Approved Withdrawn | 2012-05-04
NU-12-T15 | 2012-04-03 | Central Connecticut Reliability Project | Transmission notification from Northeast Utilities Service Company (“NU”) to expand North Bloomfield 2A Substation by adding a 3rd 345-kV bay consisting of two 345-kV circuit breakers having a nameplate rating of 3000 A and an interrupting capability of 50 kA. Terminate the new North Bloomfield to Frost Bridge 345-kV line. | 2017-12-01 | Approved | 2012-05-04
NU-12-T16 | 2012-04-03 | Central Connecticut Reliability Project | Transmission notification from Northeast Utilities Service Company (“NU”) to install the second 345-kV variable 75-150 MVAR reactor and one 345-kV circuit breaker at the Beseck 9F Substation. | 2017-12-01 | Approved | 2012-05-04
ALG-12-G01 | 2012-04-04 | Algonquin Generator Capacity Increase Project | Generator notification from Algonquin Power (“ALG”) for the capacity increase to the existing Dexter generator (Resource ID #392) located in Windsor Locks, CT through the construction of a new 16.44 MW gas turbine generator. The project will be connected to the Dexter 13.8 kV substation alongside an industrial load and existing Algonquin Power combined cycle plant which consists of a 40 MW gas turbine generator and a 16 MW steam turbine generator. | 2012-07-01 | Approved | 2012-05-16
DEM-12-X01 | 2012-04-05 | Brayton Point 1 & 2 Static Exciter Replacement Project | Transmission notification from Dominion Energy New England (“DEM”) for the replacement of the existing voltage regulators and static excitation systems on the Brayton Point steam generating units 1 & 2 due to equipment obsolescence with GE EX 2011e digital excitation systems and power systems. Equipment replacement for Unit 1 will be during the spring 2012 overhaul. Equipment replacement for Unit 2 will be during the spring 2014 overhaul. | 2014-04-01 | Approved | 2012-05-16
IBR-12-G01 | 2012-03-30 | Groton Wind Generation and Transmission Project | Generator notification from Iberdrola Renewables (”IBR”) on behalf of Groton Wind, LLC for the construction of twenty four 2.0 MW wind turbine generators totaling 48 MWs net output power located in Grafton County, NH. | 2012-09-30 | Approved | 2012-05-16
IBR-12-T01 | 2012-03-30 | Groton Wind Generation and Transmission Project | Transmission notification from Iberdrola Renewables (”IBR”) on behalf of Groton Wind, LLC for the construction of the Groton Wind Collector Substation consisting of 34.5/115 kV transformer rated at 30/40/50 MVA with an impedance of aprox. 9%, connecting the Groton Wind Project with the new NU 115 kV Huckins Hill Switching Station on the Beebe River – Ashland Tap 115 kV Line E115. | 2012-09-30 | Approved | 2012-05-16
NU-12-T06 | 2012-03-30 | Groton Wind Generation and Transmission Project | Transmission Notification from Northeast Utilities Service Company (“NU”) for the construction of the 115 kV Huckins Hill Switching Station with three 115-kV circuit breakers, bifurcating 115-kV Line E115 located in Holderness, NH, providing a point of interconnection for the proposed generator project. | 2012-10-01 | Approved | 2012-05-16
NU-12-T07 | 2012-03-30 | Groton Wind Generation and Transmission Project | Transmission Notification from Northeast Utilities Service Company (“NU”) for the upgrade of the thermal capability of the existing 115 kV Line E115, Huckins Hill (POI)- Ashland Tap; to achieve the required summer thermal LTE rating of 150 MVA. The upgrade will result in summer thermal ratings of 125/159/164 MVA and winter thermal ratings of 153/180/185 MVA. The upgrade is to be achieve by increasing the maximum allowable conductor temperature to 140C. | 2013-12-01 | Approved | 2012-05-16
NU-12-T08 | 2012-03-30 | Groton Wind Generation and Transmission Project | Transmission Notification from Northeast Utilities Service Company (“NU”) for the addition of two 115-kV circuit breakers to the Merrimack Substation. The circuit breakers will be placed in series with existing bus tie circuit breakers ‘BT12’ and ‘BT23’. | 2014-12-01 | Approved | 2012-05-16
FLP-12-X01 | 2012-03-24 | Shepaug Automatic Voltage Regulator Replacement | Transmission notification from First Light Power Resources (“FLP”) for the replacement of the existing Automatic Voltage Regulator on the Shepaug Hydro generator, interconnected at the Shepaug 69 kV substation with a Basler DECS400 voltage regulator. | 2012-09-24 | Approved | 2012-05-16
NSTAR-12-G02 | 2012-04-09 | Airport Way Nominee Solar Project | Generator Notification from NSTAR Electric and Gas Company (“NSTAR) for the construction of a 1.24 MW solar array in Barnstable, MA. Generator will be interconnected through a recloser to a street lateral of the 23 kV #92A feeder out of NSTAR’s Hyannis Junction Substation #961. | 2012-05-01 | Notification | 2012-04-30
NEP-12-GNF07 | 2012-04-10 | Devens Solar Project | Generator notification from New England Power Company (“NEP”) on behalf of Citizens Energy Corporation (“CEC”) for the construction of a 2.5 MW solar array located in Devens, MA. Project will interconnect to the Devens Utilities 13.8 kV distribution system fed by the Devens West Maine Substation. | 2012-08-01 | Notification | 2012-04-30
BBHP-12-G01 | 2012-03-23 | Medway Hydro Capacity Increase Project | Generator Notification from Bangor Hydro Electric Company on behalf of Black Bear Hydro Partners (“BBHP”) for a 0.8 MW capacity increase to the existing Medway Hydro generator (Resource ID #16525) located in Penobscot, ME. Project will increase net capacity to 4.776 MWs. | 2013-09-01 | Notification | 2012-04-30
BBHP-12-G02 | 2012-03-23 | Stillwater Station B Capacity Increase Project | Generator Notification from Bangor Hydro Electric Company on behalf of Black Bear Hydro Partners (“BBHP”) for the construction of a 2.4 MW hydro generator located in Penobscot, ME. Generator will be interconnected to the existing BHE 12.5 kV Stillwater Avenue Substation. | 2012-08-01 | Notification | 2012-04-30
BBHP-12-G03 | 2012-03-23 | Orono Station B Capacity Increase Project | Generator Notification from Bangor Hydro Electric Company on behalf of Black Bear Hydro Partners (“BBHP”) for the construction of a 4.0 MW hydro generator located in Penobscot, ME. Generator will be interconnected to the existing BHE 12.5 kV Orono Substation. | 2012-08-01 | Notification | 2012-04-30
UI-08-T05-Rev.2 | 2012-03-20 | Grand Avenue Switching Station Modernization | Transmission notification from United Illuminating Company (“UI”) to revise the previously approved Grand Avenue Switching Station Project. Due to physical construction reasons involving the underground duct line and the Grand Avenue GIS equipment, the 88003A and 89003B underground 115 kV lines will have their terminations at Grand Avenue Switching Station swapped. | 2012-05-01 | Notification | 2012-04-30
NU-12-G01 | 2012-03-27 | Hartford Water Pollution Control Facility Steam Generator Project | Generator notification from Northeast utilities Service Company (“NU”) for the construction of a 2MW steam turbine generator located in Hartford, CT. Generator will interconnect to the CL&P South Meadow 115kV Substation, Primary circuit 1A130 and Alternate 1A116. | 2012-03-30 | Notification | 2012-04-30
NEP-12-GNF-03 | 2012-04-05 | Quabbin Solar Project | Generator notification from New England Power Company (“NEP”) for the construction of a 2 MW solar array located in Barre, MA. Generator will interconnect to the NGRID 13.8 kV distribution circuit #604W2 supplied from the Barre Substation. | 2012-03-02 | Notification | 2012-04-30
FW-12-G01 | 2012-02-29 | Bull Hill Wind Generation and Transmission Project – QP #317 | Generation notification from First Wind LLC (“FW”) on behalf of Blue Sky East, LLC for the construction of nineteen 1.815 MW wind turbine generators (34.5 MWs gross) and interconnecting to the Bangor Hydro Electric Company (“BHE”) 115 kV Line 66 by means of a new BHE switching Station and FW Bull Hill Switching Station located in Eastbrook, ME. | 2012-09-30 | Approved | 2012-03-21
FW-12-T01 | 2012-02-29 | Bull Hill Wind Generation and Transmission Project – QP #317 | Transmission notification from First Wind LLC (“FW”) on behalf of Blue Sky East, LLC for the construction of a new Bull Hill Substation to interconnect the Bangor Hydro Electric (BHE”) Bull Hill Switching Station and the Bull Hill Wind Farm. | 2012-09-30 | Approved | 2012-03-21
BHE-12-T01 | 2012-02-29 | Bull Hill Wind Generation and Transmission Project – QP #317 | Transmission notification from Bangor Hydro Electric Company (“BHE”) for the construction of a new Bull Hill, Switching Station with a new three breaker ring bus,segmenting the existing BHE Line 66 between Rebel Hill and Deblois Switching Stations to service the Bull Hill wind Farm. | 2012-09-30 | Approved | 2012-03-21
BHE-12-T02 | 2012-02-29 | Bull Hill Wind Generation and Transmission Project – QP #317 | Transmission notification from Bangor Hydro Electric Company (“BHE”) for the rerate of the 4 mile overhead existing BHE line 69 from present summer LTE rating of 39MVA to a minimum summer LTE rating of 45MVA from the Columbia Tap in Columbia, ME to the Epping Switching Station in Epping, ME.. Engineering on this effort is ongoing but it is anticipated that with clearance changes this rerating can be done without changing the conductor. | 2013-03-01 | Approved | 2012-03-21
CMP-12-X01 | 2012-02-14 | Rumford Temporary SPS and PSS Project | Transmission Notification from Central Maine Power Company (“CMP”) for the temporary Rumford Area SPS (NPCC Type III SPS) being installed to reject generation at Rumford Power Associates (RPA) for faults on Sections: 210, 211, 217, 221, 228, 243, various Rumford Area buses, and breaker failure conditions at Kimball Road during the construction of Section 243A as part of the Maine Power Reliability Program (MPRP). This change is required to maintain system stability during the construction period. The expected duration of the 115 kV transmission outages is expected to be from 10 to 12 months from the Fall of 2012 to the Fall of 2013. | 2012-09-01 | Approved | 2012-03-21
CPEM-12-X01 | 2012-02-14 | Rumford Temporary SPS and PSS Project | Transmission Notification from Capital Power Corporation (“CPEM”) on behalf of Rumford Power for the installation of a Power System Stabilizer at Rumford Power Inc. The expected installation of this software is to be completed prior to November 1, 2012 in preparation for certain transmission outages in the local area commencing in the Fall of 2012 to the Fall of 2013. | 2012-11-01 | Approved | 2012-03-21
NSTAR-12-G05 | 2012-03-05 | Dartmouth Solar Project | Generator notification from NSTAR Electric and Gas Company (“NSTAR”) for the construction of a 3.0 MW photovoltaic solar array located in Dartmouth, MA. Generator will be interconnected to the NSTAR Industrial Park Substation #636, 13.2 kV feeder #107. | 2012-07-01 | Notification | 2012-03-21
NSTAR-12-G03 | 2012-03-05 | Edgartown Solar Project | Generator notification from NSTAR Electric and Gas Company (“NSTAR”) for the construction of a 1.083 MW photovoltaic solar array located in Edgartown, MA. Generator will be interconnected to the NSTAR Falmouth Substation #933, 23 kV #99 Line. | 2012-08-01 | Notification | 2012-03-21
NSTAR-12-G04 | 2012-03-05 | Dennis Landfill Solar Project | Generator notification from NSTAR Electric and Gas Company (“NSTAR”) for the construction of a 2.5 MW photovoltaic solar array located in Dennis, MA. Generator will be interconnected to the NSTAR #92B 23 kV distribution feeder our of the Harwich Substation #968. | 2012-05-01 | Notification | 2012-03-21
NSTAR-10-T07-Rev.1 | 2012-02-15 | Line 123 Reconnect Project | Transmission notification from NSTAR Electric and Gas Company (“NSTAR”) to revise the original PPA for this project (NSTAR-10-T07) described expanding the Barnstable 115 kV Substation with a fifthbay. The existing Barnstable – Hyannis #124 line was going to be reconnected to the new fifth bay position and the Barnstable – Hyannis #123 Line was going to be reconnected to the present #124 Line position. However, in order to avoid 115 kV crossovers for a future line from Barnstable supplying the lower Cape area, the Line #124 was reconnected to Bay #6 and Line #123 was reconnected to Bay #5. | 2011-12-01 | Notification | 2012-03-21
BLP-12-T01 | 2012-02-04 | Stockhouse Road Substation Project | Transmission notification from Bozrah Light & Power (“BLP”) for the installation of a new 115 kV, 3000 ampere, 40 kA circuit breaker in series with the 1490 and 1070 lines. New wave traps and line protection will be installed to enable sectionalizing of a faulted circuit without interrupting 100% of the load from Stockhouse Road. New SF6 1200 ampere circuit switchers and 1200 ampere disconnect switches have been installed for high side protection and electrical isolation of the three power transformers. | 2012-04-01 | Approved | 2012-03-05
TCMWD-11-G01 | 2012-01-25 | Kibby Wind Expansion Project – QP #310 | Generator notification from TransCanada Maine Wind Development (“TCMWD”) for the construction of 11 Vestas V90 Wind Turbine generators each rated at 3.0 MWs (33 MWs net output) and interconnecting to the Kibby Expansion Substation located in Franklin County, ME. | 2012-09-01 | Approved | 2012-03-05
TCMWD-11-T01 | 2012-01-25 | Kibby Wind Expansion Project – QP #310 | Transmission notification from TransCanada Maine Wind Development (“TCMWD”) for the construction of a 115/34.5 kV substation interconnecting to Section 267 approximately 1200 ft. from the existing Kibby Wind Farm. Also construct one string collector operating at 34.5 kV nominal tying into the Kibby Substation using approximately 5.8 miles of 1113 KCML ACSR at 34.5 kV. In addition, install an under load tap changing 121/34.5 kV step up transformer (25/33/41.5 MVA at the collector substation | 2012-09-01 | Approved | 2012-03-05
CMP-11-T07 | 2012-01-25 | Kibby Wind Expansion Project – QP #310 | Transmission notification from Central Maine Power Company (“CMP”) to construct facilities to interconnect the TransCanada Maine Wind Development Project Q310, 33 MW wind farm into the CMP transmission system by tying into customer owned Section 267 approximately 1,200 feet from the existing Kibby Wind collector substation. This PPA covers the required CMP system upgrades include installing four +/- 4 MVAR dynamic reactive sources at Bigelow Substation; installing a dedicated 115/34.5 kV transformer for the dynamic reactive sources at Bigelow Substation; automating the high-voltage switching controls for both 18 MVAR shunt capacitor banks at Wyman Hydro Substation; and installing an additional 5.4 MVAR shunt capacitor at Starks Substation | 2012-09-01 | Approved | 2012-03-05
MPP-12-X01 | 2012-02-06 | Millennium AVR Replacement Project | Transmission notification from Millennium Power Partners (“MPP”) for the replacement of the existing WDR2000 automatic voltage regulator (AVR) systems for the combustion turbine and steam turbine units with a Basler ECS/RW AVR systems. Replacement is due to the existing AVR has become obsolete | 2012-04-01 | Approved | 3/5//2012
NSTAR-12-T02 | 2012-02-06 | Brook Street Station 115 kV Bay Addition Project | Transmission Notification form NSTAR Electric and Gas Company (“NSTAR”) for the new 115 kV Bay at Brook Street Station with a new 30/40/50 MVA 115/23 kV transformer located in Plympton, MA | 2011-12-01 | Approved | 2012-03-05
UI-12-T04 | 2012-02-06 | East Shore Substation Capacity Upgrade Project | Transmission Notification form United Illuminating Company (“UI”) for the reconfiguration of the 60 and 70 bays of the existing breaker-and-a-half configuration of the East Shore 115 kV Substation, including the addition of new 115 kV circuit breakers and disconnect switches, and modification of the 115 kV bus. In addition, installation of two (2) new 30/40/50 MVA, 118/14.9 kV power transformers, with load tap changers (LTCs) and installation of a new Powe Delivery Center (PDC) for interconnecting the existing distribution circuits. Also,removal of the existing distribution substation, including 115 kV oil circuit breakers, 22T and 32T | 2013-06-01 | Approved | 2012-03-05
RPM-09-G01-Rev.1 | 2012-01-18 | Johnston Landfill Generator and Transformer Project Revision | Generator Notification from Rhode Island GenCo, LLC (“RPM”) for the reduction in MW output of the Johnston Landfill Gas Generator from 38.6 MWs to 32.6 MWs due to diminished gas supply. | 2012-10-03 | Approved | 2012-03-05
RPM-09-T01-Rev.1 | 2012-01-18 | Johnston Landfill Generator and Transformer Project Revision | Transmission Notification from Rhode Island GenCo,LLC (“RPM”) for the rating reduction of a 35 MVA 13.8/115 kV generator step up transformer at the Johnston LFG generating plant and interconnecting to the NGRID Ridgewood #124 Switchyard. Reduction reflects the change in generation output of the Johnston Landfill Gas Generator. | 2012-10-03 | Approved | 2012-03-05
CMP-11-T02-Rev.1 | 2012-01-30 | Lakewood PPA Revision | Transmission notification revision from Central Maine Power Company (“CMP”) to Sectionalize Section 241 by adding four 115 kV circuit breakers in a ring bus configuration at the existing Lakewood Substation. Also, install a second 115/34.5 kV 20/37 MVA transformer at the existing Lakewood Substation. Construct 4 miles of new 115 kV Bluejay (1113 45/7) conductor from the Section 83 corridor to the Lakewood Substation in the existing Section 83B (future Section 241) Right-of-Way. Also, rebuild the existing 115 kV line Section 83B (future Section 241) with Bluejay (1113 45/7) conductor (4 miles). The previous submittal of PPA CMP-11-T02, did not capture the proposed Lakewood project in its entirety. The associated transmission line work was inadvertently omitted from the application. | 2013-12-01 | Approved | 2012-03-05
CMP-12-T01 | 2012-01-30 | Leeds Substation Project | Transmission notification from Central Maine Power Company (“CMP”) to Tap Line Section 200 roughly 14.1 miles north of the Gulf Island 115 kV Substation, between pole structures 133 and 134. Install a 115/34.5 kV 20/37 MVA transformer and three 34.5 kV distribution circuits | 2012-02-01 | Approved | 2012-03-05
NEP-12-GNF02 | 2012-01-17 | Lightolier Wind Project | Generator notification from New England Power Company) (”NEP”) for the installation of one 2 MW wind turbine generator interconnected to the NGRID 13.8 kV distribution system through 13.8 kV circuit #28W51 via a new 13.8 kV tap on Sykes Road in Fall River, MA. | 2012-01-31 | Notification | 2012-03-05
CMP-12-T02 | 2012-01-30 | North Augusta Substation Upgrade Project | Transmission notification from Central Maine Power Company (“CMP”) for the sectionalize of Section 213 by adding two 115 kV circuit breakers at the existing North Augusta Substation. Also install a 115/34.5 kV 20/37 MVA transformer at the existing North Augusta. | 2013-12-01 | Approved | 2012-03-05
NSTAR-12-T03 | 2012-02-06 | West Medway AutoTransformer Replacement Project | Transmission Notification from NSTAR Electric and Gas Company (“NSTAR”) for the replacement of the existing 345/230 kV auto transformer (345A) at West Medway Substation located in Medway, MA. | 2013-02-01 | Approved | 2012-03-05
NSTAR-12-T04 | 2012-02-06 | West Medway AutoTransformer Replacement Project | Transmission Notification from NSTAR Electric and Gas Company (“NSTAR”) for the replacement of the existing 345/230 kV auto transformer (345B) at West Medway Substation located in Medway, MA | 2013-02-01 | Approved | 2012-03-05
CTMEEC-11-T01 | 2011-12-22 | South Norwalk Substation Project | Transmission Notification from Connecticut Transmission Municipal Electric Energy Cooperative (“CTMEEC”) on behalf of South Norwalk Electric and Water District for the construction of a new 115/13.8 kV Substation having a 115 kV bus tie breaker and two 40 MVA two winding transformers located in Norwalk CT. Interconnecting via a looped tap into a 6.37 mile overhead transmission line 1890 “E” extending from South Norwalk 115 kV Substation to Sherwood 115 kV Substation located in Westport CT via a tap into the 0.17 mile overhead transmission line segment 1890 “W” from the South Norwalk 115 kV Substation to the Ely Avenue Junction located in Norwalk CT. | 2013-06-01 | Approved | 2012-02-03
HW-12-G01 | 2012-01-09 | Highland Wind Transmission Project | Generation Notification from Highland Wind LLC (“HW”) for the construction of thirty nine 3.0 MW Siemens wind turbine generators for a total nameplate output of 117 MWs located in Highland Plantation, ME. | 2013-12-01 | Approved Withdrawn | 2012-02-03
HW-12-T01 | 2012-01-09 | Highland Wind Transmission Project | Transmission Notification from Highland Wind LLC (“HW”) for the construction Of the Highland Wind Collector Substation and interconnection of a generator lead connecting the Highland Wind generator project with the CMP 115 kV Wyman Hydro Substation | 2013-12-01 | Approved Withdrawn | 2012-02-03
CMP-11-T04 | 2012-01-09 | Highland Wind Transmission Project | Transmission Notification from Central Maine Power Company (“CMP”) for the construction of facilities to terminate the Highland Wind generator lead on Bus 3 at Wyman Hydro Substation next to Section 241, including necessary transmission structures to cross the Kennebec River, and taller H Frame structures on Sections 215, 63, and 83 within the Wyman Hydro Substation to accommodate the Highland Wind generator lead crossing underneath them. | 2013-12-01 | Approved Withdrawn | 2012-02-03
UI-12-T03 | 2011-12-20 | 8300 Reconfiguration Project | Transmission Notification from United Illuminating Company for the installation of a new fifth breaker and one half bay to the 115 kV gas insulated switch gear (GIS) at Grand Avenue Switching Station located in New Haven, CT. | 2013-06-01 | Approved | 2012-02-03
UI-12-T02 | 2011-12-20 | 8300 Reconfiguration Project | Transmission Notification from United Illuminating Company for the Relocation of the Mill River end of the existing 8300 115 kV line from Quinnipiac Substation into a new terminal position at the Grand Avenue Switching Station located in New Haven, CT | 2013-06-01 | Approved | 2012-02-03
UI-12-T01 | 2011-12-20 | 8300 Reconfiguration Project | Transmission Notification from United Illuminating Company for the installation of a new 260 foot 115 kV transmission line between the existing 8300 line terminal at Mill River and a new terminal position at Grand Avenue located in New Haven, CT. | 2013-06-01 | Approved | 2012-02-03
NU-12-X01 | 2012-01-06 | Altresco 41A 1715/1816 SPS Modification | Transmission Notification from Northeast Utilities Service Company (“NU) for the Altresco 41A 1715/1816 SPS Modification from the Altresco 41A Substation to the Doreen 19A Substation Line #1715 and from the Altresco 41A Substation to the Doreen 19A Substation Line #1816 located in Pittsfield, MA. Winter set points will be changed from 475 amperes to 580 amperes. Summer set point will remain at 475 amperes. Also, modifications will be made to the SPS to facilitate changing the SPS relay set point for the summer and winter periods via SCADA control command initiated by CONVEX. | 2012-03-31 | Approved | 2012-02-03
PPHC-12-G01 | 2012-01-06 | Altresco Generator Increase and SPS Modification Project | Generator Notification from Pawtucket Power Holding Company, LLC (“PPHC”) for a 8.95 MW increase in gross winter output generation output for each of the three gas turbines and a 0.06 MW increase in gross winter output of the steam turbine generator at the Altresco generating station located in Pittsfield, MA.. | 2012-03-31 | Approved | 2012-02-03
NSTAR-11-G07 | 2011-01-09 | Fairhaven Wind Project | Generation Notification form NSTAR Electric and Gas Company (“NSTAR”) for the construction of two 1.5 MW wind turbine generators (3.0 MWs total net output) located in Fairhaven, MA. Generator will interconnect to the Arsene Street Substation #654 13.2 kV feeders #220 and #221. | 2012-04-01 | Notification | 2012-02-03
NSTAR-11-G16 | 2011-01-09 | Kingston Wind Project | Generation Notification form NSTAR Electric and Gas Company (“NSTAR”) for the construction of a 2.0 MW wind turbine generator located in Kingston, MA. Generator will interconnect to the NSTAR #17 23 kV distribution feeder out of the NSTAR Kingston Substation #735. | 2011-12-01 | Notification | 2012-02-03
NEPM-11-G02 | 2011-12-07 | Southbridge Landfill Generator | Construction of a 1.5 MW Landfill Gas generator located in Southbridge, MA. Generator will interconnect to 413L4. | 2011-12-09 | Approved | 2012-01-05
BHE-06-T02-Rev. 1 | 2011-10-21 | BHE Downeast Reliability Project Rev. 1 | Change in project line numbers from Tap L57 from Boggy Brook in Hancock to Tap L69 near Harrington Substation located in Harrington, ME. In addition. Overhead line distance has been revised from 35 miles to 43 miles. Also, two small transformers were replace with one larger one rated at 20/26.7/33.3 MVA at Trunk. | 2012-12-01 | Approved | 2012-01-05
NSTAR-11-T12 | 2011-12-02 | Trapelo Road Station Upgrade | Addition of a new 115/14 kV transformer at the Trapelo Road Station #450. The transformer will be tapped off the existing 320-508 line between Waltham and Lexington. In addition, two 115 kV breakers will be installed between the taps of the transformers 110A and 110C in a series breaker configuration. The section of the 115 kV line between Trapelo Road and Waltham will be renumbered to 450-508. | 2012-06-01 | Approved | 2012-01-05
NU-11-T14 | 2011-11-30 | West Springfield 8C Substation Restoration | Construction of a Gas Insulated Substation The new substation will be built on the existing substation easement and configured in a breaker-and-half design. Existing yard structures will be demolished, and a new control house, battery building, and storage building constructed. Existing transformers and pipe cables will not be relocated. Connections into the GIS will be made using underground cables. New structures will be constructed in the yard to transition from underground cable to overhead conductors connecting to distribution and generation transformers. The structures serving distribution transformers 8C-1X and 8C-2X will be designed to allow installation of transformer high side motor operated disconnect switches. | 2014-12-31 | Approved | 2012-01-05
GDF-11-G01 | 2011-10-31 | Northfield Solar Generator | Construction of a 1.7 MW net output photovoltaic generator located in Northfield, MA and interconnecting to the French King 21B 115 kV Substation via WMECO’s 21B8 13.8 kV distribution circuit | 2012-01-01 | Approved | 11/21//2011
NU-11-G08 | 2011-10-28 | CCSU Fuel Cell generator | Construction of a 1.4 MW total net output fuel cell generator located in New Britain, CT and interconnecting to the New Britain, CT/CL&P Feeder Numbers 7L82. | 2011-11-16 | Approved | 11/21//2011
NU-11-G06 | 2011-10-20 | Whatley Solar Generator | Construction of three 0.50 MW (1.5 MW total net output) photovoltaic generators located in Whately, MA and interconnecting to the Podick 18G 115 kV Substation via WMECO’s 18G8 13.8 distribution circuit. | 2012-06-01 | Approved | 11/21//2011
NU-11-G07 | 2011-10-21 | Rvermore-Citizens Agawam Solar Generator | Construction of three 0.50 MW (1.5 MW total net output) photovoltaic generators located in Agawam, MA and interconnecting to the Agawam 16C 115 kV Substation via WMECO’s 16C16 13.8 distribution circuit. | 2012-06-01 | Approved | 11/21//2011
NEP-11-T11 | 2011-10-24 | Johnston Transformer Replacement | Replacement of the existing Johnston Substation transformer rated at 115/12.47 kV with a new transformer rated at 115/12.47 kV and 33/44/55 MVA located in Johnston, RI. | 2012-10-01 | Approved | 11/21//2011
BHE-11-T01 | 2011-10-21 | BHE Harrington Transformer Replacement | Replacement of the Harrington T1 115/34.5 kV load serving transformer and regulators with a thermally larger unit rated at 8/24/33.6 MVA with LTC. | 2nd Quarter 2012 | Approved | 11/21//2011
BHE-11-T02 | 2011-10-21 | BHE Ellsworth Falls Transformer Replacement | Replacement of the Ellsworth Falls T2 115/34.5 kV load serving transformer with a thermally larger unit rated at 62.6 MVA with LTC. | 2nd Quarter 2012 | Approved | 11/21//2011
HE-11-G02 | 2011-10-21 | Mueller Road Solar Generator | Construction of a 2.691 MW (net) photovoltaic generator located in Holyoke, MA and interconnecting to the 39C4 West Holyoke Substation distribution feeder supplied from the Ingleside 52W transmission Substation. | 2011-10-19 | Approved | 2011-10-26
NU-11-G05 | 2011-10-03 | Route 57 Solar Generator | Construction and interconnection of three 0.5 MW photovoltaic generators (1.5 MWs net output) interconnecting to the Silver 30A 115 kV substation via the WEMECO 30A6 13.8 kV line located in Agawam, MA. | 2012-06-01 | Approved | 2011-10-26
NEP-11-T10 | 2011-10-04 | G 33 Line Reconductoring | Reconductoring of the G-33 69 kV transmission line from the Vernon Substation to the Bellows Falls substation in VT. | 2012-04-01 | Approved | 2011-10-26
NSTAR-11-G14 | 2011-10-07 | MWRA Charlestown Wind generator | Construction of a 1.5 MW wind turbine generator located in Charlestown, MA and interconnecting to the NSTAR Mystic Station #250, 14 kV Line 585-114H. | 2011-10-01 | Approved | 2011-10-26
NSTAR-11-T11 | 2011-10-03 | 201-501 and 201-502 Line Reconductoring | Reconductoring of the 201-501 (D-130) and 201-502 (C-129N) 115 kV transmission lines from Medway substation #65 in Medway, MA to the Depot Street Sub Tap in Milford, MA. | 2013-06-01 | Approved | 2011-10-26
NSTAR-11-G11-Rev.1 | 2011-09-14 | Dartmouth Landfill Generator | Revision of the project interconnection of the previously approved 1.25 MW photovoltaic generator by GLC Dartmouth, LLC located in Dartmouth, MA. and interconnecting to the NSTAR Fisher Road Substation #657. Interconnection will now consist of three 200 volt, 500 kW inverters interconnecting via three separate, 500 kVA 200 Volt to 13.2kV step up transformers. | 2012-12-01 | Approved | 2011-10-26
HGE-11-G01 | 2011-09-21 | Meadow Street Solar Generator | Construction of a 0.82 MW (net) photovoltaic generator located in Holyoke, MA and interconnecting to the 62W9 distribution feeder supplied from the Ingleside 52W transmission Substation. | 2011-10-19 | Approved | 2011-10-26
VELCO-11-T08 | 2011-10-03 | Georgia Transformer | Installation of a 115/34.5 kV step down transformer at the Georgia Substation located in Georgia, VT. The installation of the transformer is proposed to relieve loading on existing nearby transformers and the local sub-transmission system, and to prevent loss of load in the St. Albans/East Fairfax area. | 2014-12-01 | Approved | 2011-10-26
TCPM-11-G01 | 2011-10-12 | Kibby Reactive Capability Reduction | Reduction of the MVAR leading capability of the Kibby Wind Farm from 0.86 MVAR per turbine to 0.35 MVAR per turbine to alleviate potential low voltage tripping issues at the generator. | 2011-10-07 | Approved | 2011-10-26
GMP-11-G01 | 2011-10-05 | Kingdom Wind Generator | Construction of twenty one 3.075 MW Vestas V112 wind turbine generators for a total net power output of 64.575 MWs and interconnecting to the new Vermont Electric Cooperative 46 kV Lowell Substation located in Lowell, VT. QP #311 interconnects twenty wind turbines, QP #367 adds one additional wind turbine. | 2012-10-01 | Approved | 2011-10-21
GenOn-11-G01 | 2011-09-23 | Kendall 3 Generator | Repowering of Kendall Steam Unit #3 with the installation of a back-pressure-steam turbine (“BPST”), air-cooled-condenser, and new generator controls. This modification will increase the maximum net power generation capability of Unit #3 by about 9MW for a total of approximately 28.5 MWs. | 2014-05-31 | Approved | 2011-10-26
NSTAR-11-G11 | 2011-09-14 | Dartmouth Landfill Solar Generator | Construction of a 1.25 MW photovoltaic generator by GLC Dartmouth, LLC located in Dartmouth, MA. and interconnecting to the NSTAR Fisher Road Substation #657. | 2011-12-01 | Approved | 2011-09-26
NU-11-T12 | 2011-09-12 | Black Rock 115 kV/69 kV Transformer and Line 680 Obsolete Terminal Equipment | Replacement of the 11H-4X 115/69 kV autotransformer and terminal equipment at the Black Rock 115 kV Substation and replacement of obsolete terminal equipment associated with the 680 Line at Black Rock located in New Britain, CT. | 21/31/2011 | Approved | 2011-09-26
NU-11-G02 | 2011-07-22 | Easthampton Solar Generator | Construction of a 2 MW photovoltaic generator located in Easthampton, MA and interconnecting to the Gunn 15A 115 kV substation via the WEMECO 15A3 23 kV line | 2011-11-15 | Approved | 2011-09-07
NU-11-T11 | 2011-08-08 | Merrimack Station Service Load | Installation of two 115 kV circuit breakers at the Merrimack 115 kV substation, providing positions for two 115/4.16 kV transformers, for installing a new stack emissions scrubber system at the Merrimack generating station which will increase the station service load to approximately 19 MWs, 10.6 MVar at 0.87 p.f. lagging. | 2012-06-01 | Approved | 2011-09-07
NEP-11GNF01 | 2011-06-29 | Mt. Wachusett Community College Wind Turbine Generator | Installation of a 3.3 MW wind turbine generator located in Gardner, MA. Generator will interconnect to the Park St. #601 Substation at the 601W3 13.8 kV distribution feeder | 2011-07-10 | Approved | 2011-09-07
BBHP-11-G01 | 2011-07-17 | Black Bear Hydro generator | Addition of two hydro generators increasing the capability of the resource from 8 MWs to 9.083 MWs (net output) located in Milford, ME. Generators will interconnect to the existing Milford 46 kV substation. | 2011-09-01 | Approved | 2011-09-07
NU-11-G04 | 2011-08-10 | ASML US Generator | Construction of a 1.8 MW net output diesel generator located in Wilton, CT. Generator will interconnect to the Wilton 35A substation 13.8 kV on the 35A6 feeder bus A2 normal via the 115 kV Wilton-Ridgefield-Peacable 1470 Line. | 2011-09-16 | Approved | 2011-09-07
NU-11-G03 | 2011-08-12 | Indian Orchard Photovooltaic Generator | Construction of a 0.5 MW net output photovoltaic generator located in Springfield, MA. Generator will interconnect to the Orchard 27A substation | 2011-11-01 | Approved | 2011-09-07
NU-04-T26-Rev. 1 | 2011-08-15 | South Meaadow 115 kV BPS Upgrade | Revision of the in service date of the South Meadow 115 kV Substation Bulk Power System Upgrade (BPS) to December 31, 2013. | 2013-12-31 | Approved | 2011-09-07
ECO-11-G02 | 2011-07-15 | Canton Mountain Wind Generator | Construction of seven 2.75 ME GE wind turbine generators with a total net output of 19.25 MWs located in Canton ME. | 2013-10-01 | Approved | 2011-08-29
ECO-11-T02 | 2011-07-15 | Canton Mountain Wind Transmission | Installation of a 1.0 mile overhead 34.5 kV transmission line from Canton Mountain Wind to the 115 kV SRW/Ludden Lane Substation located in Canton, ME. where it will interconnect to a new 15/20/25 MVA 34.5/115 kV step up transformer. | 2013-10-01 | Approved | 2011-08-29
MMWEC-11-G04 | 2011-05-24 | Ameresco/Chicopee Landfill Generator | Construction of four 1.8 MW landfill gas generators with a total net output of 7.383 MWs and interconnecting to the 13.8 kV distribution system in Chicopee, MA. | 2011-05-01 | Approved | 2011-08-29
VELCO-11-G01 | 2011-08-15 | Georgia Mountain Wind | Construction of four 2.75 wind turbine generators with a total net output of 11.0 MWs and interconnecting to the 34.5 radial transmission line feeding the Husky Tap on the Milton to Fairfax Falls 34.5 kV line located in Milton, VT | 2012-11-30 | Approved | 2011-08-29
VELCO-11-G02 | 2011-08-15 | Fair Haven Biomass Generator | Construction of a 32.3 MW (net output) biomass generator located in Fair Haven, VT. | 2013-03-31 | Approved Withdrawn | 8/29/2011 7/23/2015
VELCO-11-T05 | 2011-08-15 | Fair Haven Biomass Transmission | Construction of a new three breaker rig bus substation connecting two 115 kV lines and the generator lead to the Beaver Wood Fair Haven generation plant. The substation will be located on the K-7 115 kV line 9Whitehall-Blissville) in Fair Haven, VT. | 2013-03-31 | Approved | 2011-08-29
VELCO-11-T06 | 2011-08-15 | Fair Haven Biomass Transmission | Construction of a 2.5 mile 115 kV transmission line from the Fair Haven substation to the Beaver Wood Fair Haven generation plant. | 2013-03-31 | Approved Withdrawn | 8/29/2011 7/23/2015
VELCO-11-T07 | 2011-08-15 | Fair Haven Biomass Transmission | Interconnection of the Fair Haven generator with a 115/13.8 kV transformer and 115/4.16 kV transformer. | 2013-03-31 | Approved Withdrawn | 8/29/2011 7/23/2015
CMP-11-X01 | 2011-08-09 | Maxcys/Bucksport SPS Modification | Revise the Maxcys/Bucksport Special Protection System (SPS) as part of construction sequencing for MPRP. During MPRP construction, the energization of one portion of the new path, 345 kV Section 3023 between Albion Road and Orrington substations, the Albion Road 345/115 kV autotransformer will require a modification of the Maxcys/Bucksport SPS. | 2012-01-01 | Approved | 2011-08-29
PSEG-11-G01 | 2011-06-29 | Bridgeport Harbor 3 Generation Capacity Increase | 5 MW increase in total net power output at the Bridgeport Harbor 3 Generator. Project increases net power output from 380 MWs to 385.0 MWs. | 2011-08-01 | Approved | 2011-07-28
NEP-11-T07 | 2011-06-29 | North Shore 115 kV Reconductoring Project | Reconductoring of 9.31 miles of the overhead S-145/T146 115 kV transmission lines from Tewksbury #22 Substation to the North Reading Tap. Projected effective date of the project is June 2014. | 2014-06-01 | Approved | 2011-07-28
NEP-11-T08 | 2011-06-29 | North Shore 115 kV Reconductoring Project | Reconductoring of 14.5 miles of the overhead B-154N/C-155N 115 kV transmission lines from King Street Tap to the South Danvers #42 Substation. Projected effective date of the project is June 2014. | 2014-06-01 | Approved | 2011-07-28
NEP-11-T09 | 2011-06-29 | North Shore 115 kV Reconduxctoring Project | Reconductoring of 8.2 miles of the overhead Y-151 115 kV transmission line from Tewksbury Junction to West Methuen #63 Substation. Projected effective date of the project is June 2014. | 2014-06-01 | Approved | 2011-07-28
NSTAR-11-T06 | 2011-04-29 | NSTAR Autosectionalized Switches | Installation of three new 2000 Amp, 115 kV, SEECO motor operated autosectionalized switches with dead line detection at the following locations: New switch # S791 to be installed on 115 kV line 211-503 on the tap to North Woburn and Reading Municipal. In service date of the project is September 24, 2011. New switch #S792 to be installed on 115 kV line 211-504 on the tap to North Woburn and Reading Municipal. In Service date of the project is October 12, 2011. New switch #19159 to be installed just outside Kingston Substation #735 on the leg of the #191 line proceeding to Auburn Street Station. In service date of the project is November 12, 2011. | 09/24/2011, 10/12/2011, 11/12/2011 | Approved | 2011-06-09
NU-11-T10 | 2011-05-11 | Stamford Reliability/South End Substation | Installation of a 115/13/2 kV transformer and two 115 kV circuit breakers at the South End Substation. | 2011-12-31 | Approved | 2011-06-09
NU-11-T09 | 2011-05-06 | 1410 115 kV Line Upgrade | Upgrade of the 8.71 mile overhead 1410 115 kV Transmission Line from Montville 4J Substation to Buddington 16L Substation. | 2012-12-01 | Approved | 2011-06-09
NSTAR-11-T03 | 2011-04-29 | Reconductor 128-518/P-168 115 kV Line | Reconductoring of the 128-518/P-168 115 kV Line from Chelsea to Revere. Line 128-518 / P-168 is 1.05 miles in length and is jointly owned by NSTAR and National Grid. The NSTAR section of the line (128-518) is 0.85 miles long and the National Grid section (P-168) is 0.2 miles long. The 1.05 mile line upgrade will be performed by NSTAR to provide higher thermal capacity. The upgraded NSTAR portion of the circuit will have a summer thermal rating of 363 MVA Normal and 63 MVA LTE. The upgraded National Grid portion of the circuit will have a summer thermal rating of 269 MVA Normal and 269 MVA LTE. | 2011-12-01 | Approved | 2011-06-07
MMWEC-11-G01 | 2011-04-05 | Stony Brook Energy Center uprate | Generation notification from Massachusetts Municipal Wholesale Electric Company (“MMWEC”) for the revision to the generation capability of Stony Brook Energy Center generation facility (Unit 1A, 1B, 1C, 2A, 2B, Steam Turbine). The revised Generator Notification is for 552.9 MWs Gross at 0 degrees and 440 MWs Net at 90 degrees. | 2011-05-01 | Approved Withdrawn | 4/21/2011 1/14/2015
MMWEC-11-G02 | 2011-05-10 | Ipswich Wind | Installation of a 1.6 MW wind turbine generator located in Ipswich, MA. Installation will be made to the Fowlers Lane Substation and supplied by 23 kV Line 2373 or Line 2394 Feed from NGRID King Street Substation. | 2011-06-29 | Approved | 2011-06-07
MMWEC-11-G03 | 2011-05-10 | Axio/Chicopee Solar | Installation of a 2.0 MW photovoltaic generator located in Chicopee, MA. Installation will be made to the 18L12 Feeder out of Chicopee Electric Light Department’s 18L Substation | 2011-12-01 | Approved | 2011-06-07
NEP-11-T04 | 2011-04-15 | Hopkinton Substation | Construction of a 115/13.2 kV Substation located in Hopkinton, RI. Two 24/32/40 MVA rated 115 kV to 13.2 transformers will serve the local distribution system. An in-line 200 A continuous, 40 kA interrupting capable circuit breaker will provide protection. The existing 1870S Line will be split into 1870S Line from Wood River to Hopkinton and the 1814 Line from Hopkinton to Shunock. | 2014-03-01 | Approved | 2011-06-07
ECO-11-G01 | 2011-05-09 | Saddleback Wind Generation | Construction of twelve GE 2.75-103 2.75 MW wind turbine generators (33 MWs total) located in Carthage, ME. | 2013-09-01 | Approved | 2011-06-07
ECO-11-T01 | 2011-05-09 | Saddleback Wind Transmission | 9.0 mile transmission line interconnection of the Saddleback Wind Generator to the new 115 kV Ludden Lane Substation in Canton, ME along with the installation 34.5/115 kV Step up Transformer. | 2013-09-01 | Approved | 2011-06-07
CMP-11-T03 | 2011-05-09 | Ludden Lane Substation | Construction of the Ludden Lane 115 kV Substation consisting of a three breaker ring bus to interconnect the Saddleback Wind generating facility. CMP’s existing Section 229 will be sectionalized into two line sections at the transmission corridor with two new transmission segments constructed and extended into the new Ludden Lane Substation, a distance of approximately 0.2 miles each. The portion of Section 229 between Ludden Lane Substation and Riley Substation will be renumbered as Section 280 and the portion between Ludden Lane Substation and Rumford IP Substation will remain as Section 229. | 2013-09-01 | Approved | 2011-06-07
CMP-11-T04 |  | Wyman Hydro | Construct facilities to terminate Highland Wind |  | Approved Withdrawn | XX/XX/XXXX 10/16/2012
HE-11-T01 | 2011-05-06 | South Holyoke Substation | Interconnection of the South Holyoke Substation (formally known as Lyman Substation) in Holyoke, MA. Project will consist of a new 115/34.5/13.8 kV Substation for the purpose of relocating the distribution load and hydroelectric generation from the HG & E Prospect 24B Substation to the proposed 115 kV South Holyoke Substation. Substation consists of two 18/24/30 MVA transformers with LTC; (each one to supply a 13.8 kV distribution bus); and two 115kV-34.5, 36/48/60 MVA transformers with LTC to connect the larger hydroelectric generation and major new loads. | 2012-12-01 | Approved | 2011-06-07
NU-11-T03 | 2011-03-03 | North Simsbury Substation | Installation of a 115 kV tie breaker to split the existing 1784 line into two separate lines from the Northeast Simsbury Substation in North Simsbury, CT to the North Bloomfield Substation in North Bloomfield, CT and from the Northeast Simsbury Substation to the Canton Substation in Canton, CT | 2013-06-01 | Approved | 2011-03-30
NEP-11-T02 | 2011-01-14 | Field Substation | Replacement of two 40 MVA 115/13.8 kV transformers with two 55 MVA 115/13.8 kV transformers at the Field Substation located in Quincy, MA. Install a 115 kV bus tie composed of one circuit switcher in series with one motor operated disconnect switch at Field St. Also addition of two 115 kV in-line breakers at Field St. substation on the 532N/533N lines (Field St. to North Quincy). Install two 115 kV circuit switchers on the 532S/533S lines (Edgar to Field St.). | 2014-05-01 | Approved | 2011-03-30
NEP-11-T03 | 2011-01-14 | North Quincy Substation | Installation of two 115 kV circuit switchers on the terminals of the 532N/533N lines (Field St. – North Quincy). Replacement of two 115 kV circuit switchers 1T115 and 2T115 at North Quincy Substation located in Quincy, MA. | 2014-05-01 | Approved | 2011-03-30
NSTAR-11-T04 | 2011-02-22 | Chelsea Substation | Installation of a new 115 kV, 36.7 MVAR shunt capacitor at the Chelsea Substation located in Chelsea, MA. The new capacitor bank is needed to support the sagging transmission voltages in the Chelsea -Revere load area for contingencies that result in the loss of 115 kV line 488-518 between Mystic and Chelsea. The Chelsea capacitor is also being installed as a part of the effort to meet Year 2011 ISO-NE Operating Procedure No.17 “Load Power Factor Correction” requirements for the Boston Load Power Factor Area. The main project components consist of the 36.7 MVAR capacitor and a 115 kV circuit breaker with a Synchronous Switching Controller. | 2011-11-01 | Approved | 2011-03-30
GRE-11-G01 | 2011-02-16 | Granite Ridge generation Station | Revision to the generation capability of Granite Ridge Energy generation facility as stated on the original 18.4 application (NEP-00-G04) and approved September 2000. The revised Generator Notification is for 821 MWs Gross at 0 degrees and 678 MWs net at 90 degrees. | 2011-03-01 | Approved | 2011-03-30
NSTAR-11-G04 | 2011-03-04 | AD Makepeace Solar Generaton Station | Installation of a 3.6 MW photovoltaic generator located in Wareham, MA. Installation will be made to the NSTAR #83 23 kV distribution feeder out of the NSTAR Wareham Substation #714 | 2011-10-01 | Approved | 2011-03-30
NSTAR-11-T05 | 2011-03-07 | Line 336 Transmission Line/Medway Disconnect | Reconductor of the 345 kV Line 336 from ANP Blackstone to NEA Bellingham Tap. Upgrade five 345 kV disconnect switches at West Medway Station from 2000 Amp to 3000 Amp associated with Line 336 (four breaker disconnect switches – 101A, 101B, 102A, 102B and one line disconnect swotch T902). Upgrade the bussing CTs on the West Medway 345B auto transformer from 2000 Amp to 3000 Amp and upgrade the metering equipment at the West Medway Station associated with Line 336. | 2012-12-31 | Approved | 2011-03-30
CMP-11-T01 | 2011-03-04 | Saco Bay Transmission | Installation of a new 115 kV radial line from Louden Substation to a new Vallee Lane Substation located in Old Orchard Beach, ME. A new Goosefare distribution Substation will be tapped mid way. In addition, a 115/34 kV transformer will be installed at the Vallee Lane Substation and a 115/12 kV transformer will be installed at the Goosefare Substation. | 2012-12-01 | Approved | 2011-03-30
NEP-11-T05 | 2011-02-16 | Everett Substation | Replacement of two existing 115-13.8Y/7.96 24/32/40 MVA transformers with two 115-13.8Y/7.96 kV 33/44/55 MVA transformers and replace five 115 kV air breaks with five 115 kV circuit switchers located in Everett, MA. | 2013-11-01 | Approved | 2011-03-30
NU-11-T01 | 2011-01-26 | Oak Hill Substation | Installation of two 13.3 MVar capacitor banks at the Oak Hill 115 kV substation located in Concord County, NH. | 2012-12-01 | Approved | 2011-02-28
VELCO-11-T02 | 2011-02-07 | Vernon Substation | Relocate the existing fixed 60 MVAR 345 kV reactor from VELCO New Haven Substation to VELCO Vernon Substation. | 2011-12-01 | Approved | 2011-03-23
VELCO-11-T03 | 2011-02-07 | Coolidge Substation | Installation of two new 34 to 60 MVAR 345 kV variable reactors at the VELCO Coolidge Substation with reactor breakers. | 2011-10-01 | Approved | 2011-03-23
VELCO-11-T04 | 2011-02-07 | New Haven Substation | Replace the existing fixed 60 MVAR 345 kV reactor and reactor breaker with one new 34 to 60 MVAR 345 kV variable reactor at the New Haven Substation on the 370 Line. The existing reactor will be relocated to the Vernon Substation (reference VELCO-11-02). | 2012-01-01 | Approved | 2011-03-23
DEM-11-G01 | 2011-02-09 | Manchester Street Generation Station | Winter uprate of the Manchester Street generators 9/9A (ID #323), 10/10A (ID #321) and 11/11A (ID# 322) from 164 MWs (winter SCC) to 170 MWs (winter SCC). | 2011-02-01 | Approved | 2011-02-28
DEM-11-X01 | 2011-02-09 | Manchester Street Generating Station | Upgrade of the existing static exciters on the CT and ST generators 9/9A (ID #323), 10/10A (ID #321) and 11/11A (ID# 322). | 2011-03-01 | Approved | 2011-02-28
NSTAR-11-G06 | 2011-02-01 | O'Donnell Family Trust Wind Farm Generating Station | Installation of three 2.0 MW Gamesa G87-2.0 wind turbines (6 MWs total output) located in Kingston, MA. Wind turbines will interconnect to the NSTAR #14 23 kV feeder at the West Pond Substation. | 2011-06-01 | Approved | 2011-02-28
NU-11-G01 | 2010-01-28 | UMASS Generation Station | Installation of one 4MW steam turbine generator and one 2 MW steam turbine generator located in Amherst, MA. Generators will serve the campus load and will not export. The proposed generators are connected to the UMass Central Heating Plant which is supplied via the distribution feeders 18G1and 18G2 from the Podick 18G Substation. | 2011-02-16 | Approved Withdrawn | 2/28/2011 11/5/2011
NU-11-T02 | 2011-01-26 | Merrimack Substation | Installation of a 115 kV circuit breaker and a new manual disconnect switch at the Northeast Utilities Merrimack Substation between Bus #1 and the existing combustion turbine transformer MT3 located in Merrimack, NH. | 2011-12-01 | Approved | 2011-02-28
NSTAR-11-T02 | 2011-02-03 | 320-507 & 320-508 Transmission Lines | Reconductoring of 5.2 miles the overhead 320-507 and 320-508 115 kV lines from Lexington Station 320 in Lexington, MA to Waltham Station 282 in Waltham, MA. | 2012-06-01 | Approved | 2011-03-02
MMWEC-09-G01-Rev.1 | 2011-02-07 | Berkshire Wind Generation Station | Revise the resource from voltage control mode to power factor control mode for the ten GE 1.5 MW wind turbines (15 MWs net) located on Brodie Mt., Lanesboro, MA. | 2011-03-01 | Approved | 2011-03-02
NSTAR-11-G01 | 2011-02-10 | Falmouth Wind Generation Station | Installation of a 1.65 MW Vestas Model V82 MKII wind turbine generator located in Falmouth, MA. Generator will interconnect at the NSTAR Falmouth Substation #933 23 kV feeder #98A. | 2011-01-15 | Approved | 2011-03-02
NSTAR-11-G05 | 2011-02-10 | Dartmouth Solar Park Generation Station | Installation of a 1.6 MW photovoltaic generator located in Dartmouth, MA. Generator will interconnect at the NSTAR Industrial Park Substation #636, 13.2 kV feeder #107. | 2011-02-01 | Approved | 2011-03-02
VELCO-11-T01 | 2011-01-10 | Jay Tap Substation | Construction of a new 4 breaker ring substation connecting two 115 kV lines and two 115/46 kV step-down transformers. The substation will be located on the K-41 line, approximately 13 mi west of the Moshers Tap. The normally open point on the 46 kV system between Vermont and Canada will be at the Moshers Corner 359 Switch. | 2012-06-01 | Approved Withdrawn | 8/29/2011 7/23/2015
VELCO-10-X01 | 2011-01-10 | Vermont Yankee SPS | Removal of the Vermont Yankee capacitor bank Special Protection System (SPS). The VY capacitor bank SPS automatically disconnects the 30 MVAr 115 kV capacitor bank any time the VY T4 345/115 kV autotransformer trips. This SPS was originally proposed to prevent a high change in voltage (delta V) when switching the 30 MVAr capacitor bank with the T4 autotransformer out of service. With the addition of the Coolidge Connector project, primarily the new Vernon 345/115 kV autotransformer, the high delta V concern with one autotransformer out of service has been eliminated. | 2011-07-01 | Approved | 2011-02-07
VELCO-11-X02 | 2011-01-10 | Vernon Road | Removal of the Vernon Road Under Voltage Load Shedding (UVLS) scheme. The Vernon Road UVLS scheme automatically disconnects both transformers at Vernon Road when the station low side voltage drops below 0.91 pu. This UVLS scheme was originally proposed to mitigate low voltages on the PSNH system near Keene for certain contingencies, such as loss of the Vermont Yankee (VY) T4 345/115 kV autotransformer. Since the installation of the scheme, various upgrades have been implemented, and as a result, the UVLS scheme will not trigger even under N-1-1 contingency scenarios. The upgrades in chronological order are the Chestnut Hill capacitor banks, the VY capacitor banks, the Fitzwilliam 345/115 kV autotransformer, and the Coolidge Connector project, which includes the Newfane injection to the local 46 kV system near Vernon Road. | 2011-07-01 | Approved | 2011-02-07
FPLE-10-G01 | 2011-01-11 | Gulf Island Generation Station | Upgrade of the Gulf Island generating Units 1 & 3 (Asset ID# 328). Upgrades include replacement of turbine runner and rewinding of Unit 1 and replacement of turbine runner on Unit 3. Work will increase generation output from 33.6 MWs to 38.9 MWs. | 2010-12-08 | Approved | 2011-02-07
NSTAR-11-G02 | 2011-01-06 | AFCEE Wind Generation Station | Installation of two 1.5 MW GE Model 1.5SLE wind turbines (3 MW Net) and interconnecting at the Pave Paws 115/23 kV substation located in Bourne, MA. | 2011-11-01 | Approved | 2011-02-07
SRTC-11-G01 | 2011-01-06 | Indian Rivier Hydro Generation Station | Installation of a 1.3 MW hydro generator and interconnecting within a new automatic loop scheme between a sectionalized recloser on the 19J1 circuit and a tie recloser between the 19J1 and 19 J2 circuit, supplied from the Blandford substation located in Russell, MA. | 2011-01-01 | Approved | 2011-02-07
NSTAR-11-T01 | 2011-01-07 | Mendall Rd Tap Station, Rochester Substation, Harwich Tap Sation | Installation of seven new 2000 ampere, 115 kV SEECO motor operated autosectionlizing switches with dead end detection | 2012-01-01 | Approved | 2011-02-07
NEP-11-T01 | 2011-01-07 | A127/B128W Transmission Line | 67 miles of overhead reconductoring of the B128W and 50 miles of overhead reconductoring for portions of the A-127W 115 kV lines from Harriman Substation in Readsboro, VT to Structure 510 in Milbury, MA. | 2014-11-01 | Approved | 2011-02-07
NEP-10-T12 | 2010-12-03 | S9 Transmission Line | Reconductor of the S9 115 kV Transmission Line from Plymouth St. to Water St. Tap. Create a loop from the 115 kV lines C3 and S9 by installing two new 115 kV breakers at Phillips Lane Substation #95 and operating the Norwell Substation #96 motor operated load break S9961 in a normally closed position. | 2013-10-01 | Approved | 2010-12-27
NEP-10-T06 | 2010-12-03 | Norwell Substation | Replacement of the existing 115/13.8Y/7.96 kV 15/20/25 MVA LTC transformer with a 115/13.8Y/7.96 kV 24/32/40 MVA LTC transformer and add a new 1200A – 20 kA 115 kV circuit switcher and update corresponding relays and controls at the Norwell Substation. | 2011-06-01 | Approved | 2010-12-27
NEP-10-G01 | 2010-12-02 | Douglas Woods Wind Farm Generation Station | Construction of the Douglas Woods Wind Farm consisting of twelve 2.5 MW wind turbines with a total output power of 30 MWs located in Douglas, MA. | 2012-12-01 | Approved Withdrawn | 12/27/2010 9/18/2013
NEP-10-T11 | 2010-12-02 | Douglas Woods Wind Farm Substation | Construction of a new interconnection substation with a single breaker and two load-break switches located in Webster, MA. In addition, construction of two new 69 kV line taps connecting the interconnecting substation to the S-19 69 kV transmission line. Connect the interconnection substation to the proposed generator substation. Upgrade the relaying for S-19 and T-20 line at Millbury and Meadow Street. | 2012-12-01 | Approved Withdrawn | 12/27/2010 9/18/2013
NEP-10-T13 | 2010-12-02 | Douglas Woods Wind Farm Substation | Construction of a new generator 69/34.5 kV substation with a 69/34.5, 18/24/30 MVA transformer and 34.5 kV switchgear to interconnect the proposed 30 MW Douglas Wind Farm | 2012-12-01 | Approved Withdrawn | 12/27/2010 9/18/2013
NEP-10-T02 | 2010-12-01 | G185S Transmission line | Upgrade of the existing 115 kV transmission line from Kent County substation to Davisville tap. In addition, replace 5.3 miles of 795 ACSR conductor to 954 ACSS. | 2013-10-01 | Approved | 2010-12-27
NSTAR-10-T07 | 2010-11-03 | Barnstable Substation | Expansion of the Barnstable 115 kV Substation with a 5th bay. The existing Barnstable – Hyannis #124 line will be reconnected to the new 5th bay position and the second Barnstable-Hyannis #123 line will be reconnected to the present #124 line position. | 2012-12-01 | Approved | 2010-11-22
CMP-10-T04 | 2010-11-01 | Hotel Road Substation | Replacement of one 115 kV automatic sectionalized switch with a 115 kV circuit breaker and the addition of a second 20/37 MVA 115/34.5 kV transformer at the Hotel Road Substation. | 2011-02-01 | Approved | 2010-11-22
UI-08-T05-Rev. 1 | 2010-11-01 | Grand Avenue Switching Station | Revision of PPA UI-08-T05 as approved by the Reliability Committee on December 18, 2008. PPA revision reflects a repositioning of some bays of the proposed breaker and a half configuration. | 2010-12-01 | Approved | 2010-11-22
PP-06-T01 | 2010-10-27 | Waterside Generation Station | Intent to withdraw PP-08-T01 due to the withdrawal of the Waterside Generator and Transmission Project.. | 2010-12-01 | Approved Withdrawn | 07/25/2006 11/17/2006
PP-06-G01 | 2010-10-27 | Waterside Generation Station | Intent to withdraw PP-08-G01 due to the withdrawal of the Waterside Generator and Transmission Project.. | 2010-12-01 | Approved Withdrawn | 07/25/2006 11/17/2006
CMP-10-T03 | 2010-11-01 | Bowman Street Substation | Addition of a second 20/37 MVA 115/34.5 kV transformer at Bowman Street Substation. | 2011-02-01 | Approved | 2010-11-22
NEP-10-T08 | 2010-10-27 | Meadowbrook Substation | Installation of two new 115/13.2 kV 33/44/55 MVA transformers tapped off the A-153 and I-161 lines and installation of two 115 kV circuit switchers at the Meadowbrook Substation located in Chelmsford, MA. Project upgrades tow radial 115 kV lines; I161 and A-153 to 795 ACSS from Sandy Pond, Tewksbury to Meadowbrook | 2014-06-01 | Approved | 2010-11-22
NU-09-T01-Rev.1 | 2010-11-09 | Eliot Switching Station | In conjunction with the MPRP Project, a name change of a 345 kV switching station changing from Three Rivers to Eliot and a change of the in service date of the project from June 2012 to December 2013. | 2013-12-01 | Approved | 2010-11-22
CMP-09-T05 | 2010-11-09 | Browns Crossing Substation | Withdrawal of the Browns Crossing Substation to remove the existing 115/12.47 kV substation and replace it with a 34.5 kV distribution substation, to make room on the right-of-way for new facilities. Browns Crossing load will be fed 34.5 kV out of Bowman Street. | 2010-12-01 | Approved | 2010-11-22
CMP-08-T29-Rev.1 | 2010-11-09 | Section 80 Transmission Line | Withdrawal of the Rebuild Existing Transmission Line Section 80, entire 23 miles from Coopers Mills Substation to Highland Substation, to create space in the Right-Of-Way to facilitate construction of new facilities. | 2010-12-01 | Approved | 2010-11-22
CMP-08-T23-Rev.1 | 2010-11-09 | Cape Substation | Withdrawal of the Cape Substation to add a new 115 kV breaker at the existing Cape Substation for terminating the new 115 kV line Section 263 from East Deering Substation. | 2010-12-01 | Approved | 2010-11-22
CMP-08-T12-Rev.1 | 2010-11-09 | Maine Yankee Substation | Withdrawal of the Maine Yankee 345 kV Substation to add a third bay to the existing breaker-and-a-half Substation, add four new 345 kV breakers, and re-terminate line Sections 375, 377, and 392. | 2010-12-01 | Approved | 2010-11-22
CMP-08-T10-Rev.1 | 2010-11-09 | East Deering Substation | Withdrawal of the East Deering Substation to construct a new three-breaker 115 kV ring bus for terminating a new 115 kV transmission line Section 262 from Raven Farm Substation and terminating a new 115 kV underground transmission line Section 263 approximately 4 miles in length to existing Cape Substation, and providing termination for a 115/34 kV transformer to serve the local area distribution system. | 2010-12-01 | Approved | 2010-11-22
CMP-08-T09-Rev.1 | 2010-11-09 | Highland Substation | Withdrawal of the Highland Substation to add a new 115 kV breaker at Highland to re-terminate Section 226 from Newcastle Substation. Terminate new 115 kV line Section 244 from Coopers Mills to previous Section 226 location. | 2010-12-01 | Approved | 2010-11-22
CMP-09-T07-Rev.1 | 2010-11-09 | Section 250 Transmission Line | Rebuild of the first 10 miles of existing Section 250 out of Three Rivers Substation to create space in the Right-Of-Way to facilitate construction of new facilities. Total Section 250 line distance is 19.5 miles, with remaining 9.5 miles composed of 795 kcmil ACSR 36/1 Coot conductor | 2013-04-01 | Approved | 2010-11-22
CMP-09-T06-Rev.1 | 2010-11-09 | Section 160 Transmission Line | Reconductor of 1.1 miles of existing Section 160 out of Cape Substation to Hinckley Pond Substation for thermal capacity | 2013-12-01 | Approved | 2010-11-22
CMP-09-T03-Rev.1 | 2010-11-09 | Monmouth Substation | Construct a new 115 kV Monmouth Substation consisting of two 115 kV breakers to split the existing Section 212 into two segments. Terminate Section 212 from Larrabee Road, terminate Section 269 from Bowman Street, and terminate two distribution transformers. This substation will serve the load presently served from Days Corner and Wales Corner Substations, which will be retired, along with the removal of 21.6 miles of 34 kV Section 41. | 2012-09-01 | Approved | 2010-11-22
CMP-09-T02-Rev.1 | 2010-11-09 | Middle Street Substation | Construct a new five breaker 115 kV Substation, configured initially as a ring-bus, to terminate a new 115 kV line Section 255 to Larrabee Road Substation, a new 115 kV underground circuit Section 256 to Lewiston Lower Substation, and three distribution transformers. | 2012-07-01 | Approved | 2010-11-22
CMP-08-T36-Rev.2 | 2010-11-09 | Section 212 Transmission Line | Rebuild of the entire 21.9 miles of existing Section 212, from Bowman Street Substation to the new Larrabee Road Substation to create space in the Right-Of-Way to facilitate construction of new facilities. The rebuilt line will terminate at Monmouth S/S and be renamed to Section 269 between Bowman Street and Monmouth. | 2012-08-01 | Approved | 2010-11-22
CMP-08-T35-Rev.2 | 2010-11-09 | Section 229 Transmission Line | Rebuild of the first 13.9 miles of existing Section 229 from Rumford IP Substation to Riley Substation to create space in the Right-Of-Way to facilitate construction of new facilities. Total Section 229 line distance is 15.2 miles with the remaining 1.3 miles composed of 795 kcmil ACSR 36/1 Coot conductor. | 2012-02-01 | Approved | 2010-11-22
CMP-08-T34-Rev.2 | 2010-11-09 | Section 89 Transmission Line | Rebuild of the first 5.1 miles of existing Section 89 from Livermore Falls Substation to Riley Substation, to create space in the Right-Of-Way to facilitate construction of new facilities. Total Section 89 line distance is 7.4 miles, with the remaining 2.3 miles composed of 795 kcmil ACSR 36/1 Coot conductor. | 2011-10-01 | Approved | 2010-11-22
CMP-08-T33-Rev.2 | 2010-11-09 | Section 88 Transmission Line | Rebuild of the first 4.9 miles of existing Section 88 out of Coopers Mills Substation to create space in the Right-Of-Way to facilitate construction of new facilities. Total Section 88 line distance from Coopers Mills to Augusta East Side is 11 miles, with the remaining 6.1 miles composed of 795 kcmil ACSR 36/1 Coot conductor. | 2011-12-01 | Approved | 2010-11-22
CMP-08-T32-Rev.2 | 2010-11-09 | Section 60 Transmission Line | Rebuild of the entire 12.4 miles of existing Section 60 from Coopers Mills Substation to Bowman Street Substation to create space in the Right-Of-Way to facilitate construction of new facilities. | 2011-11-01 | Approved | 2010-11-22
CMP-08-T31-Rev.2 | 2010-11-09 | Section 167 Transmission Line | Rebuild of the first 3.0 miles of existing Section 167 out of Surowiec Substation to create space in the Right-Of-Way to facilitate construction of new facilities. Total Section 167 line distance from Surowiec to Moshers is 21.0 miles, with the remaining 18.0 miles composed of 795 kcmil ACSR 36/1 Coot conductor (16.9 miles) and 795 kcmil ACSR 26/7 Drake conductor (1.1 miles). | 2011-06-01 | Approved | 2010-11-22
CMP-08-T30-Rev.1 | 2010-11-09 | Section 166 Transmission Line | Rebuild of the first 3.2 miles of existing Section 166 out of Surowiec Substation to create space in the Right-Of-Way to facilitate construction of new facilities. Total Section 166 line distance from Surowiec to Spring Street is 24.2 miles, with the remaining 21.0 miles composed of 795 kcmil ACSR 36/1 Coot conductor (19.8 miles) and 795 kcmil ACSR 26/7 Drake conductor (1.21 miles). | 2011-08-01 | Approved | 2010-11-22
CMP-08-T26-Rev.2 | 2010-11-09 | Section 203 Transmission Line | Rebuild of the first 25 miles of existing Section 203 out of Detroit Substation to create space in the Right-Of-Way to facilitate construction of new facilities. Total Section 203 line distance from Detroit to Bucksport is 34.1 miles, with the remaining 9.1 miles composed of 795 kcmil ACSR 36/1 Coot conductor (8.6 miles) and 795 kcmil ACSR 30/19 Mallard conductor (0.5 miles). | 2012-02-01 | Approved | 2010-11-22
CMP-08-T24-Rev.2 | 2010-11-09 | Section 66 Transmission Line | Rebuild of the first 1.8 miles of existing Section 66 out of Detroit Substation to create space in the Right-Of-Way to facilitate construction of new facilities. Total Section 66 line distance from Detroit to Wyman Hydro is 33.4 miles, with the remaining 31.6 miles composed of 795 kcmil ACSR 36/1 Coot conductor. | 2011-03-01 | Approved | 2010-11-22
CMP-08-T22-Rev.2 | 2010-11-09 | Livermore Falls Substation | Livermore Falls Substation to construct a three-bay breaker-and-a-half substation with eight 115 kV breakers to terminate existing Sections 63 from Sturtevant, 89 from Riley, 200 from Larrabee Road, and new Sections 251 from Larrabee Road and 243A from Rumford IP; and termination of existing 115/34.5 kV and 115/12 kV distribution transformers to serve the local distribution load. | 2013-07-01 | Approved | 2010-11-22
CMP-08-T21-Rev.3 | 2010-11-09 | Rumford Industrial Falls Substation | Install two new 115 kV line switches on the proposed CMP 115 kV Section 243 from Rumford 115 kV Substation to Rumford IP Substation to create a junction near Rumford IP Substation. Install a third 115 kV line switch to terminate a new 115 kV transmission line Section 243A from Livermore Falls at the junction of Section 243. | 2012-08-01 | Approved | 2010-11-22
CMP-08-T19-Rev.2 | 2010-11-09 | Larrabee Road Substation | Construct a new 345 kV and 115 kV substation to NPCC BPS standards. Construct a two-bay breaker-and-a-half substation with six 345 kV breakers to terminate new 345 kV transmission line Sections 3025 from Coopers Mills Substation and 3026 from Surowiec Substation; and termination of a new 240/448 MVA 345/115/13.8 kV autotransformer with two 40 MVAR reactors connected on the tertiary winding. Construct a five-bay breaker-and-a-half substation with fifteen 115 kV breakers to terminate existing Sections 61 from Norway, 64 from Surowiec, 200 from Livermore Falls, 201 from Crowleys, 212 from Monmouth (new substation), and 268 from Gulf Island and new Sections 251 from Livermore Falls and Sections 255 from Middle Street; and relocation of an existing 30 MVAR switched capacitor bank. | 2014-08-01 | Approved | 2010-11-22
CMP-08-T18-Rev.2 | 2010-11-09 | Gulf Island Substation | Remove terminations for existing 115 kV line Sections 61, 64, 200, 201, and 212 (reterminate at new Larrabee Road Substation). Relocate 30 MVAR 115 kV capacitor bank to new Larrabee Road Substation. Section 268 from Larrabee Road Substation to Gulf Island Substation will supply the existing 115/34.5 kV transformer at Gulf Island. Section 268 is a partially new 115 kV transmission line comprised of a 1.0 mile segment from the old Section 212 with 795 kcmil ACSR 36/1 Coot conductor and a 0.4 mile segment of new 115 kV overhead transmission line built with 1113 kcmil ACSR 45/7 Bluejay conductor. | 2013-05-01 | Approved | 2010-11-22
CMP-08-T17-Rev.2 | 2010-11-09 | Lewiston Lower Substation | Remove existing 115/34.5 kV transformer (T5) and terminations. Add a new 115 kV breaker to terminate the new 115 kV underground Section 256 from the new Middle Street Substation. | 2012-06-01 | Approved | 2010-11-22
CMP-08-T16-Rev.2 | 2010-11-09 | Maguire Road Substation | Construct a new 345 kV Switchyard to NPCC BPS standards. Construct a two-bay breaker-and-a-half substation with six 345 kV breakers to terminate new 345 kV transmission line Sections 3021 from South Gorham Substation and 3022 from Eliot Substation; and termination of a new 240/448 MVA 345/115/13.8 kV autotransformer. Construct an additional breaker-and-a-half bay onto existing 115 kV substation with addition of two new 115 kV breakers to terminate autotransformer. New 345 kV transmission line Section 3021 is approximately 21 miles in length to South Gorham Substation and new 345 kV transmission line Section 3022 approximately 19.2 miles in length to the Eliot Switching Station. | 2011-12-01 | Approved | 2010-11-22
CMP-08-T15-Rev.2 | 2010-11-09 | South Gorham Substation | Construct a new 345 kV and 115 kV substation to NPCC BPS standards. (Note: South Gorham exists today as a tap to Section 386 and is designed and built to BPS standards), and shall consist of an eight-breaker 345 kV three-bay breaker-and-a-half bus configuration and provide termination for a new 345 kV transmission line Section 3021 approximately 21 miles in length to Maguire Road Substation, provide for terminating the existing line Sections 3040 to Raven Farm Substation and 386 to Buxton Substation, provide for the termination of one existing 240/448 MVA 345/115/13.8 kV autotransformer (T1) and the termination of a second new 240/448 MVA 345/115/13.8 kV autotransformer (T2) with low-side (115 kV) breaker. Replace twelve existing 115 kV definite purpose breakers with Independent Pole Tripping (IPT) breakers to mitigate short-circuit and TRV requirements (K219-1, K220-1, K223-1, KT1L, K162/219, K169/220, K223/231, K162-3, K169-3, K231-1, KT2L, KB2/CAP). Also, rebuild 1.7 miles of existing Section 238 between Louden and Maguire Road to create space in the Right-Of-Way to facilitate construction of new facilities. | 2011-07-01 | Approved | 2010-11-22
CMP-08-T13-Rev.2 | 2010-11-09 | Surowiec Substation | Add eight new 345 kV breakers, with one of these new breakers an upgrade of breaker K374/377 to Independent Pole Tripping (IPT) capability, to the existing 345 kV bus to create a four-bay, breaker and-a-half configuration; terminate a new 345 kV transmission line Section 3026 from the new Larrabee Road Substation; terminate a new 345 kV transmission line Section 3020 from the new Raven Farm Substation; and split line Section 375 into two line segments, Section 375 to Maine Yankee Substation and Section 3038 to Buxton Substation, and terminate both line Sections into the new Surowiec 345 kV bus arrangement. Provide termination for the two existing 345 kV transmission lines Section 374 and Section 377, and the existing 240/448 MVA 345/115/13.8 kV autotransformer (T1). In addition, install one 115 kV breaker to create a two breaker bay for terminating Section 208 from Raymond Substation. | 2013-04-01 | Approved | 2010-11-22
CMP-08-T08-Rev.2 | 2010-11-09 | Belfast 115 kV Substation | Addition of two 115 kV breakers to the existing 115 kV bus to split Section 86 into two segments and build new 115 kV line from the right-of-way into the Belfast Substation. This will allow for termination of Section 86 from Bucksport Substation and Section 266 from Lincolnville. Addition of a 10.8 MVAR capacitor bank and associated breakers on the 34.5 kV bus. | 2014-09-01 | Approved | 2010-11-22
CMP-08-T04-Rev.2 | 2010-11-09 | Albion Road Substation | Construct a new 345 kV and 115 kV substation to NPCC BPS standards. Construct a three breaker 345 kV ring bus to terminate new 345 kV transmission line Sections 3023 from Orrington Substation and 3024 from Coopers Mills Substation; and termination of a new 240/448 MVA 345/115/13.8 kV autotransformer with two 40 MVAR reactors connected on the tertiary winding. Construct a four-bay breaker-and-a-half substation with ten 115 kV breakers to terminate existing Sections 67 from Detroit, 84 from Winslow, 259 (formerly 67A) from Heywood Road, 257 (formerly 67) from Coopers Mills and 258 (formerly 84) from Coopers Mills | 2014-03-01 | Approved | 2010-11-22
CMP-10-T07 | 2010-11-09 | Section 375/377 Double Circuit Tower | Section 377 will be removed from the double circuit structures with Section 375 and added to a new double circuit structure that will also accommodate 115 kV Section 81 for 2.5 miles. | 2013-06-01 | Approved | 2010-11-22
CMP-10-T06 | 2010-11-09 | Section 65/205 Double Circuit Tower | Separation from Bucksport Substation to Orrington Substation. | 2012-12-01 | Approved | 2010-11-22
CMP-10-T05 | 2010-11-09 | Norway Substation | Replace existing 115 kV line switch 61-4 and circuit switcher K87-1 at Norway Substation with 115 kV circuit breakers to terminate existing Section 61/61A to Larrabee Road and Hotel Road Substations, and Section 87 to Kimball Road Substation. This substation will continue to serve the load presently served from Norway’s 34.5 kV and 12 kV busses. | 2014-09-01 | Approved | 2010-11-22
CMP-10-X04 | 2010-11-09 | Orrington T1 SPS | Retirement of the Orrington T1 Special Protection System (SPS), NPCC #182 – Type III. | 2014-07-01 | Approved | 2010-11-22
CMP-10-X03 | 2010-11-09 | Bucksport 65/205/Reverse Power SPS | Retirement of the Bucksport 65/205 Reverse Power Special Protection System (SPS), NPCC #22 – Type III. | 2014-07-01 | Approved | 2010-11-22
CMP-10-X02 | 2010-11-09 | Section 386 SPS | Retirement of the Section 386 Temporary Special Protection System (SPS), NPCC #198 – Type I. | 2012-12-01 | Approved | 2010-11-22
CMP-10-X01 | 2010-11-09 | Maxcy/Bucksport SPS | Retirement of the Maxcys - Bucksport Special Protection System (SPS), NPCC #178 – Type I. | 2014-07-01 | Approved | 2010-11-22
CMP-09-T04-Rev.1 | 2010-11-09 | Spring Street Substation | Remove terminations for 115 kV Sections 232 from Westbrook Substation and Section 234 from Redbrook and connect these two circuits together in Right-of-Way. The newly formed circuit connecting Westbrook to Redbrook will be designated as Section 234. | 2014-12-01 | Approved | 2010-11-22
CMP-08-T37-Rev.2 | 2010-11-09 | Section 86 Transmission Line | Rebuild of an 8.7 mile portion and reconductor a 0.5 mile portion of existing Section 86 between Bucksport Substation and Section 86A tap and new 0.25 mile line into Belfast 115 Substation to uprate thermal capacity. The reconductor preserves the existing structures that comprise the Penobscot River crossing leaving Bucksport. Total Section 86 line distance from Bucksport to Belfast is 15.7 miles, with the remaining 6.2 miles composed of 1272 kcmil AAC 61/0 Narcissus. | 2011-05-01 | Approved | 2010-11-22
CMP-08-T25-Rev.2 | 2010-11-09 | Section 67 Transmission Line | Rebuild of the first 1.8 miles of existing Section 67 out of Detroit Substation and additional 1.3 mile and 0.3 mile segments to create space in the Right-Of-Way to facilitate construction of new facilities. Total Section 67 line distance from Detroit to Albion Road is 19.4 miles, with the remaining 16.0 miles composed of 795 kcmil ACSR 26/7 Drake conductor. Rebuild segments totaling 10.4 miles of Section 67 between Albion Road and Coopers Mills Substation which is redesignated to Section 257 to create space in the Right-Of-Way to facilitate construction of new facilities. Total Section 257 line distance from Albion Road to Coopers Mills is 21.2 miles, with the remaining 10.8 miles composed of 795 kcmil ACSR 26/7 Drake conductor | 2011-02-01 | Approved | 2010-11-22
CMP-08-T27-Rev.2 | 2010-11-09 | Section 84 Transmission Line | Rebuild of a 12.3 mile portion of existing Section 84 between Coopers Mills Substation and Albion Road Substation (now designated Section 258) and utilize 8.9 miles of existing Section 67 to create space in the Right-Of-Way to facilitate construction of new facilities. The remaining 4.7 miles from Albion Road Substation to Winslow Substation is unchanged and remains designated Section 84. | 2014-10-01 | Approved | 2010-11-22
CMP-08-T14-Rev.2 | 2010-11-09 | New Raven Farm Substation | Construct a new 345 kV substation to NPCC BPS standards. Construct a two-bay breaker-and-a-half substation with four 345 kV breakers to terminate existing 345 kV transmission line Sections 3040 from South Gorham and 3039 from W.F. Wyman Substations (Section 386 between South Gorham and W.F. Wyman split into two segments – 3039 and 3040) and new 345 kV transmission line Section 3020 to Surowiec Substation. The Raven Farm Substation shall be operated as a ring bus but configured for a future full breaker-and-a-half layout | 2013-03-01 | Approved | 2010-11-22
CMP-08-T11-Rev.2 | 2010-11-09 | Coopers Mill Substation | Construct a new 345 kV and 115 kV substation to NPCC BPS standards and replace the existing Maxcys Substation. Construct a three-bay breaker-and-a-half substation with nine 345 kV breakers to terminate existing 345 kV transmission line Sections 388 from Orrington Substation and 392 from Maine Yankee Substation and new 345 kV transmission line Sections 3024 from Albion Road Substation and 3025 from Larrabee Road Substation; and termination of a new 240/448 MVA 345/115/13.8 kV autotransformer with two 40 MVAR reactors connected on the tertiary winding. Construct a five-bay breaker-and-a-half substation with fifteen 115 kV breakers to terminate existing Sections 80 from Highland, 60 from Bowman St., 68 from Mason, 88 from Augusta East Side, 257 (formerly 67) from Albion Road and 258 (formerly 84) from Albion Road and new Section 254 from Orrington; termination of existing 115/34.5 kV distribution transformer; and termination of the two existing 50 MVAR switched capacitor banks. | 2014-08-01 | Approved | 2010-11-22
CMP-08-T03-Rev.2 | 2010-11-09 | Orrington Substation | Install one 345 kV breaker in existing two-bay breaker-and-a-half for retermination of existing 345 kV line Section 388 from Coopers Mills Substation (formerly Maxcys) which will also utilize partial new construction to location in Right-of-Way near the junction of 115 kV Section 203. The new Section 3023 between Orrington Substation and Albion Road Substation (to pass by Detroit Substation with no termination) will utilize the existing structures and conductors of Section 388 from Orrington to the junction of Section 203. Install two 115 kV breakers in a new fourth-bay of the breaker-and-a-half substation, and build a new 115 kV line, Section 254, from Orrington to Coopers Mills Substation. 2.4 miles of existing Section 388 (portion which will become 3023) will be rebuilt at the vicinity of the Penobscot River crossing to make room on right-of way for Section 254 which will utilize existing river crossing portion of Section 388. | 2014-07-01 | Approved | 2010-11-22
UI-10-T02 | 2010-10-22 | New Haven Harbor Transmission Line | Terminate and connect the 115 kV underground line connecting the New Haven Harbor Peaking Plant to the East Shore 115 kV Substation with the installation of two additional 115 kV 3000 A 63 kA circuit breakers at East Shore 115 kV Substation to accommodate the generation interconnection. | 2012-06-01 | Approved | 2010-11-22
PSEG-10-T01 | 2010-10-22 | New Haven Harbor Transformer | Installation of a 13.8/115 kV Step Up Transformer and 1000 ft. underground transmission interconnection to the East Shore 115 kV Substation. | 2012-06-01 | Approved | 2010-11-22
PSEG-10-G01 | 2010-10-22 | New Haven Harbor Generator | Construction and interconnection of three GE LM6000 gas turbine generators each rated at 71.176 MVA and 51 MWs. Total gross output totals for a 153 MW located in New Haven, CT. | 2012-06-01 | Approved | 2010-11-22
VELCO-10-T06 | 2010-10-29 | Bennington Substation | Rebuild of the existing straight bus Bennington substation to a new 6 breaker ring substation connecting two 115 kV lines, one 115/69 kV transformer and two 115/46 kV step down transformers. | 2013-03-01 | Approved | 2010-11-22
VELCO-10-T05 | 2010-10-29 | Ascutney Substation | Rebuild of the existing straight bus Asuctney substation to a new 6 breaker ring substation connecting four 115 kV lines and a 115/46 kV step down transformer. | 2013-03-01 | Approved | 2010-11-22
VELCO-10-T04 | 2010-10-29 | Georgia Substation | Rebuild of the existing straight bus Georgia substation to a new 6 breaker ring substation connecting four 115 kV lines, one 25 MVAR capacitor bank and a future 115/34.5 kV step down transformer (to be added one year later). | 2013-03-01 | Approved | 2010-11-22
NU-10-T20 | 2010-10-12 | 310-348 & 371-383 Double Circuit Towers and Retire Milstons SLOD SPS | Split the 310-348 and 371-383 double circuit towers and eliminate the associated double circuit tower contingencies. The 310-348 double circuit tower construction extends north out of the Millstone 345-kV Substation approximately four miles while the 371-383 double circuit tower construction extends north out of Millstone 345-kV Substation approximately two miles. Project includes change in conductor type on #310 circuit to 2-1272 ACSS and #371 circuit to 2-954 ACSS. This Project will include the retirement of the Millstone Severe Line Outage Detection (SLOD) Special Protection System (SPS) once the configuration of the 345-kV lines has been completed. The SLOD SPS is a Northeast Power Coordinating Council (NPCC) Type I SPS (NPCC SPS #23). | 2013-12-01 | Approved | 2010-11-02
NMLD-10-T02 | 2010-10-08 | Dean Street 495 Substation | Replace aging transformers A & B and install new transformer D. Also install 5th and 6th circuit breakers in existing 115 kV ring bus to interconnect third transformer. | 2010-11-30 | Approved | 2010-11-02
NMLD-10-T01 | 2010-10-08 | Ellis Avenue 469 Substation | Expansion of the Ellis Ave. #469 Substation in Norwood, MA, to add six 13.8 kV distribution feeders for use by NSTAR. Install third 33/44/55 MVA, 115 kV to 13.8 transformer and related 115 kV switching equipment. Also install 5th and 6th circuit breakers in existing 115 kV ring bus to interconnect third transformer. | 2010-11-05 | Approved | 2010-11-02
RMLD-10-T01 | 2010-09-27 | Reading 494 Substation | Replacement of three existing Reading 115/13.8 kV transformers at the Reading 494 Substation with larger transformers (36/48/60 MVA). | 2010-10-01 | Approved | 2010-11-02
VELCO-10-T03 | 2010-10-04 | Essex Switch | Operate the Essex #230 switch normally closed. | 2011-03-01 | Approved | 2010-11-22
VELCO-10-T02 | 2010-10-04 | West Rutland Substation | Installation of two 25 MVAR capacitor banks at the West Rutland 115 kV substation to resolve criteria violations for contingencies, in particular the loss of the Coolidge – West Rutland 345 kV line. | 2012-03-01 | Approved | 2010-11-22
BHE-10-T03 | 2010-10-01 | Orrington Substation | Add a series breaker adjacent to existing Orrington breaker K396-1 such that a line fault on 396 and a stuck breaker K396-1 would not result in the loss of the Orrington T1 autotransformer, potentially resulting in loss of all three autotransformers on the BHE system. | 2012-12-01 | Approved | 2010-10-22
BHE-10-T02 | 2010-10-01 | Keene Road Substation | Installation of a top rated 300MVA autotransformer between the Keene Rd 345kV and Keene Rd 115kV facilities. This includes the addition of several breakers at the Keene Rd 115kV substation to complete the breaker and half scheme as well as the enabling of transmission protection schemes at the Keene Rd 345kV substation such that the 396 and 3001 line sections will operate independently. The circuit breaker between the Chester SVC and the new autotransformer will be operated normally open. This PPA compliments previously approved BHE-10-T01 to complete the Keene Rd facility. | 2010-12-01 | Approved | 2010-10-22
NU-10-T19 | 2010-08-24 | Southwick Substation | Replace two existing transformers (115/14.4 kV (1X) and 114/13.8 kV (2X)) at the Southwick 29A substation. New transformers will be rated at 110/23 kV. The proposed in service date for the 2X transformer is 2011 and the proposed in service date for the 1X transformer is 2013. | 2011 & 2013 | Approved | 2010-09-28
BHE-10-G01 | 2010-09-14 | PPL Great Works Generation Station | Reconnect 9.5MW gas turbine “behind the fence” generation at a mill complex in Old Town Maine (aka Red Shield/Old Town – Asset ID#12163). The facility presently has ISO-NE approval to export up to 16MW and requests the ability to not only interconnect the noted generator, but to expand this export capability to 27.1 MWs. | 2010-09-30 | Approved | 2010-09-28
NU-10-T09 | 2010-09-03 | Agawam 16C Substation | Modifications at Agawam 16C 115-kV substation to make it NPCC Bulk Power System (BPS) compliant. This is required for the Pioneer Valley Energy Center generator to interconnect to the pre-NEEWS/GSRP system. | 2013-12-01 | Approved | 2010-11-02
NU-10-T08 | 2010-09-03 | East Springfield 5J Substation | Modifications at East Springfield 5J substation to make it NPCC Bulk Power System (BPS) compliant. This is required for the Pioneer Valley Energy Center generator to interconnect to the pre-NEEWS/GSRP system. | 2013-12-01 | Approved | 2010-11-02
NU-10-T07 | 2010-09-03 | Buck Pond 34B Substation | Upgrade the following terminal equipment at Buck Pond substation for the 1657 (Buck Pond to Southampton Jct.) line terminal to match or exceed the conductor ratings: substation conductor, manual switch, wave trap, primary and back up relays and metering. Upgrading the terminal equipment will result in the 1657 (Buck Pond to Southampton Jct.) line conductor being the limiting facility. | 2013-12-01 | Approved | 2010-11-02
NU-10-T06 | 2010-09-03 | Buck Pond 34B Substation | Upgrade the following terminal equipment at Buck Pond 34B substation for the 1302 (Buck Pond to PVEC) line terminal to match or exceed the conductor ratings: substation conductor, manual switch, wave trap, primary and backup relays and metering. Upgrading the terminal equipment will result in the 1302 (Buck Pond to PVEC) line conductor being the limiting facility. This assumes that the Pioneer Valley Energy Center generator will back down its generation (manually) in 15 minutes such that the loading is below the line LTE rating during emergency operating conditions. | 2013-12-01 | Approved | 2010-11-02
NU-10-T05 | 2010-09-03 | Agawam 16C Substation | Upgrade the following terminal equipment at Agawam 16C substation for the 1302 (Agawam to Pochassic tap) line terminal to match or exceed the conductor ratings: substation conductor, manual switch, wave trap, Watt/VAR transducer inside breaker 16C-35T-2 control cabinet, primary and backup relays and metering. Upgrading the terminal equipment will result in the 1302 (Agawam to Pochasstap) line conductor being the limiting facility. This assumes that the Pioneer Valley Energy Center generator will back down its generation (manually) in 15 minutes such that the loading is below the line LTE rating during emergency operating conditions upgrade the following terminal equipment at Buck Pond 34B substation for the 1302 (Buck Pond to PVEC) line terminal to match or exceed the conductor ratings: substation conductor, manual switch, wave trap, primary and backup relays and metering. Upgrading the terminal equipment will result in the 1302 (Buck Pond to PVEC) line conductor being the limiting facility. This assumes that the Pioneer Energy Center generator will back down its generation (manually) in 15 minutes such that the loading is below the line LTE rating during emergency operating conditions. | 2013-12-01 | Approved | 2010-11-02
NU-10-T04 | 2010-09-03 | Fairmont 16H Switching Station | upgrade Fairmont 16H switching station to be NPCC Bulk Power System (BPS) compliant by adding a second DC system. This is required for the Pioneer Valley Energy Center generator to interconnect to the post-NEEWS/GSRP system. | 2013-12-01 | Approved | 2010-11-02
NU-10-T03 | 2010-09-03 | Pioneer Valley Switching Station | Installation of a new four breaker 115 kV switching station in a ring bus configuration consisting of four 115 kV 40 kA circuit breakers associated breaker disconnects, control house, and protection and controls. Loop line 1302 (between Buck Pond and Pochassic tap) into the new switching station and terminate to establish new lines from Buck Pond 34B substation to PVEC switching station (length approximately 1.0 mile) and from Pochassic substation tap to PVEC switching station (length approximately 2.12 miles). Also, terminate the leads for the steam turbine generator step-up transformer and the gas turbine generator step-up transformer into the new switching station. | 2013-12-01 | Approved | 2010-11-02
EMI-10-X01 | 09/072010 | Pioneer Valley Energy Center SPS | Special Protection System (SPS) SPS to protect against loading in excess of DAL on HG&E lines (1657, 1292 &1525) in the event of the loss of the 1302 south coupled with a loss of both the 1327&1428 lines due to a DCT failure with Mt. Tom generating at full capacity. | 2013-12-01 | Approved Withdrawn | 11/2/2010 12/18/2012
EMI-10-T02 | 2010-09-07 | Pioneer Valley Energy Center Substation | Generator Step Up Transformer to interconnect the PVEC Steam Turbine generator to the PVEC substation at the 115 kV 1302 transmission line between Buck Pond and Pochassic substations. | 2013-12-01 | Approved Withdrawn | 11/2/2010 12/18/2012
EMI-10-T01 | 2010-09-07 | Pioneer Valley Energy Center Substation | Generator Step Up Transformer to interconnect the PVEC Combustion Turbine generator to the PVEC substation at the 115 kV 1302 transmission line between Buck Pond and Pochassic substations. | 2013-12-01 | Approved Withdrawn | 11/2/2010 12/18/2012
EMI-10-G01 | 2010-09-07 | Pioneer Valley Energy Center Generation Station | Construction and interconnection for a 400 MW combined cycle generator in Westfield, MA. | 2013-12-01 | Approved Withdrawn | 11/2/2010 12/18/2012
BHE-08-T03 | 2010-09-08 | Keene Road Substation | Withdrawal of the Keene Rd PPA (BHE-08-T03). This application (recommended for approval by the NEPOOL RC November 2008) has been superseded by the BHE-10-T01 (see above) and a future PPA that will address the related 115kV changes and the addition of the auto transformer. | 2010-12-01 | Approved | 2010-09-21
BHE-10-X01 | 2010-09-08 | Chester SVC | Disable the Chester Static VAR Compensator (SVC) Supplemental Modulation Control (SMC – a.k.a SMF). This control was added to the SVC, as part of the original installation, to permit better coordination with what was commonly known as the Keswick GCX SPS. The GCX SPS was removed from service with the installation of the Northeast Reliability Interconnect Project (NRI – line 390) in 2007. Recent studies associated with the Keene Rd project were performed with Keene Rd in-service and the system changes associated with the NRI, as well as with and without the planned MPRP changes. These studies indicated that there was unacceptable system response with the SMC in service, and acceptable response with the SMC removed from service. | 2010-10-01 | Approved | 2010-09-21
BHE-10-T01 | 2010-09-08 | Keene Road Substation | Add breakers into Line 396 near the Chester SVC. These breakers will initially be installed such that their operation imitates the present line configuration with respect to line faults and relay response. It is anticipated that an additional application will be brought forward with the addition of a transformer at this facility, at which time the protection and operation of the Keene Road 345kV breakers will be modified to be in line with that application. | 2012-10-01 | Approved | 2010-09-21
CMP-10-T02 | 2010-09-09 | Starks Switching Station | Addition of four 115 kV circuit breakers in a breaker and a half configuration and two 18 MVAR capacitor bank at a new Starks Switching Station. | 2012-12-01 | Approved | 2010-09-28
NU-10-T18 | 2010-07-14 | Lost Nation - Paris Drummer Transmission | Upgrade of the 12.5 mile overhead 115 kV O154 Line from Lost Nation - Northumberland, NH to Paris-Drummer NH. | 2012-10-01 | Approved | 2010-08-25
NU-10-T17 | 2010-07-14 | Lost Nation - Whitefield Transmission | Upgrade of the 18 mile overhead 115 kV D142 Line from Lost Nation - Northumberland, NH to Whitefield NH. | 2012-10-01 | Approved | 2010-08-25
NU-10-T16 | 2010-07-14 | Berlin - Whitefield Transmission | Upgrade of the 27 mile overhead 115 kV S136 Line from Berlin, NH to Whitefield NH. | 2012-10-01 | Approved | 2010-08-25
NU-10-T15 | 2010-07-14 | Berlin Substation | Installation of a generator step up transformer rated at 48/64/80 MVA, 13.8/118 kV, 0.92 mile 115 kV circuit. In addition, installation of a 115 kV circuit breaker connection to the 115 kV Berlin Substation. | 2012-10-01 | Approved | 2010-08-25
NU-10-G04 | 2010-07-14 | Laidlaw Berlin Biopower Generator | Construction of a 65.9 MW wood fired biomass generator interconnecting to the Berlin Substation in Berlin, NH | 2012-10-01 | Approved | 2010-08-25
NU-10-T14 | 2010-07-13 | Berlin Substation | Installation of a generator step up transformer rated at 30/36 MVA, 13.8/115 kV, 0.5 mile 115 kV circuit. In addition, installation of a 115 kV circuit breaker connection to the 115 kV Berlin Substation. | 2012-09-01 | Approved | 2010-08-25
NU-10-G03 | 2010-07-13 | CPD Berlin Biomass Generator | Construction of a 29 MW wood fired biomass generator interconnecting to the Berlin Substation in Berlin, NH. | 2012-08-01 | Approved | 2010-08-25
NU-10-G02 | 2010-07-08 | Bradley Energy Center | Installation of a 1.8 MW natural gas fired generator to the existing Bradley Energy Center Generators (new total output is 5.65 MWs net) interconnecting at the 27.6 kV Enfield 12C Substation feeder 12C48 located in Windsor Locks, CT. | 2010-07-18 | Approved | 2010-07-27
SG-10-G01 | 2010-07-01 | Waterbury Generator Station | Capacity increase for the Waterbury generator of 7.8 MWs (50 degrees) and 5.5 MWs (0 degrees) located in Waterbury, CT. | 2010-08-01 | Approved | 2010-07-27
NU-10-T13 | 2010-07-09 | Derry Transformer | Construction of a new 30 MVA 115/12.47 kV transformer in Derry, NH. | 2011-12-01 | Approved | 2010-07-27
NU-10-T12 | 2010-07-09 | Thorton Substation | Construction of a new Thornton Substation with a 44.8 MVA 115/34.5 kV transformer for the Merrimack, NH area to eliminate distribution issues in the area. | 2012-06-01 | Approved | 2010-07-27
UI-10-G03 | 2010-06-07 | Milford Fuel Cell | Construction of three gas-fired fuel cell generators, each rated at 2.8 MWs and a gas fired induction generator with an output of 1.8 MWs (10.2.MWs total) located in Milford CT. Project will interconnect at the UI 13.8 kV distribution system at Milton 115/13.8 kV substation via two 13.8 kV circuits. In addition, a 13.8 kV isolation transformer will be utilized to interconnect each fuel cell, while a 2.5 MVA, 6/6/13.8 kV step up transformer will interconnect the generator to the 13.8 kV bus. | 2011-05-01 | Approved Withdrawn | 7/27/2010 8/15/2013
NSTAR-10-G02 | 2010-06-08 | Notis Wind I | construction of one 1.65 MW wind turbine generator interconnecting at the NSTAR Falmouth Substation #933 via a 23 kV feeder #98A located in East Falmouth, MA. | 2010-06-15 | Approved | 2010-06-17
ECO-10-G02 | 2010-06-03 | Spruce Mountain Wind | Project expansion of Spruce Mountain Wind Project (#290) for construction of one 2 MW wind turbine generators with a total output of 2 MWs to be located in Woodstock, ME. | 2010-11-01 | Approved | 2010-06-17
ECO-10-G01 | 2010-06-03 | Spruce Mountain Wind | Construction of nine 2 MW wind turbine generators with a total output of 18 MWs to be located in Woodstock, ME. | 2010-11-01 | Approved | 2010-06-17
NU-10-T11 | 2010-06-02 | Caldwell Switching Station | Construction of a 115/13.8 kV Generator Step Up (GSU) Transformer at Palmer Renewable Energy Center generating station and generator lead to interconnect to dwell 115 kV switching station. In addition, install a 115 kV, 63 kA circuit breaker at Palmer Renewable Energy Center generation station, a 115 kV, 63 kA circuit breaker at Cadwell 115 kV switching station and associated disconnect switches, protection and controls. | 2012-05-01 | Approved | 2010-06-17
NU-10-G01 | 2010-06-02 | Palmer Renewable Energy Center | Construction of a 37 MW wood burning steam generator to be located in Springfield, MA. | 2012-05-20 | Approved | 2010-06-17
MMWEC-10-T01 | 2010-05-04 | Stony Brook Substation | Installation of one 15.0/345 kV step up transformer and one 16.5/345 kV step up transformer interconnected through a single 345 kV circuit breaker to Stony Brook 54B substation 345 kV bus. In addition, install one 345 kV circuit breaker to provide switching capability/isolation for the existing Stony Brook generation. | 2014-05-31 | Approved Withdrawn | 1/17/2012 10/16/2012
MMWEC-10-G01 | 2010-05-04 | Stony Brook Generation Station | Construction of a 280 MW Combined Cycle generator located in Ludlow, MA. | 2014-05-31 | Approved Withdrawn | 1/17/2012 10/16/2012
CMP-10-T01 | 2010-04-20 | Glass Face Switching Station | Central Maine Power proposal for the construction of the Glass Face Switching Station consisting of a new 115 kV bus with one new 115 kV circuit breaker for Section 271 feeding north to Roxbury substation and one new 115 kV breaker for the Longfellow Wind Collector Substation. The new Switching Station will be located aprox. 9200 ft. from CMP’s existing Rumford 115 kV Substation. | 2011-12-01 | Approved Withdrawn | 1/17/2012 10/16/2012
FW-10-T01 | 2010-04-21 | Longfellow Wind Substation | First Wind proposal for the construction of the Longfellow Wind Collector Substation rated at 30/40/50 MVA interconnecting the Longfellow Wind Project with the new CMP S270 line by means of CMP Glass Face switching station. | 2011-12-31 | Approved Withdrawn | 1/17/2012 10/16/2012
FW-10-G01 | 2010-04-21 | Longfellow Wind Generator | First Wind proposal for the construction and installation of twenty 2.5 MW wind turbine generators totaling 50 MWs rated at 16.4 MVARs leading and lagging. Project is located in Rumford, ME. | 2011-12-31 | Approved Withdrawn | 1/17/2012 10/16/2012
VELCO-10-T01 | 2010-04-12 | Deerfield Wind Substation | Vermont Electric Company proposal for the construction of a 3 breaker ring substation connecting to the Y25 line, between the Bennington 69 kV and the Sleepy Hollow/Searsburg Wind tap. | 2011-12-01 | Approved Withdrawn | 5/24/2010 2/25/2015
IBR-10-T01 | 2010-04-12 | Deerfield Wind Transmission | Iberdrola Renewables proposal on behalf of Deerfield Wind for the construction and installation of the Deerfield Wind Collector Substation consisting of a 34.5/69 kV transformer rated at 18/24/30 MVA with an impedance of 8%, interconnecting the Deerfield Wind Project with the new CVPS 69 kV interconnection switchyard on the Bennington-Searsburg 69 kV line (Line Y25N). rated at 9.9 MVARs leading and lagging. Project is located in Bennington County, VT. | 2011-10-01 | Approved Withdrawn | 5/24/2010 2/25/2015
IBR-10-G01 | 2010-04-12 | Deerfield Wind Generator | Iberdrola Renewables proposal on behalf of Deerfield Wind for the construction and installation of fifteen 2.0 MW wind turbine generators totaling 30 MWs rated at 9.9 MVARs leading and lagging. Project is located in Bennington County, VT. | 2011-12-31 | Approved Withdrawn | 5/24/2010 2/25/2015
NEP-10-T01 | 2010-02-09 | East Main Street Transformer and Breaker | New England Power Company proposal for the installation of a 115/13.8 kV 24/32/40 MVA transformer at the East Main Street Substation located in Westborough, MA. In addition, installation of a new 0.3 mile tap line and inline breaker to loop the 115 kV E-157 line at the East Main Street Substation. | 2013 | Approved | 2010-04-26
UI-10-G02 | 2010-03-19 | Sikorsky Aircraft Generator | United Illuminating proposal for the installation a 9.2 MW Gas Turbine Generator interconnecting at the UI 13.8 kV distribution system at Trap Falls 115/13.8 kV Substation, via four 13.8 kV circuits. | 2010-08-01 | Approved | 2010-03-18
TLMP-10-T01 | 2010-02-16 | Taunton Transmission | Taunton Municipal Lighting Plant proposal to reconductor the 115 kV V-5 and S-8 tap lines interconnecting the Cleary Substation to the New England Power Company (“NGRID”) transmission lines that run from Bridgewater Substation to Somerset Substation. In addition, construct a new three bay (9 breaker) breaker and a half 115 kV substation to replace the existing ring bus in the Cleary Substation and interconnect four existing 115 kV lines, the existing and proposed generator, and distribution load. | 2013-12-31 | Approved Withdrawn | 3/18/2010 10/19/2011
TLMP-10-G01 | 2010-02-16 | Taunton Generator | Taunton Municipal Lighting Plant proposal for the construction of a new 301 MW combined cycle generator interconnecting at the Cleary Substation | 2013-12-31 | Approved Withdrawn | 3/18/2010 10/19/2011
NEP-10-T03 | 2010-02-16 | Taunton Transmission | New England Power Company proposal to upgrade the junctions of tap lines to the Cleary substation on the 115 kV V5 and S8 lines and upgrade the terminal elements of the 115 kV V5 line inside the Somerset substation and replacement of a 115 kV breaker 1620 at Bridgewater substation. | 2012-03-01 | Approved Withdrawn | 3/18/2010 10/19/2011
NU-10-T02 | 2010-03-04 | MeridenTransmission | Northeast Utility System Company Proposal for the addition of a 1.1 mile radial 345 kV line from the new three breaker 345 kV ring substation to the Meridian generating facility. | 2010-06-01 | Approved Withdrawn | 3/18/2010 8/15/2010
NU-10-T01 | 2010-03-04 | Meriden Substation | Northeast Utility System Company proposal for the addition of a three breaker, 345 kV ring bus substation by splitting the 3754 line (Southington – Beseck 345 kV line) aprox. 5 miles from the Southington 345 kV Substation. | 2010-06-01 | Approved Withdrawn | 3/18/2010 8/15/2010
NRG-10-T01 | 2010-03-04 | Meriden 345 kv Ring Bus | NRG Energy proposal for construction of a new 345 kV 3 breaker ring bus on the 3754 line (Southington-Beseck 345 kV Line). A radial 1.1 mile 345 kV transmission line will connect the project collector bus at Meridian to the new 345 kV ring bus on the 3745 Line. | 2010-06-01 | Approved Withdrawn | 3/18/2010 8/15/2010
NRG-10-G01 | 2010-03-04 | Meriden Generator | NRG Energy proposal for construction of a 510 MW (net output) combined cycle generator interconnecting to a the transmission system at a new 345 kV 3 breaker ring bus on the 3754 line (Southington-Beseck 345 kV line. | 2012-06-01 | Approved Withdrawn | 3/18/2010 8/15/2010
BMLD-10-T01 | 2010-01-07 | Belmont Substation | Belmont Municipal Light Department proposal to construct a new 115 kV to 13.8 kV distribution substation interconnected to two existing 115 kV underground cables running between North Cambridge Station and Brighton Station. Both circuits are to be extended to a ring bus in the new substation that will interconnect two new 115 kV to 13.8 kV transformers. Ring bus will be equipped with redundant high speed relaying to comply with NPCC BPS requirements. | 2012 | Approved | 2010-03-01
UI-10-G01 | 2010-01-11 | Yale Sterling Power Plant | United Illuminating proposal for the construction of two gas turbine generators, each with a net rating of 7.3 MW Winter and 6.5 MW Summer interconnecting via four 13.8 kV circuits at the UI Water Street 115/13.8 kV Substation located in New Haven, CT. | 2010-03-01 | Approved | 2010-01-21
NU-09-G03 | 2010-01-04 | Merrimack 2 Generator Uprate | Northeast Utility System Company proposal to increase the generating capacity on the Merrimack 2 generator (Asset #490) located in Bow, New Hampshire, by 17 MWs from 351.5 MWs to 368.5 MWs. | 2010-06-01 | Approved | 2010-01-21
NU-09-X05 | 2010-01-04 | Merrimack 2 PSS | Northeast Utility System Company proposal to addand enable a digital Power System Stabilizer (PSS) to the Merrimack # 2 generator located in Bow, New Hampshire. | 2010-01-01 | Approved | 2010-01-21
NSTAR-10-T01 | 2010-01-06 | West Walpole 345 kV Reactor | NSTAR Gas & Electric proposal to install a new 345 kV, 160 MVAR regulating shunt reactor in order to absorb excess reactive power and installation of a 345 kV circuit breaker with synchronous switching controller at the West Walpole Substation located in Walpole, MA. | 2010-05-01 | Approved | 2010-01-21
CMP-09-X02 | 2010-01-20 | 386 SPS | Central Maine Power proposal to Expand the existing Buxton to Yarmouth Transfer Trip on Section 386 into a Special Protection System, to due to the addition of the 345 kV breakers at South Gorham. | 2010-03-01 | Approved | 2010-01-21
NSTAR-09-T11 | 2009-12-03 | West Framingham 115 kV Capacitor Bank | NSTAR Gas & Electric addition of a new 115 kV 54 MVAR capacitor bank and 115 kV circuit breaker (#5) to switch the capacitor bank in and out of service to counter effects of low voltage due to a loss of the 455-507 from Sherborn. | 2010-06-01 | Approved | 2009-12-17
ANGEN-09-G01 | 2009-09-29 | Ansonia Generator | Ansonia Generation, LLC proposal for construction of a combined cycle generator (1 gas turbine and 1 steam turbine) with a net rating of 63 MWs Summer and 68 MWs Winter, located in Ansonia CT. | 2012-05-31 | Approved Withdrawn | 11/5/2009 5/5/2012
ANGEN-09-T01 | 2009-09-29 | Ansonia Generator Transmission Line | Ansonia Generation, LLC proposal for installation of a ¼ mile overhead 115 kV transmission line from the Ansonia Generator to the Ansonia substation located in Ansonia, CT. | 2012-05-31 | Approved Withdrawn | 11/5/2009 5/5/2012
UI-09-T02 | 2009-10-01 | Ansonia Substation | United Illuminating proposal to terminate and connect the 115 kV transmission line from the Ansonia Generator to the Ansonia 115 kV substation. Substation will be reconfigured into a three-breaker ring bus by the installation of two additional 115 kV 50 kA circuit breakers. | 2012-05-31 | Approved Withdrawn | 11/5/2009 5/5/2012
UI-09-T01 | 2009-09-28 | Shelton 115/13.8 kV Substation | Project will consist of installation of two 115 kV line terminal structures, one 115 kV SF6 gas insulated circuit breaker, twelve vertical break disconnect switches, two 30/40/50 MVA, 118/14.9 kV power transformers with load tap changers, two prefabricated Power Distribution Centers with 13.8 kV metal clad switchgear, a 13.8 kV bus duct system connecting the power transformers to the PDCs and connecting the PDCs to each other. The overhead 1560 line will be sectionalized by looping it into the Shelton Substation to result in a Shelton-Trap Falls line aprox. 3500 feet in length and a Shelton – Stevenson line aprox. 8.2 miles long. | 2013-06-01 | Approved | 2009-11-05
NU-09-T17 | 2009-09-25 | Line Reconfiguration for Shelton Substation | Looping of the 1560S line into and out of the proposed Shelton Substation. | 2013-06-01 | Approved | 2009-11-05
RPM-09-G01 | 2009-10-02 | Ridgewood CoGen Generator | Ridgewood Rhode Island Generation, LLC, proposal for construction and interconnection of six 6.3 MW Solar Taurus 60 combustion turbine generators and one 13 MW steam turbine generator totaling 49.2 MWs, located in Johnston, RI. | 2011-06-01 | Approved | 2009-11-05
RPM-09-T01 | 2009-10-02 | Ridgewood CoGen Transformer | Ridgewood Rhode Island Generation, LLC, proposal to install a 70 MVA 13.8/115 kV generator step up transformer connected to the the 115 kV system via the S-171 main line, which shares right of way with the 115 kV T-172 Hartford Avenue – Drumrock substations. | 2011-06-01 | Approved | 2009-11-05
NEP-09-T02 | 2009-10-13 | Ridgewood CoGen Substation | NGRID Proposal to construct a new 115 kV, three breaker ring bus substation in Johnson, RI. Loop in and interconnect the 171S line into the new substation an connect the Ridgewood generation plant to the new substation | 2011-06-01 | Approved | 2009-11-05
NEP-09-T04 | 2009-10-19 | Long Term Lower SEMA | Reconductor the Bell Rock to High Hill 115 kV D21 Line | Fall 2012 | Approved | 2009-11-05
NSTAR-09-T05 | 2009-10-19 | Long Term Lower SEMA | Expand the Carver 345 kV Substation with a fourth bay comprised of two 345 kV circuit breakers. Reconnect the existing #322 line into the new fourth bay position. Connect a new 345 kV line to the present #322 line position. The new 17.9 mile overhead line 345 kV line will be constructed from Carver 345 kV to the vicinity of the Bourne 115 kV Substation on existing right of way. At Bourne, the existing Canal–Barnstable #120 line will be cut and the line section from Canal will be connected to Bourne 115 kV. The line section from Bourne–Barnstable will be connected to the new 345 kV line from Carver. The Bourne to Sandwich portion of the Bourne-Barnstable 120 Line section will be operated at 345 kV. (See NSTAR-09-T07 for a description of the Sandwich Substation. | Fall 2012 | Approved | 2009-11-05
NSTAR-09-T06 | 2009-10-19 | Long Term Lower SEMA | The existing Canal – Bourne #126 line will be reconnected to the #121 line position and the #120 line from the Canal 345 kV Substation will be connected to the present #126 line position. | Fall 2012 | Approved | 2009-11-05
NSTAR-09-T07 | 2009-10-19 | Long Term Lower SEMA | Install a new nominally 550 MVA 345/115kV auto-transformer at Sandwich and install a 345 kV and 115 kV circuit breaker on either side of the auto-transformer. The high side of the auto-transformer will be supplied with a 345 kV line from Carver 345 kV (see NSTAR-09-T05). | Fall 2012 | Approved | 2009-11-05
NSTAR-09-T08 | 2009-10-19 | Long Term Lower SEMA | Separate existing 345 kV double circuit tower (DCT) crossing of Cape Cod Canal. The two 345 kV lines are on DCT structures for a single span crossing Cape Cod Canal. The two 345 kV lines are the Canal – Pilgrim – Auburn #342 line and Canal – Carver #322 line. | Fall 2012 | Approved | 2009-11-05
DEM-09-X01 | 2009-08-17 | Salem Harbor 2 Exciter Replacement | Dominion Energy New England, Inc. proposal for replacement of the Excitation Control System (AVR) at Salem Harbor 2 Generator Station. Plans include replacing the existing Salem Harbor 2 exciter with a GE Ex 2100 static excitation system. | 2009-11-01 | Approved | 2009-09-29
RHW-09-G01 | 2009-09-04 | Record Hill Wind Collector Substation | Record Hill Wind LLC’s proposal for construction of twenty-two 2.3 MW Siemens wind turbine generators with a combined net output of 50.6 MWs located in Roxbury, ME. | 2010-07-01 | Approved | 2009-09-29
RHW-09-T01 | 2009-09-04 |  | Construct a new Record Hill Wind substation connecting Record Hill Wind project with the new CMP Roxbury 115 kV substation fed from the Rumford substation. | 2010-07-01 | Approved | 2009-09-29
CMP-09-T09 | 2009-09-08 | Rumford 115 kV Substation Modifications | Record Hill Wind Collector Substation | 2010-07-01 | Approved | 2009-09-29
CMP-09-T10 | 2009-09-08 | Roxbury Substation | New Roxbury Substation: Transformer T2 (115/34.5 kV, 10/14 MVA) will be moved from the Rumford 115 kV Substation to the new Roxbury 115 kV Substation. Transformer T2 will be used to supply the existing 34.5 kV Frye Substation and transmission Sections 52 to Andover Substation and Section 54 to Rangeley Substation. The new Roxbury Substation will consist of two 115 kV circuit breakers, one for the feed to T2, and one to terminate the new 115 kV line Section 270 from the Rumford 115 kV Substation (reference CMP-09-T09). The new Roxbury Substation will serve as the Point of Interconnection for QP#197, 50.6 MW Record Hill Wind Farm (reference under separate cover: RHW-09-G01, RHW-09-T01). | 2010-07-01 | Approved | 2009-09-29
GMP-09-G01 | 2009-08-24 | GMP Gorge Generator Addition | Green Mountain Power Corp. proposal for construction of a three dual fuel (gas/oil) Solar Titan 130-205015 Axial Turbine combustion turbine generating units at the Gorge Substation located in Colchester, VT. Generator combined gross output of 42 MWs (14 MWs per unit). The existing combustion turbine will be replaced. The generator set will be stepped-up to 34.5 kV by one GSU and interconnect at the existing Gorge substation 35.5 kV bus. | 2011-06-01 | Approved Withdrawn | 9/29/2009 11/13/2012
FPL-09-X02 | 2009-08-21 | Wyman 2 Exciter Replacement | Replace the exictation control system (AVR) at Wyman 2 Generator Station. Plans include the replacing the existing Wyman 2 exciter with a Basler DESC-400 digital controller, which will be aded to the existing rotating DC exciter in the place of Amplidyne type voltage regulator. | 2009-10-01 | Approved | 2009-09-29
NU-09-T13 | 2009-08-26 | Waterside Ring Bus | Transmission PPA for Waterside 22M 3rd 115 kV circuit breaker addition on 15 kV A2 bus position. Re-terminate Waterside Power connection through new underground cable. Relocate circuit breaker 22M-1X1-2 between new 115 kV A1 bus and 115 kV A2 bus and renumber to 22M-1T-2. Re-terminate 1440 line (Glenbrook-Waterside) into new 115 kV A1 bus and complete associated protective relaying schemes. | 09/01/2009 and 04/01/2010 | Approved | 2009-09-29
NU-09-T14 | 2009-08-26 | Waterside Ring Bus | Transmission PPA for Waterside 22M to install three-breaker 115 kV ring bus. Install 3rd circuit breaker (22M-4T-2, 63 kA interrupting and 3 kA continuous current rating) on the 115 kV A3 bus between Glenbrook-Waterside 1440 Line and Waterside-Cos Cob Railroad 1740 Line. Install two 115 kV disconnects and install a 115 kV underground cable to connect 3rd circuit breaker (22M-4T-2) to 115 kV A1 bus to complete ring bus configuration. Complete associated protective relaying schemes. Replace obsolete CCVT’s 1740-22M-H1 PH 1, 2, & 3. Upgrade line limiting terminal equipment for Waterside 22M 1740 Line. | 2011-06-01 | Approved | 2009-09-29
NU-09-X02 | 2009-08-26 | Waterside Relay | Upgrade protective relaying to include second high-speed relay scheme on the 1440 line between Glenbrook and Waterside substations. | 2011-06-01 | Approved | 2009-09-29
MATEP-09-G01 | 2009-10-04 | MATEP Generator | Proposal for construction of a third Siemens SGT-400 gas turbine generator located in Boston, MA. Net output is 12.5 MWs through the existing interconnection with NSTAR via three 13.8 kV tie lines from Brighton Station #329. | 2012-06-01 | Approved Withdrawn | 9/29/2009 1/22/2013
NU-09-G02 | 2009-07-06 | Foxwoods CHP Generator Addition | Generator PPA for construction and interconnection of two gas turbine generators, each with a net rating of 8.28 MWs Winter and 6.68 MWs Summer. Project will be located at Foxwoods Resort and Casino, CT. Generator 1 will interconnect at the Tunnel 12S5 and 12S3. Generator 2 will interconnect at the Mystic 13K48. | 2010-02-01 | Approved | 2009-08-27
NOBLE-09-G02 | 2009-07-02 | Granite Reliable Wind | Generator PPA proposal for the construction of thirty-three 3.00 MW Vestas wind turbine generators totaling 99.0 MWs located in Coos County, NH, a collector system, collector substation and 5.8 mile 115 kV overhead line interconnecting at the NU (PSNH) Paris Substation. | 2010-12-01 | Approved | 2009-07-28
NOBLE-09-T02 | 2009-07-02 | Granite Reliabile Power Substation | Transmission PPA for the construction of a new Granite Reliable Power collector substation and installation of a 34.5/115 kV GSU rated at 66/88/110 MVA. Also included is the installation of a 5.8 mile 115 kV line Y185 from Granite Reliable Power Collector Substation to the Paris Switching Substation located in Dummer, NH. | 2010-12-02 | Approved | 2009-07-28
NU-09-T08 | 2009-07-01 | Paris Switching Station | Transmission PPA for the construction of a new 115 kV Paris Switching Station with three 115 kV circuit breakers, bifurcating 115 kV line W179, providing a three terminal point of interconnection for the proposed generator project located in Dummer, NH. | 2010-12-01 | Approved | 2009-07-28
NU-09-T09 | 2009-07-01 | Upgrade of W179 East Line | Transmission PPA for the upgrade the thermal capability of the existing 115 kV overhead line W179-East (Paris-Pontook-Berlin) from Paris - Dummer, NH to Berlin - Berlin, NH to achieve the required summer thermal LTE rating of 101 MVA. Upgrade will result in summer thermal ratings of 114/114/114 MVA and winter thermal ratings of 133/133/133 MVA | 2010-12-01 | Approved | 2009-07-28
NU-09-T10 | 2009-07-01 | Upgrade of W179 West Line | Transmission PPA for the upgrade the thermal capability of the existing 115 kV overhead line W179-West (Lost Nation-Paris) from Lost Nation – Northumberland, NH to Paris – Dummer, NH to achieve the required summer thermal LTE rating of 101 MVA. Upgrade will result in summer thermal ratings of 123/123/123 MVA and winter thermal ratings of 141/141/141 MVA | 2010-12-01 | Approved | 2009-07-28
NU-09-T11 | 2009-07-01 | 1J95 Switch Close at Littleton 115 kV Substation | Transmission PPA for the closing an existing switch, 1J95, at the Littleton 115 kV Substation. Creates a three terminal line between Moore–Littleton–Whitefield Substations. Protection and controls relaying is to be added to the Littleton terminal. | 2010-12-01 | Approved | 2009-07-28
NU-09-T12 | 2009-07-01 | Upgrade of D142 Line | Transmission PPA for the upgrade the thermal capability of the existing 115 kV overhead line D142 (Lost Nation-Whitefield) from Lost Nation – Northumberland, NH to Whitefield – Whitefield, NH to achieve the required summer thermal LTE rating of 81 MVA. Upgrade will result in summer thermal ratings of 84/97/126 MVA and winter thermal ratings of 111/105/127 MVA | 2010-12-01 | Approved | 2009-07-28
NU-09-X01 | 2009-07-01 | Beebe River Auto-Switch Controls | Transmission PPA for the addition of automatic switching controls, based on voltage, for the existing Beebe River 115 kV capacitor banks, 3x 13.3 MVAR banks located at Beebe River – Campton, NH. This is required to mitigate post-contingency 115 kV over voltages. | 2010-12-01 | Approved | 2009-07-28
DEM-09-G01 | 2009-06-06 | Brayton Point 3 Uprate | Dominion Energy Marketing’s proposal to increase the output capability of the Brayton Point #3 generator by 36 MWs in the summer (previously 612 MWs) and 31 MWs in the winter (previously 633 MWs) through a turbine steam path efficiency upgrade and a corresponding upward revision to the original generator rating by the OEM, Siemens Westinghouse, following future modifications to increase hydrogen gas cooling. The generator modifications will change the nameplate rating from 695 MVA at 0.93 pf to 745 MVA at 0.94 pf, and decrease the reactive lagging capability to 234 MVAR (previously 260 MVAR). Reactive leading capability will not change. | 2011-12-01 | Approved | 2009-07-28
CMP-09-T08 Rev 1 | 2009-06-06 | Madison Electric Works Substation Revision | Sectionalize Section 63 into two parts by adding two 115 kV circuit breakers at the Sturtevant 115 kV Substation; Section 63N to Wyman Hydro Substation and 63S to Livermore Falls Substation. In addition, a 25 MVAR capacitor bank will be added at the Sturtevant 115 kV Substation. | 2010-03-01 | Approved | 2009-07-28
NOBLE-09-G01 | 2009-06-12 | Passadumkeag Wind | Generator PPA proposal for the construction of twenty-five 1.54 MW GE wind turbine generators totaling 38.5 MWs with their own dedicated 575/34.5 kV GSU to be located in Penobscot County, ME. Project is to be interconnected through three collector strings operating at 34.5 kV nominal. String one will interconnect 5 generator wind turbines. String two will interconnect 14 generator wind turbines. String three will interconnect 6 generator wind turbines. Each string shall tie into one 34.5 kV collector bus. | 2011-11-01 | Approved Withdrawn | 7/27/2009 5/24/2011
NOBLE-09-T01 | 2009-06-12 | Passadumkeag Transmission Line Installation | Transmission PPA for the construction of a new 10 mile 34.5 kV transmission line from the new Noble Passadumkeag Windpark to the Bangor Hydro Electric Passadumkeag 115 kV three breaker ring bus and Substation tapping Line 64 linking Graham 115 kV and Keene Road 115 kV. | 2011-11-01 | Approved Withdrawn | 7/27/2009 5/24/2011
BHE-09-T09 | 2009-06-12 | Install GSUs at Passadumkeag Substation | Transmission PPA for the installation of one 34.5/115 kV and 45 MVA step-up transformer at the Passadumkeag 115 kV Substation. | 2011-11-01 | Approved Withdrawn | 7/27/2009 5/24/2011
NU-09-T02 | 2009-05-18 | 2nd Deerfield Auto Transformer | Transmission PPA for the construction of the 2nd Deerfield 345/115 kV Autotransformer | 2011-06-01 | Approved | 2009-06-26
NU-09-T03 | 2009-05-18 | Rebuild L175 Line | Transmission PPA to rebuild 115 kV L175 Line | 2011-06-01 | Approved | 2009-06-26
NU-09-T04 | 2009-05-18 | Reconductor M183 Line | Transmission PPA to reconductor portion of the 115 kV M183 Line | 2011-06-01 | Approved | 2009-06-26
NU-09-T05 | 2009-05-18 | Reconductor C129 Line | Transmission PPA to reconductor portion of the 115 kV C129 Line | 2011-06-01 | Approved | 2009-06-26
NU-09-T06 | 2009-05-18 | Circuit Breaker Replacement at Deerfield Substation | Transmission PPA for the replacement of five (5) 115 kV Circuit Breakers at the Deerfield Substation | 2011-06-01 | Approved | 2009-06-26
NU-09-T07 | 2009-05-18 | Transformer Addition at Rochester Substation | Transmission PPA for the addition of a 115/34.5 kV transformer at the Rochester Substation | 2011-06-01 | Approved | 2009-06-26
FLP-09-G01 | 2009-06-03 | Northfield Efficiency Improvement | Replacement of the hydraulic runners and rewind each of the motor generator stators for each of the 4 generators sequentially over a 4 year period. Resulting work will increase the capacity of each generator from 270 MWs to 292 MWs. | 06/01/2011 - Gen 1 | Approved | 2009-06-29
FLP-09-T01 | 2009-06-03 | Replace Northfield GSU | Replacement of the 666 MVA 3X generator step-up transformer. | 2011-06-01 | Approved | 2009-06-29
TEL-08-G01-Rev1 | 2009-05-31 | Towantic Generator | Generation PPA for construction and operation of combined cycle generating facility increasing the capacity of the generator from 540 MWs to 568 MWs, located in Oxford, CT | 2013-04-01 | Approved Withdrawn | 6/29/2009 2/14/2012
TEL-08-T01-Rev1 | 2009-05-31 | Towantic GSU | Transmission PPA for construction and operation of generator leads and generator step-up transformer for the generation facility. | 2013-04-01 | Approved Withdrawn | 6/29/2009 2/14/2012
NU-08-T73-Rev2 | 2009-06-02 | Towantic Substation | Construction of Towantic 115 kV substation and termination of 1575, 1585, and 1990 115 kV lines to Towantic 115 kV substation | 2013-04-01 | Approved Withdrawn | 6/29/2009 2/14/2012
NU-08-T74-Rev1 | 2009-06-02 | Reconductor 1585N Line | Reconductor/rebuild 115 kV 1585N Line | 2013-04-01 | Approved Withdrawn | 6/29/2009 2/14/2012
NU-08-T75-Rev 1 | 2009-06-02 | 1990S Line Series Reactor | 1990S Line Series Reactor | 2013-04-01 | Approved Withdrawn | 6/29/2009 2/14/2012
NSTAR-09-T03 | 2009-04-28 | Edgar Station Shunt Reactor | Installation of two (2) 115 kV, 40 MVAR shunt reactors each with a 115 kV circuit breaker with a synchronous switching controller. One reactor will connect to the Edgar 115 kV North bus, and the other reactor will connect to the Edgar 115 kV South bus. Installation of the reactors is required to absorb excess reactive power during light load periods. | 2009-12-01 | Approved | 2009-06-01
VELCO-09-T02 | 2009-05-04 | Lyndonville Substation | Construct a new 4-breaker ring substation at Lyndonville with a 56 MVA 115/34.5 kV transformer with a 0.19 pu impedance on a 100 MVA base and two 115 kV 12.5 MVAr capacitor banks. The Lyndonville substation prevents loss of load for loss of the St. Johnsbury transformer by providing redundant service to the area and allow for expected load growth at a local ski resort. | 2011-12-01 | Approved | 2009-06-01
FW-09-G01-Rev1 | 2009-04-30 | Dundee Wind Revision | Evergreen Wind III, LLC proposes the interconnection of its Dundee Mountain Wind Units 1 - 22 (the “Project”) located at Dundee Mountain in Penobscot County, Maine. The Project will consist of 22 General Electric wind turbines, each containing a 1.545 MW, 575-V line-to-line, variable-speed wound-rotor induction generator. | 2009-12-01 | Approved | 2009-06-01
FPL-09-X01 | 2009-05-04 | Seabrook PSS | FPL‟s proposal to commission the Seabrook Power System Stabilizer (PSS) originally installed during the 2006 capacity uprate in order to enhance positive damping characteristics of the generator. | 2009-05-01 | Approved | 2009-05-28
NEP-09-T01 | 2009-04-07 | Devens Transmission Reinforcement | Convert two 69 kV lines (U-21E and V-22E), approximately 0.5 circuit miles each, from Ayer substation to a new 115 kV switching station within the Devens Commerce Center (utilizing 1590 ACSR conductor). At Ayer substation, reconfigure the in-line 115 kV circuit breaker so that is on the Pratts Jct side of the K-137 line. | 2011-06-01 | Approved | 2009-07-28
NSTAR-09-T02 | 2009-04-06 | Woburn Mobile Transformer | NSTAR’s proposal for installation of a 50 MVA, 115/14.4 kV mobile transformer at Woburn Station 211. The mobile transformer installation will provide N-1 distribution system capacity to cover possible transformer contingencies throughout the Woburn-Burlington Region. | 2009-06-01 | Approved | 2010-06-03
NEP-07-T47-Rev1 (Revision available) | 2009-04-03 | Auburn Street Upgrades | Addition of 2nd 345/115kV 448 MVA transformer, expansion of the 345kV switchyard, construction of new breaker and third 115 kV switchyard rated at 63kA, and removal of two 115 kV ring buses. | 2012-06-01 | Approved | 2010-02-10
NEP-07-T48-Rev1 | 2009-04-03 | Dupont Substation Expansion | Addition of two 115 kV circuit breakers rated at 40 kA and addition of 2nd 115/13.8 kV 60 MVA transformer | 2012-06-01 | Approved | 2010-02-10
NEP-09-T03 | 2009-04-03 | Avon Substation | Construction of new 115/13.8 kV substation off A94 line between Parkview and Auburn St. Load at the Avon substation to be supplied by a 40 MVA 115/13.8 kV transformer. | 2012-06-01 | Approved | 2010-02-10
BRP-09-G01 | 2009-03-10 | Bear Swamp Generator Upgrade | Proposed upgrade to increase each of the two hydro generators by 33 MWs (66 MWs total). In addition, the upgrade will expand each generator’s MVAr capacity by 15 MVAr lagging and 86 MVAr leading. Phased in-service dates: for Unit 1, March 31, 2011; and for Unit 2, March 30, 2012. | 03/31/2011 - Gen 1, 03/30/2012 - Gen 2 | Approved Withdrawn | 4/29/2009 8/23/2011
FW09-G01 | 2009-03-04 | Dundee Wind | Generation PPA for the construction of twenty-one 1.54 MW GE wind turbine generators, totaling 32 MW, to be located in Penobscot County, ME. Each turbine will be interconnected along a collector string running approximately 41,000 foot to a circuit breaker at Rollins Mountain Substation. | 2009-12-01 | Approved | 2009-04-29
FW-08-G01-Rev1 | 2009-03-04 | Stetson Wind Phase II | Generation PPA for the updating the unit count at Rollins Wind | 2009-12-01 | Approved | 2009-04-29
FW-08-T01-Rev1 | 2009-03-04 | Stetson Wind Phase II GSU | Transmission PPA for each generator to be interconnected via its own 1.75 MVA 575V/34.5/115 kV step-up transformer and via a collector string to Rollins Mountain substation 39,000 feet away. In addition, upgrading the 34.5/115 kV Rollins Mountain substation transformer from 20/26.6/33.2 MVA to 34.5/50/62.5 MVA. | 2009-12-01 | Approved | 2009-04-29
FW-09-G02 | 2009-03-04 | Jimmy/Owl Wind | Generation PPA for the construction of seventeen 1.54 MW GE wind turbine generators, totaling 26 MW, to be located in Washington County, ME. Each turbine will be interconnected along a collector string running approximately 39,000 foot to a circuit breaker at Stetson Mountain Substation. | 2009-12-01 | Approved | 2009-04-29
UPC-07-G01-Rev 2 | 2009-03-04 | Stetson Wind Phase I | Generation PPA updating the unit count at Stetson Wind | 2009-12-01 | Approved | 2009-04-29
UPC-07-T01-Rev1 | 2009-03-04 | Stetson Wind Phase I GSU | Transmission PPA for each generator to be interconnected via its own 1.75 MVA 575V/34.5/115 kV step-up transformer and via a collector string to Stetson Phase I substation 41,000 feet away. In addition, upgrading the 34.5/115 kV Stetson Phase I transformer from 37.5/50/62 MVA to 60/80/100 MVA. | 2009-12-01 | Approved | 2008-12-23
CMP-09-T01 | 2009-01-20 | Section 241 Transmission Line | Central Maine Power’s Transmission PPA for constructing a new 38.8-mi.115 kV line, Section 241, between the proposed Heywood Road Substation in Benton, ME, and the Wyman Hydro Station in Bingham, ME, as a parallel line to the existing 115 kV Section 83 Line | 2012-12-01 | Approved | 2009-03-20
CMP-06-T13-Rev1 | 2009-01-20 | Heywood Road Substation | Central Maine Power’s Transmission PPA for constructing a new Heywood Road Substation in Benton, ME, revised for a change in scope. | 2009-03-01 | Approved | 2009-03-20
NEP-08-T62 | 2008-12-31 | Bloomingdale-Vernon Hills Underground Cable | New England Power’s Transmission PPA for constructing a new 3.6-mi. 115 kV underground line between Bloomingdale and Vernon Hill Substations in MA and for reconfiguring the #M-165 and #E-157 Lines at Millbury #2 115 kV Substation into separate breaker positions. This plan improves the recovery time for the loss of supply to the Worcester area. | 2013-06-01 | Approved | 2009-02-27
WRP-08-G01 | 2009-01-21 | Watertown Biomass Generator | Generation PPA for the construction of a steam turbine generator with a net output of 26.25 MW. The unit’s boiler will be fueled primarily with chipped or ground wood waste and secondarily with natural gas. | 2010-11-01 | Approved Withdrawn | 2/24/2009 10/20/2010
WRP-08-T01 | 2009-01-21 | Watertown Biomass Interconnection | Transmission PPA for its interconnection via a 24/40 MVA 115/13.8 kV step-up transformer to a tap from the 115 kV #1238 Carmel Hill-Frost Bridge Line. | 2010-11-01 | Approved Withdrawn | 2/24/2009 10/20/2010
NU-08-T78 | 2008-12-23 | Watertown Biomass Substation | Supporting Transmission PPA for the construction of the Watertown Biomass 115 kV Substation by looping the #1238 Line into the substation to a ring bus for terminating the 300-foot lead to the generator transformer. | 2010-11-01 | Approved Withdrawn | 2/24/2009 10/20/2010
NU-07-T04 Rev. 1 | 2008-03-01 | Russell Biomass Power Plant | Russell Biomass Power transmission upgrades. | 2011-06-01 | Approved Withdrawn | 6/6/2007 5/15/2012
NSTAR-08-T01 | 2008-02-14 | Mystic Station #250 | Install two West bus and two East bus 115 kV circuit breakers, and move the connection of 115/14 kV transformer 110B to an open board position. | 2008-11-01 | Approved | 2008-03-10
DEM-08-T01 | 2008-02-08 | Millstone Unit 2 | Project will replace existing three phase GSU transformer for Millstone Unit 2 with three single phase Mitsubishi GSU units and ISO phase bus so that the new TRF impedance is within +/- 4% of existing TRF. | 2008-05-01 | Approved | 2008-03-03
NU-08-T01 | 2008-02-05 | Devon and Trumball 115 kV Substation | Trumbull 45P Substation (UI) - CL&P Modifications. | 2008-06-01 | Approved | 2008-03-13
BHE-08-T02 | 2008-02-01 | Boggy Brook 115kV & Ellsworth Falls 46kV | New 28MVA top rated transformer from Boggy Brook 115kV to Ellsworth Falls 46kV, replacing T3 which has a top rating of 15MVA and was sourced from Ellsworth Falls 34.5kV. | 2008-10-01 | Approved | 2008-03-31
APNA-08-T01 | 0/30/2008 | Brockton Power | Brockton Power Project | 2010-12-01 | Approved | 2001-03-10
APNA-08-G01 | 2008-01-30 | Brockton Power | Brockton Power Project | 2010-12-01 | Approved | 2008-03-10
NEP-08-T02 | 2008-01-30 | Brockton Substation | Construct a new 115kV Brockton substation. Construct a new 115kV line connecting the Brockton power plant with the Brockton substation. | 2010-06-01 | Approved | 2008-03-10
NEP-08-T03 | 2008-01-30 | F19N Line | Reconductor the F19N line. Replace the in-line 19-1 switch. | 2010-06-01 | Approved | 2008-03-10
NEP-08-T04 | 2008-01-30 | Bridgewater | Replace the Bridgewater 1631 circuit breaker with a new one rated at 63kA IC. | 2010-06-01 | Approved | 2008-03-10
NEP-08-T05 | 2008-01-30 | Brockton | Reconductor F19S line between Brockton and Belmont tap. Replace the in-line 19-2 switch. Upgrade S1 line terminal equipment at Belmont substation. | 2010-06-01 | Approved | 2008-03-10
NEP-08-T06 | 2008-01-30 | Auburn and Bridgewater | Replace seven 115 kV breakers at Auburn St. and one 115kV breaker at Bridgewater. | 2010-06-01 | Approved | 2008-03-10
NEP-08-T07 | 2008-01-30 | Tewksbury 22A/22 | Create a new 345-115 kV substation at Wakefield Junction by looping the 345 kV # 339 line from Tewksbury to Golden Hills and the two 115 kV lines S-145 and T-146 from Tewksbury to Golden Hills to Salem Harbor into new switchgear; install four 345-115 kV 448 MVA autotransformers; The new substation will include three bays of 345 kV gas insulated switchgear (GIS) in a breaker-and-third configuration with independent pole tripping (IPT) capable units and three bay positions for future expansion as well as three bays of 115 kV gas insulated switchgear (GIS) in breaker-and-third configuration with independent pole tripping (IPT) capable units and one bay position for expansion. The relay systems at the at the remote ends of the involved lines (Tewksbury 22/22A, Mystic 250, Maplewood, Lynn No. 21, and Salem Harbor) shall be modified to coordinate with those installed at the new Wakefield Junction substation on the 345 kV and 115 kV systems. | 2009-05-01 | Approved | 2008-04-01
NEP-08-T08 | 2008-01-30 | Golden Hills | Reconfigure the 115kV terminals at Golden Hills. Bypass and remove the existing two 115kV breaker and half schemes, tieing the S-145 to the F-158N and the T-146 to the Q-169 line. De-gas and remove the existing 115kV gas-insulated switchgear (GIS). Reconfigure the 345kV terminals at Golden Hills. Bypass and remove the existing three 345kV breaker and half schemes, tieing the 339 and the 349X and 349Y lines. De-gas and remove the existing 345kV gas-insulated switchgear (GIS). Remove the 2-345/115 kV transformers. | 2009-04-01 | Approved | 2008-04-01
NEP-08-T09 | 2008-01-30 | Wakefield Junction | Reconductor 2.2 miles of the present S-145 and T-146 115 kV lines from Wakefield Junction to Golden Hills Tap. This will increase the ratings of the 115kV lines to Normal 359 MVA / LTE 446 MVA / STE 524 MVA / DAL 692 MVA during summer and Normal 446 MVA / LTE 511 MVA / STE 607 MVA and DAL 741 MVA in the winter. | 2009-06-01 | Approved | 2008-04-01
NEP-08-T10 | 2008-01-30 | Melrose #2 Substation | Convert the Melrose # 2 substation from supply by three 115kV lines , S-145, T-146 and Q-169 to two 115kV lines Q-169 and F-158N from Wakefield Junction #88. Replace three 115-23kV step-down transformers with two 115-23kV 33/44/55 MVA units. | 2009-06-01 | Approved | 2008-04-01
NEP-08-T11 | 2008-01-30 | Revere #7 Substation | 115kV 30MVAr capacitor bank installation at Revere #7 installed off the A-179 115kV line via a 40kA synchronous closing circuit breaker. | 2009-06-01 | Approved | 2008-04-01
NEP-08-T12 | 2008-01-30 | West Amesbury and King Street Substations | King Street - West Amesbury convert a 7 mile 23kV sub transmission line, the 2377, to 115 kV from King Street Substation to the West Amesbury Substation West Amesbury Substation � Install an outdoor 115 kV bus with four breakers bays, install additional four 3000 Amp 115kV breakers; IC 63kA and 3000A disconnect switches (NEP-05-T11 installed one breaker and one 115/23 kV transformer) for a total of five breakers installed, ultimate layout to allow the addition of an additional four breakers in the future. Also install a 45/60/75 MVA 115/23 kV transformer and circuit switcher along with a 40MVA 115/13.2 kV transformer along with a circuit switcher. King Street Substation install one 3000 Amp. 115kV breaker, IC 63 KAmp along with 3000 Amp disconnect switches. | 2009-06-01 | Approved | 2008-04-01
NSTAR-08-T02 | 2008-01-25 | Newton Substation #292 | Upgrade Newton #292 | 2008-06-01 | Approved | 2008-03-10
NSTAR-08-T03 | 2008-01-25 | Walpole Station | Replace 110A and 110C transformers with new transformers. | 2008-06-01 | Approved | 2008-03-10
UI-08-T01 | 2008-01-24 | Trumbull 45P Substation | Construct a new 115/13.8 kV substation in Trumbull, Connecticut (CT) to be known as Trumbull 45P Substation. Install two new 118/14.9 kV, 24/32/40 MVA transformers at Trumbull 45P Substation, and three 115 kV circuit breakers in a ring bus arrangement. Terminate the existing 1730 line at Trumbull 45P Substation. | 2008-06-01 | Approved | 2008-03-13
BHE-08-T01 | 2008-01-09 | Graham 115 kV & Graham 46 kV | New 100MVA top rated transformer from Graham 115kV to Graham 46kV, replacing T9 which has a top rating of 28MVA. | 2007-11-01
NU-08-G01 | 2008-01-04 | Kimberly Clark Corporation | KC-New Milford #1, #2, #3. | 2008-04-20 | Approved | 2008-03-10
BELD-07-T02 | 2007-12-07 | Station 11 and Station 16 | 115-16-11 Underground Cable Upgrade | 2010-06-01
BELD-07-T03 | 2007-12-07 | Station 16 & Station 10 | 115-10-16 Underground Cable Upgrade | 2010-06-01
NEP-07-T44 | 2007-12-04 | Belmont Substation | Terminal equipment (buswork and line drops) at Belmont 115 kV substation. Install two high speed protection systems. | 2008-10-01 | Approved | 2008-01-28
NEP-07-T45 | 2007-12-04 | E. Bridgewater Substation | Reconductor L1 Line with 795 ACSR. | 2008-06-01 | Approved | 2008-01-28
NEP-07-T46 | 2007-12-04 | Bridgewater 115 kV Substation | Bridgewater 115 kV substation upgrades: replace three 115kV breakers with 63kA & upgrade G18, F19 lines terminal equipment (buswork, disconnect switches and wavetraps) | 2009-06-01 | Approved | 2008-01-28
NU-07-G04 | 2007-11-30 | UNH Cogen | UNH Cogen | 2007-12-01 | Approved | 2008-02-07
NEP-06-T06 Rev. 2 | 2007-11-27 | Bellows Falls Substation | Replace the three existing, three-winding GSUs with two new two-winding 115-6.6 kV, 24/32/40 MVA GSUs (No. 1 and No. 2). Install a new 115-69 kV, 33.6/44.8/56 MVA autotransformer (No. 4) and a new 115-46 kV, 30/40/50 MVA autotransformer (No. 5) to replace the capacity provided by the existing three-windings GSUs. Install a new 115kV 30MVar capacitor bank (C1) for system voltage support. Remove the existing 69-46 kV, 8 MVA autotransformer (No. 3). Replace three 115kV Oil Circuit Breakers (OCB) (W-149S, J-136N and I-135N) with Gas Circuit Breakers (GCB) (W- 149, J-136 and I-135); Install two new 115kV circuit switchers (4T-115 and 5T-115); Install one new 115kV GCB for the C1 capacitor bank (C1). Install one new 69 kV GCB (G33). Install one new 115kV bus tie breaker (115BT). | 2010-10-01 | Approved | 2008-01-28
NU-07-T22 | 2007-11-16 | Waterford 25Y | Construction of a 115-kV bus with a 115-kV tie breaker to be known as the new Waterford 25Y substation. Addition of two 60 MVA 115/23-kV two-winding transformers. Loop existing circuit 1605 (New Waterford Substation 115-kV- Cohanzie Junction- Montville 115-kV-Willaims 115-kV substations). Loop new circuit 1617 (Flanders 115-kV to New Waterford Substation 115-kV). | 2010-05-30 | Approved | 2008-01-11
BELD-07-G01 | 2007-11-14 | Thomas A. Watson Generating Station | Thomas A. Watson Generating Station | 2009-03-03 | Approved with conditions | 2008-02-28
BELD-07-T01 | 2007-11-14 | Thomas A. Watson Generating Station | Thomas A. Watson Generating Station 115 kV interconnection. | 2009-03-03 | Approved with conditions | 2008-02-28
NEP-07-X03 | 2007-10-29 | Comerford Phase I HVdc Runback SPS | Retirement of the Comerford Phase I HVdc Runback SPS | 2007-03-31 | Approved | 2007-12-21
CMP-07-T05 | 2007-10-25 | Bigelow Substation | Install one 115 kV breaker at Bigelow substation in association with the Kibby Wind Farm project. | 2008-12-01 | Approved | 2007-12-21
CMP-07-T06 | 2007-10-25 | Wyman Hydro Substation | Install two switched 115 kV capacitor banks, 18 MVAr each, at Wyman Hydro substation in association with the Kibby Wind Farm project | 2008-12-01 | Approved | 2007-12-21
NRG-07-G03 | 2007-10-24 | Middletown Unit 11 | Middletown Unit 11 | 2009-01-31 | Withdrawn | 2011-08-23
CMP-07-T04 | 2007-10-23 | Wyman Hydro and Detroit Substations | Install two (2) 115 kV breakers on Section 66 between Detroit and Wyman Hydro substations in Athens, Maine and construct a new 115/12.47 kV substation for the purpose of supplying an initial load of 3 MW for a new customer. This new substation will become the new distribution source for the Athens area to replace the existing Harmony substation. | 2009-06-01 | Approved | 2007-12-21
GRE-07-T01 | 2007-10-23 | Granite Ridge Energy | Steam turbine GSU transformer replacement. | 2007-12-01 | Approved | 2007-12-20
GRE-07-T02 | 2007-10-23 | Granite Ridge Energy | Tap Setting Change for Each of Two Combustion Turbine GSU Transformers. | 2008-12-01 | Approved | 2007-12-20
MPP-07-G01 | 2007-10-23 | L'Energia Energy Center | Steam/Turbine Generator Unit reactivation. | 2008-08-01 | Approved with conditions | 2007-12-18
NRG-07-G02 | 2007-10-23 | Devon Station | Devon Units 15-18 | 2009-03-31 | Approved with conditions | 2007-12-18
NU-07-T14 | 2007-10-18 | Berkshire Substation | A second 345/115-kV auto transformer, identical to the existing transformer will be installed, and energized, at Berkshire substation. | 2008-06-30 | Approved | 2008-02-07
TCPM-07-G01 | 2007-10-17 | Kibby Wind Power | Kibby Wind Power Project | 2008-12-31 | Approved | 2007-12-21
TCPM-07-T01 | 2007-10-15 | Kibby Wind Farm and Central Maine Power Bigelow | 115/34.5 kV substation and 115 kV transmission line. | 2008-12-31 | Approved | 2007-12-21
NEP-07-T14 | 2007-10-02 | Greendale Sub | Upgrade Greendale 115 kV breaker. | 2009-06-01 | Approved | 2007-12-17
NEP-07-T15 | 2007-10-02 | P-142 Overheard Line | Reconductor P-142 overhead line. | 2010-06-01 | Approved | 2007-12-17
NEP-07-T16 | 2007-10-02 | O-141S Overhead Line | Reconductor O-141S overhead line. | 2010-06-01 | Approved | 2007-12-17
NEP-07-T17 | 2007-10-02 | Millbury Sub | Upgrade Millbury 115 kV terminal equipment. | 2009-06-01 | Approved | 2007-12-17
NEP-07-T18 | 2007-10-02 | Carpenter Hill | Replace five 115 kV breakers at Carpenter Hill. | 2009-06-01 | Approved | 2007-12-17
NEP-07-T19 | 2007-10-02 | Wachusett Substation | Install 3rd Wachusett 345-115 kV autotransformer. | 2011-06-01 | Approved | 2007-12-17
NEP-07-T20 | 2007-10-02 | W-175 115 kV Line | Reconductor W-175 115 kV line. | 2011-06-01 | Approved | 2007-12-17
NEP-07-T21 | 2007-10-02 | Searsburg 69 kV Station | Searsburg 69 kV : Install in-line breaker. | 2010-06-01 | Approved | 2007-12-17
NEP-07-T22 | 2007-10-02 | Millbury | Reconductor A-127E and B-128E 115 kV lines. | 2010-06-01 | Approved | 2007-12-17
NEP-07-T23 | 2007-10-02 | Cabot Tap | Reconductor portions of A-127W 115 kV line. | 2010-06-01 | Approved | 2007-12-17
NEP-07-T24 | 2007-10-02 | Deerfield #4 | 2nd Deerfield 115-69 kV autotransformer. | 2010-06-01 | Approved | 2007-12-17
NEP-07-T25 | 2007-10-02 | Bear Swamp | Reconductor and Retension E205W 230 kV line. | 2011-06-01 | Approved | 2007-12-17
NEP-07-T26 | 2007-10-02 | Adams Substation | Adams substation - Add 115 kV Breaker. | 2011-06-01 | Approved | 2007-12-17
NEP-07-T27 | 2007-10-02 | Pratts Jct | Upgrade I-135S and J-136S 115 kV Circuits. | 2010-06-01 | Approved | 2007-12-17
NEP-07-T28 | 2007-10-02 | Pratts Jct | Upgrade Pratts Jct 230-115 kV autotransformer T8 and install 230 kV breaker. | 2010-06-01 | Approved | 2007-12-17
NEP-07-T29 | 2007-10-02 | Bear Swamp | Upgrade Pratts Jct 230-115 kV autotransformer T8 and install 230 kV breaker. | 2010-06-01 | Approved | 2007-12-17
NEP-07-T30 | 2007-10-02 | Millbury | Build new 115 kV Overhead Line from Millbury to Tower 510 (Auburn). | 2011-06-01 | Approved | 2007-12-17
NEP-07-T31 | 2007-10-02 | Millbury | Install one (1) 115 kV breaker at Millbury to terminate new line to Tower 510. | 2011-06-01 | Approved | 2007-12-17
NEP-07-T32 | 2007-10-02 | Webster Street | Install two 115 kV breakers at Webster St. | 2010-06-01 | Approved | 2007-12-17
NEP-07-T33 | 2007-10-02 | E Winchendon & Otter River | Build new 115 kV Overhead Line from E Winchendon substation to Otter River Substation. | 2011-06-01 | Approved | 2007-12-17
NEP-07-T34 | 2007-10-02 | E Winchendon | Install one (1) 115 kV breaker at E Winchendon sub to terminate new line to Otter River. | 2011-06-01 | Approved | 2007-12-17
NEP-07-T35 | 2007-10-02 | Otter River Substation | Expand Otter River substation to 6 breaker ring bus configuration and install two new 115-69 kV transformers. | 2011-06-01 | Approved | 2007-12-17
NEP-07-T36 | 2007-10-02 | East Westminster | Install in-line 69 kV Breaker at E Westminster Substation (associated with Otter River substation reinforcement). | 2011-06-01 | Approved | 2007-12-17
NEP-07-T37 | 2007-10-02 | Palmer Sub | Convert O-15S 69 kV line to 115 kV. | 2011-06-01 | Approved | 2007-12-17
NEP-07-T38 | 2007-10-02 | Palmer Sub | Install additional 115 kV breaker at Palmer to terminate converted O-15S line, and upgrade Palmer 115 kV buswork. Install 115/23 kV transformer. | 2011-06-01 | Approved | 2007-12-17
NEP-07-T39 | 2007-10-02 | Hampden Sub | Build new 115 kV swiching station in Hampden MA. This station will connect the NU 1515 line to the National Grid O-15S line via a four breaker ring bus. | 2011-06-01 | Approved | 2007-12-17
NEP-07-T40 | 2007-10-02 | Hampden Sub | Convert Hampden 69/13 kV transformer to 115/13 kV for O-15S line conversion to 115 kV. | 2011-06-01 | Approved | 2007-12-17
NEP-07-T41 | 2007-10-02 | Hampden Sub | Convert E Longmeadow 69/13 kV transformer T1 to 115/13 kV for O-15S line conversion to 115 kV. | 2011-06-01 | Approved | 2007-12-17
NEP-07-T42 | 2007-10-02 | Shaker Rd | Convert Shaker Rd 69/13 kV transformer to 115/13 kV for O-15S line conversion to 115 kV. | 2011-06-01 | Approved | 2007-12-17
NEP-07-T43 | 2007-10-02 | Carpenter Hill | Carpenter Hill transformer Upgrades: - Install a 115-69 kV transformer (56 MVA) at Carpenter Hill. - Replace Carpenter Hill 345-115 kV autotransformer T1 (300 MVA) with a standard 448 MVA transformer. | 2015-06-01 | Approved | 2007-12-17
NU-07-T15 | 2007-10-01 | Frost Bridge 345/115-kV Substation | Replace the 345/115-kV Autotransformer at Frost Bridge Substation. | 2007-11-01 | Approved | 2007-10-20
NU-07-T17 | 2007-10-01 | North Bloomfield 115-kV Substation | Install 2% Series Reactor w/ by-pass Switch on 1784 Line at North Bloomfield Substation. | 2009-12-01 | Approved | 2007-10-20
NEP-05-T11 Rev. 1 | 2007-09-25 | West Amesbury Substation | 345 kV air-insulated substation addition, addition of one 345-115kV 448 MVA transformers, one 345 kV transformer high side circuit breaker, tapping the 345kV #394 line at West Amesbury substation, between Seabrook and Ward Hill, 115 kV air-insulated substation, one 115/23 kV 45/60/75 MVA transformer, and transfer of approximately 64 MW of local load from the King Street 23 kV system to the new West Amesbury 23 kV system. | 2009-03-01 | Approved | 2007-10-20
GMP-07-G02 | 2007-09-18 | Essex Junction #19 | Essex Junction #19 Asset ID #1221 | 2007-11-18
NEP-07-T03 | 2007-09-12 | Tewksbury 22A/22 | Create a new 345-115 kV substation at Wakefield Junction by looping the 345 kV # 339 line from Tewksbury to Golden Hills and the two 115 kV lines S-145 and T-146 from Tewksbury to Golden Hills to Salem Harbor into new switchgear; install four 345-115 kV 448 MVA autotransformers; The new substation will include three bays of 345 kV gas insulated switchgear (GIS) in a breaker-and-third configuration with independent pole tripping (IPT) capable units and three bay positions for future expansion as well as three bays of 115 kV gas insulated switchgear (GIS) in breaker-and-third configuration with independent pole tripping (IPT) capable units and one bay position for expansion. | 2009-06-01
NEP-07-T04 | 2007-09-12 | Golden Hills Substation | Reconfigure the 115kV terminals at Golden Hills. Bypass the existing two 115kV breaker and half schemes, tieing the S-145 to the F-158N and the T-146 to the Q-169 line. De-gas and remove the existing 115kV gas-insulated switchgear (GIS). | 2009-06-01
NEP-07-T05 | 2007-09-12 | Wakefield Junction | Reconductor 2.2 miles of the present S-145 and T-146 115 kV lines from Wakefield Junction to Golden Hills Tap. This will increase the ratings of the 115kV lines to Normal 359 MVA / LTE 446 MVA / STE 524 MVA / DAL 692 MVA during summer and Normal 446 MVA / LTE 511 MVA / STE 607 MVA and DAL 741 MVA in the winter | 2009-06-01
NEP-07-T06 | 2007-09-12 | Melrose #2 Substation | Convert the Melrose # 2 substation from supply by three 115kV lines , S-145, T-146 and Q-169 to two 115kV lines Q-169 and F-158N from Wakefield Junction #88 (as described in NEP-07-T03). Replace three 115-23kV step-down transformers with two 115-23kV 33/44/55 MVA units. | 2009-06-01
NEP-07-T07 | 2007-09-12 | Revere #7 Substation | 115 kV 30MVAr capacitor bank installation at Revere #7 installed off the A-179 115kV line via a 40kA synchronous closing circuit breaker. | 2009-06-01
NU-07-T16 | 2007-09-11 | Jackman Substation | Installation of temporary F162 Line Special Protection System. | 2006-11-01 | Approved | 2007-09-27
NU-06-T06 Rev. 1 | 2007-09-05 | Fitzwilliam | New Substation - Fitzwilliam Autotransformer Impedance Change | 2007-12-01
NU-06-T10 Rev. 1 | 2007-09-05 | Fitzwilliam | New Substation - Fitzwilliam Autotransformer Impedance change from one 3 phase unit to 3 (single phase) units. | 2008-12-31 | Approved | 2007-09-27
NU-07-T12 | 2007-09-04 | Rood Avenue 24J | Addition of a 46.7 MVA 115/23-kV two-winding transformer at new substation. Construct a 115kV bus with a 115-kV tie breaker at new substation, 3. Loop the line 1751 (Manchester 3A, Northwest Hartford 2N, N Bloomfield 2A) into the new substation, and at Manchester substation, addition of a 115-kV circuit breaker at 1751 line terminal and upgrade relay and wave trap. | 2009-06-01 | Approved | 2007-09-27
NU-07-T13 | 2007-09-04 | Enfield 12C Substation | Add a second 115/23-kV transformer (47 MVA) and new switchgear at Enfield 12C. | 2008-05-01 | Approved | 2007-09-27
BHE-07-G01 | 2007-08-27 | Lincoln, ME | New 13.5MW biomass co-generation addition to the existing mill load and generation facilities in Lincoln, Maine. | 2007-11-01 | Approved | 2007-09-27
CVPS-07-G01 | 2007-08-23 | St. Albans Diesel Plant 1 & 2 | St. Albans Diesel Plant 1 & 2 - St. Albans, Vermont - Welden St. 34.5 kV Bus. | 2007-11-01 | Approved | 2007-09-27
NEP-07-T12 | 2007-07-30 | Auburn Street 115 kV Substation | Install two new 115 kV circuit breakers at the Auburn Street south ring bus and reconnect the Auburn - Kingston #191 line to a new 115 kV bus position at Auburn Street. This is required by the new Brook Street - Auburn Street proposed #194 line addition. | 2007-09-30 | Approved | 2007-08-17
NSTAR-07-T08 | 2007-07-30 | Carver 345 kV Substation | Expand Carver Substation. | 2008-09-30 | Approved | 2007-08-17
NSTAR-07-T09 | 2007-07-30 | Tremont 115 kV Substation | Install one 115 kV circuit breaker at the Tremont 115 kV Substation. Install a second 8.3 mile Carver - Tremont 115 kV line as the proposed #134 line on the same towers as the 127 and 128 lines. | 2007-09-30 | Approved | 2007-08-17
NSTAR-07-T10 | 2007-07-30 | Brook Street 115 kV Substation | Expand the Brook Street 115 kV Substation with five 115 kV circuit breakers into a breaker-and a half design. Connect the spare conductors of the Jordan Road - Auburn Street #342 line as a new circuit from the Brook Street Substation to the Auburn Street. | 2007-09-30 | Approved | 2007-08-17
NSTAR-07-T11 | 2007-07-30 | Kingston 115 kV Substation | Upgrade the Kingston terminal of the Kingston -Auburn #191 line by replacing a disconnect switch at the Kingston 115 kV Substation. Reduce the clearing of the #117 line at Kingston for a fault at Brook Street from 47 cycles to 29 cycles. | 2007-09-30 | Approved | 2007-08-17
NSTAR-07-T12 | 2007-07-30 | Barnstable 115 kV Substation | Expand the Barnstable 115 kV Substation with a 5th bay with two 115 kV circuit breakers. Install a 100 MVAR STATCOM dynamic voltage control device at the Barnstable Substation. | 2007-09-30 | Approved | 2007-08-17
VELCO-07-T04 | 2007-07-29 | Duxbury | Construct from the proposed Duxbury Switching station a 9.5 mile 115 kV 1272 ACSR line to Stowe Vermont where the voltage will be stepped down from 115 kV to 34.5 kV in a four breaker ring substation. | 2008-09-30 | Approved | 2007-08-16
UPC-07-G02 | 2007-07-24 | Sheffield Wind | Sheffield Wind Project | 2008-04-01 | Approved with conditions | 2007-08-16
UPC-07-T02 | 2007-07-24 | Sheffield Wind Project Substation | Sheffield Wind Project Substation | 2008-04-01 | Approved with conditions | 2007-08-16
VELCO-07-T03 | 2007-07-24 | Sheffield 115 kV | Construction of a three-breaker 115 kV ring station, located between Irasburg and St Johnsbury, to interconnect the Sheffield wind project. | 2008-04-01 | Approved with conditions | 2007-08-16
VELCO-07-T01 | 2007-07-19 | Middlesex Substation | Installation of a 115 kV breaker in existing Middlesex Substation. | 2007-12-01 | Approved | 2007-08-16
VELCO-07-T02 | 2007-07-19 | Duxbury Switching Station | Construct new three SCADA controlled 115 kV switching station in Duxbury, VT. | 2007-12-01 | Approved | 2007-08-16
DEM-07-G01 | 2007-06-26 | Millstone Power Station | Millstone Power Station Unit 3 Power Uprate. | 2008-11-01 | Approved with conditions | 2007-08-14
NU-07-T10 | 2007-06-22 | Scobie Pond Substation | Add 3rd Scobie Pond 345/115-kV Autotransformer. | 2008-05-01 | Approved | 2007-07-27
NU-07-T11 | 2007-06-22 | Mammoth Road Substation | Add 2nd Mammoth Rd. 115/34.5-kV Transformer. | 2008-05-01 | Approved | 2007-07-27
NSTAR-07-G01 | 2007-06-20 | MATEP 474 Brookline Avenue | Relocation of MATEP's existing Diesel Generators #2 #3 and #4 for a total of 20.25MW from the present 14kV distribution connection at Brighton Station #329 to a new 14kV distribution connection at Colburn Street Station #350. | 2007-09-15 | Approved | 2007-08-16
UI-07-T01 | 2007-06-20 | Baird Substation | Replace Two 115-kV Circuit Breakers at Baird Substation. | 2007-06-01
BHE-07-T01 | 2007-06-15 | Keene Road Substation | Keene Road substation breaker addition. | 2007-05-01 | Approved | 2007-07-27
UPC-07-G01 | 2007-06-15 | Stetson Mountain Wind Units 1-40 | New 60MW wind generation addition on Stetson Mountain. | 2008-07-01 | Approved | 2007-07-27
UPC-07-T01 | 2007-06-15 | Keene Road Substation | 115 kV transmission line/generator lead addition. This transmission line will be the generator lead from the BHE Keene Road substation to the Stetson Wind V Project. | 2007-12-01 | Approved with conditions | 2007-07-27
NU-07-T09 | 2007-05-22 | Silver Substation | Silver Substation Replace 30MVA Transformer with 47MVA Transformer Project. | 2007-06-01 | Approved | 2007-06-15
NU-07-T07 | 2007-05-21 | Swanzey Substation | Swanzey Substation Replace 5MVA Transformer with 15MVA Transformer Project. | 2009-06-01 | Approved | 2007-06-15
NU-07-T06 | 2007-05-14 | Jackman Substation | Jackman Substation replace 20MVA transformer with a 44MVA transformer. | 2008-06-01 | Approved | 2007-06-15
ENB-07-DR01 | 2007-05-11 | New Boston | Put New Boston Unit 1 into deactivated reserve status. | 2007-08-01 | Approved | 2007-07-10
NU-07-T04 | 2007-05-11 | Russell Biomass | Construct and interconnect a nominally rated 55 MW, General Electric turbine generator at Russell, MA, via a 65 MVA 13.8/115 kV generator step-up transformer and 5.3 miles of 115 kV transmission line to the 115 kV #1512 Line, between Elm Substation and Granville Junction. | 2009-06-01 | Approved with conditions Withdrawn | 6/6/2007 5/15/2012
NU-07-T05 | 2007-05-11 | Ludlow 345 kV | Ludlow 345 kV 6T circuit breaker addition. | 2008-06-01 | Approved | 2007-06-15
NSTAR-07-T05 | 2007-05-10 | Walpole Station | Install new 37/50/62.5 MVA, 117/15.12 kV Transformer 110B. | 2007-06-01 | Approved with conditions | 2007-06-15
FLP-07-X01 | 2007-05-08 | Mount Tom Generating Station | Replace existing Amplidyne voltage regulator with a dual Basler DECS-400. | 2007-05-30 | Approved | 2007-06-06
NRG-07-G01 | 2007-05-02 | Cos Cob | Cos Cob 13 & 14 generation. | 2008-02-01 | Approved with conditions | 2007-05-15
NRG-07-T01 | 2007-05-02 | Cos Cob Village | Generator lead and new generator step up transformer For Cos Cob Station. | 2008-02-01 | Approved with conditions | 2007-06-06
GB-07-RR01 | 2007-05-01 | Newport Diesel | Retirement of the Newport diesels assets #522-523. | 2007-07-01 | Approved | 2007-06-08
NU-07-G03 | 2007-05-01 | Biomass-Fired Power Plant | Interconnect a nominally rated 55 MW, General Electric turbine generator at Russell, MA, via a 65 MVA 13.8/115 kV generator step-up transformer and 5.3 miles of 115 kV transmission line to the 115 kV #1512 Line. | 2009-06-01 | Approved with conditions Withdrawn | 6/6/2007 5/15/2012
NU-07-G02 | 2007-04-30 | Plainfield Renewable Energy | Construct and interconnect a nominally rated 44 MW, wood-fired General Electric turbine generator at Plainfield, CT, via a 50MVA 13.8/115 kV generator step-up transformer and 0.5 mile of 115 kV radial transmission line tapped on the 115 kV #1505 Line between Fry Brook Substation and Plainfield Junction. | 2008-12-29
NSTAR-07-T04 | 2007-04-27 | 115 kV | Installation of three new 115 kV shunt capacitor banks and and the uprate of three | 2007-06-01 | Approved | 2007-06-05
UI-05-T01 Rev. 1 | 2007-04-27 | Singer, Pequonnock, and Bridgeport Substations | Withdraw: Construct Singer 345-kV Substation, Modify Pequonnock 115-kV Substation, and Modify Bridgeport Energy's Interconnection. | 2009-12-01
UI-05-T02 Rev. 1 | 2007-04-27 | East Devon Substation & Singer Substation | Build two 345-kV underground circuits from East Devon Substation to Singer Substation. | 2009-12-01 | Approved with conditions | 2007-06-08
UI-05-T03 Rev. 1 | 2007-04-27 | Elmwest Substation & West River Substation | Withdraw previous application to install two 115-kV circuit breakers at Elmwest Substation | 2007-04-27 | Approved with conditions | 2007-06-08
UI-05-T05 Rev. 1 | 2007-04-27 | Baird, Bridgeport RESCO, Broadway, Devon Tie... | Reclassify and Modify Eight Existing Substations as Northeast Power Coordinating Council (NPCC) Bulk Power System (BPS) Facilities, Independent of NRI Status. Facilities being reclassified are Baird 115-kV, Bridgeport RESCO 115-kV, Broadway 115-kV, Devon Tie 115-kV, Mill River 115-kV, Water Street 115-kV, and West River 115-kV. | 2009-12-01 | Approved with conditions | 2007-06-08
PMLD-07-RR01 | 2007-04-25 | Princeton Wind Farm | Retirement of the Princeton Wind Farm, Asset No. 968. | 2007-05-01 | Approved | 2007-05-16
NEP-07-T02 | 2007-04-24 | West Methuen | 115 kV Transmission Line G-133W and 115 kV circuit breaker and disconnect switches @ West Methuen. | 2007-12-01 | Approved | 2007-06-08
NU-03-T15 Rev. 1 | 2007-04-21 | Machester & Hopewell Substations | Re-conductor the 115-kV 1767 line from Manchester to Hopewell substations in Connecticut. | 2007-04-01 | Approved | 2007-06-08
NU-07-G05 | 2007-04-18 | UMASS Amherst | UMASS Amherst #1 11.25 MVA Generator. | 2008-03-31 | Approved with conditions | 2007-07-23
TCH-07-G01 | 2007-04-17 | Vernon Station | The installation of four new 4 MW 2.8 meter semi-Kaplan hydro units, and the removal of four units that have been retired in place, designated #5, 6, 7, and 8. | 2007-12-31 | Approved with conditions | 2007-06-05
TCH-07-G02 | 2007-04-17 | Comerford Station | Replacement of all waterwheels at Comerford Station. | 2007-03-01 | Approved with conditions | 2007-06-05
NU-07-X02 | 2007-03-22 | Merrimack Generating Station | Merrimack Unit 2 voltage regulator replacement. | 2007-05-01 | Approved | 2007-04-11
DEM-07-X02 | 2007-03-21 | Salem Harbor Unit 3 (Asset ID # 553) | Generator excitation system replacement. | 2007-05-01 | Approved | 2007-04-11
NU-06-T15 Rev. 1 | 2007-03-21 | Barbour Hill 23J | Barbour Hill 23J 345/115-kV substation - 600 MVA autotransformer. | 2008-06-30 | Approved | 2007-04-11
NU-07-T03 | 2007-03-20 | Plainfield Renewable Energy | 115-kV Transmission Line (Plainfield, CT - Frybrook/Plainfield, CT). | 2009-07-30
DEVON-07-G01 | 2007-03-16 | Devon Station | Devon Unit 7 return to service. | 2007-10-04 | Approved with conditions | 2007-04-17
DEVON-07-G02 | 2007-03-16 | Devon Substation | Devon Unit 8 return to service. | 2007-06-06 | Approved with conditions | 2007-04-17
GMP-07-G01 | 2007-03-15 | Essex Junction | Construction of Asset ID 410, Essex Hydro Min. Flow unit #9, rated at .830 MW. | 2007-03-15 | Approved | 2007-09-27
GMP-07-410-C-5 | 2007-03-14 | Essex Junction | Construction of Asset ID 410, Essex Hydro Min. Flow unit #5, rated at .830 MW. | 2007-06-15
GMP-07-RR01 | 2007-03-14 | Essex #19 | Retirement of Asset ID 1221, Essex Diesels units IC #5, rated at 1.0 MW. | 2007-05-01 | Approved | 2007-06-08
GMP-07-RR02 | 2007-03-14 | Essex #19 | Retirement of Asset ID 1221, Essex Diesels units IC #6, rated at 1.0 MW. | 2007-05-01 | Approved | 2007-06-08
GMP-07-RR03 | 2007-03-14 | Essex #19 | Retirement of Asset ID 1221, Essex Diesels units IC #7 rated at 1.0 MW. | 2007-05-01 | Approved | 2007-06-08
GMP-07-RR04 | 2007-03-14 | Essex #19 | Retirement of Asset ID 1221, Essex Diesels units IC #8, rated at 1.0 MW. | 2007-05-01 | Approved | 2007-06-08
RESERVE | 2007-03-14 | Essex Junction | RESERVE | 2007-05-01
NU-05-T35 Rev. 2 | 2007-03-06 | Beacon Falls Substation | Reconductor the 115-kV 1570 Line Tap into Beacon Falls Substation. | 2009-12-01 | Approved | 2007-04-11
NEP-04-T24 Rev. 1 | 2007-02-27 | L-190 Line | Construction of a new 12.3 mile extension of the L-190 115 kV line from the Old Baptist Road Tap to the West Kingston Substation with 1590 ACSR. | 2008-06-01 | Approved with conditions | 2007-04-11
NEP-04-T25 Rev. 1 | 2007-02-27 | West Kingston Substation | Install 2nd 115 kV breaker and two (2) disconnect switches, replace existing 115 kV breaker #7085 and associated disconnect switches,install new 115 kV bus structures and conductors, install new substation fence, install new dead end structures with two (2) motor operated air break switches for the G185S and L190 lines within the new substation fence, and reterminate the West Kingston No. 2 115-34.5 kV transformer to the new line from the 1870N line. | 2008-06-01 | Approved with conditions | 2007-04-11
NEP-04-T26 Rev. 1 | 2007-02-27 | L-190 Line | Reconductor the 115 kV Line L190 from Kent County Substation to Old Baptist Road Tap. | 2008-06-01 | Approved with conditions | 2007-04-11
NEP-04-T27 Rev. 1 | 2007-02-27 | West Kingston and Kenyon | Reconductor the 115 kV Line 1870N from West Kingston Substation to Kenyon Substation. | 2008-06-01 | Approved with conditions | 2007-04-11
NEP-04-T28 Rev. 1 | 2007-02-27 | Kenyon and Wood River | Reconductor the 115 kV Line 1870 from Kenyon Substation to Wood River Substation. | 2008-06-01 | Approved with conditions | 2007-04-11
NEP-07-X01 | 2007-02-26 | Wood River and Shunock Substations | Removal of the 1870 Special Protection System following completion of the L-190 extension, West Kingston Substation expansion, L-190 reconductoring, 1870N reconductoring, and 1870 reconductoring as part of the Southern Rhode Island Project. | 2008-07-01 | Approved with conditions | 2007-04-11
NU-05-T23 Rev. 1 | 2007-02-26 | Scovill Rock 345 kV Switching Station | Expand the 345 kV Scovill Rock Switching Station and terminate associated 345 kV Lines. | 2009-12-01 | Approved with conditions | 2007-04-11
NU-05-T24 Rev. 1 | 2007-02-26 | Beseck Junction | Construct Beseck 345 kV Switching Station and terminate associated 345 kV Lines. | 2009-12-01 | Approved with conditions | 2007-04-11
NU-07-T02 | 2007-02-20 | Weare Substation | 44.8 MVA 115/34.5kV transformer, two 115kV circuit breakers which will sectionalize the F162 Line. A 115kV 28.8 MVAR capacitor bank at Jackman Substation. | 2008-06-01 | Approved | 2007-04-11
CMEEC-07-T01 | 2007-02-02 | Wallingford 115 kV Substation | Construction of new 115-kV circuit breaker and line position and addition of a new generator step-up transformer at the Wallingford 115-kV Substation to interconnect the proposed Pierce Generation Unit. | 2007-07-08 | Approved with conditions | 2007-03-08
CMEEC-07-G01 | 2007-02-01 | Pierce Generation Unit | Wallingford Pierce Generator | 2007-10-01 | Approved with conditions | 2007-03-08
CMP-07-T01 | 2007-01-31 | Maine Yankee 115 kV | Add a new distribution substation with a 10/14 MVA, 115/12.47 kV transformer, at the former Maine Yankee 115 kV yard. Section 207A already exists at the proposed site. | 2007-06-01 | Approved | 2007-03-09
NU-07-X01 | 2007-01-31 | Millstone 345kV Substation | Millstone SLOD Type 1 SPS. | 2007-03-30 | Approved | 2007-03-09
SHELD-07-T01 | 2007-01-31 | Pineshed 23F Substation | Replace the existing 2X transformer, which is rated 15/20/25 MVA with a larger transformer rated 33/44/55 MVA. | 2008-05-15 | Approved | 2007-04-11
CMP-06-T11 Rev. 1 | 2007-01-30 | Buxton Substation | Install four 345 kV breakers in a breaker-and-a-half configuration at Buxton substation and re-terminate Section 386 and Section 374. | 2007-12-01 | Approved | 2007-03-09
NEP-07-T01 | 2007-01-30 | Monroe Converter Station | To retire the Monroe converter station and related Phase I HVDC facilities; retain four (4) 20 Mvar of switched shunt reactors and four (4) 31.5 Mvar of switched capacitors. | 2007-03-31 | Approved with conditions | 2007-03-08
NSTAR-07-X01 | 2007-01-29 | Edgar | Trip setting of existing Edgar Special Protection System. | 2007-01-04 | Approved | 2007-03-20
NU-04-T03 Rev. 1 | 2007-01-29 | Norwalk & Peaceable 115 kV Stations | 115-kV line from Norwalk to Peaceable (1470) reconfiguration. | 2005-11-01 | Approved | 2007-03-09
NU-05-T09 Rev. 1 | 2007-01-29 | Norwalk and Glenbrook Substations | Installation of two, 115-kV 3500 kcmil XLPE cables between Glenbrook and Norwalk. | 2008-12-01 | Approved | 2007-03-09
NU-04-T01 Rev. 1 | 2007-01-25 | Plumtree and Norwalk 345 kV Stations | 345-kV Plumtree to Norwalk line and associated substation changes. | 2006-03-20 | Approved | 2007-03-09
NU-07-T01 | 2007-01-19 | Monadnock | Mobile 35 MVA 115/34.5-kV Transformer Installed at Monadnock, located in Monadnock New Hampshire in the Public Service Company of New Hampshire (PSNH) service territory. | 2006-07-01 | Approved | 2007-03-09
NSTAR-07-T03 | 2007-01-17 | Fisher Road Substation | Upgrade the Fisher Road Substation #657 Transformer #1 from a 10/12 MVA 115/13.2kV non-LTC transformer to a 12/16/20 [22.4] MVA 115/13.2kV transformer with LTC, remove secondary regulators, and associated upgrades. | 2007-06-15 | Approved | 2007-03-09
DEM-07-X01 | 2007-01-03 | Brayton Point Station | Replacement of Automatic Voltage Regulator on Brayton Point Unit 3. | 2006-05-01 | Approved with conditions | 2007-01-18
NU-07-G01 | 2007-01-02 | Pratt and Whitney | 9 MVA, 7.2 MW @ 0.8 PF Gas Turbine Generator. | 2007-09-30 | Approved with conditions | 2007-03-18
EME-06-T01 Rev. 1 | 2006-12-29 | Nash Stream Substation | Construction of the new Maine Mountain Windpower's Electric Harvest Substation. | 2007-12-31 | Approved | 2007-03-18
BP-06-T01 | 2006-12-28 | Rumford Falls Hydro | Re-connect existing Rumford Falls Hydro generation through new 11.5 kV : 115 kV generator step up transformer to new NewPage 115 kV Substation. | 2008-06-01 | Approved | 2007-03-18
CMP-06-T17 | 2006-12-21 | Rumford Substation | Add three 115 kV breakers in a ring-bus configuration, with a spare position for a future 115 kV circuit breaker, at a new NewPage 115 kV Substation, in Rumford, Maine, at the radial terminus of 115 kV line Section 218. | 2008-06-01 | Approved | 2007-01-18
NEP-06-T12 | 2006-12-20 | Sandy Pond HVDC | Convert two (2) existing 345 kV capacitor banks at Sandy Pond HVDC yard to 5th Harmonic Filters. | 2007-09-30 | Approved | 2007-01-18
NSTAR-07-T01 | 2006-11-29 | Marshfield Substation #739 | Upgrade Marshfield Substation #739 from a 12/16/20 MVA transformer to a 30/40/50 MVA transformer, and upgrade associated ancillary equipment. | 2007-06-01 | Approved | 2007-01-18
NSTAR-07-T02 | 2006-11-29 | Otis Substation #915 | Upgrade Otis Substation #915 from a 16/21/26 MVA transfomer to a 30/40/50 MVA transformer. | 2007-06-01 | Approved | 2007-01-18
CMP-06-T13 | 2006-11-28 | Benton Switching Station | Install six (6) 115 kV breakers in a ring-bus configuration and a 20 MVAr capacitor bank at the proposed new Benton 115 kV switching station in Benton, Maine. | 2008-12-01 | Approved with conditions | 2007-01-18
NEP-06-T06 Rev. 1 | 2006-11-21 | Bellows Falls Substation | Bellows Falls Substation revitalization. | 2008-05-01 | Approved | 2007-03-21
NU-06-G01 | 2006-11-19 | Lempster Wind Generating Facility | Modification of the existing protective relaying scheme that transfer trips the Hemp Hill generation for loss of the Webster-North Road and North Road-Ascutney 115 kV transmission lines. | 2006-11-01 | Approved with conditions | 2006-12-27
BHE-05-G01 Rev. 1 | 2006-11-16 | Georgia Pacific Mill | Interconnect a 16 MW generator at Georgia Pacific. | 2002-05-31 | Approved with conditions | 2006-11-30
CON-06-RR01 | 2006-10-30 | Asset # 1259 | Retirement of generator, J&L Electric Biomass One (Asset # 1259). | 2006-11-01 | Approved | 2007-03-20
CON-06-RR02 | 2006-10-30 | Asset # 10566 | Retirement of generator, J&L Electric Biomass One (Asset # 10566). | 2006-11-01 | Approved | 2007-03-20
NEP-06-T11 | 2006-10-19 | Wareham St. Substation | Close the E1-M1 115kV line loop at Wareham St. substation by adding three 115kV circuit breakers on the ring bus. | 2007-10-01 | Approved with conditions | 2006-12-14
NSTAR-06-T07 | 2006-10-18 | Tremont Substation | Addition of two bus tie breakers to Tremont 115-kV Substation to Sectionalize the Bus. | 2006-12-15 | Approved | 2006-12-14
VELCO-03-T02 Rev. 1 | 2006-10-18 | Blissville 115 kV | Upgrade the Blissville substation with a phase angle regulating transformer (PAR) rated 350 MVA and +/-60. | 2006-12-21 | Approved | 2006-12-18
VELCO-03-T06 Rev. 1 | 2006-10-18 | Granite 115 kV and 230 kV | At the Granite substation, replace the existing 230/115 kV autotransformer, and add a second 230/115 kV autotransformer, two 115 kV PARs rated 350 MVA and +/-60o, three 115 kV breakers, four 25 MVAr synchronous condensers, and 230 kV bus work with two breakers. | 2007-12-31 | Approved | 2006-12-20
VELCO-03-T07 Rev. 1 | 2006-10-18 | Granite 115 kV | Reconductor the Granite-Barre 115 kV line. | 2006-05-01 | Approved | 2006-12-18
VELCO-03-T10 Rev .1 | 2006-10-18 | West Rutland 345 kV | Construct a new 35.7 mi 345 kV line with bundled 954 ACSR conductors from West Rutland to New Haven. | 2006-12-31 | Approved | 2006-12-18
VELCO-03-T11 Rev. 1 | 2006-10-18 | Vergennes | Construct a new Vergennes 115 kV substation with two breakers, and a 115/34.5 kV 15 MVA transformer. | 2007-06-01 | Approved | 2006-12-19
VELCO-03-T15 Rev. 1 | 2006-10-18 | Queen City | Rebuild the Queen City 115 kV substation from a radial bus to a six-position, four-breaker 115 kV ring bus. | 2007-06-01 | Approved | 2006-12-19
VELCO-03-T16 Rev. 1 | 2006-10-18 | 115 kV line New Haven - Queen City | Replace the 27.2-mile 46kV/34.5 kV sub-transmission line with a 115 kV line from New Haven to Vergennes to North Ferrisburg to Charlotte to Shelburne to Queen City, single pole construction with 1272 ACSR conductors. Approximately 1.7 miles of this line will be underground 2500 MCM CU between Shelburne and Queen City. | 2007-12-31 | Approved | 2006-12-18
VELCO-06-T06 | 2006-10-18 | West Rutland 115 kV | Increase the length of the K-30 line (West Rutland-Middlebury) by approximately 1,050 feet. | 2006-12-31 | Approved | 2006-12-18
VELCO-06-T07 | 2006-10-18 | Middlebury 115 kV | Decrease the length of the K-63 line (Middlebury-New Haven) by approximately 600 feet. | 2006-12-31 | Approved | 2006-12-18
VELCO-06-T08 | 2006-10-18 | New Haven 115 kV | Increase the length of the K-43 line (New Haven-Williston) by approximately 1,100 feet. | 2006-12-31 | Approved | 2006-12-18
DEM-06-X01 | 2006-10-17 | Salem Harbor Unit 1 | Project will replace existing rotating AC excitation system for Salem Harbor Unit 1 with GE EX2100 static excitation system. | 2006-11-01 | Approved with conditions | 2006-11-14
NU-05-T22 | 2006-10-17 | Cedar Heights | Two new 115 kV circuit breakers and 115/13.8 kV transformer. | 2007-05-01 | Approved | 2005-11-08
NEP-06-T10 | 2006-10-11 | Melrose | At Melrose #25 substation, install a new 115/13.8kV low profile substation with two 55MVA transformers. | 2006-11-15 | Approved | 2006-11-14
VELCO-06-X01 | 2006-10-07 | Highgate | Modify the Highgate HVDC Converter runback schemes. | 2007-06-01 | Approved | 2006-10-24
ENB-06-DR01 Rev. 1 | 2006-09-27 | New Boston | New Boston Unit 1 deactivation. | 2006-11-15 | Approved | 2006-10-24
NEP-06-T09 | 2006-09-20 | Auburn St. Substation | Install new 345kV gas circuit breaker on line #335 at Auburn St. | 2006-06-01 | Approved | 2006-10-24
CMEEC-06-T01 | 2006-09-18 | Buddington | New 16L-4T-2 115-kV circuit breaker and 1410 line relay replacement. | 2006-10-31 | Approved | 2006-10-24
CMP-06-T12 | 2006-09-08 | Anson Substation | Tap Sect. 63B (customer owned) and construct a new 115/34.5 kV substation. | 2006-12-31 | Approved | 2006-10-27
VELCO-06-T03 | 2006-09-07 | East Avenue Substation | Rebuild the East Avenue substation to a 4-breaker ring. | 2007-06-01 | Approved | 2006-10-24
VELCO-06-T04 | 2006-09-07 | Gorge Substation | Construct a new 2-breaker substation at Gorge. | 2010-06-01 | Approved | 2006-10-24
VELCO-06-T05 | 2006-09-07 | Tafts Corner | Rebuild the K-25 line from H-frame to single-pole and construct a new single-pole 115 kV line on the same ROW. | 2009-06-01 | Approved | 2006-10-24
NEP-05-T06 | 2006-08-18 | Tewksbury 22 Substation | Swapping of the L-164 and A-153 115 kV radial line positions. | 2005-11-01 | Approved | 2005-07-25
NEP-05-T10 | 2006-08-16 | Snow St Substation | Replacement of two 115/23kV transformers with two 115/13.2kV transformers at Snow St substation in Southbridge, Massachusetts. | 2006-04-01 | Approved | 2005-09-02
NEP-05-T11 | 2006-08-16 | West Amesbury Substation | West Amesbury substation installation of the 345/115 kV and 115/23 kV transformers and a 345 kV and a 115 kV breakers. | 2005-09-20 | Approved | 2005-11-08
NEP-05-T13 | 2006-08-16 | Shaker Road Substation | Replacement of existing 69/13.8 kV transformer at Shaker Road substation. | 2005-11-14 | Approved | 2005-12-27
NU-05-T27 | 2006-08-15 | East Devon and Devon 115 kV Substations | Build Two 115 kV Circuits from East Devon Substation to Devon Substation. | 2009-12-01 | Approved | 2005-12-20
NU-05-T31 | 2006-08-15 | Devon 115 kV Substation | Install an additional 115 kV circuit breaker and permanently open the 1480 bus tie at the Devon 115 kV Substation. | 2009-12-01 | Approved | 2005-12-20
NU-05-T51 | 2006-08-14 | Haddam Neck 14B and Southington 4C Substations | Upgrade the Line 362 terminals at the Haddam Neck 14B and Southington 4C substations. | 2006-12-30 | Approved | 2005-12-27
NSTAR-06-G01 | 2006-07-19 | Medical Area Total Energy Plant | Medical Area Total Energy Plant. | 2006-12-21 | Approved | 2006-09-11
NU-06-T15 | 2006-07-18 | Barbour Hill | New 345-115 kV 600 MVA autotransformer to be located at the Barbour Hill 23J Substation. | 2008-06-30 | Approved | 2006-09-11
NU-06-T18 | 2006-07-13 | Oak Hill | Proposes adding a 2nd distribution transformer at Oak Hill substation and two breakers. | 2007-06-30 | Approved | 2006-09-11
NU-06-T19 | 2006-07-13 | Timber Swamp | Adding a new 345/34.5kV transformer and construct a four breaker ring bus at Timber Swamp Substation. | 2007-06-30 | Approved | 2006-09-11
PP-06-G01 | 2006-07-13 | Waterside Power | Construction of the 210.9 MW gross (at 50 F) Waterside Power Generation Project. | 2010-03-10 | Approved Withdrawn | 7/25/2006 11/17/2010
PP-06-T01 | 2006-07-13 | Waterside 22M Substation | Interconnecting the Waterside Power Generation Project at the Waterside 22M Substation. | 2010-03-10 | Approved Withdrawn | 7/25/2006 11/17/2010
NU-06-T16 | 2006-07-10 | Waterside | Replace 69MW of emergency peaking generation with an interconnection request of permanent generation. | 2010-03-01 | Approved | 2006-07-25
NU-06-X02 | 2006-07-10 | South End Substation | South End Substation and 1977 line relaying modifications. | 2010-03-01 | Approved | 2006-07-25
NU-06-T17 | 2006-07-05 | Scobie Pond | Reinforcement of the Scobie Pond 115 kV Substation to the Hudson 115 kV Substation. | 2008-05-01 | Approved | 2006-07-25
CMP-06-T03 | 2006-06-30 | Wyman Hydro Substation | Modification of the current configuration at Wyman Hydro with regard to Section 215 and Section 63. | 2007-07-01 | Approved | 2006-06-16
NEP-06-G02 | 2006-06-30 | Lowell | Install a new 115 kV tap (0.1 mile) utilizing 795 ACSR by tapping J-162 line to interconnect Lowell Power generation facilities. | 2007-12-01 | Approved Withdrawn | 7/25/2006 12/18/2012
NEP-06-T07 | 2006-06-30 | Lowell | Install a new 115 kV tap (0.1 mile) utilizing Lowell Power generation facilities. | 2007-12-01 | Approved Withdrawn | 7/25/2006 12/18/2012
NEP-06-T08 | 2006-06-30 | Sandy Pond | At Sandy Pond 115 kV substation replace two 115 kV circuit breakers. | 2007-12-01
CMP-06-T05 | 2006-06-13 | Maguire Road | Installation of nine (9) 115 kV circuit breakers in a breaker and a half configuration. | 2007-12-01 | Approved | 2006-06-23
CMP-06-T06 | 2006-06-13 | Louden and Maguire Road | The rebuild of 12 miles of 115 kV Section 163 between the Louden and the Maguire Road Substations. | 2008-01-01 | Approved | 2006-06-23
CMP-06-T07 | 2006-06-13 | Quaker Hill and Three Rivers | The rebuild of 9 miles of 115 kV Section 197 between the Quaker Hill and the Three Rivers Substations. | 2008-01-01 | Approved | 2006-06-23
CMP-06-T08 | 2006-06-13 | South Gorham and Louden | The rebuild of 9 miles of 115 kV Section 219 between the South Gorham and the Louden Substations. | 2008-12-01 | Approved | 2006-06-23
CMP-06-T09 | 2006-06-13 | South Gorham and Louden | The reconductoring of 9 miles of 115 kV Section 220 between the South Gorham and Louden Substations. | 2008-01-01 | Approved | 2006-06-23
CMP-06-T10 | 2006-06-13 | Sanford | The installation of a 30MVAr capacitor at the Sanford Substation. | 2007-12-01 | Approved | 2006-06-23
CMP-06-T11 | 2006-06-13 | Buxton | The installation of three (3) 345 kV breakers at the Buxton Substation by expanding the existing breaker and a half configuration. | 2008-12-01 | Approved | 2006-06-23
NU-06-X01 | 2006-06-13 | Lake Road | Modify the existing Lake Road Type III generation rejection special protection system (SPS). | 2006-12-31 | Approved with conditions | 2006-09-11
CMP-06-T02 | 2006-06-12 | Raymond Substation | Add (2) 115 kV line breakers and 2nd transformer. | 2006-12-31 | Approved | 2006-06-23
CMP-06-T04 | 2006-06-06 | Louden and Branch Brook Substations | Construction of a new 115 kV West Kennebunk Substation. | 2006-12-31 | Approved | 2006-06-23
EME-06-G01 | 2006-05-30 | Maine Mountain Power Windfarm | Addition of a new wind powered generating station, the Maine Mountain Power Windfarm. | 2007-12-31 | Approved with conditions | 2006-06-16
EME-06-T01 | 2006-05-24 | Nash Stream Substation | Construction of the new Maine Mountain Windpower's Electric Harvest Substation. | 2007-12-31 | Approved with conditions | 2006-06-10
NEP-06-G01 | 2006-05-24 | Fitchburg | Construction of the 7.2 MW Westminster Landfill Generation Project. | 2007-06-01 | Approved | 2006-06-16
DEVON-06-G01 | 2006-05-09 | Devon Station | Interconnection of Devon Power LLC's Unit #10. | 2006-06-29 | Approved with conditions | 2006-06-23
NEP-06-RR01 | 2006-05-06 | Nantucket | Retirement of six Nantucket diesel generators. | 2006-10-31 | Approved | 2006-07-25
NSTAR-06-T01 | 2006-05-02 | Chelsea Substation | Construct a six breaker 115 kV ring bus at Chelsea Substation #488. | 2006-06-01 | Approved with conditions | 2006-05-10
ENB-06-DR01 | 2006-05-01 | New Boston | Deactivated Reserve Asset # 505, the New Boston Unit No. 1 generating plant. | 2007-01-01 | Approved | 2006-07-25
NEP-06-T01 | 2006-05-01 | Sykes Road | Install a new 115 kV Tap from the M13 line, a 40 MVA 115/13.8 kV transformer, a 115 kV circuit switcher, and two 115 kV wave traps. | 2007-04-01 | Approved with conditions | 2006-06-16
NU-06-T13 | 2006-04-18 | Dooley 30K | Installation of a 115 kV circuit breaker. | 2006-06-01 | Approved | 2006-05-10
NU-06-T14 | 2006-04-18 | Sasco Creek 21R | Installation of a temporary 18 MVA, 115/13.8 kV transformer and a 115 kV circuit breaker at the Sasco Creek 51R Substation. | 2006-06-01 | Approved Withdrawn | 5/10/2006 6/20/2012
BHE-06-T01 | 2006-04-17 | Boggy Brook | Construction of a new 115 kV radial overhead transmission Line 61. | 2007-12-01 | Approved | 2006-05-10
BHE-06-T02 | 2006-04-14 | Boggy Brook | 35 miles of new 115 kV network transmission line originating as a tap on the new Line 61. | 2009-12-01 | Approved | 2006-05-10
NU-06-T12 | 2006-04-13 | Deerfield Substation | Install a new 345-kV circuit breaker at the Deerfield Substation. | 2006-06-01 | Approved | 2006-05-10
NEP-06-T06 | 2006-04-12 | Bellows Falls | Transmission upgrades in support of the Bellows Falls No. 14 Station Revitalization Project. | 2008-05-01 | Approved | 2006-05-10
NSTAR-06-T06 | 2006-03-24 | Sudbury Substation | Installation of a 52.5 MVA, 118 kV capacitor bank and a 115 kV isolating circuit breaker at the Sudbury Substation. | 2006-06-01 | Approved | 2006-05-10
NEP-06-X03 | 2006-03-23 | Millennium Power Plant | Activate power system stabilizers and modify excitation system parameters. | 2005-11-01 | Approved | 2006-04-07
NSTAR-06-T05 | 2006-03-23 | Needham Substation | Addition of a 37/50/62.5 MVA, 117/15.12 kV transformer at the Needham #148 Substation. | 2006-06-01 | Approved | 2006-05-10
CMP-06-X01 | 2006-03-01 | Maxcy's and Bucksport | NPCC Type I Special Protection System. | 2007-01-01 | Approved | 2006-03-24
NU-06-T06 | 2006-03-01 | Greggs Falls and Jackman | The F162 115 kV transmission line will be replaced with a new 1590 kcmil ACSR transmission line. | 2009-12-31 | Approved | 2006-03-24
NU-06-T07 | 2006-03-01 | Garvins and Webster | The V182 115-kV transmission line will be replaced with a new 1590 kcmil ACSR transmission line. | 2009-12-31 | Approved | 2006-03-24
NU-06-T08 | 2006-03-01 | Keene and Chestnut Hill | Replace a 5 mile section of the A152 115-kV transmission line with a new 1590 kcmil ACSR transmission line. | 2009-12-31 | Approved | 2006-03-24
NU-06-T09 | 2006-03-01 | Monadnock | Replace the 115-kV tap conductor that connects the Monadnock Substation. | 2009-12-31 | Approved | 2006-03-24
NU-06-T10 | 2006-03-01 | Fitzwilliam | Construction of a new 600MVA, 345/115-kV substation in Fitzwilliam, New Hampshire. | 2009-12-31 | Approved | 2006-03-24
NU-06-T11 | 2006-03-01 | Webster | Replace limiting secondary equipment at the Webster Substation 115 kV bus on the M127 115 kV transmission line terminal. | 2009-12-31 | Approved | 2006-03-24
WGE-06-T01 | 2006-03-01 | Buck Pond Substation | Addition of a second 25 MVA self cool/46.667 MVA FOA, 115/23 kV distribution transformer at the Buck Pond Substation. | 2007-06-01 | Approved | 2006-04-07
NSTAR-06-T02 | 2006-02-14 | Tremont Substation | Upgrading the existing Tremont Substation #113 transformer from a 12 MVA 115/23 kV transformer to a 12/16/20 MVA 115/23 kV transformer. | 2006-06-01 | Approved | 2006-03-24
NSTAR-06-T03 | 2006-02-14 | Orleans Substation | Upgrading the existing Orleans Substation #119 transformer from a 20/26/33 MVA 115/23 kV transformer to a 30/40/50 MVA 115/23 kV transformer. | 2006-06-01 | Approved | 2006-03-24
NSTAR-06-T04 | 2006-02-14 | Rochester Substation | upgrading the existing Rochester Substation #114 transformer from a 5/7 MVA 115/13.2 kV transformer to a 10/12.5 MVA 115/13.2 kV transformer. | 2006-06-01 | Approved | 2006-03-24
NEP-06-T03 | 2006-02-06 | Bellows Falls and Ascutney Tap | Retension the 115 kV W-149S line between Bellows Falls substation and Ascutney Tap. | 2006-04-01 | Approved | 2006-03-24
NEP-06-T04 | 2006-02-06 | Bellows Falls | Reconductoring the 51 mile long 115 kV I-135N Line between the Bellows Falls Substation and the Flagg Pond Substation. | 2008-06-01 | Approved | 2006-03-24
UI-06-T01 | 2006-02-06 | Milvon Substation | Replace fixed tap transformers at Milvon Substation with Load Tap Changing (LTC) transformers. | 2006-06-01 | Approved | 2006-03-22
UI-06-T02 | 2006-02-06 | Ansonia Substation | Replace fixed tap transformers at Ansonia Substation with Load Tap Changing (LTC) transformers. | 2006-12-01 | Approved | 2006-03-24
VELCO-06-T01 | 2006-02-06 | Coolidge Substation | Install a dynamic reactive device capable of a 150 MVAr range. | 2009-06-01 | Approved | 2006-03-24
VELCO-06-T02 | 2006-02-06 | North Rutland | Replacement of the 800 ampere K35 breaker. | 2009-06-01 | Approved | 2006-03-24
NEP-06-T02 | 2006-02-01 | E. Bridgewater | Install new 115 kV tap to the L1 line and 115/13.8 kV transformer at East Bridgewater substation. | 2006-12-30 | Approved | 2006-02-17
NU-06-T03 | 2006-02-01 | Scobie Pond | Addition of the Brentwood 115/34.5 kV substation. | 2006-05-01 | Approved | 2006-02-17
NU-06-T04 | 2006-02-01 | Scobie Pond | Addition of 115 kV Line N124. | 2006-05-01 | Approved | 2006-02-17
NU-06-T05 | 2006-02-01 | Scobie Pond 115 kV Substation | Reconfiguration of the 115 kV Scobie Pond Substation. | 2006-05-01 | Approved | 2006-02-17
NEP-06-X01 | 2006-01-31 | Moore and Comerford | Replacement of existing BJ-30 type voltage regulators with new voltage regulators. | 2010-12-31 | Approved | 2006-02-17
CES-06-DR01 | 2006-01-27 | Androscoggin Energy Center | Place in Deactivated Reserve the Androscoggin Energy Center. | 2006-04-30 | Approved | 2006-04-07
NU-05-T52 | 2006-01-26 | Oxford Substation | Construction of the new Oxford 26N 115/13.8 kV Substation. | 2008-05-01 | Approved | 2006-01-26
NU-06-T02 | 2006-01-18 | South End 1G | Addition of a 3rd 115 kV circuit breaker back-to-back with the existing Breaker 6T at the South End 1G Substation. | 2007-05-01 | Approved | 2006-02-17
NU-06-T01 | 2006-01-06 | 115 kV Ludlow 19S Substation | Addition of a circuit breaker in the 42T position at the 115 kV ludlow 19S Substation. | 2006-03-08 | Approved | 2006-02-17
NU-05-T55 | 2005-12-23 | Saco Valley Substation | Addition of a phase angle regulator on the Y-138 line with two 115 kV circuit breakers and a bypass switch. Addition of a 115 kV circuit breaker on the K1214 line connecting Saco Valley to the Maine border. | 2008-12-31 | Approved | 2006-01-26
NU-05-T56 | 2005-12-23 | White Lake Substation | Addition of a 14.4 MVar 115 kV capacitor bank with a 115 kV circuit switcher. Addition of a 7.2 MVar 115 kV capacitor bank with a 115 kV circuit switcher. Addition of 115 kV circuit breakers on the Y138 and B112 lines. | 2008-12-31 | Approved | 2006-01-26
NU-05-T57 | 2005-12-23 | Beebe River Substation | Addition of a phase angle regulator at the Saco Valley substation with circuit breakers at White Lake and Saco Valley and capacitors at White Lake and Beebe River. | 2006-12-31 | Approved | 2006-01-26
NSTAR-05-T09 | 2005-12-15 | Lexington Substation | Install a new 345 kV, 160 MVAR regulating shunt reactor at Lexington substation. | 2006-05-01 | Approved | 2005-12-27
VELCO-03-T01 Rev. 1 | 2005-12-15 | VELCO Sandbar Substation | Upgrade existing VELCO Sandbar Substation. | 2004-06-03 | Approved | 2005-12-27
NU-05-T53 | 2005-12-14 | Mansfield 12J | Replacement of circuit breakers at Mansfield 12J. | 2006-01-26 | Approved | 2006-01-26
NU-05-T23 | 2005-11-23 | Scovill Rock 345 kV Switching Station | Add 4 new 345 kV circuit breakers at Scovill Rock Substation. | 2009-12-01 | Approved | 2005-12-20
NU-05-T24 | 2005-11-23 | Beseck Junction | Construct a 345-kV Switching Station at Beseck Junction. | 2009-12-01 | Approved | 2005-12-20
NU-05-T25 | 2005-11-23 | East Devon 345 kV Substation | Construct East Devon 345 kV and 115 kV Substations. | 2009-12-01 | Approved | 2005-12-20
NU-05-T26 | 2005-11-23 | Beseck and East Devon 345 kV Substations | Build the 345 kV 3029 Line between Beseck Switching Station and East Devon Substation. | 2009-12-01 | Approved | 2005-12-20
NU-05-T28 | 2005-11-23 | 3165 & 3177 345 kV lines | Build Two 345-kV Underground Cables from East Devon Substation to Singer Substation. | 2009-12-01 | Approved | 2005-12-20
NU-05-T29 | 2005-11-23 | Norwalk 345 kV & 115 kV Substations | Expand the 345-kV Substation at Norwalk and Install Transfer Trip Relaying Scheme on the 1389 Line between Norwalk and Flax Hill Substations. | 2009-12-01 | Approved | 2005-12-20
NU-05-T30 | 2005-11-23 | Norwalk and Singer 345 kV Substations | Build two 345 kV underground cables from Singer Substation to Norwalk Substation. | 2009-12-01 | Approved | 2005-12-20
NU-05-T32 | 2005-11-23 | Norwalk Harbor Substation | Replace the 138/115 kV autotransformer at Norwalk Harbor Substation. | 2009-12-01 | Approved | 2005-12-20
NU-05-T34 | 2005-11-23 | North Wallingford and East Meriden Substations | Rebuild Portions of the 115 kV 1466 Line between North Wallingford-East Meriden substations. | 2009-12-01 | Approved | 2005-12-20
NU-05-T35 | 2005-11-23 | Beacon Falls Substation | Reconductor the 115-kV 1570 line tap into Beacon Falls Substation. | 2009-12-01 | Approved | 2005-12-20
NU-05-T36 | 2005-11-23 | Southington and June Street 115 kV Substations | Rebuild a portion of the 115 kV 1610 line between Cook Hill Junction and June Street Substation. | 2009-12-01 | Approved | 2005-12-20
NU-05-T37 | 2005-11-23 | Devon and Wallingford 115 kV Substations | Rebuild portions of the 115 kV 1640 line between Cook Hill Junction and Devon Substation. | 2009-12-01 | Approved | 2005-12-20
NU-05-T38 | 2005-11-23 | Branford and New Haven 115 kV Substations | Rebuild a portion of the 115 kV 1655 line between East Wallingford Junction and New Haven Junction. | 2009-12-01 | Approved | 2005-12-20
NU-05-T39 | 2005-11-23 | Devon and June Street 115 kV Substations | Rebuild a portion of the 115 kV 1685 line between June Street and Devon substations. | 2009-12-01 | Approved | 2005-12-20
NU-05-T40 | 2005-11-23 | Devon 115 kV Substation | Remove the 115-kV 1690 line from Devon Substation to Cook Hill Junction. | 2009-12-01 | Approved | 2005-12-20
NU-05-T41 | 2005-11-23 | Devon 115 kV Substation | Rebuild the 115-kV 1780 and 1790 lines from Devon Substation to Devon Tie Switching Station. | 2009-12-01 | Approved | 2005-12-20
NU-05-T42 | 2005-11-23 | East Meriden and Haddam 115 kV Substations | Rebuild a portion of the 115-kV 1975 line between East Meriden and Haddam substations. | 2009-12-01 | Approved | 2005-12-20
NU-05-T43 | 2005-11-23 | Flax Hill 115 kV Substation | Reclassify Flax Hill 115 kV Substation as an NPCC Bulk Power System Facility. | 2009-12-01 | Approved | 2005-12-20
NU-05-T44 | 2005-11-23 | Glenbrook, Southington, and Millstone Substations | Replace six 115-kV and two 345-kV circuit breakers to mitigate over-duty conditions. | 2009-12-01 | Approved | 2005-12-20
NU-05-X02 | 2005-11-23 | Scovill Rock 345 kV Switching Station | Formerly NU-05-T33 - Modify the Cross Sound Cable 387 line end-open special protection system. | 2009-12-01 | Approved | 2005-12-20
UI-05-T01 | 2005-11-23 | Singer & Pequonnock substations | Contruct Singer 345 kV Substation, Modify Pequonnock 115 kV Substation, and Modify Bridgeport Energy's Interconnection. | 2009-12-31 | Approved | 2005-12-20
UI-05-T02 | 2005-11-23 | 3165 & 3177 345 kV lines | Install two 345 kV underground circuits from East Devon to Singer substation. | 2009-12-31 | Approved | 2005-12-20
UI-05-T03 | 2005-11-23 | Elmwest substation | Install two 115 kV circuit breakers at Elmwest substation. | 2009-12-31 | Approved | 2005-12-20
UI-05-T04 | 2005-11-23 | Devon Station and Devon Tie Switching Station | Rebuild 1780 and 1790 circuits from Devon substation to Devon Tie Switching Station | 2009-12-31 | Approved | 2005-12-20
UI-05-T05 | 2005-11-23 | Baird, Bridgeport RESCO, Broadway, Devon Tie... | Elmwest, Mill River, Water Street, & West River to be modified & reclassified. | 2009-12-31 | Approved | 2005-12-20
VELCO-02-T01 Rev. 1 | 2005-11-01 | Highgate Substation | Rebuild the existing VELCO and CZN Highgate Substations into a single Highgate Substation with a 115 kV ring bus, now revised to reflect a changed ring bus design. | 2005-12-01 | Approved | 2005-11-08
VELCO-02-T03 Rev. 1 | 2005-11-01 | St. Johnsbury Substation | Modify St. Johnsbury substation and replace switch 39-3 with a circuit breaker, now revised to reflect the replacement of both the 39-3 and 29-3 motor operated switches with circuit breakers. | 2005-12-01 | Approved | 2005-11-08
VELCO-03-T03 Rev. 1 | 2005-11-01 | Hartford Substation | Upgrade Hartford Substation to add a 24.75 MVAR capacitor bank. | 2005-12-01 | Approved | 2005-12-27
NSTAR-05-G01 | 2005-10-09 | BioGen Idec Campus | Adding a generator at the BioGen Idec Campus. | 2005-12-15 | Approved | 2005-10-14
NU-05-T20 | 2005-09-27 | Stepstone 35L Substation | Construction of the new Stepstone 35L Substation. | 2007-06-01 | Approved | 2005-11-08
NU-05-T21 | 2005-09-23 | Green Hill 30R | Installation of a third 47 MVA 115/13.2 kV distribution transformer and a 115 kV circuit breaker, with associated disconnects, at the Green Hill 30R Substation. | 2007-06-01 | Approved | 2005-11-08
NEP-05-T12 | 2005-09-19 | Hobart Street Substation | Additional third transformer at Hobart Street Substation. | 2006-04-01 | Approved | 2005-10-14
NU-05-T19 | 2005-09-08 | Cos Cob, Tomac, and South End Substations | Line 1750 (5 spans) and terminal equipment at South End. | 2006-12-01 | Approved | 2005-10-14
CMP-05-T01 | 2005-08-31 | Kimball Road Substation | Install two new 30 MVAR capacitor banks and 115/34 kV transformer at the Kimball Rd Substation. | 2007-05-01 | Approved | 2005-11-08
NU-05-T18 | 2005-08-30 | Dooley 30K | Addition of a 115/13.2 kV 2 winding transformer at Dooley 30K. | 2005-06-30 | Approved | 2005-10-14
NU-05-T17 | 2005-08-23 | Haddam 11C Substation | Install 115/23 kV, 28/37.3/46.7 MVA distribution transformer and a 115 kV circuit breaker at Haddam 11C Substation. | 2004-12-01 | Approved | 2005-10-14
NSTAR-05-T08 | 2005-08-03 | Tremont Substation | Upgrade Tremont #114 transformer to a 12/16/20 MVA 115/23kV. | 2005-08-08 | Approved | 2005-10-14
EMI-05-G01 | 2005-07-15 | Nantucket | Installation of a new offshore wind powered generating system. | 2006-06-01 | Approved | 2005-10-06
NSTAR-05-T07 | 2005-07-15 | Cape Wind | Two 115 kV underground/submarine lines + 4-115 kV shunt reactors. | 2006-12-31 | Approved Withdrawn | 10/6/2005 1/1/2014
NSTAR-05-X02 | 2005-07-15 | Barnstable | Modify the Barnstable SPS for the 2nd Nantucket interconnection project, to ramp down gen to 300 MW. | 2006-12-31 | Approved Withdrawn | 10/6/2005 1/1/2014
NSTAR-05-X03 | 2005-07-15 | Canal substation | Install SPS at Canal to trip Canal #2 or Cape Wind for l/o 322/345 DCT. | 2006-12-31 | Approved Withdrawn | 10/6/2005 1/1/2014
NEP-05-T07 | 2005-07-13 | Ward Hill Substation | Expansion of the 345 and 115 kV switchgear. | 2006-06-01 | Approved | 2005-10-06
NEP-05-T08 | 2005-07-13 | Salem Harbor Substation | Installation of two 63 MVAr 115 kV capacitor banks. | 2005-12-31 | Approved | 2005-10-06
NEP-05-T09 | 2005-07-13 | Golden Hills and Lynn Substations | Reconductor the 115 kV Q-169 line between Golden Hills Substation and Lynn Substation. | 2006-06-01 | Approved | 2005-09-02
NEP-05-X01 | 2005-07-13 | South Danvers Substation | Protection Modifications to meet NPCC requirements | 2007-12-31 | Approved | 2005-10-06
NEP-05-X02 | 2005-07-13 | East Methuen substation | Protection Modifications to meet NPCC requirements | 2007-12-31 | Approved | 2005-10-06
NEP-05-X03 | 2005-07-13 | West Methuen substation | Protection modifications to meet NPCC requirements | 2007-12-31 | Approved | 2005-10-06
NSTAR-05-T06 | 2005-07-11 | Mystic and Chelsea Substations | Upgrade 115 kV line 488-518 / P-168 between Mystic and Chelsea stations. | 2005-12-01 | Approved | 2005-09-02
NU-05-T05 | 2005-07-01 | Barbour Hill | Add second 115/23 kV, 47 MVA transformer and 115 kV circuit breaker. | 2006-12-01 | Approved | 2005-07-25
NU-05-T14 | 2005-06-28 | Pleasant and Woodland Substations | Install 2-14.4 MVAR 115 kV capacitor banks at both Pleasant and Woodland. | 2006-05-31 | Approved | 2005-07-25
NU-05-T11 | 2005-06-22 | Three Rivers 115 kV Substation | Add a 115 kV circuit breaker to the Three Rivers Substation on Line N133. | 2004-05-01 | Approved | 2005-07-25
NU-05-T12 | 2005-06-20 | Millstone 15G | Remove circuit breakers 3t and 6T due to the retirement of Millstone Unit 1. | 2005-09-30 | Approved | 2005-06-24
NU-05-T09 | 2005-06-14 | Glenbrook and Norwalk Substations | Installation of two, 115-kV 3500 kcmil XLPE cables between Glenbrook and Norwalk Substations. | 2008-12-31 | Approved | 2005-08-03
NU-05-T15 | 2005-06-10 | Plumtree 30G | Install a new 115 kV circuit breaker and a 47 MVA 115/13.8 kV transformer. | 2007-03-30 | Approved | 2005-09-01
NU-05-RR02 | 2005-06-07 | Beech Mill Hydro-Electric Facility | Retirement of Beech River Mill hydro-electric facility. | 2005-09-01 | Approved | 2005-06-24
NU-05-T08 | 2005-06-03 | Fairmont 16H | Install circuit switchers at Fairmont 16H substation. | 2005-11-15 | Approved | 2005-07-25
NU-03-T13 Rev. 2 | 2005-05-31 | Haddam 11C Substation | Upgrades to the Haddam 11C Substation. | 2005-12-01 | Approved | 2005-07-25
DEM-05-T01 | 2005-05-27 | Brayton Point Station | Install 115 kV station service supply system for new air emission control equipment. | 2005-10-31 | Approved with conditions | 2005-06-24
LOWELL-05-DR01 | 2005-05-20 | Lowell Power | Request to deactivate upon approval of application. | 2005-06-01 | Approved | 2005-05-17
NSTAR-05-T05 | 2005-05-17 | North Cambridge Station #509 | In service Fall 2005. Install shunt reactor and IPT circuit breaker w/ synchronous controller. | 2005-10-31 | Approved | 2005-05-17
NU-05-T10 | 2005-05-16 | 1750 Line at Cos Cob 11R | Upgrade terminal equipment on the 1750 line at Cos Cob 11R. | 2005-06-01 | Approved | 2005-06-24
NU-05-T06 | 2005-05-03 | Ashland, Hudson, & Long Hill | Replace existing distributuin 115/34.5 kv transformers with 44.8 MVA transformers. | 2006-06-06 | Approved | 2005-06-24
NU-05-T04 | 2005-04-28 | Wilton 35A | New substation with two 115/13.8 transformers connecting on the 1470 line. | 2007-03-31 | Approved | 2005-06-24
NSTAR-05-T04 | 2005-04-26 | Chelsea Substation | Replace the 115/13.8 kV Chelsea Station #488 transformer 110C. | 2005-06-01 | Approved | 2005-06-24
CMEEC-05-G01 | 2005-04-22 | South Norwalk Electric Works Substation | Reactivation of the SNEW emergency engine with a nominal rating of 1.1 MW gross and net. | 2005-06-01 | Approved with conditions | 2005-05-20
CNEEC-05-G01 | 2005-04-22 | South Norwalk | Reactivate the SNEW EE unit (old name SNES Diesel #5) | 2005-06-05 | Approved with conditions | 2005-05-20
NU-05-T07 | 2005-03-28 | Flanders 11Y | 115 kV circuit breaker circuit switcher and MOD addition. | 2006-06-01 | Approved | 2005-04-06
BHE-05-G01 | 2005-03-01 | Georgia Pacific Mill | Interconnect a 16 MW generator at Georgia Pacific. | 2005-03-13 | Approved with conditions | 2005-03-21
CMP-05-G01 | 2005-02-23 | Union Street substation | 6 MW temporary generation to be used as backup for contingency coverage. | 2005-06-06 | Approved | 2005-03-10
NSTAR-05-T03 | 2005-02-23 | Dover Station | Install an additional 115/13.8 kv transformer at Dover station. | 2005-05-31 | Approved with conditions | 2005-03-21
NEP-05-T05 | 2005-02-22 | East Dracut | New 115/13kV trans., replace existing trans. and install two 115kV circuit switchers at East Dracut. | 2005-03-10 | Approved | 2005-03-10
NSTAR-05-T02 | 2005-02-22 | Barnstable substation - Merchant's Way | Expand Barnstable sub with 4th bay, new line Barnstable-Merchant's Way, 2 cap banks(Falmouth&Orleans). | 2005-12-15 | Approved | 2005-03-10
NSTAR-05-X01 | 2005-02-22 | Barnstable Substation | SPS will trip the #118 line, Mashpee load and block Nantucket load transfer for loss of 122/120 DCT. | 2005-12-15 | Approved | 2005-03-10
NEP-05-T04 | 2005-02-17 | 115 kV line E-183W | Relocate line E-183W between Franklin Square substation and the Phillipsdale Tap. | 2006-05-01 | Approved | 2005-03-10
NEP-05-T03 | 2005-02-15 | Merchant's Way | New distribution substation to be know as "Merchant's Way." | 2005-12-15 | Approved | 2005-03-10
NU-05-T03 | 2005-02-15 | Tioga Power Project | Build two new 115 kV substations; Bedford & N. Merrimack & line upgrades. | 2005-06-01 | Approved | 2005-03-23
NU-05-T02 | 2005-02-03 | Amherst Substation | Amherst transformer replacement - existing 18/24/30 MVA; new 28/37/47 MVA | 2005-05-31 | Approved | 2005-03-10
DEM-05-RR01 | 2005-02-02 | Salem Harbor Station | Retirement of Salem Harbor unit 1. | 2005-05-03 | Not approved | 2005-02-25
DEM-05-RR02 | 2005-02-02 | Salem Harbor Station | Retirement of Salem Harbor unit 2. | 2005-05-03 | Not approved | 2005-02-25
DEM-05-RR03 | 2005-02-02 | Salem Harbor Station | Retirement of Salem Harbor unit 3. | 2005-05-03 | Not approved | 2005-02-25
DEM-05-RR04 | 2005-02-02 | Salem Harbor Station | Retirement of Salem Harbor unit 4. | 2005-05-03 | Not approved | 2005-02-25
NEP-05-G01 | 2005-01-24 | Hoosac Wind Farm | Connection of 20, 1.5 MW wind turbines w/2 collector stations. | 2005-12-31 | Approved with conditions | 2005-02-05
NEP-05-T01 | 2005-01-24 | Hoosac Wind Farm substation | New 69/34.5 kV substation connected to Y-25S line between Deerfield and Harriman. | 2005-12-31 | Approved with conditions | 2005-02-08
NEP-05-T02 | 2005-01-24 | Y-25S | Reconductor 69 kV Y-25S line between Deerfield 5 and Harriman substations. | 2005-12-31 | Approved | 2005-02-08
VELCO-05-T01 | 2005-01-24 | Y-25 Line & Bennington Substation | Reconductor the 69 kV Y-25 line from Bennington to NGRID border & replace 115/69 trans. @ Bennington | 2005-06-01 | Approved | 2005-02-08
NU-05-G01 | 2005-01-21 | UCONN Co-Gen Facility | Interconnection of new CC generation with no net injection to NE system. | 2005-06-01 | Approved with conditions | 2005-03-21
NU-05-T01 | 2005-01-21 | UCONN Project Interconnection | Interconnection of UCONN generation to the 800 line between Mansfield and Card substations. | 2005-06-01 | Approved with conditions | 2005-03-21
NEP-04-T05 Rev. 1 | 2005-01-10 | Wachusett No. 47 | Expansion of the existing Wachusett sub. to loop 345 kV lines 314 & 343. Add new 345 kV GIS sub. | 2006-09-29 | Approved | 2005-01-28
NSTAR-05-T01 | 2005-01-04 | Framingham and Speen Street Stations | The relocation of 115 kV Line 433-507 from a double circuit tower structure onto a set of new structures to be constructed. | 2005-06-01 | Approved | 2005-01-28
ENTERGY-03-X01 | 2005-01-03 | Vermont Yankee Substation | Install an NPCC Type III Special Protection System (for tripping the proposed 30 MVAR cap bank). | 2005-03-30
NU-04-X01 Rev. 1 | 2005-01-03 | Lake Road | Modify the existing Lake Road Type III Special Protection System (SPS). | 2006-12-01 | Approved with conditions | 2005-01-28
NEP-04-G01 Rev. 1 | 2004-12-22 | Fotistar Peabody | Construct a new simple cycle plant with a net capability of 97.2 MW. | 2006-05-01 | Approved | 2005-01-28
NU-04-T41 | 2004-12-22 | West Side 7A | Replacement of a 110/14.4 kV autotransformer at West Side 7A. | 2005-01-30 | Approved | 2005-01-28
UI-04-T04 | 2004-12-07 | Pequonnock 115 kV Substation | Uprate the 15 existing gas circuit breakers at the Pequonock 115 kV substation. | 2005-07-31 | Approved | 2005-01-28
NEP-04-T30 | 2004-11-23 | Foristar Peabody | Construction of the Fortistar Peabody 115 kV switchyard. | 2006-05-01 | Approved | 2005-01-28
NSTAR-04-T04 Rev. 1 | 2004-11-23 | Stoughton Station | Phase I: New 345 kV Stoughton open air switching station with numerous associated upgrades. Phase II: Additional parallel cables to those installed in Phase I, numerous associated upgrades. Addition to the NSTAR Electric 345 kV Transmission Reliability Project as previously identified in the original submittal of NSTAR-04-T04 with the following protection system upgrades: Type III SPS. | 2006-06-01 | Approved with conditions | 2005-02-10
NU-04-T39 | 2004-11-23 | Portland 21H Substation | Replace the 115/13.2 kV transformer, add bus tie CB and add 3 circuit switchers. | 2006-05-31 | Approved | 2005-01-28
NEP-04-T27 | 2004-11-22 | West Kingston and Kenyon | Reconductoring 4.3 miles of the 115 kV 1870N Line portion from the West Kingston No. 62 Substation to the Kenyon No. 68 Substation. | 2007-06-01 | Approved | 2005-01-28
NEP-04-T28 | 2004-11-22 | Kenyon and Wood River | Reconductoring 3.9 miles of the 115 kV 1870 Line portion from the Kenyon No. 68 Substation to the Wood River No. 85 Substation. | 2007-06-01 | Approved | 2005-01-28
NSTAR-04-T05 | 2004-11-22 | Mamonet Substation | The replacement of an existing 12/16/20 MVA, 115/23 kV transformer with a 30/40/50 MVA, 115/23 kV transformer at the Manomet 115 kV Substation. | 2005-06-01 | Approved | 2004-12-17
NSTAR-04-T07 | 2004-11-22 | Roxbury | Construct a new 115/14 kV substation in Roxbury, MA. | 2005-06-01 | Approved | 2004-12-17
NU-04-T37 | 2004-11-18 | Plumtree & Triangle Substations | Bring the Plumtree-Middle River-Triangle area performance in compliance with planning criteria. | 2007-05-31 | Approved | 2004-12-17
NU-04-T38 | 2004-11-04 | Three Rivers 115 kV Substation | Addition of a 115 kV circuit breaker to line N133 for providing fault isolation. | 2004-05-31
BHE-04-T01 | 2004-10-26 | Graham and Rebel Hill Substations | Reconductoring of 13 miles of BHE 115 kV transmission, utilizing size 795 kcm conductor and the replacement of 71 structures. | 2005-07-01 | Approved | 2004-12-17
BHE-04-T02 | 2004-10-26 | Boggy Brook and Rebel Hill Substations | Reconductoring of 13.7 miles of BHE 115 kV transmission, utilizing size 795 kcm conductor and the replacement of 63 structures. | 2005-07-01 | Approved | 2004-12-17
NU-04-T17 | 2004-10-20 | Farmington 1C | Installation of 115/23 kV transformer and two 115 kV breakers at Farmington substation. | 2004-12-30 | Approved | 2004-11-18
NU-04-T36 | 2004-10-20 | Todd 30L | Installation of 115-13.8 kV transformer and 115 kV circuit reaker at Todd substation. | 2004-10-31 | Approved | 2004-11-10
NEP-04-T24 | 2004-10-18 | L190 line | Extend 115 kV line L190 from Davisville/Old Baptist Road tap to West Kingston substation. | 2007-05-31 | Approved | 2004-11-10
NEP-04-T25 | 2004-10-18 | West Kingston | Rebuild West Kingston Substation; install two 115 kV breakers, four disconnect switches. | 2007-05-31 | Approved | 2004-11-10
NEP-04-T26 | 2004-10-18 | L190 line | Reconductor the 115 kV line L190 from Kent County substation to Davisville/Old Baptist Road Tap. | 2007-05-31 | Approved | 2004-11-10
NU-04-G02 | 2004-10-17 | Uncasville 1Q | New 14.5 MW duel-fuel gas turbine will operate to reduce load at the cogeneration facility. | 2004-11-14 | Approved | 2004-11-08
BEMI-04-G03 | 2004-10-14 | Powersville Road | Temporarily interconnect two units of the Weldon Power Station to the Bangor Hydro line 84 during the generation frequency conversion. | 2004-03-22 | Approved with conditions | 2004-11-10
BEMI-04-G04 | 2004-10-14 | Powersville Road | Permanently reconnecting the four converted units (19.2 MW converted from 40 Hz to 60 Hz). | 2005-08-14 | Approved with conditions | 2004-11-10
UI-04-T03 | 2004-10-13 | 1710/1730 Pequonnock - Seaview 115 kV cables | Maintain the ratings of the 1710/1730 cable circuits. The measures being undertaken will not result in changes in transmission line ratings or capacity. | 2004-09-30 | Approved | 2004-11-08
CMP-04-T02 | 2004-10-11 | Fore River Substation | Construct the new Fore River 115 kV to 12.47 kV distribution substation. The new substation will tap the 275 115 cable between Sewall St. and Cape substations. | 2005-06-30 | Approved | 2004-11-08
NU-04-T20 Rev. 1 | 2004-10-07 | Tracy 14M | Construct new 345/115 kV Killingly 2G substation for installation of the new autotransformer. | 2006-11-30
NEP-04-T22 Rev. 1 | 2004-09-23 | Whitins Pond Substation | Install a new tap at the existing Whitins Pond substation to the 115 kV R-144 line, a 55 MVA 115/13.8 kV transformer, and a 115 kV circuit switcher; replace a 20 MVA 115/13.8 kV transformer with a 55 MVA unit and 115 kV air break w/ circuit switcher. | 2006-06-30 | Approved | 2004-11-10
NEP-04-T23 Rev. 1 | 2004-09-23 | Rocky Hill Substation | Install a new tap at the existing Rocky Hill substation to the 115 kV D-130 line, a 55 MVA 115/13.8 kV transformer, a 115 kV circuit switcher, and two in-line load breaks. | 2006-06-30 | Approved | 2004-11-10
LOWELL-04-DR01 | 2004-09-22 20:00 | Lowell Power, LLC | Place Lowell Power LLC generating unit into deactivated reserve.
LOWELL-04-DR01 | 2004-09-22 20:00 | Lowell Power, LLC | WITHDRAWN: Place Lowell Power LLC generating unit into deactivated reserve.
CMEEC-04-G02 | 2004-09-20 | SNEW Power Station | Install three 16.3 MW (net) generators interconnected to the Norwalk 9S substation through distribution lines. | 2006-05-31 | Approved with conditions Withdrawn | 10/7/2004 8/23/2011
UI-04-T02 | 2004-09-19 | East Shore - Grand Avenue - Totoket Junction | Relocation of structures, overhead and underground lines for the I-95 New Haven Harbor Crossing Corridor Improvement Program. (387, 1460, 8100, 8200, 88003A&B, 8500 lines with no changes to configuration and length.) | 2005-01-31 | Approved | 2004-10-08
HGE-04-T01 | 2004-09-13 | Ingleside 52W Substation | Addition of third 115/13.8 kV transformer and second 115 kV circuit breaker. | 2005-10-14 | Approved | 2004-10-07
NU-04-T35 | 2004-08-29 | Ashfield substation | Replace the single set of 115 kV fuses with two circuit switchers to allow for automatic transfer of Ashfield substation load. | 2004-11-29 | Approved | 2004-10-07
NEP-04-T22 | 2004-08-26 | Whitins Pond Substation | Install a new tap at the existing Whitins Pond substation to the 115 kV R-144 line, a 55 MVA 115/13.8 kV transformer, and a 115 kV circuit switcher; replace a 20 MVA 115/13.8 kV transformer with a 55 MVA unit and 115 kV air break w/ circuit switcher. | 2006-06-30
NEP-04-T23 | 2004-08-26 | Rocky Hill Substation | Install a new tap at the existing Rocky Hill substation to the 115 kV D-130 line, a 55 MVA 115/13.8 kV transformer, a 115 kV circuit switcher, and two in-line load breaks. | 2006-06-30
NU-04-T34 | 2004-08-26 | Rochester Substation | Addition of a second 115 kV line and 115 kV circuit breaker to the Rochester substation. | 2004-09-30 | Approved | 2004-09-02
NEP-04-T19 | 2004-08-23 | X-176 115 kV line | Upgrade the X-176 115 kV circuit (Palmer substation - NEP/NU border). This involves reconductoring of the overhead line as well as terminal equipment upgrades at Palmer substation. | 2005-04-01 | Approved | 2004-10-07
FPLE-04-G02 | 2004-08-19 | Seabrook Station | The Seabrook Power Uprate will increase the output of the Seabrook Station to a maximum gross output of 1,318 MW. Phase II will occur after approval by the NRC of a license amendment to reduce the measurement uncertainty of the secondary coolant flow. | 2006-09-30 | Approved with conditions | 2004-09-02
FPLE-04-G02 Rev. 1 | 2004-08-19 | Seabrook Station | Removal of conditions 5 and 6 in ISO Approval Letter. The Seabrook Power Uprate will increase the output of the Seabrook Station to a maximum gross output of 1,318 MW. Phase II will occur after approval by the NRC of a license amendment to reduce the measurement uncertainty of the secondary coolant flow. | 2006-09-30 | Approved with conditions | 2006-10-24
NU-04-G01 | 2004-08-19 | Berkshire WindPower | Connect 10, 1.5 MW wind turbine generators. These generators will connect at distribution voltage at the Partridge 115 kV substation. | 2004-12-31 | Approved with conditions | 2004-09-02
NU-04-T33 | 2004-08-17 | Shaws Hill Substation | Install a second 115/13.8 kV transformer and a 115 kV tie breaker. | 2005-06-29 | Approved | 2004-09-02
CMEEC-04-G01 | 2004-08-03 | Norwalk 9S | Installation of three Catapillar diesel generators. | 2004-07-31 | Approved with conditions | 2004-08-12
NU-04-T25 | 2004-08-02 | Berlin Substation | Upgrade the Berlin substation to bulk power system standards. | 2007-12-30 | Approved | 2004-09-02
NU-04-T26 | 2004-08-02 | South Meadow Substation | Upgrade the South Meadow substation to bulk power system standards. | 2005-12-30 | Approved | 2004-09-02
NU-04-T27 | 2004-08-02 | Southwest Hartford substation | Upgrade the Southwest Hartford substation to bulk power system standards. | 2008-12-30 | Approved | 2004-09-02
NU-04-T28 | 2004-08-02 | East Hartford substation | Upgrade the East Hartford substation to bulk power system standards. | 2006-12-30 | Approved | 2004-09-02
NU-04-T29 | 2004-08-02 | Northwest Hartford Substation | Upgrade the Northwest Hartford substation to bulk power system standards. | 2006-12-30 | Approved | 2004-09-02
NU-04-T30 | 2004-08-02 | East Springfield substation | Upgrade the East Springfield substation to bulk power system standards. | 2005-12-30 | Approved | 2004-09-02
NU-04-T31 | 2004-08-02 | South Agawam substation | Upgrade the South Agawam substation to bulk power system standards. | 2007-12-30 | Approved | 2004-09-02
NU-04-T32 | 2004-08-02 | Garvins Substation | Upgrade the Garvins substation to bulk power system standards. | 2008-12-30 | Approved | 2004-09-02
NU-04-T15 | 2004-07-12 | Hanover 12F Substation | Installation of 115-23 kV transformer and circuit switchers with removal of 115 kV breaker at Hanover substation. | 2004-04-30 | Approved | 2004-08-03
NSTAR-04-T04 | 2004-07-08 | Stoughton 345 kV Switching Station | Phase I: New 345 kV Stoughton open air switching station with numerous associated upgrades. Phase II: Additional parallel cables to those installed in Phase I, numerous associated upgrades. | 2006-06-01 | Approved with conditions | 2004-08-03
NU-04-T24 | 2004-07-07 | Canton 5R | Install of a 47 MVA 115/ 23 kV distribution transformer at the Canton 5R Substation to be used as emergency backup in the event of a failure of 1X or 2X. | 2004-12-30 | Approved | 2004-07-26
NEP-01-G01 Rev. 1 | 2004-07-06 20:00 | UAE Lowell Power | WITHDRAW: Construct new simple cycle generating plant consisting of 2 CT's with a combined net capacity of 95.2 MW at 20 degrees F to be built adjacent to existing UAE Lowell Facility | 2001-05-31 20:00 | Approved | 2004-08-03 20:00
NEP-02-G01 Rev. 1 | 2004-07-06 | Tewksbury Substation | WITHDRAW: Construct a new gas-fired, simple cycle generation plant consisting of 3-CTs designated the UAE Tewksbury Station with a combined net capability of 548.6 MW at 20 F, 554.6 MW at 50 F and 540.0 MW at 90 F. | 2002-12-31 | Approved | 2004-08-03
NEP-02-T02 Rev. 1 | 2004-07-06 | Tewksbury Substation | WITHDRAW: Installation of two (2) new 345 kV two-breaker GIS bays along with associated buswork switches and terminal equipment. | 2002-12-31 | Approved | 2004-08-03
NU-04-T23 | 2004-06-22 | Falls Village (9A) | Replace two Generator Step-Up Transformers with a single Generator Step-Up Transformer at Falls Village (9A) Substation. | 2004-09-30 | Approved | 2004-07-26
NU-04-T10 | 2004-06-17 | South End Substation | Upgrade line 1977 terminal equipment at South End Substation. | 2005-05-31 | Approved | 2004-07-26
NU-04-X01 | 2004-06-16 | Lake Road Generation Plant | Modify the existing Lake Road Type III Special Protection System (SPS). | 2006-11-30 | Approved with conditions | 2004-08-03
NSTAR-04-T03 | 2004-06-15 | East Cambridge Substation | Addition of the new 115kV/13.8 kV East Cambridge substation. | 2005-08-31 | Approved with conditions | 2004-09-02
NEP-04-T20 | 2004-06-10 | Reconductor B-154N & C-155N lines | Reconductor 115 kV lines B-154N & C-155N. | 2005-11-30 | Approved | 2004-07-26
NEP-04-T21 | 2004-06-10 | Reconductor line G-133E. | Reconductor 115 kV line G-133E. | 2005-11-30 | Approved | 2004-07-26
NU-04-T22 | 2004-05-27 | Fort Hill Farms | Add a second 115/34.5 kV autotransformer at the Fort Hill Farms substation. | 2004-06-29 | Approved | 2004-06-24
NSTAR-04-T02 | 2004-05-24 | Chelsea Station #488 | Replace the 115/13.8 kV Chelsea Station 110A and 110B transformers. Add 115 kV circuit breaker and 115/13.8 kV Chelsea transformer 110C. | 2004-05-31 | Approved | 2004-06-04
NU-04-T19 | 2004-05-18 | Chester Substation | Addition of a second transformer and 115 kV circuit breaker to the Chester Substation. | 2004-05-31 | Approved with conditions | 2004-06-04
NU-04-T20 | 2004-05-18 | Tracy 14M | Reconfigure the Tracy Substation and add three 115 kV circuit breakers. Sectionalize the 345 kV 347 line. Addition of a new 345/115 kV auto-transformer at the Tracy Substation. | 2006-11-30 | Approved | 2004-08-03
NU-04-T21 | 2004-05-18 | Card 11F | Addition of a new 345 kV circuit breaker in series with the Card Substation 11F-2T-2 circuit breaker. This upgrade is associated with the Tracy Autotransformer Project. | 2006-11-30 | Approved | 2004-08-03
PP-04-G01 | 2004-05-12 | Waterside 22M | Temporary installation of three TM2500 gas turbine generators at the Waterside Substation. This installation will interconnect the machines through a single GSU to the existing mobile transformer position on the 1440 line side of the Waterside bus. | 2004-05-31 | Approved with conditions | 2004-05-23
NU-04-T18 | 2004-05-10 | Waterside 22M | Temporary installation of three TM2500 gas turbine generators at the Waterside Substation. This installation is temporary and shall expire on December 31, 2004. | 2004-05-31 | Approved | 2004-05-23
NU-04-T16 | 2004-05-09 | Torrington Terminal 8A Substation | 1788 and 1900 line terminal equipment at Torrington Terminal substation will be upgraded. Following these upgrades, the lines will be conductor limited. | 2004-06-03 | Approved | 2004-06-04
BEMI-04-G02 | 2004-04-25 | Berlin, NH | A new cogeneration unit is added to the existing load and generation at Fraser Paper Berlin/Gorham system, which includes the existing James River hydro aggregate. This represents a capacity increase from 13 MW to 25 MW. | 2004-04-30 | Approved with conditions | 2004-05-06
NEP-04-T16 | 2004-04-25 | Point Street | Add second 13/115 kV transformer at Point Street S/S and connect it through a new tap with T3 line between Franklin Square and Point St. Install a circuit switcher in line T3 toward South St. | 2004-05-31 | Approved | 2004-06-04
NEP-04-T17 | 2004-04-25 | Johnston Substation | Add second 13/115 kV transformer at Johnston S/S and connect it to the existing tap off the T-172 line. | 2004-05-31 | Approved | 2004-06-04
NEP-04-T18 | 2004-04-25 | Kilvert Street | Install a tap off the I-187 line in Warwick, RI and connect the proposed Kilvert St. distribution S/S with the tap through. | 2004-05-31 | Approved | 2004-06-04
NU-04-T13 | 2004-04-18 | Cos Cob Railrod 11R Substation | Add a circuit breaker at the Cos Cob Railroad substation on the 1750 line. | 2004-12-30 | Approved | 2004-05-06
NSTAR-04-T01 | 2004-04-15 | Framingham Station #240 | Replace the 115/13.8 kV Framingham Transformers 110B and 110C. | 2004-05-31 | Approved | 2004-05-07
NU-04-T11 | 2004-04-15 | 115 kV line Z156 | Addition of a 115 kV radial line connecting the Schiller Substation to the existing Portsmouth Substation. The new line will supply the Portsmouth substation. | 2004-05-31 | Approved | 2004-05-06
NU-04-T12 | 2004-04-15 | Pleasant 16B | Addition of a 3rd 30 MVA 115/23 kV transformer and 2-115 kV circuit breakers. The need for this additional transformer is load growth, no additional load at Pleasant. No load being swapped to Pleasant. | 2004-05-31 | Approved | 2004-05-06
NU-04-T14 | 2004-04-15 | Blandford 19J Substation | Replace the existing 12/16 MVA transformer with a new 18/24/30 MVA transformer at Blandford substation. | 2004-06-30 | Approved | 2004-05-06
NU-02-T04 Rev. A | 2004-04-14 20:00 | Shunock 32P - N. Stonington | Addition of a new 115 kV substation: Shunock 32P - North Stonington, CT (proposed) - this revision represents the change from one three winding transformer to two two winding transformers at Shunock for increased reliability. | 2005-04-30 20:00 | Approved | 2004-05-06 20:00
DNC-04-G01 | 2004-03-31 | Millstone Power Station | Millstone Unit No. 3 power uprate consists of replacing all three LP steam turbine rotors. | 2004-04-30 | Approved with conditions | 2004-04-07
MIR-04-DR04 Rev. 1 | 2004-03-31 | Kendall Steam 3 | Place the Kendall Steam 3 generating unit into deactivated reserve. | 2004-09-30 | Approved with conditions | 2004-09-22
NEP-04-G01 | 2004-03-21 | Johnston Substation | Add six new units rated at 12 MVA total to the landfill gas burning facility connected to the 23 kV distribution line at terminating at Johnston 23/115 kV substation. | 2004-05-31 | Approved | 2004-04-07
NEP-04-T14 | 2004-03-21 | Lynn # 21 | Install two 3-phase 115/13.8 kV transformers, two 115 kV circuit switchers, and replace two sacrificial airbreaks with circuit switchers. | 2006-11-30 | Approved | 2004-04-07
NEP-04-T15 | 2004-03-21 | Railyard # 49 | Install one 3-phase 115/13.8 kV transformer and a 115 kV circuit switcher. | 2005-06-30 | Approved | 2004-04-07
NEP-04-T01 | 2004-03-08 | Woodside | Install 69 kV breaker at Woodside. Operate W-23 line normally closed at Woodside. | 2003-12-31 | Approved with conditions | 2004-04-08
NEP-04-T02 | 2004-03-08 | Wachusett | Install second 115 - 69 kV transformer at Wachusett substation. | 2003-12-31 | Approved with conditions | 2004-04-08
NEP-04-T03 | 2004-03-08 | Millbury | Replace two 115 - 60 kV autotransformers at Millbury substaion. | 2003-12-31 | Approved with conditions | 2004-04-08
NEP-04-T04 | 2004-03-08 | Pratts Junction | Transfer half of Prospect St. load to Pratts Jct. Install two additional 115 - 69 kV autotransformers and replace all 8 69 kV circuit breakers at Pratts Jct. Substation. | 2003-12-31 | Approved with conditions | 2004-04-08
NEP-04-T05 | 2004-03-08 | Wachusett | Install two 345 - 115 kV autotransformers (448 MVA) and two additional 115 - 69 kV autotransformers at Wachusett Station. | 2004-12-31 | Approved with conditions | 2004-04-08
NEP-04-T06 | 2004-03-08 | Quinsigamond Jct - Greendale - Nashua St. | Reconductor O-141N 115 kV line (Quinsigamond Jct - Greendale - Nashua St.) | 2004-12-31 | Approved with conditions | 2004-04-08
NEP-04-T07 | 2004-03-08 | Wachusett - W. Boylston | Reconductor P-142 115 kV line (Wachusett - W. Boylston) | 2007-12-31 | Approved with conditions | 2004-04-08
NEP-04-T08 | 2004-03-08 | Wachusett - Fitch Road | Reconductor M-39 69 kV line (Wachusett - Fitch Rd.) | 2004-12-31 | Approved with conditions | 2004-04-08
NEP-04-T09 | 2004-03-08 | Pratts Jct. - Fitch Road | Reconductor N-40 69 kV line (Pratts Jct. - Fitch Rd.) and upgrade 69 kV terminal equipment at Pratts Jct. | 2004-12-31 | Approved with conditions | 2004-04-08
NEP-04-T10 | 2004-03-08 | Rolf Ave. | Upgrade 115 kV breaker at Rolfe Avenue substation. | 2004-12-31 | Approved with conditions | 2004-04-08
NEP-04-T11 | 2004-03-08 | Carpenter Hill - W. Charlton | Reconductor W-175 115 kV line (Carpenter Hill - W. Charlton). | 2004-12-31 | Approved with conditions | 2004-04-08
NEP-04-T12 | 2004-03-08 | West Boylston | Upgrade West Boylston 115 kV substation to meet NPCC bulk power system requirements. | 2004-12-31 | Approved with conditions | 2004-04-08
NEP-04-T13 | 2004-03-08 | Marlboro Tap | Upgrade W-23 69 kV disconnect device at the Marlboro Tap. | 2004-12-31 | Approved with conditions | 2004-04-08
CMP-04-T01 | 2004-02-12 | Bolt Hill Substation | Add a 115/34/5 kV transformer at Bolt Hill substation as part of the Southern York County System Reinforcement Project | 2004-05-31 | Approved | 2004-03-12
NU-02-T09 Rev. 1 | 2004-02-11 | Glenbrook Substation | Install a new 115 kV 1977-line position at the Glenbrook substation, tap existing Darien to South End 1977-line forming a new three terminal transmission line. Install new primary and backup 1977 line protection at Glenbrook, Darien, and South End. | 2004-05-31 | Approved | 2004-04-08
BEMI-04-G01 | 2004-01-26 | Berlin Substation | A new COGEN unit is being installed at the Fraser Paper Berlin/Gorham load and generation complex. The 13 MW capability of the aggregate will remain the same. | 2004-02-29 | Approved with conditions | 2004-02-10
FPLE-04-G01 | 2004-01-22 | Seabrook Nuclear Station | Phase I of the Seabrook Power Uprate will increase the maximum gross output by 86 MW (1209 MW to 1295 MW). | 2004-04-01 | Approved with conditions | 2004-02-10
FPLE-04-G01 Condition 3 | 2004-01-22 | Seabrook Nuclear Station | Phase I of the Seabrook Power Uprate will increase the maximum gross output by 86 MW (1209 MW to 1295 MW). REMOVAL OF CONDITION 3. | 2004-04-01 | Approved with conditions | 2004-05-09
UI-04-T01 | 2004-01-22 | Pequonnock | Install a 3% series reactor (100 MVA base), with bypass switch, in the Bridgeport Harbor 2 generator leads. | 2005-05-31 | Approved | 2004-04-07
NU-04-T01 | 2004-01-19 | Norwalk-Plumtree Substations | New 345 kV circuit between Norwalk and Plumtree substations. | 2005-10-31 | Approved with conditions | 2004-02-10
NU-04-T02 | 2004-01-19 | Plumtree to Peaceable Substations | Reconfiguration of the existing 115 kV 1565 line between Plumtree and Peaceable. | 2005-10-31 | Approved with conditions | 2004-02-10
NU-04-T03 | 2004-01-19 | Norwalk to Peacable Substations | Reconfiguration of the existing 115 kV 1470 line between Norwalk and Peaceable. | 2005-10-31 | Approved with conditions | 2004-02-10
NU-04-T04 | 2004-01-19 | 1910 line at Southington | Install 3% series reactor (100 MVA base) with bypass switch on the 1910 line at Southington. | 2005-10-31 | Approved with conditions | 2004-02-10
NU-04-T05 | 2004-01-19 | 1950 line at Southington | Install 3% series reactor (100 MVA base) with bypass switch on the 1950 line at Southington. | 2005-10-31 | Approved with conditions | 2004-02-10
NU-04-T06 | 2004-01-19 | Long Mountain | Install the 7T breaker at Long Mountain 345 kV and reterminate the 398 line (Long Mtn. - Pleasant Valley). | 2005-10-31 | Approved with conditions | 2004-02-10
NU-04-T07 | 2004-01-19 | 348 Line | Replace limiting terminal equipment on the 345 kV 348 line (Millstone to Southington). | 2005-10-31 | Approved with conditions | 2004-02-10
NU-04-T08 | 2004-01-19 | Norwalk Harbor | Replace 3T, 5T, and 6T circuit breakers at Norwalk Harbor substation. | 2005-10-31 | Approved with conditions | 2004-02-10
NU-04-T09 | 2004-01-19 | Glenbrook | Install Type III SPS at Glenbrook Substation. | 2005-10-31 | Approved with conditions | 2004-02-10
SNE-01-G01 Rev. 1 | 2003-12-08 | West Medway Station | WITHDRAW: New Gas Trubine Generating plant consisting of three single-cycle natural gas fired generators (Units 4, 5 & 6). | 2002-05-31
CMP-03-G01 Rev. 3 | 2003-12-04 | Redington Mountain Windpower | Add a 30 MW generation plant; consisting of 15, 1.8 MW wind turbines, connecting to the new 115 kV Electric Harvest substation. | 2004-11-30 | Approved with conditions | 2003-12-11
ENTERGY-03-G02 Rev. 1 | 2003-12-01 | Vermont Yankee | The project will uprate the output of the Vermont Yankee Nuclear Power Station to a maximum gross output of 667 MW to be implemented in two phases. Modified Conditions. | 2004-06-01 | Approved | 2004-03-12
NEP-03-T03 Rev. 1 | 2003-11-17 | Woodside | WITHDRAW: Install 69 kV breaker at Woodside. Operate W-23 line normally closed at Woodside. | 2003-11-17
NEP-03-T04 Rev. 1 | 2003-11-17 | Wachusett | WITHDRAW: Install second 115 - 69 kV transformer at Wachusett substation. | 2003-11-17
NEP-03-T05 Rev. 1 | 2003-11-17 | Millbury | WITHDRAW: Replace two 115 - 60 kV autotransformers at Millbury substaion. | 2003-11-17
NEP-03-T06 Rev. 1 | 2003-11-17 | Pratts Junction | WITHDRAW: Transfer half of Prospect St. load to Pratts Jct. Install two additional 115 - 69 kV autotransformers and replace all 8 69 kV circuit breakers at Pratts Jct. Substation. | 2001-01-01
NEP-03-T07 Rev. 1 | 2003-11-17 | Wachusett | WITHDRAW: Install two 345 - 115 kV autotransformers (448 MVA) and two additional 115 - 69 kV autotransformers at Wachusett Station. | 2003-11-17
NEP-03-T08 Rev. 1 | 2003-11-17 | Quinsigamond Jct - Greendale - Nashua St. | WITHDRAW: Reconductor O-141N 115 kV line (Quinsigamond Jct - Greendale - Nashua St.) | 2003-11-17
NEP-03-T09 Rev. 1 | 2003-11-17 | Wachusett - W. Boylston | WITHDRAW: Reconductor P-142 115 kV line (Wachusett - W. Boylston) | 2003-11-17
NEP-03-T10 Rev. 1 | 2003-11-17 | Wachusett - Fitch Road | WITHDRAW: Reconductor M-39 69 kV line (Wachusett - Fitch Rd.) | 2003-11-17
NEP-03-T11 Rev. 1 | 2003-11-17 | Pratts Jct. - Fitch Road | WITHDRAW: Reconductor N-40 69 kV line (Pratts Jct. - Fitch Rd.) and upgrade 69 kV terminal equipment at Pratts Jct. | 2003-11-17
NEP-03-T12 Rev. 1 | 2003-11-17 | Rolf Ave. | WITHDRAW: Upgrade 115 kV breaker at Rolfe Avenue substation. | 2003-11-17
NEP-03-T13 Rev. 1 | 2003-11-17 | Carpenter Hill - W. Charlton | WITHDRAW: Reconductor W-175 115 kV line (Carpenter Hill - W. Charlton) | 2003-11-17
NEP-03-T14 Rev. 1 | 2003-11-17 | West Boylston | WITHDRAW: Upgrade West Boylston 115 kV substation to meet NPCC bulk power system requirements. | 2003-11-17
NEP-03-T15 Rev. 1 | 2003-11-17 | Marlboro Tap | WITHDRAW: Upgrade W-23 69 kV disconnect device at the Marlboro Tap. | 2003-11-17
INDECK-00-G01 Rev. 1 | 2003-11-09 | Indeck - North Smithfield Energy Center | WITHDRAW: Construction of a new 350 MW gas turbine combined cycle facility. | 2003-06-30 | Approved | 2003-12-10
CMP-03-G01 Rev. 2 | 2003-11-06 | Redington Mountain Windpower | Add a 30 MW generation plant; consisting of 15, 1.8 MW wind turbines, connecting to the new 115 kV Electric Harvest substation. | 2004-11-30
CMP-03-G01 Rev. 1 | 2003-11-05 19:00 | Redington Mountain Windpower | Add a 30 MW generation plant; consisting of 15, 1.8 MW wind turbines, connecting to the new 115 kV Electric Harvest substation. | 2004-11-30 19:00
CMP-03-T05 Rev. 1 | 2003-11-05 | Electric Harvest 115 kV Substation | A new Endless Energy substation will be constructed and connected to CMP's Bigelow substation. | 2004-11-30 | Approved with conditions | 2003-12-10
CMP-03-T05 | 2003-11-04 19:00 | Electric Harvest 115 kV Substation | A new Endless Energy substation will be constructed and connected to CMP's Bigelow substation. | 2004-11-30 19:00
CMP-03-G01 | 2003-11-04 | Redington Mountain Windpower | Add a 30 MW generation plant; consisting of 15, 1.8 MW wind turbines, connecting to the new 115 kV Electric Harvest substation. | 2004-11-30 | Approved
CMP-03-T04 | 2003-11-02 | Challenger Drive | Tap the 115 kV section 75 (Hotel Road - Lewiston Lower) and add the Challenger Drive distribution substation. | 2004-06-30 | Approved | 2003-11-18
NSTAR-01-T01 Rev. 1 | 2003-10-30 | West Medway Station | WITHDRAW: Modify the West Medway 345 kV station to install breaker 113 and connect the Sithe 345 kV generator lead. Upgrade breakers 101, 103, 104, 106, 107 and 109. | 2003-12-11 | Approved | 2003-12-11
MMED-03-T01 | 2003-10-29 | New substation Bird Road | Construct a new 115 - 13.8 kV substation in Mansfield, MA. The station will consist of a single 115 - 13.8 kV transformer and will connect on the E1 line. | 2006-05-31 | Approved | 2003-11-19
NEP-00-G05 Rev. 1 | 2003-10-26 | Brockton Power Generating Plant | WITHDRAW: Construction of a 288 MW Winter/267 Summer Combined Cycle Plant | 2002-12-31 | Approved | 2003-11-18
NEP-00-T16 Rev. 1 | 2003-10-26 | 328 line | WITHDRAW: Construct a three breaker ring bus substation on the 328 line for the interconnection of the North Smithfield power plant. | 2002-02-28 | Approved | 2003-12-10
NEP-00-T22 Rev. 1 | 2003-10-26 | Brockton Power | WITHDRAW: Construct three bkr ring bus. | 2002-04-30 | Approved | 2003-11-18
NEP-00-T23 Rev. 1 | 2003-10-26 | Brockton Power | WITHDRAW: Reconductor F19 Line. | 2002-04-30 | Approved | 2003-11-18
NEP-00-T24 Rev. 1 | 2003-10-26 | Brockton Power | WITHDRAW: Replace the 1601 Bkr. | 2002-04-30 | Approved | 2003-11-18
NEP-00-T25 Rev. 1 | 2003-10-26 | Brockton Power | WITHDRAW: Rebuild the S8 line. | 2002-04-30 | Approved | 2003-11-18
NEP-00-T26 Rev. 1 | 2003-10-26 | Brockton Power | WITHDRAW: Upgrade thermal capacity of the northern Auburn Street 115 kV ring bus. | 2002-04-30 | Approved | 2003-11-18
NEP-00-X05 Rev. 1 | 2003-10-26 | Brockton Power | WITHDRAW: Install Type III SPS at Auburn Street station. | 2002-04-30 | Approved | 2003-11-18
NEP-01-T12 Rev. 1 | 2003-10-26 | Millbury Station Bkr #314 | WITHDRAW: Upgrade breaker 314 at the Millbury station to achieve Independent Pole tripping capability. | 2002-05-31 | Approved | 2003-12-11
NEP-03-T16 | 2003-10-26 | E1 115 kV line | Split the existing E1 line into two independent line sections by adding two circuit breakers. | 2006-05-31 | Approved | 2003-11-18
NEP-03-T17 | 2003-10-26 | E1 115 kV line | Extend 115 kV line E1 from Easton and terminate at the new Bird Road substation at Mansfield. | 2006-05-31 | Approved | 2003-11-18
NU-03-T13 Rev. 1a | 2003-10-26 | Haddam | Reconfigure Haddam Substation 11C to a breaker and a half scheme, install 345/115 kV auto-transformer, install shunt capacitor, tap the 345 kV 348 line & the 115 kV 1620 line terminating at Haddam. Rev. 1: change in rating & impedance of autotransformer. | 2005-04-30 | Approved | 2003-11-18
NU-03-T24 Rev. 1 | 2003-10-18 | Webster | WITHDRAW: Replacement of an air break switch (J40) with a 2000 amp circuit breaker at the PSNH Webster 115 kV substation. | 2003-10-23
NU-03-T25 | 2003-10-15 | Pine Hill | Addition of a second transformer and 115 kV circuit breaker to the PSNH Pine Hill substation. | 2002-12-31 | Approved | 2003-11-18
NU-03-T13 Rev. 1 | 2003-10-09 20:00 | Haddam | Reconfigure Haddam Substation 11C to a breaker and a half scheme, install 345/115 kV auto-transformer, install shunt capacitor, tap the 345 kV 348 line & the 115 kV 1620 line terminating at Haddam. Rev. 1: change in rating & impedance of autotransformer. | 2005-04-30 20:00
NU-03-T24 | 2003-10-09 | Webster | Replacement of an air break switch (J40) with a 2000 amp circuit breaker at the PSNH Webster 115 kV substation. | 2003-10-23 | Approved | 2004-06-25
NU-03-T23 | 2003-10-08 | Amherst | Addition of a second transformer and 345 kV ring bus to the Amherst 345 kV substation. | 2003-11-14 | Approved | 2003-11-18
NU-03-T17 Rev. 1 | 2003-10-06 | Southington 4C | Add 115/13.8 kV transformer and 115 kV breaker at Southington 4C substation. | 2003-12-30 | Approved | 2003-09-08
CMP-03-T03 | 2003-10-01 | Crowley's 115 kV substation | Install a 50 MVAR capacitor bank at the Crowley's 115 kV substation to provide reactive supply for power factor correction per OP-17 Power Factor Survey. | 2003-10-31 | Approved | 2003-11-18
DNC-03-G01 | 2003-09-29 | Millstone | Replace the two LP rotors on Millstone Unit No. 2 steam turbine. This will increase the real power output to 905.7 MW net winter, 897.5 MW net summer. | 2003-10-31 | Approved with conditions | 2003-10-07
FPLE-03-RR01 | 2003-09-28 | Mason | Retire Mason Unit # 3. | 2003-11-01 | Approved | 2003-10-08
FPLE-03-RR02 | 2003-09-28 | Mason | Retire Mason Unit # 4. | 2003-11-01 | Approved | 2003-10-08
FPLE-03-RR03 | 2003-09-28 | Mason | Retire Mason Unit # 5. | 2003-11-01 | Approved | 2003-10-08
ENTERGY-03-T01 | 2003-09-25 | Vermont Yankee | Install two 115 kV 15 MVAR switched shunt capacitor banks and one 115 kV 30 MVAR switched shunt capacitor bank at the Vermont Yankee 115 kV substation. | 2003-04-01 | Approved with conditions | 2003-10-08
NU-03-G01 | 2003-09-24 | Kleen Energy | Construct an 634.2 MW gross winter/634.0 MW gross summer combined cycle gas/oil plant. | 2006-05-31 | Approved with conditions | 2003-10-08
NU-03-T22 | 2003-09-24 | Kleen Energy | Addition of new Kleen Energy 345 kV switchyard. | 2006-05-31 | Approved | 2003-10-08
NEP-03-T05 | 2003-09-23 20:00 | Millbury | Replace two 115 - 60 kV autotransformers at Millbury substaion.
NEP-03-T06 | 2003-09-23 20:00 | Pratts Junction | Transfer half of Prospect St. load to Pratts Jct. Install two additional 115 - 69 kV autotransformers and replace all 8 69 kV circuit breakers at Pratts Jct. Substation.
NEP-03-T07 | 2003-09-23 20:00 | Wachusett | Install two 345 - 115 kV autotransformers (448 MVA) and two additional 115 - 69 kV autotransformers at Wachusett Station.
NEP-03-T08 | 2003-09-23 20:00 | Quinsigamond Jct - Greendale - Nashua St. | Reconductor O-141N 115 kV line (Quinsigamond Jct - Greendale - Nashua St.)
NEP-03-T09 | 2003-09-23 20:00 | Wachusett - W. Boylston | Reconductor P-142 115 kV line (Wachusett - W. Boylston)
NEP-03-T10 | 2003-09-23 20:00 | Wachusett - Fitch Road | Reconductor M-39 69 kV line (Wachusett - Fitch Rd.)
NEP-03-T11 | 2003-09-23 20:00 | Pratts Jct. - Fitch Road | Reconductor N-40 69 kV line (Pratts Jct. - Fitch Rd.) and upgrade 69 kV terminal equipment at Pratts Jct.
NEP-03-T12 | 2003-09-23 20:00 | Rolf Ave. | Upgrade 115 kV breaker at Rolfe Avenue substation.
NEP-03-T13 | 2003-09-23 20:00 | Carpenter Hill - W. Charlton | Reconductor W-175 115 kV line (Carpenter Hill - W. Charlton)
NEP-03-T14 | 2003-09-23 20:00 | West Boylston | Upgrade West Boylston 115 kV substation to meet NPCC bulk power system requirements.
NEP-03-T15 | 2003-09-23 20:00 | Marlboro Tap | Upgrade W-23 69 kV disconnect device at the Marlboro Tap.
NEP-03-T03 | 2003-09-23 | Woodside | Install 69 kV breaker at Woodside. Operate W-23 line normally closed at Woodside. | 2003-10-01
NEP-03-T04 | 2003-09-23 | Wachusett | Install second 115 - 69 kV transformer at Wachusett substation. | 2004-10-01
NU-03-T21 | 2003-08-27 | East Springfield 5J | Add third 115/13.8 kV transformer at East Springfield. | 2003-12-29 | Approved | 2003-10-08
NU-03-T19 | 2003-08-24 | Franconia 22H | Replace the 3X 115 kV 13.8 kV transformer at Franconia. | 2003-06-29 | Approved | 2003-10-08
NU-03-T17 | 2003-08-17 | Southington 4C | Add 115/13.8 kV transformer and 115 kV breaker at Southington 4C substation. | 2003-12-31 | Approved | 2003-09-08
NU-03-T18 | 2003-08-17 | Torrington Terminal 8A | Add 115 kV/13.2 kV transformer at Torrington Terminal 8A substation. | 2003-11-30 | Approved | 2003-09-08
UI-03-T02 | 2003-07-24 | 115 kV lines 8809A and 8909B | Increase the clearance between UI lines 8809A and 8909B and railroad conductors. | 2003-09-30 | Approved | 2003-08-06
NSTAR-02-T03 Rev 1 | 2003-07-22 | Barnstable 115 kV | Install a 15 MVAR 115 kV shunt capacitor bank at the Barnstable 115 kV substation. | 2003-11-30 | Approved | 2003-08-07
NU-03-T16 | 2003-07-20 | Southwick | Add second 115 - 13.8 kV transformer at Southwick to provide additional load serving capacity. | 2002-08-31 | Approved | 2003-09-08
NU-03-T12 | 2003-07-17 | Portsmouth Substation | Addition of the Portsmouth Substation 50 MVA, 115/34.5 kV transformer. | 2003-05-31 | Approved | 2003-08-06
NU-03-T13 | 2003-07-17 | Haddam | Reconfigure Haddam Substation 11C to a breaker and a half scheme, install 345/115 kV auto-transformer, install shunt capacitor, tap the 345 kV 348 line and the 115 kV 1620 line terminating at Haddam. | 2005-04-30 | Approved | 2003-08-07
NU-03-T14 | 2003-07-17 | Branford Substation | Install a 115 kV, 37.8 Mvar (nominal) shunt capacitor bank at the Branford Substation. | 2005-04-30 | Approved | 2003-08-06
NU-03-T15 | 2003-07-17 | 115 kV line Manchester - Hopewell | Reconductor the 115 kV line 1767 from Manchester Substation (Manchester, CT) to Hopewell Substation (Glastonbury, CT). | 2005-04-30 | Approved | 2003-08-07
UI-03-T01 | 2003-07-17 | Devon Tie Switching Station | Replace the four existing 115 kV oil circuit breakers with four new SF6 gas circuit breakers. | 2003-09-30 | Approved | 2003-08-06
NEP-03-T02 | 2003-06-23 | Sherman Road | Install circuit breaker 140A in series with existing circuit breaker 140 at Sherman Road. | 2003-09-30 | Approved | 2003-08-06
NSTAR-03-T06 2 | 2003-06-03 20:00 | Mystic | Replace the 115/13.8 kV Mystic 110A and 110B transformers | 2003-06-30 20:00
NSTAR-03-T05 | 2003-06-03 | Sudbury | Replace the 115/13.8 kV Sudbury 110A and 110B transformers. | 2003-06-30
NSTAR-03-T07 | 2003-06-03 | K Street | New K Street 115/14kV substation. | 2003-06-30 | Approved | 2003-06-16
NSTAR-03-T08 | 2003-06-03 | Sudbury Station | Two new 115/13.8 kV LTC transformers will be installed at Sudbury Station #342 to replace the existing transformers 110A and 110B. | 2003-06-30 | Approved | 2003-06-15
NSTAR-03-T09 | 2003-06-03 | Mystic Station | Two new 115/13.8 kV LTC transformers will be installed at Mystic Station #250 to replace the existing transformers 110A and 110B. | 2003-06-30 | Approved | 2003-06-16
NU-03-T11 | 2003-06-03 | Great Bay | Addition of 115 kV substation Great Bay which will segment the H141 line between Scobie Pond and Ocean Road. | 2003-05-31 | Approved | 2003-06-15
NSTAR-03-T03 | 2003-05-22 | Dover | Relocation of 115 kv / 53.6 MVAR capacitor bank from Needham to Dover substation | 2003-05-31 | Approved | 2003-06-16
NSTAR-03-T04 | 2003-05-22 | North Woburn | Addition of a third 115/13.8 kV transformer at North Woburn substation. | 2003-05-31 | Approved | 2003-06-16
NU-03-T06 | 2003-05-18 | Middle River | Add third 115/13.8 kv transformer at Middle River to increase load serving capacity. | 2002-05-31 | Approved | 2003-06-16
NU-03-T07 | 2003-05-18 | Cos Cob | Add 115/13.8 kv transformer at Cos Cob to increase load serving capacity. | 2002-05-31 | Approved | 2003-06-16
NU-03-T08 | 2003-05-18 | Peaceable | Add second 115/13.8 kv transformer at Peaceable to increase load serving capacity. | 2002-11-30 | Approved | 2003-06-15
NU-03-T09 | 2003-05-18 | Card | Add sedond 115/13.8 kV transformer at Card to increase load serving capacity. | 2002-08-31 | Approved | 2003-06-16
NU-03-T10 | 2003-05-14 | Waterside | GE TM2500 to be interconnected in the existing mobile transformer position. This installation to be removed on October 1, 2003. The GTs to be connected to the Waterside bus through a single 13.8 kV - 115 kV GSU. | 2003-05-31 | Approved with conditions | 2003-06-05
CMEEC-03-G01 | 2003-05-12 | South Norwalk | Add GE TM2500 generator for summer '03 operation for dispatchable or emergency operation. | 2003-06-01 | Approved with conditions | 2003-06-17
PP-03-G01 | 2003-05-12 | Waterside | Make three GE TM2500 generators available for summer '03 emergency operation. | 2003-05-27 | Approved with conditions | 2003-06-05
ENB-03-RR01 | 2003-05-08 | K Street | Retire Generating unit New Boston 1. | 2003-12-30 | Not approved | 2003-09-08
NU-02-T22 | 2003-05-01 | Madbury | Addition of two 25.2 Mvar fixed shunt capacitor banks to the Madbury 115 kV substation. | 2004-05-31 | Approved | 2003-06-15
NSTAR-03-T06 | 2003-04-27 | Canal | Expand the Canal 345 kV substation with a third bay and install a second Canal to Bourne 345/115 kV auto transformer w/115 kV overhead line. | 2003-05-31 | Approved with conditions | 2003-05-12
NSTAR-03-G01 | 2003-04-03 | MATEP | Addition of two 12.5 MW CT generators to the existing installed generation. Aggregate MATEP generation will not provide a net power interchange to the NSTAR system. | 2003-04-30 | Approved | 2003-04-16
PPLW-03-DR01 | 2003-04-01 | PPL Wallingford Unit 2 | Place PPL Wallingford Unit No. 2 in deactivated reserve status. | 2003-06-30 | Not approved | 2003-06-09
PPLW-03-DR02 | 2003-04-01 | PPL Wallingford Unit 3 | Place PPL Wallingford Unit No. 3 in deactivated reserve status. | 2003-06-30 | Not approved | 2003-06-09
PPLW-03-DR03 | 2003-04-01 | PPL Wallingford Unit 4 | Place PPL Wallingford Unit No. 4 in deactivated reserve status. | 2003-06-30 | Not approved | 2003-06-09
PPLW-03-DR04 | 2003-04-01 | PPL Wallingford Unit 5 | Place PPL Wallingford Unit No. 5 in deactivated reserve status. | 2003-06-30 | Not approved | 2003-06-09
CMP-99-G02 Rev. 2 | 2003-03-30 19:00 | Westbrook Units 1, 2, 3 | Removal of 18.4 Subordinate status of Westbrook Energy Center Project: New 578 MW generation plant
VELCO-03-T18 | 2003-03-27 | Tafts Corner | Construct a new 115/34.5 kV substation Tafts Corner by tapping the 115 kV Essex to Williston line. | 2004-06-01 | Approved | 2003-02-16
NU-03-T05 | 2003-03-25 | Connecticut Yankee | The existing 115 kV substation is being reduced in size. The Haddam - CY 1206 and the P&W - CY 1772 lines will be tied together at the existing CY termination structures. | 2003-09-29 | Approved | 2003-04-16
NEP-03-T01 | 2003-03-20 | King Street | Addition of a forth 75 MVA, 115 kV transformer at the King Street substation to provide firm backup to the sub-transmission circuits supplied by the existing transformers. | 2003-06-30 | Approved | 2003-04-16
CMP-03-T01 | 2003-03-12 | Gulf Island Substation | Install a 30 MVAR switched shunt capacitor bank at Gulf Island substation on the 115 kV bus # 3. | 2005-12-31 | Approved with conditions | 2003-03-19
CMP-03-T02 | 2003-03-12 | Kimball Road Substation | Install a 30 MVAR switched shunt capacitor bank at Kimball Road substation on the 115 kV bus # 1. | 2005-12-31 | Approved with conditions | 2003-03-19
CMP-03-X01 | 2003-03-12 | Maine Yankee DCT SPS | Modify existing Maine Yankee DCT SPS to send a signal to NBP Maritimes Islanding SPS for additional generation rejection to remove the requirement for NEPOOL thermal exclusion. | 2005-12-31 | Approved with conditions | 2003-03-19
NU-00-T07 Rev. 1 | 2003-03-12 | Towantic Substation | WITHDRAW: Construct a new 115 kV Towantic substation to facilitate the interconnection of the generators on the 1575, 1585, and 1990 lines. Install a 4% reactor on the 1990S line, improve clearances on the 1580 line, improve the rating of the 1585 line. | 2002-12-31 | Approved | 2003-04-16
BHE-03-T01 | 2003-03-11 | Line 3016: Orrington - Point Lepreau | Construct the new 345 kV line 3016 from Orrington, ME to Point Lepreau, New Brunswick. | 2005-12-31 | Approved with conditions | 2003-03-19
BHE-03-T02 | 2003-03-11 | New series compensation for section 388, Orrington | Addition of 25 ohm series capacitor on the 388 line to be located at or near Orrington. | 2005-12-31 | Approved with conditions | 2003-03-19
NMLD-02-T01 Rev. 1 | 2003-03-04 19:00 | Ellis Ave Substation | Construct a new 115/13.8 kV substation at Ellis Ave - connected to the exisitng Dean St Subst. Via a 2.2 mile cable. Application being revised with and updated "as built" oneline diagram. | 2002-11-30 19:00
CPN-00-G01 Rev. 1 | 2003-03-02 | Towantic Energy Project | WITHDRAW: New 548 MW gas-fired combined cycle power plant. | 2003-03-02 | Approved | 2003-04-16
NEP-03-X01 | 2003-02-23 | Carpenter Hill | The V-174 overload SPS will be removed following V-174 line reconductoring. The new conductor is sized adequately to allow removal of the V-174 overload SPS. | 2003-05-31 | Approved | 2003-04-15
NEP-03-X02 | 2003-02-23 | Brayton Point & West Farnum | NEP studies have identified protection modifications required at Brayton Point & West Farnum substations to maintain compliance with NPCC and NEPOOL criteria. | 2003-11-30 | Approved | 2003-04-16
NU-02-T11 Rev. 1 | 2003-02-23 | Glenbrook Substation | Installation of three (3) 50.4 Mvar mechanically switched shunt capacitor banks, one on the B bus & two on the A bus, as part of the overall static var system being installed to assist in maintaining acceptable voltages during a DCT line contingency | 2004-05-31 | Approved | 2003-03-09
NU-03-X01 | 2003-02-20 | Millstone | Retire Millstone failed breaker detector SPS. Millstone station is no longer capable of exceeding the 2200 MW threshold required by this SPS. | 2003-03-31 | Approved | 2003-03-10
NU-03-X02 | 2003-02-20 | Millstone | Retire Millstone double line trip detector SPS. Millstone station is no longer capable of exceeding the 2200 MW threshold required by this SPS. | 2003-03-31 | Approved | 2003-03-10
NU-03-T01 | 2003-02-18 | Stony Hill | Addition of two 115 kV 37.8 Mvar mechanically switched shunt capacitor banks at Stony Hill. | 2003-05-31 | Approved | 2003-03-09
NU-03-T02 | 2003-02-18 | Stony Hill | Addition of two 13.8 kV interconnected +/- 8 Mvar DVAR devices at Stony Hill substation. | 2003-05-31 | Approved | 2003-03-09
NU-03-T03 | 2003-02-18 | Bates Rock | Addition of a 13.8 kV 8 Mvar shunt mechanically switched capacitor bank controlled by a DVAR device at Bates Rock substation. | 2003-05-31 | Approved | 2003-03-09
NU-03-T04 | 2003-02-18 | Bates Rock | Addition of a 13.8 kV interconnected +/- 8 Mvar DVAR device at Bates Rock substation. | 2003-05-31 | Approved | 2003-03-09
NU-02-T10 Rev. 1 | 2003-01-21 | Glenbrook Substation | Installation of two +/- 75 Mvar STATCOMs connected to the 115 kV System at the Glenbrook Substation to assist in maintaining acceptable voltages during a DCT line contingency. An additional circuit breaker bay is required. | 2003-11-30 | Approved | 2003-03-09
BHE-02-G01 | 2003-01-09 | Powersville Road | Change in capability for GLHA/GNP generation. | 2003-05-23 | Approved | 2003-01-28
BHE-02-T04 | 2003-01-09 | Powersville Road - Millinocket Sub4 | New GLHA transmission line 6. | 2003-04-30 | Approved | 2003-01-28
BHE-02-T05 | 2003-01-09 | MS#4 | New 15 MVAR manually switched capacitor bank at MS#4. | 2003-04-30 | Approved | 2003-01-28
BHE-02-T06 | 2003-01-09 | Powersville Road | New Great Lakes Hydro America/Great Northern Paper Powersville Road substation. | 2003-04-30 | Approved | 2003-01-28
FPLE-00-G01 Rev. 1 | 2002-12-29 | IDC Bellingham Power Project | WITHDRAW: application to construction of 560 MW winter / 450 MW summer generating station. | 2002-12-29
BHE-02-T01 | 2002-12-23 | Line 62 115 kV | New transmission line 62 to new Keene Road 115 kV Switching Station to the new Powersville Road 115 kV Substation. | 2003-04-30 | Approved | 2003-01-28
BHE-02-T02 | 2002-12-23 | Keene Road 115 kV | New Keene Road switching station. | 2003-04-30 | Approved | 2003-01-28
BHE-02-T03 | 2002-12-23 | Graham 115 kV | Graham 115 kV substation reconfiguration. | 2003-04-30 | Approved | 2003-01-28
NSTAR-02-T04 | 2002-12-22 | West Walpole | Replace West Walpole circuit breakers 104, 105, 108, and 109 with IPT capability breakers. | 2003-06-01 | Approved | 2003-01-09
VELCO-03-T01 | 2002-12-19 | Sandbar | Installation of a Phase Angle Regulating Transformer on the PV20 tie to the NYPA Plattsburgh Substation to be located at the Sandbar 115 kV Substation. | 2004-04-30 | Approved | 2003-01-09
VELCO-03-T02 | 2002-12-19 | Blissville | Installation of a Phase Angle Regulating Transformer on the Blissville to Whitehall tie line to the Niagara Mohawks Whitehall Substation to be located at the Blissville 115 kV Substation. | 2004-11-30 | Approved | 2003-01-09
VELCO-03-T03 | 2002-12-19 | Hartford | Upgrade Hartford substation with a 24.75 MVAR capacitor bank and a breaker on the K26 line. | 2004-11-30 | Approved | 2003-01-09
VELCO-03-T04 | 2002-12-19 | Williston | At Williston substation, replace the two breaker radial bus with a three breaker ring bus. | 2004-11-30 | Approved | 2003-01-09
VELCO-03-T05 | 2002-12-19 | Essex | Add a line breaker on the K24 line at Essex substation. | 2004-11-30 | Approved | 2003-01-09
VELCO-03-T06 | 2002-12-19 | Granite | Granite substation upgrades to include: add LTC transformer, add a 230 kV, 550 MVA, 60 PAR, expand 115 kV ring bus, add two 24.75 MVAR cap banks, add +/-75 MVAR dynamic voltage control device. | 2005-11-30 | Approved | 2003-01-09
VELCO-03-T07 | 2002-12-19 | 115 kV line K26 Granite - Barre | Reconductor the 115 kV K26 line Granite to Barre. | 2005-11-30 | Approved | 2003-01-09
VELCO-03-T08 | 2002-12-19 | West Rutland | Close the 345 kV ring at West Rutland substation with two breakers. | 2006-11-30 | Approved | 2003-01-09
VELCO-03-T09 | 2002-12-19 | New Haven | New Haven substation: Rebuild to add 345 bus work, two LTC transformers, a 60 MVAR shunt reactor and six breaker ring bus. | 2006-11-30 | Approved | 2003-01-09
VELCO-03-T10 | 2002-12-19 | New 345 kV line West Rutland - New Haven | Add new 35.5 mile 345 kV line from West Rutland sub. to New Haven sub. | 2006-11-30 | Approved | 2003-01-09
VELCO-03-T11 | 2002-12-19 | Vergennes | Rebuild Vergennes sub to 115 kV with a 115/12.5 kV, 12 MVA transformer and in/out breakers. | 2006-11-30 | Approved | 2003-01-09
VELCO-03-T12 | 2002-12-19 | North Ferrisburg | Rebuild North Ferrisburg sub to 115 kV primary with a 115/12.5kV, 12 MVA transformer. | 2006-11-30 | Approved | 2003-01-09
VELCO-03-T13 | 2002-12-19 | Charlotte | Rebuild Charlotte sub to 115 kV primary with a 115/12.5kV, 12 MVA transformer. | 2006-11-30 | Approved | 2003-01-09
VELCO-03-T14 | 2002-12-19 | Shelburne | Rebuild Shelburne sub to 115 kV primary with a 115/12.5kV, 12 MVA transformer. | 2006-11-30 | Approved | 2003-01-09
VELCO-03-T15 | 2002-12-19 | Queen City | Rebuild Queen City sub from 115 kV radial bus to a five breaker 115 kV ring bus. | 2006-11-30 | Approved | 2003-01-09
VELCO-03-T16 | 2002-12-19 | 115 kV line New Haven - Queen City | Replace 27.2 46 kV/34.5 kV subtransmission line with 115 kV line from New Haven to Vergennes to North Ferrisburg to Charlotte to Shelburne to Queen City. | 2006-11-30 | Approved | 2003-01-09
VELCO-03-T17 | 2002-12-19 | Granite | Expand the Granite dynamic voltage control device from +/- 75 MVAR to +/- 150 MVAR and add two 24.75 cap banks. | 2007-11-30 | Approved | 2003-01-09
NU-02-T21 | 2002-12-17 | Ocean Road | Addition of (2) 25.4 Mvar fixed shunt capacitor banks to Ocean Road 115 kV substation. | 2003-05-31 | Approved | 2003-01-09
NU-02-T23 | 2002-12-17 | Three Rivers | Addition of (2) 25.4 Mvar fixed shunt capacitor banks to the Three Rivers 115 kV substation. | 2003-05-31 | Approved | 2003-01-09
NU-02-X27 | 2002-12-11 | Shunock | Relocate/duplicate the SPS relaying at the Mystic s/s 13k to the new Shunock s/s 32P. | 2004-04-30 | Approved | 2003-01-09
NEP-02-T20 | 2002-12-01 | Raynham Substation | Add two 115 kV/13.8 kV transformers and associated equipment at Raynham substation. | 2003-06-01 | Approved | 2002-12-16
NU-02-T24 | 2002-11-25 | Glenbrook, Frost Bridge, Hanover, Manchester, Mont | Replace overstressed 115 kV breakers at Glenbrook, Frost Bridge, Hanover, Manchester, Montville, and Norwalk substations. | 2003-12-30 | Approved | 2002-12-16
NU-02-T25 | 2002-11-25 | West Springfield, East Springfield, and Clinton | Replace overstressed 115 kV breakers at West Springfield, East Springfield, and Clinton substations. | 2003-12-30 | Approved | 2002-12-16
NU-02-T26 | 2002-11-24 | Norwalk Harbor, CT - Northport, NY 1385 cable | Replace the existing 1385-circuit cables from Norwalk Harbor, CT to Northport, NY with three separate 3-phase circuits. | 2004-05-31 | Approved | 2002-12-16
BELD-02-T01 Rev. 1 | 2002-11-21 | Middle Street Substation | Close the Braintree 115 kV loop at Middle Street substation by closing circuit breaker #102. | 2003-05-31 | Approved | 2002-12-16
BELD-02-T02 Rev. 1 | 2002-11-21 | Potter Substation | Install a 115 kV, 3 ohm series reactor at Potter station on cable 115-10-16. Install 115 kV circuit switcher to isolate Potter GSU. | 2003-05-31 | Approved | 2002-12-16
BELD-02-X01 Rev.1 | 2002-11-21 | Grove St.-Plain St. 115-9-5 Line | Install a second high speed protection group on BELD cable 115-9-4 between Grove Street and Plain Street. | 2003-05-31 | Approved | 2002-12-16
DNC-02-RR01 | 2002-11-18 | Millstone Power Station | Permanently retire Millstone Unit No. 1 and to permanently remove fuel from the reactor vessel. | 2002-11-18 | Approved | 2002-12-16
NU-02-T19 | 2002-11-17 | Southington Substation | Install three 115 kV 50.4 Mvar mechanically switched shunt capacitor banks at the Southington substation. | 2003-05-31 | Approved | 2002-12-16
NU-02-T20 | 2002-11-17 | Frost Bridge Substation | Install two 115 kV 50.4 Mvar mechanically switched shunt capacitor banks at the Frost Bridge substation. | 2003-05-31 | Approved | 2002-12-16
NSTAR-02-T03 | 2002-11-14 | Hyannis Junction | Increase the size of the existing 115 kV shunt capacitor located at Hyannis Junction from 40 MVAR to 55 MVAR. | 2003-03-31 | Approved | 2002-12-16
ENTERGY-02-T01 Rev. 1 | 2002-10-24 | Vermont Yankee Station | Replacement of the Vermont Yankee GSU. | 2002-09-30 | Approved with conditions | 2002-12-17
SNE-02-G01 | 2002-10-22 | New Boston | Reactivation of New Boston Unit 1 due to fire at New Boston Unit 2. | 2002-10-31 | Approved | 2002-10-29
SNE-02-RR02 | 2002-10-22 | New Boston | Retirement of New Boston Unit 2 due to fire. | 2002-10-31 | Approved | 2002-10-29
ENTERGY-02-T01 | 2002-10-20 | Vermont Yankee Station | Replacement of the Vermont Yankee GSU. | 2002-09-30 | Approved | 2002-11-06
NEP-02-X02 | 2002-09-26 20:00 | ANP Bellingham | Installation of a type III Special Protection System (SPS) at the ANP Bellingham generating plant to trip the Unit 2 generator breaker following the tripping of breaker 03-20 initiatyed by the 3520 line relaying | 2002-10-31 19:00 | Approved | 2002-10-20 20:00
BELD-02-T01 | 2002-09-25 | Middle Street Substation | Close the Braintree 115 kV loop at Middle Street Substation. | 2003-05-31 | Approved | 2002-12-17
BELD-02-T02 | 2002-09-25 | Potter Substation | Installation of a 115 kV, three (3) ohm series reactor inserted in the Station ring bus between Breaker #162 and Cable 115-10-16. | 2003-05-31 | Approved | 2002-12-17
BELD-02-X01 | 2002-09-25 | Middle Street Substation | Install a second high speed protection group on BELD calbe 115-9-4 between Grove St. and Plain St. Substations. | 2003-05-31 | Approved | 2002-12-17
NU-02-T18 | 2002-09-19 | Webster-Laconia J125 Line | Construct a second 14 mile 115 kV line, in the exisiting rights of way, between Webster and Laconia. | 2003-05-31 | Approved | 2002-10-20
VELCO-02-T01 | 2002-09-02 | Highgate Substation | Rebuild the existing VELCO and CZN Highgate Substations into a single Highgate Substation with a 115 kV ring bus. | 2004-11-30 | Approved | 2002-09-25
VELCO-02-T02 | 2002-09-02 | Irasburg Substation | Expand existing Irasburg substation to accommodate in and out circuit breakers. | 2004-11-30 | Approved | 2002-09-25
VELCO-02-T03 | 2002-09-02 | St. Johnsbury Substation | Modify St. Johnsbury substation and replace switch 39-3 with a circuit breaker | 2004-11-30 | Approved | 2002-09-25
VELCO-02-T04 | 2002-09-02 | St. Albans tap | At the St. Albans tap point, construct a switching station with SCADA controled circuit switchers on the lines toward Highgate and Georgia | 2004-11-30 | Approved | 2002-09-25
VELCO-02-T05 | 2002-09-02 | Irasburge Substation | Build a 6.6 mile double circuit 115 kV line between Moshers tap and the Irasburg substation | 2004-11-30 | Approved | 2002-09-25
NEP-02-T19 | 2002-08-28 | 447-508 line | Add a 3-phase 24/32/48 MVA xfmr to be connected to 447-508 line at the S. Randolph Substation. | 2004-06-01 | Approved | 2002-09-25
NEP-02-T14 | 2002-08-11 | Fitch Rd. Substation Rebuild | Rebuild the 69 kV Fitch Rd. Substation which is in-line breaker arrangement with a breaker and a half design. | 2002-09-01 | Approved | 2002-09-25
NU-02-T17 | 2002-07-28 | 364 Line | Upgrade the 345 kV 363 line terminals from Montville 4J to Haddam Neck 14B. | 2003-11-30 | Approved | 2002-08-11
NU-02-T15 | 2002-07-25 | 1310 line & 1635 line | Replace exisitng conductor in the Manchester-Wapping Junction section of the 1310 line and the Wapping Junction-Barbour Hill section of the 1635 line. | 2005-05-31 | Approved | 2002-08-11
NU-02-T16 | 2002-07-25 | 625 line | Convert the exisiting 625 line from 69 kV to 115 kV from Babbour Hill Substation To Rockville Substation. | 2002-08-31 | Approved | 2002-08-11
NEP-02-T17 | 2002-07-22 | Kent County Sbstation | Add 3-phase 33/44/56 MVA transformer to be connected to K-189 Line at the Kent County Substation. | 2003-06-01 | Approved | 2002-08-11
NEP-02-T15 | 2002-07-21 | Read Street Substation | New 115/13 kV 40 MVA transformer at the Read Street Substation. | 2004-06-01 | Approved | 2002-08-11
NEP-02-T16 | 2002-07-21 | Chartley Pond Substation | Replacement of the 115/23 kV (T2) with 55 MVA transformer at Chartley Pond Subst. | 2003-06-01 | Approved | 2002-08-11
NEP-02-T01 Rev. 1 | 2002-07-06 | Tewksbury Substation | WITHDRAW: Installation of four (4) 345 kV breakers along with associated buswork, switches and terminal equipment | 2002-12-31 | Approved | 2004-08-03
NEP-02-X02 | 2002-07-01 20:00 | Carpenter Hill to Millbury 2 Subst. | Removal of the V-174 Overlad SPS at Carpenter Hill, which is no longer required following completion of the reconductoring (NEP-02-T13) | 2003-05-31 20:00
CMP-02-T02 | 2002-07-01 | Spring St. Substation | Addition of a second 30/40/50 MVA 115/34.5 kV transformer and the installation of high & low side breakers at the Spring Street Substation. | 2002-11-30 | Approved | 2002-07-17
NEP-02-T13 | 2002-07-01 | Carpenter Hill to Millbury 2 Subst. | Reconductoring of the 115 kV line V-174 from Carpenter Hill subst #435 to Millbury 2 subst #302. | 2003-05-31 | Approved | 2002-07-17
NEP-02-X02 Rev. 1 | 2002-07-01 | Carpenter Hill to Millbury 2 Subst. | WITHDRAW application to remove of the V-174 Overlad SPS at Carpenter Hill, which is no longer required following completion of the reconductoring (NEP-02-T13). | 2003-05-31
NEP-97-T09 | 2002-07-01 | Carpenter Hill to Millbury Subst. | WITHDRAW - Reconductoring of the 115 kV line V-174 from Carpenter Hill subst #435 to Millbury | 2002-07-16 | Approved | 2002-07-17
NEP-98-T08B | 2002-07-01 | West Medway to ANP Bellingham | WITHDRAW - Reconductor 345 kV line 3520 from West Medway to ANP-Bellingham with 2-1113 kcmil ACSR conductor. | 2002-07-01 | Approved | 2002-07-16
NEP-98-T09 Rev. 1 | 2002-07-01 | Millbury to Sandy Pond | WITHDRAW - Reconductor 345 kV line 343 from Millbury to Sandy Pond with 2-1113 kcmil ACSR conductor, and upgrade associated disconnect switches at Sandy Pond. | 2002-07-01 | Approved | 2002-07-16
NEP-98-T10 Rev. 1 | 2002-07-01 | Millbury to West Medway | WITHDRAW - Reconductor 345 kV line 323 from Millbury to West Medway with 2-1113 kcmil ACSR conductor. | 2002-07-16 | Approved | 2002-07-16
NEP-98-T11 Rev. 1 | 2002-07-01 | Millbury Substation | WITHDRAW - Upgrade 345 kV terminal equipment and buswork on lines 302 and 314 at Millbury substation. | 2002-07-01 | Approved | 2002-07-16
NEP-98-T12 Rev. 1 | 2002-07-01 | Carpenter Hill to NEP/NU Boarder | WITHDRAW - Reconductor 345 kV line 301 from Carpenter Hill to the NEP/NU border with 2-1113 kcmil ACSR conductor. | 2002-07-01 | Approved | 2002-07-16
NEP-98-T13 Rev. 1 | 2002-07-01 | Millbury to Carpenter Hill | WITHDRAW - Reconductor 345 kV line 302 from Millbury to Carpenter Hill with 2-1113 kcmil ACSR conductor. | 2002-07-01 | Approved | 2002-07-16
NEP-98-T14 Rev. 1 | 2002-07-01 | Chartley Pond Subst. | WITHDRAW - Upgrade 115 kV terminal equipment on line C-181S at Chartley Pond substation. | 2002-07-01 | Approved | 2002-07-16
NEP-98-T15 Rev. 1 | 2002-07-01 | Millbury substation | WITHDRAW - Upgrade 115 kV terminal equipment and buswork on lines P-142 and C-129N at Millbury substation. | 2002-07-01 | Approved | 2002-07-16
NEP-98-T16 Rev. 1 | 2002-07-01 | Medway to Depot St to Milford Power | WITHDRAW - Reconductor 115 kV line C-129N from Medway to the Depot Street tap, and the Depot Street tap to Milford Power with 795 kcmil ACSR conductor. | 2002-07-01 | Approved | 2002-07-16
NEP-98-T17 Rev. 1 | 2002-07-01 | Davisville tap to W. Kingston | WITHDRAW - Reconductor 115 kV line G-185S from the Davisville tap to West Kingston with 795 kcmil ACSR conductor, and replace the 115 kV circuit breaker and associated disconnect switches at West Kingston. | 2002-07-01 | Approved | 2002-07-16
NEP-98-T18 Rev. 1 | 2002-07-01 | Palmer to Carpenter Hill | WITHDRAW - Reconductor 115 kV line W-175 from Palmer to Carpenter Hill with 1590 kcmil ACSR conductor. | 2002-07-01 | Approved | 2002-07-16
NEP-02-T11 | 2002-06-24 | South Wrentham Station | Install 3rd 115/23 kV Transformer (37.3 MVA) at S. Wrentham Station, Wrentham, MA. | 2003-05-31 | Approved | 2002-07-17
NEP-02-T12 | 2002-06-24 | Slayton Hill Substation | Install 2nd 115/13.8 kV transformer at the Slayton Hill Substation. | 2003-05-31 | Approved | 2002-07-17
NU-02-T12 | 2002-06-24 | North Simsbury Substation | Addition of new 115/23 kV Northeast Substation to be supplied by tapping the exisitng N. Bloomfield to Canton 1784 line. | 1999-02-28 | Approved | 2002-07-17
NU-02-T13 | 2002-06-24 | Great Bay Substation | Addition of new 115/34.5 kV Great Bay Substation to be supplied by tapping the exisitng Scobie Pond to Ocean Rd H141 line | 2003-05-31
NU-02-T14 | 2002-06-24 | Pine Hill Substation | Addition of new 115/34.5 kV Pine Hill substatioin to be suplied by tapping the exisitng Greggs to Deerfield O161 line | 2003-05-31 | Approved | 2002-07-17
CMEEC-02-DR01 | 2002-06-20 | South Norwalk 1 | Deactivation of generator due to economics of repairing & evironmental compliance. | 2002-06-30 | Approved | 2002-07-17
CMEEC-02-DR02 | 2002-06-20 | South Norwalk 2 & 4 | Deactivation of generator due to economics of repairing & evironmental compliance. | 2002-06-30 | Approved | 2002-07-17
CMEEC-02-DR03 | 2002-06-20 | South Norwalk 3 & 5 | Deactivation of generator due to economics of repairing & evironmental compliance. | 2002-06-30 | Approved | 2002-07-17
CMEEC-02-DR04 | 2002-06-20 | South Norwalk 6 | Deactivation of generator due to economics of repairing & evironmental compliance. | 2002-06-30 | Approved | 2002-07-17
NEP-02-T10 | 2002-05-28 | Marcus Beebe Substation | Replacement of the existing 40 MVA 115/13.8 kV T-2 transformer at the Marcus Beebe Substation with a new 55 MVA transformer. | 2002-06-30 | Approved | 2002-06-14
NEP-02-G01 | 2002-05-27 | UAE Tewksbury Substation | Construct a new gas-fired, simple cycle generation plant. | 2002-12-31 | Approved | 2002-06-12
NEP-02-T08 | 2002-05-27 | Sandy Pond Substation | Replacement of the existing 115 kV circuit breakers K-137W, K-137T, L-138W, and L-138T with four (4) new 115 kV GIS circuit breakers with a 63 kAIC rating at the Sandy Pond Substation. | 2002-12-31 | Approved | 2002-06-14
NEP-02-T09 | 2002-05-27 | Golden Hills Substation | Replacement of the existing 115 kV breakers F-158 and 45-58 with two (2) new 115 kV circuit breakers with a 63 kAIC rating at the Golden Hills Substation. | 2002-12-31 | Approved | 2002-06-14
NSTAR-02-T01 | 2002-05-23 | Needham Substation | Replacement of the existing 30/40 MVA 115/13.8 kV non-LTC transformer 110B with a new 37/50/62.5 LTC transformer at Needham Substation #148. | 2002-05-31 | Approved | 2002-06-13
NSTAR-02-T02 | 2002-05-23 | Waltham Substation | Replacement of the existing 30/40 MVA 115/13.8 kV LTC transformer 110A with a new 37/50/62.5 LTC transformer at Waltham Substation. | 2002-05-31 | Approved | 2002-06-13
NU-02-T03 | 2002-05-05 | Mystic Substation | Addition of 2-shunt 115 kV 25.2 MVAR mechanically switched capacitor banks at the Mystic Substation. | 2002-07-31 | Approved | 2002-06-14
NU-02-T04 | 2002-05-05 | Shunock 32P - N. Stonington | Addition of a new 115 kC substation: Shunock 32P -North Stonington, CT (proposed). | 2003-04-30 | Approved | 2002-06-13
NU-00-T04 Rev.1 | 2002-05-01 20:00 | Transmission Upgrades | Application revised to reflect new generator GSU configuration (from 2-ABB gen's to 3-GE gen's) and name of the new substation on the 362 line to South Kensington Subst. | 2002-06-29 20:00
NRG-02-DR01 | 2002-05-01 | Devon Substation | Request for Deactivated Reserve status of the Devon Generator 7. | 2002-07-31 | Not approved | 2002-07-24
NRG-02-DR02 | 2002-05-01 | Devon Substation | Request for Deactivated Reserve status of the Devon Generator 8. | 2002-07-31 | Not approved | 2002-07-24
NRG-02-DR03 | 2002-05-01 | Devon Substation | Request for Deactivated Reserve status of the Devon Generator 10. | 2002-07-31 | Not approved | 2002-07-24
NU-02-T09 | 2002-05-01 | Glenbrook Substation | Tapping of the 1977 115 kV line (Darien Substation to South End Substation) at the Glenbrook Substation to convert it to a three terminal line. | 2004-05-31 | Approved | 2002-06-13
NU-02-T10 | 2002-05-01 | Glenbrook Substation | Installation of a +/- 150 Mvar STATCOM connected to the 115 kV System at the Glenbrook Substation to assist in maintaining acceptable voltages during a DCT line contingency. | 2004-05-31 | Approved | 2002-06-13
NU-02-T11 | 2002-05-01 | Glenbrook Substation | Installation of three (3) 50.4 Mvar mechanically switched shunt capacitor banks at the Glenbrook Substation as part of the overall static var system being installed to assist in maintaining acceptable voltages during a DCT line contingency. | 2004-05-31 | Approved | 2002-06-13
SNE-02-RR01 | 2002-05-01 | New Boston | Retirement of the New Boston Unit 1 due to termination of the RMR Agreement on July 1, 2002. | 2002-06-30 | Approved | 2002-06-14
NU-02-T08 | 2002-04-28 | Waterside Substation | Provide for the temporary inteconnection of the Waterside CT's through a single GSU. | 2002-05-31 | Approved | 2002-05-12
NU-02-T05 | 2002-03-21 | Scobie Substation | Addition of a second 400 MVA, 345/115 kV Autotransformer at the Scobie Subsation to eleiminate unacceptable branch loadings & voltage conditions during contingency conditions. | 2004-11-30 | Approved | 2002-04-11
NU-02-T06 | 2002-03-21 | Scobie Pond 115 kV Substation | Reconfigure the Scobie Pond 115 kV Substation from a straight line bus configuration to a breaker-and-half scheme to reliablity interconnect the second 345/115 kV autotransformer. | 2004-11-30 | Approved | 2002-04-12
NU-02-T07 | 2002-03-21 | G146 Line | Rebuild the 115 kV Deerfield-Garvins G146 Line with 1272 MCM ACSR conductor to increase power flow capability and eliminate branch loadings under normal & contingency operations. | 2003-11-30 | Approved | 2002-04-12
CONED-02-G01 Rev. 1 | 2002-03-07 | West Springfield Station | Redevelopment of the exisiting West Springfield Power Plant, installation of 2 GE LM6000 CT, rated at 49 MW each. | 2002-04-30 | Approved | 2002-03-14
CONED-02-G01 | 2002-02-24 | West Springfield Station | Redevelopment of the exisiting West Springfield Power Plant, installation of 2 GE LM6000 CT, rated at 49 MW each. | 2002-04-30 | Approved | 2002-03-14
CONED-02-RR01 | 2002-02-24 | West Springfield Station | Retirement of the existing West Springfield Units 1 & 2 (48 MW each). | 2002-03-31 | Approved | 2002-03-14
NU-02-T02 | 2002-02-21 | West Springfield Station | Connect the West Springfield Power Plant replacement units GT-1 and GT-2 at the West Springfield Substation. | 2002-03-31 | Approved | 2002-03-15
CMP-99-G03 Rev. 1 | 2002-02-18 19:00 | Gorham Units 1, 2 & 3 - WITHDRAW | Withdraw - New 850 MW generation plant at Buxton Sta. | 2001-11-30 19:00 | Approved | 2002-03-11 19:00
CMP-99-T04 Rev. 2 | 2002-02-18 19:00 | Buxton Substation -WITHDRAW | Withdraw - 10 mile 345 kV circuit from Buxton Sta. to Gorham Energy Project | 2000-11-30 19:00 | Approved | 2002-03-11 19:00
NEP-02-T01 | 2002-02-14 | UAE Tewksbury Substation | Add 4-345 kV breakers and associated buswork, switches and termial equipment at the new Tewksbury Generation Station. Also add underground cable from generation polant to steel structure outside the Substation fence. | 2002-12-31 | Approved | 2002-06-14
NEP-02-T02 | 2002-02-14 | UAE Tewksbury Substation | Add (2) 345 kV two-breaker GIS bays; relocate the 337 line and 338 line to the two new GIS bays; install a stell structure outside the substation to transistion the underground cable generator lead to the overhead position presently occupied by 337 line. | 2002-12-31 | Approved | 2002-06-14
NEP-02-T03 | 2002-02-14 | Auburn Street Substation | Install a 115 kV breaker at Auburn Street Substation on the low of the 210 autotransformer. | 2002-05-31 | Approved | 2002-03-11
NEP-02-T04 | 2002-02-14 | Auburn Street Substation | Reconductor the 115 kV line F19 from Bridgewater station to the S1 tap to provide higher thermal capacity. | 2002-05-31 | Approved | 2002-03-11
NEP-02-T05 | 2002-02-14 | Auburn Street Substation | Reconductor the 115 kV line G18 from Bridgewater station to Dupont substation to provide thermal capacity. | 2002-05-31 | Approved | 2002-03-11
NEP-02-T06 | 2002-02-14 | Phillips Lane Substation | At the new Phillips Lane Substation add: one 3-phase 28/33.3/46.5 MVA 115/13.2 kV Xfmr, one 115 kV circuit switcher and a 7.2 MVAR 13.8 kV capacity bank. | 2002-02-28 | Approved | 2002-03-11
NEP-02-T07 | 2002-02-14 | Burtt Rd. Substation | Second 115/13 kV trasformer addition at Burtt Rd. Substation. | 2002-06-30 | Approved | 2002-03-11
NRG-02-G01 | 2002-02-14 | Meriden Power Units 1 and 2 | Revise & Replace App PDC-00-G01. New Application for Installation of two-unit Meriden Power project totaling 546 MW winter / 500 MW summer (10/8/04 removal of subordinate status & 3rd conditon of approval requiring additional short circuit anayses.) | 2003-05-31 | Approved | 2004-10-07
CMP-02-T01 | 2002-02-04 | Sanfod Substation | Install a 30.6 MVAR Capacitor bank at the Sanford 115 kV Substation. This capacitor bank was removed from the Maine Yankee substation (CMP-98-T01) in 1998. | 2002-04-01 | Approved | 2002-03-11
NU-00-T25 Rev. 1 | 2002-01-22 | Scovill Rock | Withdraw Application for Installing a new 9T bkr at Scovill Rock and reterminate the 376 line between the 8T and new 9T bkr. | 2002-05-01 | Approved | 2002-02-12
NU-00-X26 Rev. 1 | 2002-01-22 | Scovill Rock | Install type III SPS at Scovill Rock to runback the East Shore HVdc Facility in the event the 387 line is open ended at Scovill Rock. | 2002-04-30 | Approved | 2002-02-12
NU-02-T01 | 2002-01-22 | N. Bloomfield (2A) to Bloomfield (3B) | Replace terminal wave traps on the 115 kV Bloomfield - N. Bloomfield 1777 line. | 2002-04-30 | Approved | 2002-02-12
NMLD-02-T01 | 2001-12-26 | Ellis Ave Substation | Construct a new 115/13.8 kV substation at Ellis Ave - connected to the exisitng Dean St Subst. Via a 2.2 mile cable. | 2002-12-31 | Approved | 2002-02-12
NSTAR-01-T05 | 2001-12-26 | Oak Street Substation | Construct a new distribution substation with a 30/40/50 MVA 115/23 kV transformer to be connected to the Bourne to Barnstable #122 115 kV. | 2003-08-31 | Approved | 2002-02-12
NSTAR-02-X01 | 2001-12-26 | Ellis Ave Substation | Install a redundant high-speed protection system between Holbrook substation, Dean St substation, & the new Ellis Ave Substation | 2002-09-01 | Approved | 2002-02-12
NEP-01-T15 | 2001-12-18 | Northboro Rd Substation | Install a 54 MVAR capacitor at the Northboro Rd 115 kV Substation to provide needed voltage support in the Central MA area. | 2001-12-31 | Approved | 2002-02-12
NEP-01-T16 | 2001-12-18 | Millbury Substation | Install a 63 MVAR capcitor at the Millbury 115 kV substation to provide needed voltage support in the Central MA area. | 2001-12-31 | Approved | 2002-02-12
NEP-01-T17 | 2001-12-18 | MWRA Substation | Tap the W-23, 69 kV line to provide load supply to a new MWRA water treatment facility. | 2002-12-31 | Approved | 2002-02-12
VELCO-01-T02 | 2001-12-17 | Sand Bar Substation | Removal of the second cap. Bank at Sand Bar Subst. And relation to the Essex Subst. 115 kV ring bus as bank #5. | 2002-05-31 | Approved | 2002-02-12
VELCO-01-T03 | 2001-12-17 | Essex Substation | Addition of one new 24.75 MVAR cap bank to the Essex Subst. 115 kV ring bus as bank #6 | 2002-05-31 | Approved | 2002-02-12
NSTAR-01-X04 | 2001-12-04 | Mystic Substation | Removal of the Type III SPS at the Mystic 345 kV Subst. Originally the SPS was installed to provide first contigency thermal coverage; four additioanl 345 kV circuits (line 349 XY, 372, 324 & 351) have been installed eliminated the need for the SPS. | 2001-12-31 | Approved | 2002-02-12
NU-01-G01 | 2001-12-02 | Cabot Hydro Station | Capacity Change - redesign Cabot Station generators (6) by converting their V output from 6.9 kV to 13.8 kV, tie the six generators together through a single collector bus, & utilize a single GSU as described in NU-01-T14. | 2003-12-31 | Approved | 2002-02-12
NU-01-T14 | 2001-12-02 | Cabot 19G/Montague 21C | Reconfiguration of the Cabot Station (19G) interconnection to the Montague Substation (21C) by replacing four (4) GSUs and a series 9/115 kV transformer with one (1) GSU (13.8/115 kV) based on the absence of preexisting 69 kV cirucits at Montague. | 2001-12-31 | Approved | 2002-02-12
NU-01-X02 | 2001-11-04 | Lake Road | Installation of a Type III SPS to be connected to all units when either the 330 or 347 lines are open, to protect the units from excessive torque during faults in which there are high import/exports conditions.. | 2001-10-31 | Approved | 2001-12-20
NU-01-T11 | 2001-10-29 | Fort Hill Substation | installation of a new 115/34.5 kV, 40 MVA Substation in Montville, CT (Fort Hill Substation). | 2002-01-31 | Approved | 2001-12-20
INDECK-01-G01 | 2001-10-18 | Indeck - Alexandria Energy Center | Reactivation of a renewable resource generating facility with a capability of 14/6 MW. | 2002-06-01 | Approved | 2001-12-20
NEP-01-T14 | 2001-09-26 | Billerica Substation | Add two 115 kV circuit switchers with motor operated disconnect switch and associated terminal equipment. | 2002-06-30 | Approved | 2001-11-14
NEP-01-T13 | 2001-08-21 | Northboro Rd. Station | Add 2nd radial 115 kV line from Northboro Road substation to the Hudson town line. Install one new 115 kV tie circuit breaker in existing bay at Northboro Road station. | 2002-11-30 | Approved | 2002-02-12
MIR-01-G01 Rev. 1 | 2001-08-15 | Kendall Station | Construct new gas fired generator (Kendall CT) with a net capability of 187 MW (Winter) and 170 MW (Summer) adjacent to the existing Kendall Steam Units at Kendall Station. | 2002-05-31
MIR-01-G01 | 2001-07-31 | Kendall Station | Construct new gas fired generator (Kendall CT) with a net capability of 187 MW (Winter) and 170 MW (Summer) adjacent to the existing Kendall Steam Units at Kendall Station. | 2002-05-31
NSTAR-01-T03 | 2001-07-31 | Kendall Station to the Putnam Station | Install 2.5 miles of solid-dielectric cable, routed in concrete duct, from the Kendall 115 kV Station to the Putnam 115 kV Substation. Connect the Kendall 115 kV generator cable to the Putnam 115 kV Substation. | 2002-05-31
NSTAR-01-T04 | 2001-07-31 | North Cambridge Station | Install two 115 kV series reactors (2.0 ohms) at the North Cambridge Station #509 in each of the 115 kV lines #329-530 and #329-531. | 2002-05-31
NU-01-T10 Rev. 1 | 2001-07-30 20:00 | RESCIND APPLICATION for North Bloomfield 2A Substa | RESCIND APPLICATION for the Upgrade the 1784 line's terminal equipment at the North Bloomfield end. | 2003-05-31 20:00
NU-01-X10 | 2001-07-30 | 1732 Line | Remove the exisiting Canton to Weingart Jct. Rd 1732 line's thermal overload relay. | 2002-05-31
NU-01-T05 | 2001-07-25 20:00 | Balck Pond Jct. | Deparation of three double circuit 345 kV support structures to single circuit support structures for the 348 & 387 line | 2003-05-31 20:00
NSTAR-01-T02 | 2001-07-12 | Chelsea Substation | Replace the 115/13.8 kV Chelsea Transformers 110A and 110B. | 2001-08-01
NU-01-T09 Rev. 1 | 2001-07-05 20:00 | Canton 5R Substation | Add one 115 kV, 39.3 MVAR mechanically switched shunt capacitor bank at the Canton 5R substation | 2003-05-31 20:00
NU-01-T10 | 2001-07-05 20:00 | North Bloomfield 2A Substation | Upgrade the 1784 line's terminal equipment at the North Bloomfield end. | 2003-05-31 20:00
NU-01-T07 | 2001-07-05 | 1732 line | Rebuild the Canton-Weingart, 1732 line. | 2002-05-31
NU-01-T08 | 2001-07-05 | Canton 5R Substation | Add two (2) 115-kV, 26.2 MVAR mechanically switched shunt capacitor banks at the Canton 5R substation. | 2003-05-31
NU-01-T09 | 2001-07-05 | Canton 5R Substation | Add one (1) 115-kV, 39.3 MVAR mechanically switched shunt capacitor bank at the Franklin Drive 1B substation. | 2003-05-31
NU-99-T10 Rev. 2 | 2001-07-05 | 1781 and 1782 lines | Interim Interconnection for the Berkshire Power Generating Station (276 MW). | 2002-09-30
CMP-01-T01 | 2001-06-28 | Redbrook Substation | Tap Section 160 and add a 115/34.5 kV Xfmr at Redbrook Substation & install 2-bkrs to Section 160 at Pleasant Hill Substation. | 2001-09-30
CMP-01-T02 | 2001-06-28 | Lincolnville Substation | Construct new 115 kV to 34.5 kV, 14 MVA substation and will tap Section 86. | 2001-09-30
NEP-01-T08 | 2001-06-21 | Shrewsbury Electric Light Plant, Rolfe Ave Subst. | Install two 30/40/50 MVA 115/13.8 kV transformers, two 115 kV circuit switchers and a new 69 kV breaker to complete the 69 kV ring bus. | 2002-05-31
NU-01-T06 | 2001-06-13 | Chestnut Hill Substation | Addition of two 26.2 MVAR capacitor banks at the NU Chestnut Hill 115 kV Substation. | 2002-04-01
NU-01-T01 | 2001-06-05 | Merrimack Substation | Replace exisitng 230/115 kV autotransformer at the Merrimack Substation with a larger autotransformer to provide approxiamte 300 MVA of summer LTE transformation capability. | 2002-12-30
NEP-01-X01 | 2001-06-04 | Bridgewater Station | Remvoe the U6 line type III SPS at Bridgewater Station based on the elimination of the conditions requireng its use. | 2001-05-31
NEP-01-T12 | 2001-06-03 | Millbury Station Bkr #314 | Upgrade breaker 314 at the Millbury station to achieve Independent Pole tripping capability. | 2002-05-31
NSTAR-01-T01 | 2001-06-03 | West Medway Station | Modify the West Medway 345 kV station to install breaker 113 and connect the Sithe 345 kV generator lead. Upgrade breakers 101, 103, 104, 106, 107 and 109 | 2002-06-01
SNE-01-G01 | 2001-06-03 | West Medway Station | New Gas Trubine Generating plant consisting of three single-cycle natural gas fired generators (Units 4, 5 & 6). | 2002-05-31
VELCO-01-T01 | 2001-05-30 | Coolidge Substation | Additional of two 24.75 MVAR capacitor banks & associated breakers at the Coolidge Substation. | 2002-05-31
NEP-01-T11 | 2001-05-29 | South Danvers Substation | South Danvers Substation - Tap the C155 Nline and rearrange the exisitng two taps oon the C-155S & B-154 lines to serve the exisiting theree 115/23 kV xfmrs. | 2001-11-30
NEP-01-T03 | 2001-05-28 | Westford Substation | Installation of a new 115/13.2 kV Substation in Wesford, MA that will tap the K-137E 115 kV line between Littleton and Bellerica. | 2001-12-31
NU-01-T05 | 2001-05-17 20:00 | Schiller-Bolt Hill N133 Line | Replace limiting termianl equipment on the 115 kV Schiller - Bolt Hill N133 line
NU-01-T04 | 2001-05-14 | Cobble Mtn. Substation | Reconfigure Cobble Mtn Substation by removing the three GSU's and replacing with one GSU. | 2001-11-30
NEP-01-T07 | 2001-04-22 | Gilbert Street Substation | Add four 115 kV circuit switches with MOD's and two electrically inter-locked motor operated 115 kV disconnect switches between lines C-181N and D-182S. | 2001-05-31
NEP-00-G01 | 2001-04-15 | AES Londonderry Stage I Station | Request to Withdraw - New gas-fired combined cycle generation plant consisting of two combustion turbine generators, one steam turbine generator, three generator step-up transformers and three 230 kV generation leads. | 2002-05-31
NEP-00-T02 | 2001-04-15 | North Litchfield Substation | Request to Withdraw - Add two new 230 kV three-breaker ring buses and associated switches and terminal equipment to sectionalize: 1) line A-201 into A-201N and A-201S, and 2) line B-202 into B-202N and B-202S. | 2001-07-31
NEP-00-T03 | 2001-04-15 | AES Generation Station to North Litchfield Substat | Request to Withdraw - Add two 230 kV breakers w/ associated buswork, switches and terminal equip. at new AES Generation Station. Add new 230 KV double circuit line from generation plant to N.Litchfield Subst. | 2001-11-30
NEP-00-T04 | 2001-04-15 | Tewksbury & Pratts Junction Substations | Request to Withdraw - At Tewksbury Subst: Upgrade the 115 kV buswork & terminal equip.; replace 8-115 kV breakers; upgrade 3-230 kV bkrs; install high speed pilot protection group to seven lines; upgrade Pratts Jct. Substation 115 buswork & terminal equip | 2001-11-30
NEP-00-T05 | 2001-04-15 | North Litchfield and Tewksbury Substations | Request to Withdraw - Re-conductor the 230 kV line A-201S between the North Litchfield and Tewksbury Substations; upgrade Tewksbury Substation 230 kV buswork and terminal equipment. | 2001-11-30
NEP-00-T06 | 2001-04-15 | Tewksbury Substation | Request to Withdraw - Replace 230/115 kV Transformer with a total three phase rating of 500 MVA and reconfigure 230 kV yard at Tewksbury Substation. | 2002-05-31
NEP-00-X01 | 2001-04-15 | Comerford Phase I HVdc | Request to Withdraw - Modify the existing Comerford Phase I HVdc Type III Special Protection System to transfer trip signal to initiate runback of the Phase I HVdc generation from the Tewksbury Substation to the new North Litchfield Substation. | 2001-07-31
NEP-00-X02 | 2001-04-15 | North Litchfield and Tewksbury substations | Request to Withdraw - Add two new NPCC Type III SPS to trip the AES Stage I generation. | 2001-11-30
NEP-01-G01 Rev. 1 | 2001-04-10 20:00 | UAE Lowell Power | Construct new simple cycle generating plant consisting of 2 CT's with a combined net capacity of 95.2 MW at 20 degrees F to be built adjacent to existing UAE Lowell Facility | 2001-05-31 20:00
NSTAR-00-T24 Rev. 1 | 2001-03-27 | Framingham Station No. 240 | Add second 115 kV autogtransformer at Framingham Station No. 240. | 2002-06-01
NSTAR-00-X04 | 2001-03-27 | Framingham to Sherborn Line | Request to Withdrawal - installation of Redundant High Speed Relaying on Framingham to Sherborn 115 kV Line No. 240-508. | 2001-04-10
NEP-01-G01 | 2001-03-25 | UAE Lowell Power | Construct new simple cycle generating plant consisting of 2 CT's with a combined net capacity of 95.2 MW at 20 degrees F to be built adjacent to existing UAE Lowell Facility. | 2001-05-31
NU-01-T02 | 2001-03-13 | Stony Hill 48C Substation | Install a 115 kV 25.2 MVAR mechanically switched shunt capacitor bank at the Stony Hill 48C Substation. | 2001-02-11
NU-01-T03 | 2001-03-13 | Rocky River 12Y Substation | Install a 115 kV 25.2 MVAR mechanically switched shunt capacitor bank at the Rocky River 12Y Substation. | 2001-02-11
NEP-00-X06 Rev. 1 | 2001-03-12 | North Quincy & Field Street Stations | Request to Withdraw - Modify exisitng protections schemes at the Quincy & Field Street substations as the result of the Fore River new generation project. | 2001-03-12
NU-00-T05 Rev. 1 | 2001-03-07 | Merrimack Substation | Request to Withdraw - Replace/upgrade or make a parallel addition to the 230/115 kV transformer at the Merrimack Substation to provide 300 MVA of summer LTE transformation capacity. | 2001-03-07
NU-00-X01 Rev. 1 | 2001-03-07 | Merrimack Substation | Request to Withdraw - Add one new NPCC Type III SPS at the Merrimack Substation to monitor loading on the Merrimack autotransformer so as to trip an AES Londonderrry unit whenever an overload condition is detected on the Merrimack autotransformer. | 2001-03-07
MIR-01-X01 | 2001-03-01 | Canal Unit 1 Exciter | Replacement of the Canal Unit #1 Exciter. | 2001-04-30
NSTAR-00-T06 Rev. 1 | 2001-03-01 | Edgar Station | Revised previous submittal to remove the requirement to install two high-speed protection systems on the Edgar-North Quincy-Dewar St Lines 517-532, 517-533, 517-524, 517-525 as confirmed by add'l analysis. | 2002-04-01
NEP-01-T04 | 2001-02-20 | Fitch Rd Substation | Reconductor and rebuild the radial 69 KV line W-23 from Fitch Rd Substation to Woodside Substation to 795 ACSR. | 2001-11-30
NEP-01-T05 | 2001-02-20 | Warren Trasformer No. 2 | Replace the 115/13.2 kV Warren Transformer No. 2. | 2002-06-01
NEP-01-T06 | 2001-02-20 | Beverly Substation | Tap the M-191 Line & install a new 115/13.2 kV substation (Beverly #12). | 2002-06-01
NEP-01-T03 Rev. 1 | 2001-02-07 | Westford Substation | Request to Withdraw - Install new 115/13.2 kV substation in Westford MA. | 2001-12-31
NEP-01-T01 | 2001-01-30 | Wareham St. Substation | Install third 24/32/40 MVA 115 kV - 13.8 kV power transmformer at the Wareham St. Substation. | 2001-06-30
NEP-01-T02 | 2001-01-30 | East Bridgewater Station | Upgrade radial 115 kV line L1 from the E20 tap to East Bridgewater station for greater thermal capabilty | 2002-04-30
NEP-00-G02 Rev. 1 | 2001-01-28 | Hope Energy (RISE) | Contruct a new combined cycle generating plant consisting of two combustion turbine generators and one steam turbine generator. | 2001-05-31
BE-98-T05 Rev. 3 | 2001-01-14 | West Medway #446 345 kV switchyard | Modify/upgrade facilities at West Medway #446 345 kV switchyard wih the replacement of 345 kV breakers, associated disconnect switches and other misc. equipment. | 2001-01-14
NU-00-T24 | 2000-12-19 19:00 | Montville - Bean Hill | Request to Withdraw - Remove clearance limitation and increase summer ratings of the Montville - Bean Hill #1000 Line | 2000-05-31 20:00
NEP-00-T29 | 2000-11-28 | Devens Commerce Center | Reconductor U-21 69kV radial line from Ayer to Pratt Junction substation, install relays & rearrange supply to Devenos Commerce Center | 2001-05-31
NEP-00-T28 | 2000-11-21 | North Quincy Station | Install new 115/32.2 kV substation - Woodchuck Hill & tap the B-154N line between King St. and Middletown. | 2000-12-31
VELCO-00-T04 Rev. 1 | 2000-11-15 | Coolidge Substation/West Rutland Substation | Reconnect & Reenergize (345 kV) the Coolidge substation to West Rutland substation. | 2002-06-01
VELCO-00-T06 Rev. 1 | 2000-11-15 | West Rutland Substation | Rebuild the West Rutland substation to incorporate interconnection through 345 kV bkrs & into a six bkr ring bus. | 2002-06-01
NEP-00-X06 | 2000-11-08 | North Quincy & Field Street Stations | Modify exisitng protections schemes at the Quincy & Field Street substations as the result of the Fore River new generation project. | 2002-04-01
NEP-00-T27 | 2000-11-07 | Kent County Substation | Install 115/12.47 kV transformer at Kent County Substation; will tap bus #2. | 2001-12-31
NU-00-T25 | 2000-11-05 | Scovill Rock | Install new 9T bkr at Scovill Rock and reterminate the 376 line between the 8T and new 9T bkr. | 2002-04-30
NU-00-X26 | 2000-11-05 | Scovill Rock | Install type III SPS at Scovill Rock to runback the East Shore HVdc Facility in the event the 387 line is open ended at Scovill Rock. | 2002-04-30
NEP-00-G05 Rev 1 | 2000-11-01 | Brockton Power Generating Plant | Construction of a 288 MW Winter/267 Summer Combined Cycle Plant. | 2002-12-31
VELCO-00-T04 | 2000-11-01 | Coolidge Substation/West Rutland Substation | Reconnect & Reenergize (345 kV) the Coolidge substation to West Rutland substation. | 2002-06-01
VELCO-00-T05 | 2000-11-01 | Coolidge Substation/West Rutland Substation | Construct a three breaker 345 kV ring bus. | 2002-06-01
VELCO-00-T06 | 2000-11-01 | West Rutland Substation | Rebuild the West Rutland substation to incorporate interconnection through 345 kV bkrs & into a six bkr ring bus. | 2002-06-01
VELCO-00-T07 | 2000-11-01 | West Rutland Substation | Rebuild the West Rutland Substation to West Rutland Tap. | 2002-06-01
VELCO-00-T08 | 2000-11-01 | Cold River Substation | Replace Motor Operated SCADA control switches at Cold River Substation. | 2002-06-01
VELCO-00-T09 | 2000-11-01 | Blissville Substation | Replace Motor Operated SCADA control switches at Blissville Substation. | 2002-06-01
NSTAR-00-T24 | 2000-10-30 | Framingham Station No. 240 | Add second 115 kV autogtransformer at Framingham Station No. 240 | 2002-06-01
NSTAR-00-T25 | 2000-10-30 | West Medway Station No. 446 | Replacement existing autotransformer No. 345B. | 2002-06-01
NSTAR-00-T26 | 2000-10-30 | Walpole Station No. 447 | Replace existing autotransformer. | 2002-06-01
NSTAR-00-T27 | 2000-10-30 | Waltham Station No. 282 | Replacement existing autotransformer. | 2002-06-01
NSTAR-00-T28 | 2000-10-30 | Waltham Station No. 282 | Add third 115 kV phase angle regulating transformer. | 2002-06-01
NSTAR-00-T29 | 2000-10-30 | West Medway/Waltham Stations | Modification of towers on the 282-602 line & 240-601 line. | 2002-06-01
NSTAR-00-T30 | 2000-10-30 | Sudbury/Speen St. Stations | Rebuild the 342-507 line. | 2002-06-01
NSTAR-00-T31 | 2000-10-30 | Towers between Speen St. & Framingham | Replace towers on the 433-507 line. | 2002-06-01
NSTAR-00-T32 | 2000-10-30 | Sherborn Rd. Station No. 274 | Replace bkrs & disconnect switches. | 2002-06-01
NU-00-T21 | 2000-10-29 | Greggs | Greggs Substation - F1620 Bkr Replacement. | 2001-12-30
NU-00-T22 | 2000-10-29 | Greggs | Greggs Sustation - J1140 Bkr Replacement. | 2001-12-30
NU-00-T23 | 2000-10-29 | Merrimack | Merrimack Substation - D121 Bkr Replacement. | 2001-12-30
NSTAR-00-T15 | 2000-10-15 | Associated Xmission for Sithe Mystic Station | Modify the Mystic 345 kV station to install line 351. | 2001-11-30
NSTAR-00-T23 | 2000-10-15 | Sithe Mystic Station | Install three 115 kV shunt reactors, one each at K Street, Woburn and Lexington. | 2002-04-01
NEP-00-T22 | 2000-10-10 | Brockton Power | Construct a three breaker ring bus station. | 2002-04-30
NEP-00-T23 | 2000-10-10 | Brockton Power | Reconductor F19 Line from Brockton Power to Auburn Street. | 2002-04-30
NEP-00-T24 | 2000-10-10 | Brockton Power | Replace the 1601 breaker at Bridgewater Station. | 2002-04-30
NEP-00-T25 | 2000-10-10 | Brockton Power | Rebuild the S8 line from Bridgewater Station to Somerset Station. | 2002-04-30
NEP-00-T26 | 2000-10-10 | Brockton Power | Upgrade thermal capacity of the northern Auburn Street 115 kV ring bus. | 2002-04-30
NEP-00-X05 | 2000-10-10 | Brockton Power | Install Type III SPS at Auburn Street station. | 2002-04-30
SNE-00-G02 | 2000-10-10 | Sithe Mystic Station | Construction of a 1700 MW Winter/1413 Summer Combined Cycle Plant | 2001-12-31
NEP-00-G05 | 2000-10-09 | Brockton Power Generating Plant | Construction of a 288 MW Winter/267 Summer Combined Cycle Plant. | 2002-12-31
NSTAR-00-T16 | 2000-10-09 | Sithe Mystic Station | Construct a new 5-breaker 115 kV ring station at Mystic to connect lines 211-514 (Mystic to Woburn), 423-515 (Mystic to Everett) and 488-518 (Mystic to Chelsea) and the Sithe 115 kV steam unit #13. | 2002-04-01
NSTAR-00-T17 | 2000-10-09 | Sithe Mystic Station | Install line 351 and a 115 kV shunt reactor at North Cambridge. | 2001-11-30
NSTAR-00-T18 | 2000-10-09 | Sithe Mystic Station | Separate line 346XY into two lines 346 & 465. | 2001-11-30
NSTAR-00-T19 | 2000-10-09 | Associated Xmission for Sithe Mystic Station | Reconductor lines 250-516 and 250-517. | 2002-04-01
NSTAR-00-T20 | 2000-10-09 | Sithe Mystic Station | Improve cable cooling on lines 329-510 and 329-511 (Mystic to Somerville to Brighton). | 2002-04-01
NSTAR-00-T21 | 2000-10-09 | Sithe Mystic Station | Improve cable cooling on lines 385-510 & 385-511 between High Street and Kingston Street. | 2002-04-01
NSTAR-00-T22 | 2000-10-09 | Sithe Mystic Station | Replace the Mystic autotransformer. | 2001-11-30
NSTAR-00-X03 | 2000-10-09 | Sithe Mystic Station | Install a Type III SPS to trip the Sithe steam unit following a stuck breaker contingency between 211-514 and 423-515 or 488-518. | 2002-04-01
NSTAR-00-T14 | 2000-10-02 | Line #282-507 | Reconductor 115 KV Line #282, Waltham, to Station # 342, Sudbury. | 2001-05-31
NU-00-T13 | 2000-10-01 | Capacitor Bank Replacement at Berlin | 115 kV Capacitor bank (6A-13K) replacement at Berlin. | 2000-12-31
NEP-00-G04 | 2000-09-21 | AES Londonderry | Construction of 767 MW Winter/ 678 MW Summer Combined Cycle gas/oil plant. | 2002-05-31
NEP-00-T18 | 2000-09-21 | AES Londonderry | Construction of new N. Litchfield substation. | 2002-05-31
NEP-00-T19 | 2000-09-21 | AES Londonderry | Construction of a new 230 KV double circuit line from Londonderry to N. Litchfield | 2002-05-31
NEP-00-T20 | 2000-09-21 | AES Londonderry | Replacement of substation transformer #2 at NEP Tewksbury; install pilot protection on various lines; Replace Pratts Junction 115 KV buswork. | 2002-05-31
NEP-00-T21 | 2000-09-21 | AES Londonderry | Re-tension NEP 230 KV line B202S & Upgrade buswork. | 2002-05-31
NEP-00-X03 | 2000-09-21 | AES Londonderry | Modify Comerford Phase I HVdc Special Protection System. | 2002-05-31
NEP-00-X04 | 2000-09-21 | AES Londonderry | Install a Type III Special Protection System at N. Litchfield substation. | 2002-05-31
NU-00-T14 | 2000-09-21 | AES Londonderry | Rebuild R-187 from Greggs to Scobie. | 2002-05-31
NU-00-T15 | 2000-09-21 | AES Londonderry | Rebuild R-169 Line from Three Rivers to Dover. | 2002-05-31
NU-00-T16 | 2000-09-21 | AES Londonderry | Replacement of 115 KV circuit breaker at Greggs Falls substation (O1610). | 2002-05-31
NU-00-T17 | 2000-09-21 | AES Londonderry | Replacement of 115 KV circuit breaker at Merrimack substation (H137). | 2002-05-31
NU-00-T18 | 2000-09-21 | AES Londonderry | Line Reactor at Greggs Substation. | 2002-05-31
NU-00-T20 | 2000-09-21 | AES Londonderry | Construct 3 breaker substation at Watts Brook on R-187 line. | 2002-05-31
NU-00-X19 | 2000-09-21 | AES Londonderry | Install Type III Special Protection System at Greggs Falls substation. | 2002-05-31
NU-00-T12 | 2000-09-04 | Capacitor Bank Replacement at Plumtree | Capacitor bank replacement at Plumtree. | 2000-12-31
NEP-00-T17 | 2000-08-07 | Sherman Road | Replace protection equipment at the Sherman Road terminal of line 347. | 2000-08-31
BE-99-T04 | 2000-07-31 | 303N line Upgrade Cancellation | Withdrawal of Application BE-99-T04. | 2000-07-31
BHE-00-G01 | 2000-07-31 | Beaver Chester Generating Plant | Reactivate 14.7 MW biomass fired generation. | 2000-08-31
FPLE-00-G01 | 2000-07-31 | IDC Bellingham Power Project | Construction of 560 MW winter / 450 MW summer generating station. | 2003-01-31
NSTAR-00-T04 | 2000-07-31 | 345 kV Ring Station | Construct a five-breaker 345 kV ring station to interconnect the IDC plant. | 2002-06-01
NSTAR-00-T05 | 2000-07-31 | 345 kV West Medway breakers | Upgrade West Medway breakers to address short circuit and stability concerns. | 2002-06-01
NSTAR-00-T06 | 2000-07-31 | Edgar Station | Modify Edgar station to connect the three Sithe units, split line 478-502XY into two separate line and relocate the Edgar to North Quincy 115 kV cables. | 2002-06-01
NSTAR-00-T07 | 2000-07-31 | Holbrook Station | Modify Holbrook Station by splitting and relocating lines, upgrading/retrofitting 115 kV breakers. | 2002-06-01
NSTAR-00-T08 | 2000-07-31 | Edgar breaker #10 and Grove Street Breaker | Upgrade Edgar breaker #10 and Grove Street breaker to address short circuit concerns. | 2002-06-01
NSTAR-00-T09 | 2000-07-31 | 115 kV transmission line 478-508 and 478-509 | Remove conductor to ground clearance limitations to achieve the full capability of the conductors. | 2002-06-01
NSTAR-00-T10 | 2000-07-31 | 115 kV transmission line 478-502 and 478-503 | Split line 478-502XY into lines 478-502 and 478-503 and re-conductor the resulting two lines. | 2002-06-01
NSTAR-00-T11 | 2000-07-31 | 115 kV transmission lines 447-508 and 447-509 | Remove conductor to ground clearance limitations to achieve the full capability of the 795 ACSR conductors. | 2002-06-01
NSTAR-00-T12 | 2000-07-31 | 115 kV transmission line 65-508 | Upgrade the line to achieve a minimum LTE rating of 220 MVA. | 2002-06-01
NSTAR-00-T13 | 2000-07-31 | 115 kV transmission line 65-502XY | Upgrade the line to achieve a minimum LTE rating of 220 MVA. | 2002-06-01
NSTAR-00-X01 | 2000-07-31 | SPS at IDC | Install a Type II SPS to trip the steam unit for any stuck breaker fault at the IDC interconnection station. | 2002-06-01
NSTAR-00-X02 | 2000-07-31 | Type III SPS | Install a Type III SPS to trip the Sithe steam unit and one gas unit for a 5% STE violation upon loss of two or more of the four lines out ot the Sithe Fore River plant after a 5-second delay. | 2002-06-01
PGE-00-G01 | 2000-07-26 | Lake Road Generating plant | Construction of a three-unit natural gas fired combined cycle power facility with a nominal rating of 792 MW. | 2004-08-01 | Approved | 2000-09-18
NU-00-T11 | 2000-07-24 | Lake Road | Provide a connection for the three Lake Road generators to the New England 345 kV transmission system on the 347 Line near the Connecticut-Rhode Island border. | 2000-08-31
SNE-00-G01 | 2000-07-10 | Fore River Station generation plant | Construct an 843 MW winter/700 MW summer combined cycle gas plant. | 2002-04-30
NU-00-G01 | 2000-07-06 20:00 | PPL Wallingford Energy | Construction of five new generating units. 10/8/04: removal of condition 3 of approval pertaining to additional short circuit related anayses.) | 2001-05-31 20:00 | Approved | 2004-10-07 20:00
NU-00-T08 | 2000-07-06 | Wallingford Energy | Substation and Transmission Upgrades to Interconnect the Wallingford Energy. | 2001-05-31
NEP-00-T15 | 2000-07-05 | Shaker Road Substation | Replace existing 69/13.2 kV transformer T-2 at Shaker Road Substation, MA. | 2001-05-31
NEP-00-T16 | 2000-07-02 | 328 Line | Construct a three breaker ring bus substation on the 328 line for the interconnection of the North Smithfield power plant. | 2002-02-28
INDECK-00-G01 | 2000-06-28 | Indeck - North Smithfield Energy Center | Construction of a new 350 MW gas turbine combined cycle facility. | 2003-06-30
NU-99-T10 Rev. 1 | 2000-06-21 | 1781 and 1782 lines | Interim interconnection for the Berkshire Power Generating Station | 2001-08-31
CPN-00-G01 | 2000-06-04 | Towantic Energy Project | New 548 MW gas-fired combined cycle power plant. | 2002-12-30
NU-00-T07 | 2000-05-30 | Towantic Energy | Construct a new 115 kV Towantic substation to facilitate the interconnection of the generators on the 1575, 1585, and 1990 lines. Install a 4% reactor on the 1990S line, improve clearances on the 1580 line, improve the rating of the 1585 line. | 2001-12-30
NU-00-T06 | 2000-05-29 | Glenbrook Substation | Reconductor two 115-kV transmission line sections: line 1880 from Glenbrok 1K substation to Rowayton Junction and line 1890 from Glenbrook 1K to Ely Ave. | 2002-05-31
NEP-00-T13 | 2000-05-24 | Litchfield Street Substation | Install a new 115/13.8 kV substation at Litchfield Street. | 2001-12-31
NEP-00-T14 | 2000-05-24 | Point Street Substation | Install a New 115/12.47 kV substation at Point Street. | 2000-12-31
BE-98-T05 Rev. 2 | 2000-05-08 | West Medway #446 345 kV switchyard | Modify/upgrade facilities at West Medway #446 345 kV switchyard wih the replacement of 345 kV breakers, associated disconnect switches and other misc. equipment. | 2000-05-08
UI-00-T01 | 2000-05-04 | East Main Street Substation | Relocation of East Main Street Substation. | 2001-06-30
VELCO-00-G01 | 2000-05-03 | Sandbar Substation | Installation of 25 MVA generator (former NRG owned, Somerset Jet #1), to maintain VELCO 115 kV voltage at Sandbar substation. | 2000-05-31
VELCO-00-T03 | 2000-05-03 | Sandbar Substation | Transmission facilities related to the installation of the 25 MVA former Somerset Jet #1 at the Sandbar 115 kV substation. | 2000-05-31
NU-00-T05 | 2000-05-01 20:00 | Merrimack Substation | Replace/upgrade or make a parallel addition to the 230/115 kV transformer at the Merrimack Substation to provide 300 MVA of summer LTE transformation capacity. | 2002-05-31 20:00
NU-00-X01 | 2000-05-01 20:00 | Merrimack Substation | Add one new NPCC Type III SPS at the Merrimack Substation to monitor loading on the Merrimack autotransformer so as to trip an AES Londonderrry unit whenever an overload condition is detected on the Merrimack autotransformer. | 2001-11-30 19:00
NEP-00-G02 | 2000-05-01 | Hope Energy (RISE) | Contruct a new combined cycle generating plant consisting of two combustion turbine generators and one steam turbine generator. | 2001-05-31
NEP-00-T07 | 2000-05-01 | Drumrock | Replace terminal equipment (circuit breakers, disconnect switches, buswork) on 115 kV line S171S and T-172S at Drumrock, and reduce local breaker failure clearing time for all six 115 kV circuit breakers at Drumrock. | 2001-05-31
NEP-00-T08 | 2000-05-01 | Woonsocket | Replace terminal equipment (circuit breakers, buswork) on 115 kV lines S-171N and T-172N at Woonsocket. | 2001-05-31
NEP-00-T09 | 2000-05-01 | Hartford Avenue | Replace two 115 kV circuit breakers (S171S and T172S) at Hartford Avenue to provide Independent Pole Tripping capability. | 2001-05-31
NEP-00-T10 | 2000-05-01 | Drumrock to Kent County | Reconductor 1.0 mile of 115 kV line G-185N from Drumrock to Kent County with 795 ACSR. | 2001-05-31
NEP-00-T11 | 2000-05-01 | W. Farnum and Riverside | Reconductor 1.9 miles of 115 kV line H-17 between W. Farnum and Riverside with 795 ACSR. | 2001-05-31
NEP-00-T12 | 2000-05-01 | Hope Energy / Hartford Ave. to Drumrock | Construct two tap lines from 115 kV lines S-171S and T-172S to the Hope Energy site, and construct a four breaker ring bus substation to terminate the two transmission lines and the two generator step-up transformers. | 2001-05-31
SNE-00-RR01 | 2000-04-25 | Edgar Jet No. 1 | Retirement of Edgar Jet No. 1. | 2000-07-25
SNE-00-RR02 | 2000-04-25 | Edgar Jet No. 2 | Retirement of Edgar Jet No. 2. | 2000-07-25
VELCO-00-T02 | 2000-04-17 | Sand Bar Switching Station | Installation of a 25 MVAR capacitor bank at Sand Bar Switching Station. | 2000-05-31
PDC-00-G01 | 2000-04-10 20:00 | Meriden Power Units 1 and 2 | Installation of two-unit Meriden Power project totaling 575 MW winter / 535 MW summer | 2002-05-31 20:00
PDC-00-G01 Rev. 1 | 2000-04-10 20:00 | Meriden Power Units 1 and 2 | Installation of two-unit Meriden Power project totaling 575 MW winter / 535 MW summer This resubmittal indicates a CHANGE in DESIGN to GE from ABB | 2003-05-31 20:00
NU-00-T04 | 2000-04-10 | Southington 4C | Upgrade 345 kV terminal at Southington 4C to match the conductor rating; install 3-breaker substation at Southington to Haddam Neck 362 line; add a 2% reactor at both the Southington to Canal 1950 line and the Southington to Todd 1910 line. | 2002-06-29
CMEEC-00-RR01 | 2000-04-05 20:00 | A. L. Pierce | Retirement of A. L. Pierce unit | 2000-06-30 20:00
BHE-00-RR01 | 2000-04-03 | Graham Unit 4 | Retire Graham Unit 4. | 2000-03-29
BHE-00-RR02 | 2000-04-03 | Graham Unit 5 | Retire Graham Unit 5. | 2000-03-29
CMP-00-G01 | 2000-04-03 | Portsmouth Naval Shipyard | Replace a 3.5 MW Steam Turbine-Generator with a 5.3 MW Gas Turbine-Generator at the Portsmouth Naval Shipyard. | 2000-11-16
NU-00-T01 | 2000-04-03 | Long Mountain Substation | Add two 345 kV breakers at the Long Mountain substation. | 2001-02-28
NSTAR-00-T02 | 2000-04-02 | Canton Substation | Install additional 40 MVA 115/13.8 kV Transformer at Station 470 Canton | 2000-06-30
NU-00-T02 | 2000-03-27 | Scobie Substation | Add on 115 kV circuit breaker at the Scobie Substation. | 2000-11-30
NU-00-T03 | 2000-03-27 | Scobie and Deerfield Substations | Replace six 345 kV wave traps at the Scobie and Deerfield Substations; upgrade protection systems on the 345 kV 385 and 391 lines. | 2000-11-30
CMP-99-T03 Rev. 1 | 2000-03-08 | Quaker Hill Substation | Rebuild approximately ten (10) miles of Section 140 from Maguire Road to Quaker Hill Substation utilizing 1113 ACSR conductor. | 2000-12-31
NSTAR-00-T01 | 2000-03-08 | North Cambridge Station #509 | Addition of a 115 kV 80 MVAr shunt reactor at Station #509 in North Cambridge. | 2000-04-30
UI-00-G01 | 2000-02-23 | English 7 | Reactivate English Station Unit 7. | 2000-05-31
UI-00-G02 | 2000-02-23 | English 8 | Reactivate English Station Unit 8. | 2000-05-31
NEP-00-T01 | 2000-02-06 | Johnston Substation | Tap S-171S Johnston tap line and install two 115 kV Airbreak switches, a 115 kV circuit switcher and one 24/32/40 MVA transformer. | 2001-05-31
BHE-00-T01 | 2000-01-30 | Orrington Substation, Line 65 | Rerate existing Line 65 from Orrington Substation to the Bucksport town line, which is the BHE share of this line. | 2000-01-31
BHE-00-T02 | 2000-01-30 | Orrington Substation, Line 205 | Rerate existing Line 205 from Orrington Substation to the Bucksport town line, which is the BHE share of this line. | 2000-02-29
BHE-00-T03 | 2000-01-30 | Orrington Substation, Line 248 | Rerate existing Line 248 from Orrington Substation to the Graham Substation. | 2000-03-31
BHE-00-T04 | 2000-01-30 | Orrington Substation, Line 249 | Rerate existing Line 249 from Orrington Substation to the Graham Substation. | 2000-03-31
VELCO-00-T01 | 2000-01-30 | Williston Substation | Replace 230-3 115 kV circuit switcher at Williston Substation with a circuit breaker. | 2000-03-30
RMLD-00-T01 | 2000-01-11 | North Reading Substation | New 115kV substation with taps off NEES transmission circuits S-145 and T-146 in the town of North Reading. | 2000-05-31
CMP-00-T01 | 2000-01-04 | Androscoggin | Add two 115/13.8 kV transformers at Androscoggin Energy Center to connect to International Paper in Jay, Maine. | 2000-01-31
NRGPM-99-RR-578 | 2000-01-03 | Somerset Jet 1 | Retirement of Somerset Jet 1. | 2000-03-05
NRGPM-99-RR-579 | 2000-01-03 | Somerset Jet 2 | Retirement of Somerset Jet 2. | 2000-03-05
NEP-99-T16 | 1999-12-30 | Brayton Point Substation | Rebuild Brayton Pt. 345 kV Switchyard using breaker and 1/2 design. | 2004-10-02
NEP-99-X02 | 1999-12-30 | Brayton Point Substation | Install Type III SPS at Brayton Pt. 345 kV Substation | 2004-10-02
NEP-99-T15 | 1999-11-14 19:00 | Pinehurst Substation | Tap M-139 line and install a 2nd 24/32/40 MVA 115/13.2 kV transformer and two 115 kV circuit switchers | 2000-05-31 20:00
NEP-99-T14 | 1999-11-01 19:00 | Deerfield Substation | Rebuilding of the 6.8 mile two-wire portion of the I-9/J-10 69 kV Adams - Deerfield (MA) lines to a single-wire line | 1999-10-31 19:00
EUA-99-G01 | 1999-10-26 20:00 | BFGSI Fall River Electric | New 7.45 MW landfill gas generator to be built by Browning Ferris Gas Services, Inc. | 1999-11-30 19:00
SP-99-T01 | 1999-10-20 20:00 | Somerset Generating Station | Replace 078 115 kV breaker at Somerset Generating Station | 2000-02-29 19:00
BE-99-T05 | 1999-10-12 20:00 | Mystic - Kingston Street Stations | New 345 kV line between Mystic station and Kingston Street station
BE-99-T06 | 1999-10-12 20:00 | Kingston Street station | New 345/115 kV autotransformer at Kingston Street station
BE-99-T07 | 1999-10-12 20:00 | K Street station | New 115 kV 80 MVAR shunt reactor at K Street station
BE-99-T08 | 1999-10-05 20:00 | North Cambridge autotransformer | Replacement of the current North Cambridge 345B autotransformer with a new autotransformer. | 1999-10-31 19:00
NEP-99-T11 | 1999-09-30 20:00 | Millbury Substation | 69 kV Substation | 2000-11-30 19:00
CMP-99-T03 | 1999-09-29 20:00 | Quaker Hill Substation | Rebuild 10 miles of Section 140 from Maguire Rd. to Quaker Hill Substation | 2000-12-31 19:00
EUA-98-G01 | 1999-09-23 20:00 | Tiverton Units 1 & 2 | Modification of conditions for approval of EUA-98-G01 to remove requirement to replace two EUA breakers at Somerset Station and add requirement to replace OCB 078 at Somerset Power | 1999-11-30 19:00
NEP-99-T08 | 1999-09-14 20:00 | Vernon and Deerfield 4 Substations | Convert double circuit 69 kV lines to single circuit | 2000-09-30 20:00
NEP-99-T09 | 1999-09-14 | East Webster Substation | Reconductor 69 kV line | 2000-05-31
NEP-99-T12 | 1999-09-13 20:00 | Burtt Road Substation | Tap T-146 line and install a new substation with a 115 kV circuit switcher and one 24/32/40 MVA transformer | 2000-03-19 19:00
NEP-99-T13 | 1999-09-13 20:00 | Golden Rock Substation | Tap G-133W line and install a new substation with a 115 kV circuit switcher and one 30/40/50 MVA transformer | 2001-01-14 19:00
NEP-99-T04 | 1999-09-09 20:00 | Sandy Pond Substation | Addition of one 115 kV Circuit Breaker | 1999-12-30 19:00
CMP-99-G02 | 1999-09-07 20:00 | Westbrook Units 1, 2, 3 | New 578 MW generation plant | 1999-12-31 19:00
CMP-99-G02 Rev. 1 | 1999-09-07 20:00 | Westbrook Units 1, 2, 3 | New 578 MW generation plant | 2000-12-31 19:00
CMP-99-T05 Rev. 2 | 1999-09-07 20:00 | Spring Street Substation, Westbrook Substation, So | Add new breakers, rebuild transmission line and add new transmission line to accommodate new Westbrook Energy Center plant | 2000-05-31 20:00
CMP-99-G04 | 1999-09-02 20:00 | Bucksport Unit 1 | Add 174 MW generating plant to 115 kV system at Champion International Corp. | 2000-10-31 19:00
CMP-99-G04 Rev. 1 | 1999-09-02 20:00 | Bucksport Unit 1 | Add 174 MW generating plant to 115 kV system at Champion International Corp. | 2000-10-31 19:00
CMP-99-G04 Rev. 2 | 1999-09-02 20:00 | Bucksport Unit 1 | Add 174 MW generating plant to 115 kV system at Champion International Corp. | 2000-10-31 19:00
CMP-99-T06 | 1999-09-02 20:00 | Bucksport Substation | Connect generator lead with 115 kV system at Champion International Corp. | 2000-03-31 19:00
CMP-99-T06 Rev. 3 | 1999-09-02 20:00 | Bucksport Energy | Connect generator lead with 115 kV system at Champion International Corp. | 2000-03-31 19:00
NU-99-T09 | 1999-09-02 | Newington Energy | Transmission upgrades to interconnect the Newington Energy Project | 2002-04-30
CMP-99-G03 | 1999-09-01 20:00 | Gorham Units 1, 2 & 3 | New 850 MW generation plant at Buxton Sta. | 2001-11-30 19:00
CMP-99-G03 Rev. 1 | 1999-09-01 20:00 | Gorham Units 1, 2 & 3 | New 850 MW generation plant at Buxton Sta. | 2001-11-30 19:00
CMP-99-T04 | 1999-09-01 20:00 | Buxton Substation / Gorham Energy | 10 mile 345 kV circuit from Buxton Sta. to Gorham Energy Project | 2000-11-30 19:00
CMP-99-T04 Rev. 2 | 1999-09-01 20:00 | Buxton Substation / Gorham Energy | 10 mile 345 kV circuit from Buxton Sta. to Gorham Energy Project | 2000-11-30 19:00
EUA-99-T02 | 1999-09-01 20:00 | Sherman Road Station | Upgrade 345 kV Breaker #141 at Sherman Road Station | 2000-01-31 19:00
NEP-97-T07 | 1999-09-01 20:00 | Carpenter Hill | Carpenter Hill 115 kV Switchyard and Type III SPS | 1999-09-30 20:00
NEP-99-T06 | 1999-09-01 20:00 | ANP Milford | Addition of one 115 kV circuit breaker | 1999-08-31 20:00
NEP-99-T10 | 1999-09-01 20:00 | Narragansett Blackburn Substation / Amtrak Warwick | Two 115 kV taps to supply Amtrak traction power system
CONED-99-G01 | 1999-09-01 | Newington Energy Units 1 and 2 | New 525 MW generating plant. | 2002-04-30
CMP-99-X01 | 1999-08-31 20:00 | Maxcys | Modify Maxcys SPS timer
NEP-98-T08-B | 1999-08-25 20:00 | ANP-Bellingham | Reconductor 2.2 mi. of 345 kV line between W. Medway and ANP-Bellingham
BE-98-T02-A | 1999-08-24 20:00 | ANP-Blackstone | Upgrade facilities for ANP Blackstone
BE-98-T02-B | 1999-08-24 20:00 | West Medway to NEA tap | Reconductor 5.5 mi. of 345 kV line between West Medway #446 and the NEA tap
BE-98-T02-C | 1999-08-24 20:00 | ANP Blackstone to NEA tap | Reconductor 2.6 mi. of 345 kV line between ANP-Blackstone tap and NEA tap
EUA-98-T04-A | 1999-08-24 20:00 | Sherman Road Station | Upgrade Sherman Rd. Station facilities for ANP Blackstone | 2000-04-30 20:00
EUA-98-T04-B | 1999-08-24 20:00 | Sherman Road Station | Upgrade Sherman Rd. Station facilities | 2000-04-30 20:00
NEP-98-T08-A | 1999-08-24 20:00 | ANP-Bellingham | Upgrade facilities for ANP Bellingham
NEP-99-T03 | 1999-08-23 20:00 | ANP Milford | Reconductor 115 kV D-130 tap (ANP Milford tap - Depot tap) | 1999-03-31 19:00
MPC-99-G01 | 1999-05-04 20:00 | Milford Power | Construct an 287 MW winter/268 MW summer combined cycle gas/oil plant. | 2000-09-30 20:00
NU-99-T04 | 1999-05-04 20:00 | Milford Power | Associated Transmission Upgrades for Milford Power Plant | 2000-09-30 20:00

## Macro1 (hidden)
Macro1 | Auto_Open
Macro10
Macro11
Macro12
Macro2
Macro3
Macro4
Macro5
Macro6
Macro7
Macro8
Macro9
Recover