2015 Economic Study

Strategic Transmission Analysis—Onshore Wind Integration
© ISO New England Inc.
System Planning | Resource Adequacy

september 2, 2016

ISO-NE PUBLIC

Contents

Figures	iii

Tables	iv

Nomenclature	v

Section 1
Executive Summary	1

1.1 ISO New England 2013 Strategic Transmission Analysis—Wind Integration Study	2

1.2 Onshore Wind—2015 Economic Study	2

1.3 Production Cost	4

1.4 Load-Serving Entity Energy Expenses	4

1.5 Environmental Metrics	4

Section 2
Introduction	5

2.1 Economic Study Process	5

2.2 Economic Study Request for the Maine Area Transmission Improvements
and the 2015 Study Scope of Work	6

2.3 The Maine Study Area and Assumed Interface Transfer Capability	7

2.4 Scenarios	8

2.4.1 RENEW-Requested Scenarios	8

2.4.2 Cases based on the Interconnection Queue	11

2.4.3 Summary of the Scenarios	12

Section 3
Data and Assumptions	14

3.1 Load Forecasts	14

3.2 Resources	14

3.2.1 Detailed Modeling of Thermal Unit Heat-Rate Curves	14

3.2.2 Resource Availability	14

3.2.3 Fuel Prices	15

3.2.4 Profiles for Energy Efficiency, Active Demand Resources, and Real-Time Emergency Generation	16

3.2.5 Photovoltaic Resources	17

3.2.6 Wind Resources	18

3.2.7 Hydroelectric Resources	19

3.3 Environmental Emission Allowances	20

3.4 Imports and Exports	20

3.4.1 Québec	21

3.4.2 Maritimes	22

3.4.3 New York	23

3.5 Transmission System Network	25

3.5.1 Representing Loads	25

3.5.2 Transmission Interfaces	25

3.5.3 Contingency Modeling	26

3.6 Production Cost Simulation Model	26

Section 4
Simulation Results	28

4.1 Simulation Metric Background	28

4.2 Energy Bottled-In Maine	28

4.2.1 Wind Energy	28

4.2.2 Hydroelectric Energy	30

4.2.3 Energy from New Brunswick Imports	31

4.3 Interface Constrained Hours	33

4.3.1 Orrington South	33

4.3.2 Surowiec South	34

4.3.3 North–South	35

4.4 Production Cost	36

4.5 Implied Range of Capital Investment Attributable to Production Cost Savings	38

4.6 Load-Serving Entity Energy Expense	38

4.7 Locational Marginal Prices	40

4.7.1 Bangor Area	40

4.7.2 Southern Maine Area	41

4.7.3 New England	42

4.8 CO2 System Emissions	43

Section 5
Observations	45

Section 6
Appendix	46

6.1 Economic Metrics from Production Simulation	46

6.1.1 Production Cost	46

6.1.2 LSE Energy Expense	46

6.2 Wind Units	47

Figures

Figure 2-1: 	Interfaces evaluated in northern Maine.	7

Figure 2-2: 	RENEW base case—STA-WI-studied wind generation, as of October 1, 2013.	9

Figure 2-3: 	RENEW Sensitivity 1—Less Wind.	10

Figure 2-4: 	RENEW Sensitivity 2—More Wind.	11

Figure 3-1: 	Fuel-price assumptions based on EIA’s 2015 Annual Energy Outlook,
updated December 21, 2015 ($/MWh).	15

Figure 3-2: 	Assumed monthly variation in the natural gas prices for New England, 2021.	16

Figure 3-3: 	Profile representing passive demand resources, active demand resources,
and real-time emergency generation, 2021 (MW).	17

Figure 3-4: 	New England aggregate photovoltaic profile, 2021 (MW).	18

Figure 3-5: 	New England aggregate wind profile, 2006 (MW).	19

Figure 3-6: 	New England aggregate hydro profile (MW).	19

Figure 3-7: 	New England’s external interfaces.	21

Figure 3-8: 	Average diurnal flows by month, representing net energy injections into New England
from Québec at HQ Phase II, 2012 to 2014 (MW).	22

Figure 3-9: 	Average diurnal flows by month, representing net energy injections into New England
from Québec at Highgate, 2012 to 2014 (MW).	22

Figure 3-10: 	Average diurnal flows by month, representing net energy injections into New England
via the New Brunswick ties (MW).	23

Figure 3-11: 	Average diurnal flows by month, representing net energy injections into New England
at the NY AC tie, 2012 to 2014 (MW).	24

Figure 3-12: 	Average diurnal flows by month, representing net energy injections into New England
across the Norwalk to Northport cable, 2012 to 2014 (MW).	24

Figure 3-13: 	Average diurnal flows by month, representing net energy injections into New England
at Cross-Sound Cable, 2012 to 2014 (MW).	25

Figure 4-1: 	LMPs for BHE ($/MWh).	40

Figure 4-2: 	LMPs for southern Maine ($/MWh).	41

Figure 4-3: 	LMPs for aggregate ISO New England ($/MWh).	42

Tables

Table 1-1 	Total Nameplate Wind for Each Case Investigated (MW)	3

Table 1-2 	Assumed Improvements in the Maine Corridor Interface Ratings	3

Table 2-1 	Assumed Maine Corridor Interface Ratings (MW)	8

Table 2-2 	Total Nameplate Wind for the Cases Investigated (MW)	13

Table 3-1 	Amount and Type of Demand Resources in New England, 2021 (MW)	16

Table 3-2 	Internal New England Interface Limits, 2021 (MW)	26

Table 4-1 	Wind Energy within Maine (GWh)	29

Table 4-2 	Bottled-In Wind Energy within Maine with the Profile as Reference (GWh)	29

Table 4-3 	Change in the in Wind Energy Output Due to Higher Transfer Limits (GWh)	29

Table 4-4 	Hydro Energy within Maine (GWh)	30

Table 4-5 	Bottled-In Hydro Energy within Maine with Profile as Reference (GWh)	31

Table 4-6 	Change in Hydro Energy Output Due to Higher Transfer Limits (GWh)	31

Table 4-7 	New Brunswick Imports (GWh)	32

Table 4-8 	Bottled-In Energy from New Brunswick with Profile as Reference (GWh)	32

Table 4-9 	Change in Imported Energy from New Brunswick Due to Higher Transfer Limits (GWh)	33

Table 4-10 	Orrington South Interface—Percentage of Hours at the Limit	34

Table 4-11 	Change in Hours the Orrington South Interface Was at the Limit and the Congestion
Eliminated (%)	34

Table 4-12 	Surowiec South Interface—Percentage of Hours at the Limit	35

Table 4-13 	Change in Hours the Surowiec South Interface Was at the Limit and the Congestion
Eliminated (%)	35

Table 4-14 	North–South Interface—Percentage of Hours at Limit	36

Table 4-15 	Change in Hours the North–South Interface Was at the Limit and the Congestion Increase (%)	36

Table 4-18 	Production Cost at Assumed Export Limit (Millions of $)	37

Table 4-19 	Production Cost Savings due to Increased Maine Corridor Capability (Millions of $)	37

Table 4-20 	Implied Range of Capital Investments Attributable to Production Cost Savings (Millions of $)	38

Table 4-21 	LSE Energy Expense at Tested Keene Road Export Limit (Millions of $)	39

Table 4-22 	LSE Energy-Expense Reductions due to Increased Keene Road Export Limit (%)	40

Table 4-23 	LMPs for BHE ($/MWh)	41

Table 4-24 	LMPs for Southern Maine ($/MWh)	42

Table 4-25 	LMPs for ISO New England ($/MWh)	43

Table 4-26 	Total New England CO2 Emissions (ktons)	43

Table 4-27 	Change in New England CO2 Emissions as Transfer Capability Increases (ktons)	44

Table 6-1 	Wind Units by Case and Subarea (MW)	47

Nomenclature

Nomenclature used in this report

BHE		Bangor Hydro Energy (i.e., northern Maine)

CO2		carbon dioxide

CSC		Cross-Sound Cable

CSO		capacity supply obligation

CT		combustion turbine

DOE		US Department of Energy

EE		energy efficiency

FCA		Forward Capacity Auction

GWh		gigawatt-hours

HQ PII		Hydro-Québec Phase II

ISO		ISO New England

kton		kiloton

kV		kilovolt

LMP		locational marginal price

LSE 		load-serving entity

MPRP		Maine Power Reliability Project

MW		megawatt(s)

MWh		megawatt-hour

N-1		first contingency

NB		New Brunswick

NNC		Norwalk–Northport

NOX		nitrogen oxides

NREL		National Renewable Energy Laboratory (US Department of Energy)

OATT		Open Access Transmission Tariff

OP 4		Operating Procedure No. 4, Action during a Capacity Deficiency (ISO New England)

PAC 		Planning Advisory Committee

PPA		Proposed Plan Application

QP		queue position

RENEW 	RENEW Northeast, Inc., Renewable Energy New England

RI		RSP area—Rhode Island/bordering MA

RSP		Regional System Plan

RTEG		real-time emergency generation

SCED		security- constrained economic dispatch

SCUC		security-constrained unit commitment

SEMA		RSP area—Southeastern Massachusetts/Newport, Rhode Island

SEMA/RI	Southeast Massachusetts/Rhode Island

SME		southern Maine

SO2		sulfur dioxide

STA-WI		Strategic Transmission Analysis—Wind Integration Study (ISO New England)

# Executive Summary

Economic studies provide metrics depicting various possible future scenarios of expanding the New England power system and quantifying the advantages and disadvantages associated with each scenario. Typically, these scenarios assess system performance under different conditions, such as with the possible addition of imports from Canada into the New England region, resource retirements, and resource additions, but not scenarios focused on the performance of individual assets.

The key metrics include estimates of production costs, transmission congestion, electric energy costs for New England consumers, and a number of others. The results of these metrics could suggest the most economic locations for resource development and the least economic locations for resource retirements. The study also assessed the effects of the various scenarios on reducing carbon dioxide (CO2) and other emissions.

This report, the Strategic Transmission Analysis—Onshore Wind Integration (Onshore Wind Economic Study), summarizes the detailed modeling methodology, input assumptions, simulation results, and general observations of a study analyzing the economic benefits of an increase in the transmission transfer capability across the Maine corridor. Additional analysis beyond this economic study would be required to fully support any market-efficiency transmission upgrades.

This study developed economic and environmental metrics quantifying the impact of higher transmission transfer limits that increase the deliverability of wind energy from Maine to the rest of the New England system. All electric energy generated in northern Maine and imports from New Brunswick must cross a number of potentially constraining interfaces, including the Orrington South interface. Competition for limited transmission export capability across the Maine transmission corridor results in bottled-in energy (e.g., wind, hydro, and imports), which necessitates the region’s consumption of higher-cost fossil fuel resources. The results of the study showed that the relief of transmission constraints would reduce bottled-in wind energy, which would then reduce fossil fuel consumption in New England. Additionally, the inability of wind resources to produce and transmit all their available energy into the New England electricity market would inhibit the further development of wind resources in Maine.

The identification of specific transmission upgrades that would be required to obtain increased transfer capability across the Maine corridor was not part of this study.

## ISO New England 2013 Strategic Transmission Analysis—Wind Integration Study

The ISO New England 2013 Strategic Transmission Analysis—Wind Integration Study (STA-WI) was the basis for a set of increases in the interface limits used in this study. The 2013 study investigated transmission constraints in Maine affecting wind resources in northern New England. However, other transmission projects have been planned after the completion of the 2013 study, which have made the specific upgrades identified in the STA-WI unnecessary or less effective.

## Onshore Wind—2015 Economic Study

RENEW Northeast, Inc. (RENEW) submitted an economic study request to assess three scenarios representing different futures for wind development in Maine and increases in transmission system transfer limits. After discussions with the ISO and the Planning Advisory Committee,  a modified scope of work for the 2015 economic study was developed for quantifying the effects of relieving transmission constraints across the Maine corridor that reflect the interface transfer limits of the STA-WI but accounts for the transmission system upgrades differently than the 2013 study.

This analysis consists of six levels of generation and a lower and higher export capability level. One of the cases evaluated the benefits of only the existing wind resources (Case 1), five analyzed various amounts of wind resources (Cases 2, 3, 4, 5, and 6), and one investigated the impact of 1,000 MW of low-cost dispatchable energy imports from the interconnections with New Brunswick (Case 5-NB). Table 1-1 shows the megawatts (MW) of wind generation assumed for the cases studied.

Table 1-1
Total Nameplate Wind for Each Case Investigated (MW)

| Case ID | Case | North of Orrington [1] | Maine [2] | Outside Maine [3] | New England [4] [2] + [3] = [4](a) |
| --- | --- | --- | --- | --- | --- |
| 1 | Existing wind in New England (in service as of April 1, 2015) | 181 | 453 | 426 | 878 |
| 2 | RENEW Sensitivity 1 (less wind) | 181 | 623 | 426 | 1,049 |
| 3 | Proposed wind in New England with project approval (as of April 1, 2015) | 230 | 857 | 488 | 1,345 |
| 4 | RENEW base case—STA-WI-studied wind (as of October 1, 2013) | 334 | 1,149 | 426 | 1,575 |
| 5 | RENEW Sensitivity 2 (more wind) | 1,185 | 2,084 | 426 | 2,510 |
| 5-NB | RENEW Sensitivity 2 (more wind) and 1,000 MW of imports from New Brunswick, available for dispatch 24 x 7 | 1,185 | 2,084 | 426 | 2,510 |
| 6 | All future New England wind in the ISO interconnection queue (as of April 1, 2015) | 2,829 | 3,727 | 678 | 4,405 |

(a) Totals may not be exact due to rounding.

As of April 1, 2015, 181 MW of wind resources were located north of the Orrington South interface, with a total of 453 MW within Maine. Also as of this date, the amount of wind generation in the ISO’s interconnection queue totaled 2,829 MW north of Orrington South, with 3,727 MW within Maine. (Section 6.2 lists the wind units used in this study.)

To provide some estimate of the benefits of improved transfer capability, this study assumed that the interface increases would be in effect regardless of the infrastructure changes necessary to implement these increases. Table 1-2 shows the transmission limits modeled in this study.

Table 1-2
Assumed Improvements in the Maine Corridor Interface Ratings

| ME Interface Export Limit | Pre-Upgrade Cases (MW) | Post-Upgrade Cases (MW) | Assumed Increase (MW) |
| --- | --- | --- | --- |
| Keene Road, Wyman, Rumford | Unconstrained | Unconstrained | Unconstrained |
| Orrington South | 1,325 | 1,650 | 325 |
| Surowiec South | 1,500 | 2,100 | 600 |
| Maine–New Hampshire | 1,900 | 2,300 | 400 |

## Production Cost

For wind installations across Maine totaling between 453 MW and 1,149 MW, production cost savings resulting from increasing the interface capability across the Maine corridor would range from no savings to $5 million annually. The Orrington South interface became more constrained as more wind resources were added north of Orrington.

With 2,084 MW to 3,727 MW of total wind in Maine, the production cost savings from increasing the Maine interface transfer limits ranged from $31 million to $75 million annually. The Orrington South interface was the major constraint because 1,185 MW and 2,829 MW of wind resources were located north of Orrington South in these higher-penetration cases. The Orrington South transfer limits affected the ability to transport economically dispatched resources (including New Brunswick imports) to customers located south of Orrington. The results also showed that when the Maine corridor was relieved and higher levels of energy flowed into southern New England from the north, the North–South interface became increasingly constrained.

## Load-Serving Entity Energy Expenses

The metric for New England load-serving entity (LSE) energy expenses showed a range of reductions comparable in magnitude to the production cost savings. For wind installations across Maine totaling between 453 MW and 1,149 MW, the LSE energy expense decreased between $0.5 million to $2.1 million annually due to increasing the throughput across the Maine corridor interfaces. With 2,084 MW to 3,727 MW of total wind in Maine, the decrease in LSE energy expenses were $38.8 million to $76.1 million annually. Dispatchable imports of up to 1,000 MW from New Brunswick resulted in a reduction in LSE energy expenses of $79.6 million annually.

## Environmental Metrics

The environmental metric for this study was carbon dioxide emissions. For wind installations across Maine from 453 MW to 1,149 MW, CO2 emissions resulting from increasing Maine corridor interfaces ranged from a decrease of 2.6 kilotons (ktons) annually to an increase of 7.3 ktons. The increase in CO2 emissions was the result of changes in unit commitment after the Maine interface limits were increased. With 2,084 MW to 3,727 MW of total wind generation in Maine and improved Maine corridor throughput, the decrease in CO2 emissions ranged from 215.8 ktons to 701.4 ktons annually. Higher levels of New Brunswick imports resulted in CO2 emission reductions of 617.5 ktons annually.

# Introduction

As a part of the regional system planning effort, ISO New England (ISO) conducts economic planning studies each year, as specified in Attachment K of its Open-Access Transmission Tariff (OATT). The economic studies provide information on system performance, such as estimated production costs, load-serving entity (LSE) energy expenses, transmission congestion, and environmental emission levels. The ISO annually performs studies requested by participants that analyze various future scenarios. This information can assist stakeholders in evaluating various resource and transmission options that can affect New England’s wholesale electricity markets. The studies may also assist policymakers who formulate strategic visions of the future New England power system.

This report, Strategic Transmission Analysis—Onshore Wind Integration, presents the results of one of the three 2015 ISO New England economic studies conducted in response to requests submitted by stakeholders participating in the Planning Advisory Committee (PAC). The report documents the study methodologies, data and assumptions, simulation results, and observations of an economic study of the impacts of improving the transmission capability across the Maine transmission corridor.

## Economic Study Process

Attachment K of the ISO’s OATT states that the ISO must conduct economic studies arising from one or more stakeholder requests submitted by April 1 of each year through the PAC. These may be requests to study the general locations for the expansion of various types of resources, resource retirements, and possible changes to transmission interface limits. By May 1 of each year, the proponents of these studies are provided an opportunity to present the PAC with the reasons for the suggested studies. The ISO discusses the draft scope(s) of work with the PAC by June 1 and reviews the study assumptions with the PAC at later meetings. The role of the PAC in the economic study process is to discuss, identify, and prioritize proposed studies. The ISO then performs up to three economic studies and subsequently reviews all results and findings with the PAC.

In fulfillment of this obligation, ISO staff presented the Strategic Transmission Analysis—Onshore Wind Integration scope of work, assumptions, draft results, and final results to the PAC. The study does not include detailed transmission analysis that would be required to fully develop generator interconnection upgrades, elective transmission upgrades, or market-efficiency transmission upgrades. The results, however, may be used to determine the need for future analyses.

## Economic Study Request for the Maine Area Transmission Improvements and the 2015 Study Scope of Work

RENEW Northeast, Inc. (RENEW) submitted an economic study request to assess three scenarios representing slightly different futures for wind development and postulated increases in transmission system transfer limits. The higher transfer limits were based on results of ISO New England’s Strategic Transmission Analysis—Wind Integration Study (STA-WI). After the completion of the 2013 STA-WI study, transmission projects have been planned and built that have made the specific enhancements identified in the STA-WI unnecessary or less effective. Thus, the ISO proposed a modified scope of work for the 2015 economic study that quantifies the effects of relieving transmission constraints across the Maine corridor, reflecting the interface transfer limits of the STA-WI, but accounts for the transmission system upgrades differently than the 2013 study.

This economic study report provides high-level estimates for the amount of investment in transmission upgrades that might be justified but without identifying specific transmission projects. This metric allows the economic benefits of increased transfer levels to be weighed against the possible costs of improvements. Other benefits of allowing the additional production of relatively inexpensive resources in northern Maine, including wind resources and hydroelectric generation, were quantified and described using various economic and environmental metrics. The results of this study inform the region about the possible benefits of transmission upgrades and the potential need for further study.

The economic study request proposed simulating a single representative year or a set of a 10 sequential years, with the study ultimately using a single year, 2021, as a proxy for all the other years. With the assumptions of low load growth, relatively constant fuel prices, and constant resources after the 2018/2019 Forward Capacity Auction #9 (FCA #9) capacity commitment period, the annual results were reasonably expected to be relatively stable from year to year and the simulation results for 2021 would be representative for the other future years.

## The Maine Study Area and Assumed Interface Transfer Capability

The Maine study area is characterized by a backbone system consisting of 345 kilovolt (kV) circuits that transmit power between New Brunswick and New Hampshire. Within Maine, electric energy is brought to, or delivered from, this backbone by a network of 115 kV lines. The backbone transmission system is limited at certain interfaces due to voltage, stability, and to a lesser extent, thermal issues. Figure 2-1 shows major interfaces within Maine. The study assumed the completion of the Maine Power Reliability Project (MPRP) and other transmission improvements as of May 18, 2015.

Figure 2-1: Interfaces evaluated in northern Maine.

The 2015 economic study assumes two levels of interface transfer capability. The “pre-upgrade” interface values were based on the limits associated with the completion of the MPRP. The “post-upgrade” interface values are higher transfer limits simulated to reflect increases in the Maine interface transfer limits. The Orrington South interface was increased by 325 MW, from the pre-upgrade limit of 1,325 MW to a post-upgrade limit of 1,650 MW. The study assumed that the pre-upgrade interface ratings for Surowiec South were increased by 500 MW, from 1,600 MW to 2,100 MW. The pre-upgrade, interface ratings for the Maine–New Hampshire interface were assumed to increase from 1,900 MW to 2,300 MW. Table 2-1 shows the assumed interface ratings for the Maine corridor.

Table 2-1
Assumed Maine Corridor Interface Ratings (MW)

| ME Interface Export Limit | Pre-Upgrade Cases | Post-Upgrade Cases | Assumed Increase |
| --- | --- | --- | --- |
| Keene Road, Wyman, Rumford | Unconstrained | Unconstrained | Unconstrained |
| Orrington South | 1,325 | 1,650 | 325 |
| Surowiec South | 1,500 | 2,100 | 600 |
| Maine–New Hampshire | 1,900 | 2,300 | 400 |

## Scenarios

This study assessed seven scenarios (named “cases” in this report) representing six levels of wind generation based on the status of projects in the ISO New England generator interconnection queue (the queue) and approval process, called the “I.3.9” process and an additional case that increased imports from New Brunswick. One of the cases evaluated the benefits of only the existing wind resources, five analyzed various amounts of wind resources, and one investigated the impact of 1,000 MW of low-cost dispatchable energy imports from the interconnections with New Brunswick.

Each case used the same resource assumptions and evaluated the system with the pre- and post-upgrade export capability across the Maine corridor. The pre-upgrade transfer limits were used as a reference. For each case, the results for the system with these lower transfer capability levels were compared with the post-upgrade transfer capability values. Thus, this study assessed 14 cases: two export capability levels for six levels of wind generation plus one for imports.

### RENEW-Requested Scenarios

The RENEW base case (Case 4) included all wind plants in the ISO interconnection queue with approved Proposed Plan Applications (PPAs) as of October 1, 2013. The specific cases requested by RENEW were based on the amounts of wind in service and in the queue as of April 1, 2015, or in the queue as of October 1, 2013 These wind resources in Maine were located in the following areas:

- Downeast

- Keene Road

- North of Orrington

- Wyman Hydro

- Rumford

Figure 2-2 shows the resources included in the RENEW base case. The simulations performed with this base case were compared with simulations from a case that reflected the post-upgrade transfer limits.

Figure 2-2: RENEW base case—STA-WI-studied wind generation, as of October 1, 2013.

The study considered two sensitivities around the RENEW base case. Sensitivity 1 includes less wind generation (Less Wind, Case 2), and Sensitivity 2 includes more wind generation (More Wind, Case 5) and a case with more wind plus 1,000 MW of imports  from New Brunswick (Case 5-NB).

Figure 2-3 shows the resources assumed for the Less Wind case and includes only operating wind resources plus those under construction as of April 1, 2015. Resources neither operational nor under construction are shown in green and were excluded from this sensitivity. The resources excluded from the reference case, totaling 526 MW, are as follows:

- QP407

- QP350-2

- QP333

- Pisgah

- QP350-1

- QP 397

- Q357

- Q327

Figure 2-3: RENEW Sensitivity 1—Less Wind.

Note: Green dots signify removed resources.

The resources for Case 5 include all the wind generation from the Renew base case plus the following representative selection of large wind projects in the queue in Maine: QP393, QP417, and QP470. This criterion adds 935 MW of wind resources to the Renew base case.

Case 5-NB assumed the same added 935 MW as Case 5 plus 1,000 MW of New Brunswick imports dispatchable in all hours. This sensitivity (Sensitivity 2) investigated the impacts on the study metrics resulting from higher interface flows along the Maine transmission corridor.

Figure 2-4 shows the resources in the two More Wind cases. The large wind projects are shown with purple dots in the figure.

Figure 2-4: RENEW Sensitivity 2—More Wind.

Note: Purple dots signify additional resources.

### Cases based on the Interconnection Queue

In addition to the RENEW base case and Less Wind and More Wind sensitivities, the scenarios include the three levels of wind studied in the 2015 Keene Road economic study. These sensitivities were based on the interconnection status of wind resources in the New England as of April 1, 2015, plus imports from New Brunswick (see Section 2.4.3).

The first queue-based sensitivity (Case 1) included all the existing wind resources operational as of April 1, 2015. The second queue-based sensitivity (Case 3) included all wind resources in the ISO interconnection queue with approved Proposed Plan Applications under Section I.3.9 of the ISO New England tariff as of April 1, 2015. The third queue-based sensitivity (Case 6) included all wind resources in the ISO interconnection queue as of April 1, 2015.

The existing amount of wind capacity in Maine as of April 1, 2015, was 453 MW, with another 170 MW of wind with a PPA, and an additional 234 MW under construction. Another 2,870 MW of wind resources were in the queue, for a total of 3,727 MW of wind resources in Maine.

### Summary of the Scenarios

A summary of the cases is as follows:

- Case 1—Existing Wind in New England (in service as of April 1, 2015): This case assumes only the amount of wind resources installed as of April 1, 2015. The total amount of wind in New England for this case is 878 MW, with 453 MW in Maine.

- Case 2—RENEW Sensitivity 1 (Less Wind): This sensitivity reflects only wind units in service as of April 1, 2015. This case excludes 522 MW from the STA-WI base case wind resources neither operational nor under construction as of April 1, 2015. The resources removed were QP407, QP350-2, QP333, Pisgah, QP350-1, QP 397, Q357, and Q327. The total amount of wind in New England for Case 2 is 1,049 MW, with 623 MW in Maine.

- Case 3—Proposed Wind in New England with I.3.9 Approval (as of April 1, 2015): This case assumes that the resources included in this study were in the ISO interconnection queue and had approved Proposed Plan Applications as of April 1, 2015. The total amount of wind in New England for this case is 1,345 MW, with 857 MW in Maine.

- Case 4—RENEW Base Case—STA-WI-Studied Wind (as of October 1, 2013): This case assumes that the resources included in this study were in the ISO interconnection queue and had approved PPAs as of April 1, 2013. The total amount of wind in New England for Case 4 is 1,575 MW, with 1,149 MW in Maine.

- Case 5—RENEW Sensitivity 2 (More Wind): This case assumes that the resources in the STA-WI study  were in service, plus the QP393, QP417, QP470 resources (totaling 935 MW) representative of large wind projects in the queue in Maine not included in the STA-WI. For this case, the total amount of wind in New England is 2,510 MW with 2,084 MW in Maine.

- Case 5-NB—RENEW Sensitivity 2 (More Wind) and 1,000 MW of NB Imports: This sensitivity is the same as Case 5 but with 1,000 MW of imported electric energy from New Brunswick available for dispatch 24 x 7.

- Case 6—All Future Queue Wind in New England (as of April 1, 2015): This case assumes that the resources included in this study were in the queue as of April 1, 2015. The total amount of wind in New England for Case 6 is 4,405 MW, with 3,727 MW in Maine.

Table 2-2 summarizes the geographic attributes of the wind resources in the cases investigated.

Table 2-2
Total Nameplate Wind for the Cases Investigated (MW)

| Case ID | Case | North of Orrington [1] | Maine [2] | Outside Maine [3] | New England [4] [2] + [3] = [4](a) |
| --- | --- | --- | --- | --- | --- |
| 1 | Existing wind in New England (in service as of April 1, 2015) | 181 | 453 | 426 | 878 |
| 2 | RENEW Sensitivity 1 (less wind) | 181 | 623 | 426 | 1,049 |
| 3 | Proposed wind in New England with I.3.9 approval (as of April 1, 2015) | 230 | 857 | 488 | 1,345 |
| 4 | RENEW base case—STA-WI-studied wind (as of October 1, 2013) | 334 | 1,149 | 426 | 1,575 |
| 5 | RENEW Sensitivity 2 (more wind) | 1,185 | 2,084 | 426 | 2,510 |
| 5-NB | RENEW Sensitivity 2 (more wind) and 1,000 MW of imports from New Brunswick, available for dispatch 24 x 7 | 1,185 | 2,084 | 426 | 2,510 |
| 6 | All future queue wind in New England (as of April 1, 2015) | 2,829 | 3,727 | 678 | 4,405 |

(a) Totals may not be exact due to rounding.

Section 6.2 shows the wind units used in this study by case and subarea.

# Data and Assumptions

This study used detailed resource modeling. The representation of thermal unit heat-rate curves allowed for deciding unit-commitment tradeoffs and determining the marginal cost of energy at each location. The representation of the transmission system was sufficiently detailed for modeling major transmission constraints. The loads and resources contained in the 2015 CELT Report provided the basis for this study. This section describes the data, assumptions, and modeling inputs used.

## Load Forecasts

The New England gross load forecast was based on the demand data for 2015 to 2024, as presented in the 2015 CELT Report. The gross summer peak load was 30,900 MW in 2021. The hourly profile was based on the historical 2006 hourly load profile, which reflected a 2006 weather pattern. The hourly profile for 2006 was used as the basis for representing the New England loads because of the availability of correlated, time-stamped estimated profiles for wind and photovoltaic resources.

## Resources

Future additions and retirements to the resource mix reflected the 2015 CELT Report, including the results of FCA #9. The supply-side resource interconnection points were based on the 2015 NERC TPL001-4 Compliance Study case for summer 2021 with a total capacity of 33,415 MW.

The major capacity additions included the 204 MW Medway gas turbine unit added in the Southeast Massachusetts (SEMA) regional system planning area and the 670 MW Towantic combined-cycle unit added in southwestern Connecticut. The major retirement was Vermont Yankee, with a capacity of 650 MW. Across New England, existing wind totaled 878 MW, 467 MW had an approved PPA, and another 3,072 MW were in the queue.

### Detailed Modeling of Thermal Unit Heat-Rate Curves

The resource model for thermal resources included generating unit operational constraints, such as start-up costs, no-load costs, and incremental heat-rate curves. The model also reflected operating limits, including minimum up time, minimum down time, and start-up time. This detailed modeling allowed for an accurate determination of the marginal costs of supplying energy.

### Resource Availability

The simulations modeled planned and forced outages of generating units. The simulations accounted for planned maintenance periods by removing generating resources from service. To reflect the reduction in available energy due to forced outages, the maximum capacity of a resource was multiplied by an equivalent availability factor. Derating capacity to represent forced outages is a simplification of a more rigorous approach that would have required the simulation of multiple Monte Carlo cases and combining the results to represent impacts when specific units were unavailable due to forced outages. A Monte-Carlo-based simulation would have more volatility in specific hours. However, past studies have demonstrated that because the simulation results are a summation of 8,760 hours, the effect of using a Monte-Carlo-based outage schedule would not have a significant impact on the annual metrics.

### Fuel Prices

The fuel-price assumptions were based on the US Department of Energy’s (DOE’s) 2015 Annual Energy Outlook. Figure 3-1 shows the EIA forecast from 2015 to 2030.

Figure 3-1: Fuel-price assumptions based on EIA’s 2015 Annual Energy Outlook, updated December 21, 2015 ($/MWh).

Fuel prices were assumed constant across all months in the year studied with the exception of natural gas prices. Natural gas prices were assumed to vary monthly to reflect the seasonal trends resulting from shifts in supply and demand. Historical trends have shown that prices are higher for natural gas during the high heating, winter months and lower during the nonheating seasons. Figure 3-2 shows the assumed monthly natural gas price multiplier.

Figure 3-2: Assumed monthly variation in the natural gas prices for New England, 2021.

### Profiles for Energy Efficiency, Active Demand Resources, and Real-Time Emergency Generation

Energy efficiency (EE), active demand resources, and real-time emergency generation (RTEG) were modeled by developing a profile for each of the three components. These profiles underscore the ISO’s expectation that active demand resources and RTEGs will be activated when needed and must be ready to respond. The demand resources modeled in New England were based on the 2018/2019 capacity supply obligations (CSOs) plus an additional 695 MW of forecast EE that can be relied on to be implemented by 2021 as shown in Table 3-1.

Table 3-1
Amount and Type of Demand Resources in New England, 2021 (MW)

| Resource Type | FCA #9/Forecast Megawatts | Modeled Megawatts |
| --- | --- | --- |
| FCA #9 energy efficiency (seasonal and on peak) | 2,305 |  |
| Forecast additional energy efficiency (2019–2021) | 695 |  |
| Total energy efficiency |  | 3,000 |
| FCA #9 real-time demand resources |  | 523 |
| FCA #9 real-time emergency generation (activated in OP 4, Action 6)(a) |  | 143 |

(a) Operating Procedure No. 4 (OP 4) actions include allowing the depletion of the 30-minute reserves and the partial depletion of 10-minute reserves (1,000 MW), scheduling market participants’ submitted emergency transactions and arranging emergency purchases between balancing authority areas (1,600 to 2,000 MW), and implementing 5% voltage reductions (400 to 450 MW). Operating Procedure No. 4, Action during a Capacity Deficiency (June 24, 2015), http://www.iso-ne.com/static-assets/documents/rules_proceds/operating/isone/op4/op4_rto_final.pdf.

Figure 3-3 presents the combined hourly profiles of EE, active demand resources, and RTEG used to modify the hourly load. These demand resources are distributed to the RSP areas based on their FCA #9 capacity obligations. For modeling purposes, the profile mimics distributed resources by adjusting the hourly loads in RSP areas. The remaining load after these adjustments is the energy that generating resources or imports served.

Figure 3-3: Profile representing passive demand resources, active demand resources, and real-time emergency generation, 2021 (MW).

### Photovoltaic Resources

The PV profile was developed from data from the US DOE’s National Renewable Energy Laboratory’s (NREL) for the Eastern Renewable Generation Integration Study. The NREL solar dataset was developed to represent a large amount of solar capacity that does not currently exist for studying the effects of the large-scale deployment of solar. These profiles were used to represent the forecasted PV fleet, which includes all forms of PV, such as FCM resources, energy-only resources, and load-reducing resources. The profiles were based on 2006 historical weather. The peak load reduction was 413 MW in 2021.

Figure 3-4 shows the aggregate profile for all the PV resources modeled in New England.

Figure 3-4: New England aggregate photovoltaic profile, 2021 (MW).

### Wind Resources

Wind resources modeled include FCA #9 resources. Additionally, some energy-only wind resources did not have a CSO. Therefore, the total existing wind capacity was assumed to be 878 MW (installed nameplate capacity) across New England.

Hourly wind profiles were based on data produced by NREL and updated in 2012 to reflect improvements in wind turbine efficiencies.

Figure 3-5 presents an aggregate wind profile for all the wind units modeled in New England using 2006 synthetic wind estimates to create a chronological profile. Individual resources were assigned a profile based on the nearest NREL synthetic data site.

Figure 3-5: New England aggregate wind profile, 2006 (MW).

### Hydroelectric Resources

Hydroelectric resources in New England were assumed to have monthly energy profiles based on historical generation. This monthly energy was then converted to an hourly profile assuming that while some amount of hydro would be produced in every hour, the hydro generation would tend to generate more when the loads were highest and generate less when loads were lower. This methodology was used in all areas of New England. The modeling of the hydro resources behind the Keene Road export interface was similar and based on the assumed hydro energy available. Figure 3-6 shows New England’s assumed aggregate hydro profile.

Figure 3-6: New England aggregate hydro profile (MW).

## Environmental Emission Allowances

Emissions from thermal units were based on the energy generated by each unit and its associated emission rates. Emission rates, developed in support of the 2014 ISO New England Electric Generator Air Emissions Report, were used. The energy imported from New Brunswick, New York, and Québec were assumed to have zero emissions.

The value of emission allowances were based on the following assumptions:

  - Carbon dioxide (CO2)—$20/short ton

  - Sulfur dioxide (SO2)—$6/short ton

  - Nitrogen oxides (NOX)—$5/short ton

In the simulations, the CO2 allowance values were the most significant. The emission rates for SO2 and NOX were much smaller than the CO2 emission rate, and coupled with the lower dollar-per-ton allowance values for the SO2 and NOX allowances, the impacts of these emissions would be negligible.

## Imports and Exports

One of the key assumptions was New England’s import/export interchange flows with New York, Québec, and New Brunswick (the Maritimes).

Figure 3-7 shows the external areas along the periphery of the New England footprint. To represent energy flows between these external areas and New England, typical diurnal profiles were developed from historical flows. This approach captured the characteristics observed within recent historical data and represented the interchange by month throughout the year. An alternative to using daily diurnal curves would use a single 8,760-hour profile from a specific year as representative of future flows. However, such a historical profile would contain event-specific anomalies that may not be appropriate to include in a planning study.

Figure 3-7: New England’s external interfaces.

Note: “HQ PII” refers to Hydro-Québec Phase II.

For this analysis, data for 2012, 2013, and 2014 were used to develop the twelve monthly 24-hour diurnal profiles of the study year. The 24-hour profile for each month was developed by using the three-year historical average of flows from the interchange profile for each hour of the day of interest. Because each month has about 30 days, and the study used three historical years of data, each hour of the profile represented the average of approximately 90 historical values.

The diurnal flows across these external interfaces are presented in Figure 3-8 to Figure 3-13. These graphs show the profiles for each of the three years with the three-year average shown as a thick blue line.

### Québec

Figure 3-8 shows the flows across Hydro-Québec Phase II (HQ PII) into Sandy Pond, and Figure 3-9  shows the flows across the Highgate interconnection.

Figure 3-8: Average diurnal flows by month, representing net energy injections into New England from Québec at HQ Phase II, 2012 to 2014 (MW).

Figure 3-9: Average diurnal flows by month, representing net energy injections into New England from Québec at Highgate, 2012 to 2014 (MW).

### Maritimes

Instead of a three year average, the New Brunswick imports, shown in Figure 3-10, were based on the maximum daily diurnal profiles for 2013 and 2014, by month, to reflect the return of the Point Lepreau nuclear generating station in 2013. Because of the potential development of hydro resources in Labrador that could be available to the northeast, a sensitivity case was developed that assumed the 1,000 MW of New Brunswick imports were dispatchable in all hours. This sensitivity was associated with the higher level of wind to investigate the impacts on the study metrics due to higher interface flows along the Maine transmission corridor.

Figure 3-10: Average diurnal flows by month, representing net energy injections into New England via the New Brunswick ties (MW).

### New York

Figure 3-11 through Figure 3-13 show the interchange profiles between New England and New York for each of the years and an average for all three years. Figure 3-11 shows the flows over the interconnection between New York and New England into the Hudson Valley region (Roseton). Figure 3-12 shows the flows over the AC cable between Norwalk and Northport (NNC) on Long Island. Figure 3-13 shows the flows across the DC Cross-Sound Cable (CSC) between New Haven and Shoreham on Long Island.

Figure 3-11: Average diurnal flows by month, representing net energy injections into New England at the NY AC tie, 2012 to 2014 (MW).

Figure 3-12: Average diurnal flows by month, representing net energy injections into New England across the Norwalk to Northport cable, 2012 to 2014 (MW).

Figure 3-13: Average diurnal flows by month, representing net energy injections into New England at Cross-Sound Cable, 2012 to 2014 (MW).

## Transmission System Network

The detailed ISO New England transmission network was based on a 2021 summer steady-state base case in ISO’s NERC TPL-001-4 Compliance Study. The case reflects transmission improvements listed in the RSP Project List as of May 18, 2015, including the Maine Power Reliability Program. Transmission lines operated at 230 kV and above were monitored to ensure that flows remained within their thermal limits.

### Representing Loads

To allocate loads to the busses across the New England network, distribution factors developed by transmission owners for a 10-year forecast period were used.

### Transmission Interfaces

Major transmission interface limits between load and generation areas were modeled consistent with transmission improvements expected to be in service by 2021. These interface limits can act to restrict flows on the paths shown in Table 3-2. Interface limits are the only mechanism available in GridView (see below) to represent voltage and stability limits in the simulations. The only significant local transmission constraints considered in this study were the 140 MW northern New Hampshire/Vermont export limits.

Table 3-2
Internal New England Interface Limits, 2021 (MW)

| Interface(a) | 2021 Limit (MW) |
| --- | --- |
| Orrington South Export | 1,325 |
| Surowiec South | 1,500 |
| Maine–New Hampshire | 1,900 |
| North–South(b) | 2,675 |
| East–West | 3,500 |
| West–East | 2,200 |
| Boston Import (N-1)(c) | 5,700 |
| SEMA/RI Import (N-1)(c) | 1,280 |
| Connecticut Import (N-1)(c) | 2,950 |
| SW Connecticut Import (N-1)(c) | 3,200 |

(a) The transmission interface limits are single-value, summer peak (except where noted to be winter), for use in subarea transportation models. The limits may not include possible simultaneous impacts and should not be considered as “firm.”

(b) The North–South transfer capability reflects the retirements of Brayton Point and Vermont Yankee.

(c) N-1 refers to a first contingency—the loss of the power element (facility) with the largest impact on system reliability.

### Contingency Modeling

Stability and voltage constraints are modeled on major interfaces that were potentially constraining. Normal transmission limits on lines rated at 230 kV and above were respected in all simulations. In addition, approximately 100 contingencies were modeled to identify potential post contingency thermal constraints on the transmission system that could limit power flows in the network.

## Production Cost Simulation Model

The GridView software application, developed by ABB Inc., simulates the economic dispatch of an electric power system, which includes transmission system constraints. The ISO uses GridView to help analyze the planning of transmission and generation assets, estimate production cost simulation trends, identify transmission system bottlenecks, and evaluate the economic impacts of changes in the configuration of the system. GridView is designed to simulate changes in transmission system expansion and the addition and retirement of supply and demand resources and to quantify metrics associated with sensitivity to changes in assumptions, such as fuel prices and available resources.

For this study, GridView was used to simulate the economic operation of a power system in hourly intervals for periods ranging from one day to many years. To perform these simulations, GridView incorporated a detailed supply, demand, and transmission system model for large-scale transmission grid representation. The program simulated security-constrained unit commitment (SCUC) and security-constrained economic dispatch (SCED) that mimicked the operation of the ISO’s system. The simulation was run chronologically to capture the intertemporal constraints by producing a realistic forecast of the power system components and energy flow patterns across the transmission grid for a given set of assumptions.

The GridView output information includes transmission and generator utilization, locational marginal prices (LMPs) for energy and transmission bottleneck metrics. The results also included an assessment of system security under contingency conditions. Costs for certain ancillary services, such as operating reserve, were modeled.

# Simulation Results

This section presents the simulation results for each of the scenarios investigated. The goal of this study was to quantify how the relaxation of the interface constraints across the Maine corridor would affect various economic study metrics. The metrics included the ISO’s regionwide electric energy production cost, LSE energy expense, and emissions under various combinations of wind resources and transfer capability.

The metrics reflect a New England system where installed wind resources increased the total available installed capacity. Holding a constant amount of capacity needed to support a specific reliability criterion was not attempted. The addition of the wind resources, however, influenced the energy produced by various fuel types and resources.

Note that the results presented in this report may not be exact due to rounding.

## Simulation Metric Background

The goal of a production cost model is to minimize the total cost of energy produced over a specified period, which includes the variable unit cost of producing electrical energy and the unit-commitment costs for startup and shutdown. For example, to minimize total production costs, GridView may select a resource with a higher marginal production cost but with a lower start-up cost. In this simulation interval, the production cost can decrease while the marginal price may be slightly higher. The expected trend would be that with more wind, both production costs and LMPs would decrease. However both metrics may not decrease when changes affecting unit commitment are small, such as when additional electric energy is available after an interface is relaxed.

## Energy Bottled-In Maine

One of the primary metrics associated with a study of an export-constrained area is the amount of bottled-in energy—energy that cannot be produced and exported because of transmission constraints. The bottled-in energy metric is important in explaining results developed during this study.

### Wind Energy

Wind was assumed to have the lowest dispatch price and has the ability to displace all other higher-priced resources. Table 4-1 shows the amount of electric energy in the input wind energy profiles and the energy produced by the wind resources within Maine for the 14 cases investigated. The input wind energy profiles define the maximum amount of wind energy a resource could produce if unconstrained and able to produce energy when available. In most cases, the amount of wind energy produced is approximately equal to the profile, suggesting that wind energy is generated to serve load whenever the wind blows. Table 4-2 shows the differences in wind energy produced compared with the input profiles, while Table 4-3 shows the difference between the pre-upgrade transfer limits and the post-upgrade transfer limit cases.

Table 4-1
Wind Energy within Maine (GWh)

| Case ID | Case | Input Wind Energy Profile | Pre | Post |
| --- | --- | --- | --- | --- |
| 1 | Existing wind in New England (in service as of April 1, 2015) | 1,468 | 1,454 | 1,454 |
| 2 | RENEW Sensitivity 1 (less wind) | 2,040 | 2,025 | 2,025 |
| 3 | Proposed wind in New England with I.3.9 approval (as of April 1, 2015) | 2,808 | 2,793 | 2,793 |
| 4 | RENEW base case—STA-WI-studied wind (as of October 1, 2013) | 3,726 | 3,634 | 3,635 |
| 5 | RENEW Sensitivity 2 (more wind) | 6,712 | 6,615 | 6,620 |
| 5-NB | RENEW Sensitivity 2 (more wind) and 1,000 MW of imports from New Brunswick, available for dispatch 24 x 7 | 6,712 | 6,620 | 6,623 |
| 6 | All future queue wind in New England (as of April 1, 2015) | 11,699 | 10,058 | 10,758 |

Table 4-2
Bottled-In Wind Energy within Maine with the Profile as Reference (GWh)

| Case ID | Case | Input Wind Energy Profile | Pre | Post |
| --- | --- | --- | --- | --- |
| 1 | Existing wind in New England (in service as of April 1, 2015) | Reference | 14 | 14 |
| 2 | RENEW Sensitivity 1 (less wind) | Reference | 14 | 14 |
| 3 | Proposed wind in New England with I.3.9 approval (as of April 1, 2015) | Reference | 15 | 15 |
| 4 | RENEW base case—STA-WI-studied wind (as of October 1, 2013) | Reference | 92 | 91 |
| 5 | RENEW Sensitivity 2 (more wind) | Reference | 97 | 92 |
| 5-NB | RENEW Sensitivity 2 (more wind) and 1,000 MW of imports from New Brunswick, available for dispatch 24 x 7 | Reference | 92 | 89 |
| 6 | All future queue wind in New England (as of April 1, 2015) | Reference | 1,641 | 941 |

Table 4-3
Change in the in Wind Energy Output Due to Higher Transfer Limits (GWh)

| Case ID | Case | Change in Energy Output(a) |
| --- | --- | --- |
| 1 | Existing wind in New England (in service as of April 1, 2015) | 0 |
| 2 | RENEW Sensitivity 1 (less wind) | 0 |
| 3 | Proposed wind in New England with I.3.9 approval (as of April 1, 2015) | 0 |
| 4 | RENEW base case—STA-WI-studied wind (as of October 1, 2013) | 1 |
| 5 | RENEW Sensitivity 2 (more wind) | 5 |
| 5-NB | RENEW Sensitivity 2 (more wind) and 1,000 MW of imports from New Brunswick, available for dispatch 24 x 7 | 2 |
| 6 | All future queue wind in New England (as of April 1, 2015) | 700 |

(a) The amounts shown equal the wind energy output for the post-upgrade transfer limits minus the wind energy output for the pre-upgrade transfer limits. Positive numbers indicate greater output and less bottled-in wind generation. The results shown might not be exact due to rounding.

Table 4-3 shows that only Case 6, accounting for all future wind in the New England queue, exhibits any significant change in bottled-in wind energy as a result of increasing transfer limits across the Maine corridor. Because transmission lines in the network model have thermal limits on how much power they can carry, local limits may prevent some wind resources from producing all their energy possible on the basis of their profiles of available energy. For example, Case 1 has 14 GWh of bottled-in energy, and this is unaffected by the limits across the Maine corridor.

Table 4-3 also shows that improved throughput across the transmission corridor does not reduce the amount of bottled-in wind, except for Case 6. In this case, increasing the transfer capability across the Maine corridor reduces the 1,641 GWh of bottled-in energy present before the assumed post-upgrade interface transfer capabilities by 700 GWh.

### Hydroelectric Energy

The amount of bottled-in hydro energy can change significantly because of the threshold price at which wind, hydro, and imports are assumed to self-curtail. On the basis of the assumed threshold prices, wind resources, which have lower threshold prices and therefore a higher priority, can displace hydro resources. Table 4-4 shows the amount of energy in the input hydro profiles and the energy produced by the hydro resources within Maine for the cases investigated. Table 4-5 shows the differences in energy production compared with the input profiles.

Table 4-4
Hydro Energy within Maine (GWh)

| Case ID | Case | Input Hydro Energy Profile | Pre | Post |
| --- | --- | --- | --- | --- |
| 1 | Existing wind in New England (in service as of April 1, 2015) | 2,071 | 2,071 | 2,071 |
| 2 | RENEW Sensitivity 1 (less wind) | 2,071 | 2,071 | 2,071 |
| 3 | Proposed wind in New England with I.3.9 approval (as of April 1, 2015) | 2,071 | 2,071 | 2,071 |
| 4 | RENEW base case—STA-WI-studied wind (as of October 1, 2013) | 2,071 | 2,071 | 2,071 |
| 5 | RENEW Sensitivity 2 (more wind) | 2,071 | 2,054 | 2,059 |
| 5-NB | RENEW Sensitivity 2 (more wind) and 1,000 MW of imports from New Brunswick, available for dispatch 24 x 7 | 2,071 | 2,058 | 2,059 |
| 6 | All future queue wind in New England (as of April 1, 2015) | 2,071 | 1,709 | 1,801 |

Table 4-5
Bottled-In Hydro Energy within Maine with Profile as Reference (GWh)

| Case ID | Case | Input Hydro Energy Profile | Pre | Post |
| --- | --- | --- | --- | --- |
| 1 | Existing wind in New England (in service as of April 1, 2015) | Reference | 0 | 0 |
| 2 | RENEW Sensitivity 1 (less wind) | Reference | 0 | 0 |
| 3 | Proposed wind in New England with I.3.9 approval (as of April 1, 2015) | Reference | 0 | 0 |
| 4 | RENEW base case—STA-WI-studied wind (as of October 1, 2013) | Reference | 0 | 0 |
| 5 | RENEW Sensitivity 2 (more wind) | Reference | 17 | 12 |
| 5-NB | RENEW Sensitivity 2 (more wind) and 1,000 MW of imports from New Brunswick, available for dispatch 24 x 7 | Reference | 13 | 12 |
| 6 | All future queue wind in New England (as of April 1, 2015) | Reference | 362 | 270 |

These results show that Case 6 was the only case with any significant amount of bottled-in hydro energy. The results for Case 6 were not unexpected because this case has 2,829 MW of wind, which was a significant increase from the 181 MW of existing wind in the area north of the Orrington South interface.

Table 4-6 shows the difference between the bottled-in hydro energy with the pre-upgrade interface rating and the post-upgrade interface rating. The higher post-upgrade interface rating resulted in 92 GWh less energy being bottled in. The bottled-in energy in Case 5 and 5-NB was reduced when the interfaces along the Maine corridor was upgraded.

Table 4-6
Change in Hydro Energy Output Due to Higher Transfer Limits (GWh)

| Case ID | Case | Change in Energy Output(a) |
| --- | --- | --- |
| 1 | Existing wind in New England (in service as of April 1, 2015) | 0 |
| 2 | RENEW Sensitivity 1 (less wind) | 0 |
| 3 | Proposed wind in New England with I.3.9 approval (as of April 1, 2015) | 0 |
| 4 | RENEW base case—STA-WI-studied wind (as of October 1, 2013) | 0 |
| 5 | RENEW Sensitivity 2 (more wind) | 5 |
| 5-NB | RENEW Sensitivity 2 (more wind) and 1,000 MW of imports from New Brunswick, available for dispatch 24 x 7 | 1 |
| 6 | All future queue wind in New England (as of April 1, 2015) | 92 |

(a) The amounts shown equal the hydro energy output for the post-upgrade transfer limits minus the hydro energy output for the pre-upgrade transfer limits. Positive numbers indicate greater output and less bottled-in hydro generation. The results shown might not be exact due to rounding.

### Energy from New Brunswick Imports

Varying the assumptions used in this study significantly changed the amount of bottled-in energy imported from New Brunswick. Energy imported from New Brunswick had the next-higher threshold price after hydro and could be displaced by either wind or hydro. Table 4-7 shows the amount of energy in the input profiles and the simulated energy imported from New Brunswick in each of the cases. In Cases 1 to 4, the imports are nearly equal to the import profile. In Cases 5,
5-NB, and 6, the interfaces across the Maine corridor and into southern New England become a significant impediment to moving energy into the rest of New England, and the amount of bottled-in imported energy increases as the amount of wind increases. Table 4-8 shows the difference in imported energy compared with the input profiles.

Table 4-7
New Brunswick Imports (GWh)

| Case ID | Case | Input Import Energy Profile | Pre | Post |
| --- | --- | --- | --- | --- |
| 1 | Existing wind in New England (in service as of April 1, 2015) | 4,592 | 4,592 | 4,592 |
| 2 | RENEW Sensitivity 1 (less wind) | 4,592 | 4,582 | 4,592 |
| 3 | Proposed wind in New England with I.3.9 approval (as of April 1, 2015) | 4,592 | 4,573 | 4,592 |
| 4 | RENEW base case—STA-WI-studied wind (as of October 1, 2013) | 4,592 | 4,535 | 4,592 |
| 5 | RENEW Sensitivity 2 (more wind) | 4,592 | 3,889 | 4,398 |
| 5-NB | RENEW Sensitivity 2 (more wind) and 1,000 MW of imports from New Brunswick, available for dispatch 24 x 7 | 8,760 | 6,325 | 7,732 |
| 6 | All future queue wind in New England (as of April 1, 2015) | 4,592 | 2,418 | 3,032 |

Table 4-8
Bottled-In Energy from New Brunswick with Profile as Reference (GWh)

| Case ID | Case | Pre | Post |
| --- | --- | --- | --- |
| 1 | Existing wind in New England (in service as of April 1, 2015) | 0 | 0 |
| 2 | RENEW Sensitivity 1 (less wind) | 9 | 0 |
| 3 | Proposed wind in New England with I.3.9 approval (as of April 1, 2015) | 19 | 0 |
| 4 | RENEW base case—STA-WI-studied wind (as of October 1, 2013) | 57 | 0 |
| 5 | RENEW Sensitivity 2 (more wind) | 702 | 194 |
| 5-NB | RENEW Sensitivity 2 (more wind) and 1,000 MW of imports from New Brunswick, available for dispatch 24 x 7 | 2,435 | 1,028 |
| 6 | All future queue wind in New England (as of April 1, 2015) | 2,174 | 1,560 |

Table 4-9 shows the difference in imports between the pre-upgrade Maine corridor limits and the post upgrade interface limits. This shows that the amount of bottled-in New Brunswick imports is greater than 60 GWh only in Cases 5, 5-NB, and 6.

Table 4-9
Change in Imported Energy from New Brunswick Due to Higher Transfer Limits (GWh)

| Case ID | Case | Change in Energy Output(a) |
| --- | --- | --- |
| 1 | Existing wind in New England (in service as of April 1, 2015) | 0 |
| 2 | RENEW Sensitivity 1 (less wind) | 9 |
| 3 | Proposed wind in New England with I.3.9 approval (as of April 1, 2015) | 19 |
| 4 | RENEW base case—STA-WI-studied wind (as of October 1, 2013) | 57 |
| 5 | RENEW Sensitivity 2 (more wind) | 509 |
| 5-NB | RENEW Sensitivity 2 (more wind) and 1,000 MW of imports from New Brunswick, available for dispatch 24 x 7 | 1,407 |
| 6 | All future queue wind in New England (as of April 1, 2015) | 614 |

(a) The amounts of imported energy shown equal the imports for the post-upgrade transfer limits minus the imports for the pre-upgrade transfer limits. Positive numbers indicate greater output and less bottled-in imported energy. The results shown might not be exact due to rounding.

## Interface Constrained Hours

The number of hours that an interface is at the limit and becomes a constraint provides insight into the capabilities and limitation of the transmission system.

### Orrington South

Table 4-10 shows the percentage of time that the Orrington South interface was binding. With the pre-upgrade value of 1,325 MW and existing wind within Maine, the interface was binding 1.3% of the hours. After the upgrade, the interface was not binding in any hours. In Cases 2, 3, and 4, the percentage of time the interface was binding increased to 6.1%, 8.1%, and 13.5% of the hours, respectively. For the higher, post-upgrade interface ratings for these cases, the interface was basically not constrained. With additional wind north of Orrington South in Cases 5, 5-NB, and 6, the results show that the interface was constrained 43.2% to 82.6% of the time. With the higher post-upgrades limits, the fraction of time the interface was constraining was much smaller, ranging between 19.1% and 56.5% of the hours. Table 4-11 shows the reduction in the percentage of the hours the interface was binding due to increased transfer capability.

Table 4-10
Orrington South Interface—Percentage of Hours at the Limit

| Case ID | Case | Pre | Post |
| --- | --- | --- | --- |
| 1 | Existing wind in New England (in service as of April 1, 2015) | 1.3 | 0.0 |
| 2 | RENEW Sensitivity 1 (less wind) | 6.1 | 0.0 |
| 3 | Proposed wind in New England with I.3.9 approval (as of April 1, 2015) | 8.1 | 0.0 |
| 4 | RENEW base case—STA-WI-studied wind (as of October 1, 2013) | 13.5 | 0.1 |
| 5 | RENEW Sensitivity 2 (more wind) | 43.2 | 19.1 |
| 5-NB | RENEW Sensitivity 2 (more wind) and 1,000 MW of imports from New Brunswick, available for dispatch 24 x 7 | 82.6 | 56.5 |
| 6 | All future queue wind in New England (as of April 1, 2015) | 68.7 | 51.5 |

Table 4-11
Change in Hours the Orrington South Interface Was at the Limit and the Congestion Eliminated (%)

| Case ID | Case | Change in Congested Hours (%)(a) | Congestion Eliminated (%)(b) |
| --- | --- | --- | --- |
| 1 | Existing wind in New England (in service as of April 1, 2015) | −1.3 | 100.0 |
| 2 | RENEW Sensitivity 1 (less wind) | −6.1 | 100.0 |
| 3 | Proposed wind in New England with I.3.9 approval (as of April 1, 2015) | −8.1 | 100.0 |
| 4 | RENEW base case—STA-WI-studied wind (as of October 1, 2013) | −13.4 | 99.5 |
| 5 | RENEW Sensitivity 2 (more wind) | −24.1 | 55.8 |
| 5-NB | RENEW Sensitivity 2 (more wind) and 1,000 MW of imports from New Brunswick, available for dispatch 24 x 7 | −26.1 | 31.6 |
| 6 | All future queue wind in New England (as of April 1, 2015) | −17.2 | 25.1 |

(a) 	% change in congested hours = (the post-upgrade % of hours the interface was at the limit minus the pre-upgrade % of hours at the limit). Negative values indicate reduced congestion.

(b) 	% congestion eliminated =
{(the pre-upgrade % of hours the interface was congested minus the post-upgrade %)(100)}/(pre-upgrade %).

### Surowiec South

Table 4-12 shows the percentage of time that the Surowiec South interface was binding. With existing wind within Maine and the Surowiec South interface limit of 1,600 MW, the interface was not binding. In Cases 2 through 4, the maximum percentage of time the interface was binding was only 4% of the hours. With the higher, post-upgrade interface ratings of 2,100 MW, the interface was not constrained in any hours for these cases. With additional wind north of Orrington South in Cases 5, 5-NB, and 6, the pre-upgrade interface was constrained slightly less, at 10.6 to 11.5% of the time. With the post-upgrade interface limit of 2,100 MW, the interface was not constrained in any hours. Table 4-13 shows the reduction in the percentage of the hours due to the increased transfer capability.

Table 4-12
Surowiec South Interface—Percentage of Hours at the Limit

| Case ID | Case | Pre | Post |
| --- | --- | --- | --- |
| 1 | Existing wind in New England (in service as of April 1, 2015) | 0.0 | 0.0 |
| 2 | RENEW Sensitivity 1 (less wind) | 0.0 | 0.0 |
| 3 | Proposed wind in New England with I.3.9 approval (as of April 1, 2015) | 0.6 | 0.0 |
| 4 | RENEW base case—STA-WI-studied wind (as of October 1, 2013) | 4.0 | 0.0 |
| 5 | RENEW Sensitivity 2 (more wind) | 10.6 | 0.0 |
| 5-NB | RENEW Sensitivity 2 (more wind) and 1,000 MW of imports from New Brunswick, available for dispatch 24 x 7 | 11.5 | 0.0 |
| 6(a) | All future queue wind in New England (as of April 1, 2015) | 11.2 | 0.0 |

(a)  For all but Case 6, only “existing wind” as of April 1, 2015, was assumed outside Maine.

Table 4-13
Change in Hours the Surowiec South Interface Was at the Limit and the Congestion Eliminated (%)

| Case ID | Case | Change in Congested Hours (%)(a) | Congestion Eliminated (%)(b) |
| --- | --- | --- | --- |
| 1 | Existing wind in New England (in service as of April 1, 2015) | 0.0 | NA(c) |
| 2 | RENEW Sensitivity 1 (less wind) | 0.0 | NA(c) |
| 3 | Proposed wind in New England with I.3.9 approval (as of April 1, 2015) | −0.6 | 100.0 |
| 4 | RENEW base case—STA-WI-studied wind (as of October 1, 2013) | −4.0 | 100.0 |
| 5 | RENEW Sensitivity 2 (more wind) | −10.6 | 100.0 |
| 5-NB | RENEW Sensitivity 2 (more wind) and 1,000 MW of imports from New Brunswick, available for dispatch 24 x 7 | −11.5 | 100.0 |
| 6 | All future queue wind in New England (as of April 1, 2015) | −11.2 | 100.0 |

(a) 	% change in congested hours = (the post-upgrade % of hours the interface was at the limit minus the pre-upgrade % of hours at the limit). Negative values indicate reduced congestion.

(b) 	% congestion eliminated =
{(the pre-upgrade % of hours the interface was congested minus the post-upgrade %)(100)}/(pre-upgrade %).

(c) Not applicable.

### North–South

Table 4-14 shows the percentage of time the North–South interface was binding. With existing wind within Maine and the North–South interface limit of 2,675 MW, the interface was binding approximately 0.5% of the hours. In Cases 2 through 4, the maximum percentage of time the interface was binding at the pre-upgrade limit was only as high as 2.3% of the hours. With the increased Maine interfaces at their post-upgrade ratings, more energy was exported outside of Maine, and this impinged on the North–South interface constraint. The interface also became more constrained for cases with more wind resources in Maine and higher imports from New Brunswick. Table 4-15  shows the increase in the percentage of the hours due to the increased transfer capability within Maine.

Table 4-14
North–South Interface—Percentage of Hours at Limit

| Case ID | Case | Pre | Post |
| --- | --- | --- | --- |
| 1 | Existing wind in New England (in service as of April 1, 2015) | 0.5 | 0.5 |
| 2 | RENEW Sensitivity 1 (less wind) | 1.0 | 1.1 |
| 3 | Proposed wind in New England with I.3.9 approval (as of April 1, 2015) | 2.0 | 2.3 |
| 4 | RENEW base case—STA-WI-studied wind (as of October 1, 2013) | 2.3 | 3.1 |
| 5 | RENEW Sensitivity 2 (more wind) | 3.5 | 9.5 |
| 5-NB | RENEW Sensitivity 2 (more wind) and 1,000 MW of imports from New Brunswick, available for dispatch 24 x 7 | 4.0 | 14.0 |
| 6 | All future queue wind in New England (as of April 1, 2015) | 6.4 | 18.0 |

Table 4-15
Change in Hours the North–South Interface Was at the Limit and the Congestion Increase (%)

| Case ID | Case | Change in Congested Hours (%)(a) | Increase in Congestion (%)(b) |
| --- | --- | --- | --- |
| 1 | Existing wind in New England (in service as of April 1, 2015) | 0.0 | 0.0 |
| 2 | RENEW Sensitivity 1 (less wind) | 0.1 | 9.5 |
| 3 | Proposed wind in New England with I.3.9 approval (as of April 1, 2015) | 0.3 | 14.3 |
| 4 | RENEW base case—STA-WI-studied wind (as of October 1, 2013) | 0.8 | 36.3 |
| 5 | RENEW Sensitivity 2 (more wind) | 5.9 | 167.1 |
| 5-NB | RENEW Sensitivity 2 (more wind) and 1,000 MW of imports from New Brunswick, available for dispatch 24 x 7 | 10.0 | 250.4 |
| 6 | All future queue wind in New England (as of April 1, 2015) | 11.6 | 180.9 |

(a) 	% change in congested hours = (the post-upgrade % of hours the interface was at the limit minus the pre-upgrade % of hours at the limit). Positive values indicate increased congestion.

(b) 	% increased congestion =
{(the post-upgrade % of hours the interface was congested minus the pre-upgrade %)(100)}/(pre-upgrade %).

## Production Cost

Production cost is the primary metric the ISO uses in its economic studies to evaluate potential changes to the New England transmission system and the addition of new types of resources. Table 4-16 provides the total production cost metrics for each of the cases.

Table 4-16
Production Cost at Assumed Export Limit (Millions of $)

| Case ID | Case | Pre | Post |
| --- | --- | --- | --- |
| 1 | Existing wind in New England (in service as of April 1, 2015) | 3,667.5 | 3,667.3 |
| 2 | RENEW Sensitivity 1 (less wind) | 3,638.9 | 3,638.0 |
| 3 | Proposed wind in New England with I.3.9 approval (as of April 1, 2015) | 3,593.3 | 3,592.2 |
| 4 | RENEW base case—STA-WI-studied wind (as of October 1, 2013) | 3,563.4 | 3,558.8 |
| 5 | RENEW Sensitivity 2 (more wind) | 3,458.3 | 3,427.1 |
| 5-NB | RENEW Sensitivity 2 (more wind) and 1,000 MW of imports from New Brunswick, available for dispatch 24 x 7 | 3,338.4 | 3,260.6 |
| 6 | All future queue wind in New England (as of April 1, 2015) | 3,350.8 | 3,276.1 |

Table 4-17 shows the savings using the initial interface ratings as the reference. For wind installations across Maine totaling between 453 MW and 1,149 MW, production cost savings due to increasing the interface capability across Maine corridor would range from $0.2 million to $4.6 million annually. Case 1 shows that with existing resources, the ability to export more energy across the Maine corridor reduced production costs by $0.2 million.

Table 4-17
Production Cost Savings due to Increased Maine Corridor Capability (Millions of $)

| Case ID | Case | Pre | Post |
| --- | --- | --- | --- |
| 1 | Existing wind in New England (in service as of April 1, 2015) | Reference | 0.2 |
| 2 | RENEW Sensitivity 1 (less wind) | Reference | 1.0 |
| 3 | Proposed wind in New England with I.3.9 approval (as of April 1, 2015) | Reference | 1.1 |
| 4 | RENEW base case—STA-WI-studied wind (as of October 1, 2013) | Reference | 4.6 |
| 5 | RENEW Sensitivity 2 (more wind) | Reference | 31.2 |
| 5-NB | RENEW Sensitivity 2 (more wind) and 1,000 MW of imports from New Brunswick, available for dispatch 24 x 7 | Reference | 77.8 |
| 6 | All future queue wind in New England (as of April 1, 2015) | Reference | 74.8 |

With 2,084 MW to 3,727 MW of total wind in Maine, production cost savings from increasing the transfer across the Maine corridor was $31 million to $77.8 million annually. The Orrington South interface was the major constraint because 1,185 MW and 2,829 MW of wind resources, respectively, were assumed to be located north of Orrington South. This constraint affected the ability to transport economically dispatched resources (including imports from New Brunswick) to customers located south of Orrington. The results also showed that as the Maine corridor was relieved and higher levels of energy flowed into southern New England load centers from the north, the North–South interface became increasingly constrained.

The results show an annual production cost savings of $74.8 million if the full wind queue of 3,727 MW in Maine were brought on line, and the transfer capability across the Maine corridor increased, specifically, if the Orrington South interface rating increased from 1,325 MW to 1,650 MW and Surowiec South increased from 1,600 to 2,100 MW.

## Implied Range of Capital Investment Attributable to Production Cost Savings

Production cost savings may be applied to the cost of transmission upgrades that relieve transmission constraints. This would happen if the annual revenue requirements (also called annual carrying charges) for transmission alternatives were less than or equal to the annual production cost savings.

Each potential transmission alternative has its annual requirements for covering fixed costs based on a project’s capital investment; financing costs, including debt service and return on investment; plus operations and maintenance costs. These annual costs can be estimated using annual carrying charges derived from representative capital costs for each alternative. This study assumes carrying charges of 14% to 16% of the capital costs.

With a “known” amount of savings in annual production costs, a range of capital investments can be estimated using these two fixed-charge rates.

Table 4-18 shows the implied range of capital investments attributable to production cost savings. For Cases 1 to 3, the production cost reductions imply that less than $10 million may be invested based solely on reductions to production costs. In Case 4, which has a greater reduction in production costs, the implied range of capital investments increases to the range of $28.9 to 33.0 million. For cases 5, 5-NB, and 6, when additional wind was added north of Orrington South, the reduction in production costs was larger, and the implied amount of capital investment that could be supported ranged from $195.1 million to $555.7 million.

Table 4-18
Implied Range of Capital Investments Attributable to Production Cost Savings (Millions of $)

| Case ID | Case | Pre | Post |
| --- | --- | --- | --- |
| 1 | Existing wind in New England (in service as of April 1, 2015) | Reference | 1.3 to 1.5 |
| 2 | RENEW Sensitivity 1 (less wind) | Reference | 6.0 to 6.9 |
| 3 | Proposed wind in New England with I.3.9 approval (as of April 1, 2015) | Reference | 6.9 to 7.9 |
| 4 | RENEW base case—STA-WI-studied wind (as of October 1, 2013) | Reference | 28.9 to 33.0 |
| 5 | RENEW Sensitivity 2 (more wind) | Reference | 195.1 to 222.9 |
| 5-NB | RENEW Sensitivity 2 (more wind) and 1,000 MW of imports from New Brunswick, available for dispatch 24 x 7 | Reference | 486.2 to 555.7 |
| 6 | All future queue wind in New England (as of April 1, 2015) | Reference | 467.2 to 533.9 |

## Load-Serving Entity Energy Expense

The metric for LSE energy expenses reflects the total amount that consumers of wholesale electric energy, including utilities and competitive power marketers, would spend to procure energy in the New England market. LSE energy expense is a proxy for costs to consumers, recognizing that many LSEs purchase electric energy through bilateral contracts rather than in the spot markets. It is equivalent to the total electric energy revenues that resources, including demand-side resources and imports from neighboring systems, would receive for supplying electric energy to the wholesale market plus the cost of congestion.

The LSE energy-expense metric is influenced by many factors and has some peculiar characteristics. For example, if excess wind causes an export-constrained area to experience low locational marginal prices, the aggregate New England LSE energy-expense metric would decrease. If the export constrained interface were then relieved, the LMPs would increase within this area and the LSE energy-expense metric associated with this area would increase. Because additional energy would be available to the rest of New England to displace the marginal resource in the rest of New England, the LMP would tend to decrease, and therefore the LSE energy-expense metric would decrease for the area outside the formerly export-constrained area. The sum of the increase and decrease in LSE energy expense, both inside and outside the formerly export-constrained area, may be positive or negative. In general, the net increase or decrease of the aggregate New England LSE energy expense would be affected by the magnitude of the load and geographic scope of the areas with LMPs that change.

Table 4-19 shows the LSE energy-expense metric for New England consumers for the 14 cases considered. Table 4-20 shows the impact on this metric when the interface limits across the Maine corridor increased to the post-upgrade rating. The metric for New England LSE energy expenses showed a range similar in magnitude to the change in production cost. For wind installations across Maine totaling between 453 MW and 1,149 MW, the reductions in LSE energy expenses due to improvements in the Maine corridor interfaces ranged from $0.5 million to $2.1 million annually. With 2,084 MW to 3,727 MW of total wind in Maine, LSE energy expense reductions were $38.8 million to $76.1 million annually. Higher levels of New Brunswick imports resulted in an LSE energy expense of $79.6 million annually.

Table 4-19
LSE Energy Expense at Tested Keene Road Export Limit (Millions of $)

| Case ID | Case | Pre | Post |
| --- | --- | --- | --- |
| 1 | Existing wind in New England (in service as of April 1, 2015) | 7,246.2 | 7,245.3 |
| 2 | RENEW Sensitivity 1 (less wind) | 7,216.6 | 7,215.4 |
| 3 | Proposed wind in New England with I.3.9 approval (as of April 1, 2015) | 7,177.8 | 7,177.3 |
| 4 | RENEW base case—STA-WI-studied wind (as of October 1, 2013) | 7,166.6 | 7,164.5 |
| 5 | RENEW Sensitivity 2 (more wind) | 7,092.8 | 7,054.0 |
| 5-NB | RENEW Sensitivity 2 (more wind) and 1,000 MW of imports from New Brunswick, available for dispatch 24 x 7 | 7,001.9 | 6,922.3 |
| 6 | All future queue wind in New England (as of April 1, 2015) | 6,958.9 | 6,882.9 |

Table 4-20
LSE Energy-Expense Reductions due to Increased Keene Road Export Limit (%)

| Case ID | Case | Pre | Post |
| --- | --- | --- | --- |
| 1 | Existing wind in New England (in service as of April 1, 2015) | Reference | 1.0 |
| 2 | RENEW Sensitivity 1 (less wind) | Reference | 1.2 |
| 3 | Proposed wind in New England with I.3.9 approval (as of April 1, 2015) | Reference | 0.5 |
| 4 | RENEW base case—STA-WI-studied wind (as of October 1, 2013) | Reference | 2.1 |
| 5 | RENEW Sensitivity 2 (more wind) | Reference | 38.8 |
| 5-NB | RENEW Sensitivity 2 (more wind) and 1,000 MW of imports from New Brunswick, available for dispatch 24 x 7 | Reference | 79.6 |
| 6 | All future queue wind in New England (as of April 1, 2015) | Reference | 76.1 |

## Locational Marginal Prices

The LSE energy expense is developed by summing the cost of electric energy at each location where there is customer demand. The energy is valued at the LMP in each hour.

### Bangor Area

Figure 4-1 and Table 4-21 show the LMPs for the Bangor area (BHE) for each of the cases. As more wind and imports are added, the LMP become significantly lower. This can be seen by looking at trend between Cases 4, 5, 5-NB, and 6. Case 6 with the highest penetration of wind resources and Case 5B with high imports from New Brunswick result in the lowest average LMP. This trend occurs for both the pre- and post-upgrade cases. Relieving the Maine transmission transfer limits increases LMPs in BHE.

Figure 4-1: LMPs for BHE ($/MWh).

Table 4-21
LMPs for BHE ($/MWh)

| Case ID | Case | Pre | Post |
| --- | --- | --- | --- |
| 1 | Existing wind in New England (in service as of April 1, 2015) | 48.65 | 48.90 |
| 2 | RENEW Sensitivity 1 (less wind) | 47.35 | 48.69 |
| 3 | Proposed wind in New England with I.3.9 approval (as of April 1, 2015) | 46.39 | 48.40 |
| 4 | RENEW base case—STA-WI-studied wind (as of October 1, 2013) | 43.66 | 47.60 |
| 5 | RENEW Sensitivity 2 (more wind) | 31.51 | 40.78 |
| 5-NB | RENEW Sensitivity 2 (more wind) and 1,000 MW of imports from New Brunswick, available for dispatch 24 x 7 | 15.42 | 27.76 |
| 6 | All future queue wind in New England (as of April 1, 2015) | 19.86 | 27.36 |

### Southern Maine Area

Figure 4-2 and Table 4-22 show the LMPs for the southern Maine area (SME) for each of the cases. The SME area is south of the Orrington South interface as well as south of the Surowiec South interface. These results show that as more wind and imports are added, the LMPs become slightly lower. This can be seen by looking at Cases 4, 5, 5-NB, and 6. Case 6, with the highest penetration of wind resources and imports from New Brunswick, has an average LMP slightly lower than the other cases. The LMP decreases as wind penetration increases for both the pre- and post-upgrade cases.

Figure 4-2: LMPs for southern Maine ($/MWh).

Table 4-22
LMPs for Southern Maine ($/MWh)

| Case ID | Case | Pre | Post |
| --- | --- | --- | --- |
| 1 | Existing wind in New England (in service as of April 1, 2015) | 48.85 | 48.84 |
| 2 | RENEW Sensitivity 1 (less wind) | 48.65 | 48.63 |
| 3 | Proposed wind in New England with I.3.9 approval (as of April 1, 2015) | 48.37 | 48.34 |
| 4 | RENEW base case—STA-WI-studied wind (as of October 1, 2013) | 48.33 | 48.24 |
| 5 | RENEW Sensitivity 2 (more wind) | 47.98 | 47.35 |
| 5-NB | RENEW Sensitivity 2 (more wind) and 1,000 MW of imports from New Brunswick, available for dispatch 24 x 7 | 47.55 | 46.47 |
| 6 | All future queue wind in New England (as of April 1, 2015) | 47.14 | 45.97 |

### New England

Figure 4-3  and Table 4-23 show the LMPs for the aggregate New England area for each of the cases. These results show that as more wind and imports are added, the LMP decrease slightly.

Figure 4-3: LMPs for aggregate ISO New England ($/MWh).

Table 4-23
LMPs for ISO New England ($/MWh)

| Case ID | Case | Pre | Post |
| --- | --- | --- | --- |
| 1 | Existing wind in New England (in service as of April 1, 2015) | 49.10 | 49.09 |
| 2 | RENEW Sensitivity 1 (less wind) | 48.90 | 48.89 |
| 3 | Proposed wind in New England with I.3.9 approval (as of April 1, 2015) | 48.64 | 48.63 |
| 4 | RENEW base case—STA-WI-studied wind (as of October 1, 2013) | 48.56 | 48.55 |
| 5 | RENEW Sensitivity 2 (more wind) | 48.06 | 47.80 |
| 5-NB | RENEW Sensitivity 2 (more wind) and 1,000 MW of imports from New Brunswick, available for dispatch 24 x 7 | 47.45 | 46.91 |
| 6 | All future queue wind in New England (as of April 1, 2015) | 47.15 | 46.64 |

## CO2 System Emissions

Environmental emissions are another important metric associated with increased transfer capability across the Maine corridor. This section summarizes the total New England CO2 emissions under the 14 cases investigated. Only the thermal units within New England contributed to the CO2 emission metric. Energy imported from external areas was assumed not to have any emissions.

Table 4-24 shows the total New England CO2 emissions for all cases. Table 4-25 shows the change in total New England CO2 emissions with increased transfer capability across the Maine corridor.

Table 4-24
Total New England CO2 Emissions (ktons)

| Case ID | Case | Pre | Post |
| --- | --- | --- | --- |
| 1 | Existing wind in New England (in service as of April 1, 2015) | 31,775.1 | 31,774.5 |
| 2 | RENEW Sensitivity 1 (less wind) | 31,482.7 | 31,485.3 |
| 3 | Proposed wind in New England with I.3.9 approval (as of April 1, 2015) | 31,046.9 | 31,054.2 |
| 4 | RENEW base case—STA-WI-studied wind (as of October 1, 2013) | 30,633.4 | 30,630.8 |
| 5 | RENEW Sensitivity 2 (more wind) | 29,461.6 | 29,245.8 |
| 5-NB | RENEW Sensitivity 2 (more wind) and 1,000 MW of imports from New Brunswick, available for dispatch 24 x 7 | 28,189.7 | 27,572.2 |
| 6 | All future queue wind in New England (as of April 1, 2015) | 28,250.3 | 27,548.9 |

Table 4-25
Change in New England CO2 Emissions as Transfer Capability Increases (ktons)

| Case ID | Case | Pre | Post | Reduction (%) |
| --- | --- | --- | --- | --- |
| 1 | Existing wind in New England (in service as of April 1, 2015) | Reference | −0.5 | 0.0 |
| 2 | RENEW Sensitivity 1 (less wind) | Reference | 2.6 | 0.0 |
| 3 | Proposed wind in New England with I.3.9 approval (as of April 1, 2015) | Reference | 7.3 | 0.0 |
| 4 | RENEW base case—STA-WI-studied wind (as of October 1, 2013) | Reference | −2.6 | 0.0 |
| 5 | RENEW Sensitivity 2 (more wind) | Reference | −215.8 | 0.7 |
| 5-NB | RENEW Sensitivity 2 (more wind) and 1,000 MW of imports from New Brunswick, available for dispatch 24 x 7 | Reference | −617.5 | 2.2 |
| 6 | All future queue wind in New England (as of April 1, 2015) | Reference | −701.4 | 2.5 |

For wind installations across Maine totaling between 453 MW and 1,149 MW, CO2 emissions resulting from higher Maine corridor interface limits ranged from an increase of 7.3 kilotons (ktons) to a reduction of 2.6 ktons annually. The expected trend would be that with greater wind generation production, CO2 emissions would decrease. However, this metric may not decrease when changes affecting unit commitment are small, such as when additional electric energy is available after an interface is relaxed. With 2,084 MW to 3,727 MW of total wind in Maine, emission reductions from higher Maine interface transfer limits were 215.8 ktons to 701.4 ktons annually. The case with 2,084 MW of wind resources plus higher levels of New Brunswick imports resulted in a reduction of CO2 emissions of 617.5 ktons annually.

# Observations

When less than 1,149 MW of wind are in the state—with 334 MW located north of Orrington South—an increase in transmission interface limits in Maine results in production cost savings of less than $5 million annually. With more than 2,084 MW of wind resources in Maine—and more than 1,185 MW north of Orrington South, the annual savings increased to the $38 to $75 million range. Increased imports from New Brunswick increase the production cost savings up to $78 million.

As the Maine corridor was upgraded to accommodate higher levels of wind resources, the downstream North–South interface was constrained in more hours.

# Appendix

## Economic Metrics from Production Simulation

The key economic metrics used to compare the cases are production cost and load-serving entity energy expense. The absolute values of these metrics are not the focus of this analysis because the aim was to quantify relative changes.

### Production Cost

The production cost metric is based on the summation of dispatch costs for each unit multiplied by the amount of energy produced. This calculation aggregates all New England resources used to serve customer demands. Production costs for resources located in external areas would be constant in all cases and therefore would not affect the relative difference between cases. Therefore, external resources were not included.

Production Cost =

Where:

i is a resource identifier (index)

h is the hour (index)

nUnit is the number of generating units in the simulation (count)

DispatchCosti is the cost of producing energy from resource ‘i’ ($/MWh)

MWhi,h is the generation of unit ‘i’ in hour ‘h’ (MWh)

### LSE Energy Expense

LSE electric energy expense is calculated by taking the hourly marginal energy cost (e.g., the locational marginal price) in an area and multiplying it by the hourly load within that same area. Total LSE energy expense is the summation of each area’s LSE energy-expense, which includes the effects of congestion.

LSE Energy Expense =

Where:

r is an “area” (typically an RSP area) (index)

h is the hour (index)

nRSP is the number of areas (count)

LMPr,h is the energy price for area ‘r’ in hour ‘h’ ($/MWh)

MWhr,h is the load of area ‘r’ in hour ‘h’ (MWh)

## Wind Units

Table 6-1 shows the wind units used in this study by case and subarea.

Table 6-1
Wind Units by Case and Subarea (MW)

| Area | Name | 1 Existing Wind in New England (In Service as of April 1, 2015) | 2 RENEW Sensitivity 1 (Less Wind) | 3 Proposed Wind in New England with I.3.9 Approval (as of April 1, 2015) | 4 RENEW Base Case—STA-WI-Studied Wind (as of October 1, 2013) | 5 RENEW Sensitivity 2 (More Wind) | 5-NB Sensitivity 2 (More Wind) and 1,000 MW of imports from NB, 24 x 7 | 6 All Queue Wind in New England (as of April 1, 2015) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| BHE | QP357_Passadumkeag Windpark | 0.0 | 0.0 | 40.0 | 40.0 | 40.0 | 40.0 | 40.0 |
| BHE | QP476_Wind | 0.0 | 0.0 | 0.0 | 52.8 | 52.8 | 52.8 | 52.8 |
| BHE | Rollins Wind Plant | 61.8 | 61.8 | 61.8 | 61.8 | 61.8 | 61.8 | 61.8 |
| BHE | Stetson II Wind Farm | 26.3 | 26.3 | 26.3 | 26.3 | 26.3 | 26.3 | 26.3 |
| BHE | Stetson Wind Farm | 58.7 | 58.7 | 58.7 | 58.7 | 58.7 | 58.7 | 58.7 |
| BHE | Bull Hill Wind | 34.5 | 34.5 | 34.5 | 34.5 | 34.5 | 34.5 | 34.5 |
| BHE | QP349_Pisgah Mountain | 0.0 | 0.0 | 9.1 | 9.1 | 9.1 | 9.1 | 9.1 |
| BHE | QP397_Hancock Wind Project | 0.0 | 0.0 | 0.0 | 51.0 | 51.0 | 51.0 | 51.0 |
| BHE | QP400_Wind | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 90.0 |
| BHE | QP403_Pisgah Mountain Increase (see QP349) | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.1 |
| BHE | QP417_Wind | 0.0 | 0.0 | 0.0 | 0.0 | 250.0 | 250.0 | 250.0 |
| BHE | QP420_Wind | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 72.6 |
| BHE | QP435_Wind | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 111.0 |
| BHE | QP458_Wind | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 104.0 |
| BHE | QP459_Wind | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 104.0 |
| BHE | QP460_Wind | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 104.0 |
| BHE | QP461_Wind | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 104.0 |
| BHE | QP462_Wind | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 104.0 |
| BHE | QP470_Wind | 0.0 | 0.0 | 0.0 | 0.0 | 600.6 | 600.6 | 600.6 |
| BHE | QP471_Wind | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 600.6 |
| BHE | QP486_Wind | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 250.0 |
| BHE Total |  | 181.3 | 181.3 | 230.3 | 334.1 | 1,184.7 | 1,184.7 | 2,829.0 |
| Area | Name | 1 Existing Wind in New England (In Service as of April 1, 2015) | 2 RENEW Sensitivity 1 (Less Wind) | 3 Proposed Wind in New England with I.3.9 Approval (as of April 1, 2015) | 4 RENEW Base Case—STA-WI-Studied Wind (as of October 1, 2013) | 5 RENEW Sensitivity 2 (More Wind) | 5-NB Sensitivity 2 (More Wind) and 1,000 MW of imports from NB, 24 x 7 | 6 All Queue Wind in New England (as of April 1, 2015) |
| ME | GMCW | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 |
| ME | Kibby Wind Power | 149.6 | 149.6 | 149.6 | 149.6 | 149.6 | 149.6 | 149.6 |
| ME | QP272_Oakfield II Wind – Keene Road | 0.0 | 147.6 | 147.6 | 147.6 | 147.6 | 147.6 | 147.6 |
| ME | Saddleback Ridge Wind | 34.2 | 34.2 | 34.2 | 34.2 | 34.2 | 34.2 | 34.2 |
| ME | Spruce Mountain Wind | 20.0 | 20.0 | 20.0 | 20.0 | 20.0 | 20.0 | 20.0 |
| ME | QP300_Canton Mountain Winds | 0.0 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 |
| ME | QP333_Bingham Wind | 0.0 | 0.0 | 184.8 | 184.8 | 184.8 | 184.8 | 184.8 |
| ME | QP350-1_Wind (Withdrawn as of April 1, 2015) | 0.0 | 0.0 | 0.0 | 92.0 | 92.0 | 92.0 | 0.0 |
| ME | QP350-2_Wind | 0.0 | 0.0 | 0.0 | 96.9 | 96.9 | 96.9 | 96.9 |
| ME | QP393_Wind | 0.0 | 0.0 | 0.0 | 0.0 | 84.0 | 84.0 | 84.0 |
| ME | QP406_Canton Increase and CNR (see QP300) | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 3.6 |
| ME | QP407_Saddleback Increase | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 1.2 |
| ME | QP452_Wind | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 85.8 |
| ME | Record Hill Wind | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 |
| ME | WND_MISC_ME | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 |
| ME Total |  | 271.2 | 441.6 | 626.4 | 815.3 | 899.3 | 899.3 | 897.9 |
| Area | Name | 1 Existing Wind in New England (In Service as of April 1, 2015) | 2 RENEW Sensitivity 1 (Less Wind) | 3 Proposed Wind in New England with I.3.9 Approval (as of April 1, 2015) | 4 RENEW Base Case—STA-WI-Studied Wind (as of October 1, 2013) | 5 RENEW Sensitivity 2 (More Wind) | 5-NB Sensitivity 2 (More Wind) and 1,000 MW of imports from NB, 24 x 7 | 6 All Queue Wind in New England (as of April 1, 2015) |
| BST | WND_MISC_BST | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 |
| CMA NEMA | WND_MISC_CMANEMA | 4.0 | 4.0 | 4.0 | 4.0 | 4.0 | 4.0 | 4.0 |
| CMA NEMA | Princeton Wind Farm Project | 3.0 | 3.0 | 3.0 | 3.0 | 3.0 | 3.0 | 3.0 |
| NH | Lempster Wind | 25.3 | 25.3 | 25.3 | 25.3 | 25.3 | 25.3 | 25.3 |
| NH | Granite Reliable Power | 120.2 | 120.2 | 120.2 | 120.2 | 120.2 | 120.2 | 120.2 |
| NH | QP415_Jericho Wind | 0.0 | 0.0 | 12.1 | 0.0 | 0.0 | 0.0 | 12.1 |
| NH | Groton Wind Project | 50.5 | 50.5 | 50.5 | 50.5 | 50.5 | 50.5 | 50.5 |
| NH | QP390_Wind | 0.0 | 0.0 | 50.8 | 0.0 | 0.0 | 0.0 | 50.8 |
| NH | QP543_Wind | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 28.4 |
| RI | WND_MISC_RI | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 |
| SEMA | WND_MISC_SEMA | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 |
| VT | Sheffield Wind Farm | 40.0 | 40.0 | 40.0 | 40.0 | 40.0 | 40.0 | 40.0 |
| VT | Searsburg Wind | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 |
| VT | Kingdom Community Wind | 81.5 | 81.5 | 81.5 | 81.5 | 81.5 | 81.5 | 81.5 |
| VT | QP532_Wind | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 19.9 |
| VT | QP536_Wind | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 5.0 |
| VT | QP488_Wind | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 96.9 |
| WMA | QP396_Berkshire Wind Increase | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 4.8 |
| WMA | QP539_CNR Only | 31.7 | 31.7 | 31.7 | 31.7 | 31.7 | 31.7 | 31.7 |
| WMA | QP477_Wind | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 30.0 |
| WMA | QP535_Wind | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 0.0 | 5.0 |
| WMA | Berkshire East Wind | 16.7 | 16.7 | 16.7 | 16.7 | 16.7 | 16.7 | 16.7 |
| WMA | WND_MISC_WMA | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 |
| Outside Maine Total |  | 425.6 | 425.6 | 488.5 | 425.6 | 425.6 | 425.6 | 678.4 |

A market-efficiency transmission upgrade is a type of transmission system upgrade primarily designed to reduce the total net production cost to supply the system load, including the costs for electric energy, capacity, reserves, and losses, as well as costs associated with the bilateral prices for electric energy.

ISO New England, Strategic Transmission Analysis: Wind Integration Study, Planning Advisory Committee (PAC) presentation (December 18, 2013), 
https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2013/dec182013/a4_wind_study.pdf. Strategic Transmission Analysis: Wind Integration Study—Stage 1—Maine, Regional Constraints, PAC presentation (May 21, 2014), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2014/may212014/a4_strategic_transmission_analysis_wind_power_update.pdf.

RENEW Northeast, Economic Study Proposal: Economic Impact of Maine Upgrades Identified in ISO New England’s Strategic Transmission Analysis for Wind Integration, email memo (April 1, 2015), http://www.iso-ne.com/static-assets/documents/2015/04/maine_upgrades_eco_study_request.pdf.

The study assumptions for wind resources and transmission limits were concisely summarized in the ISO’s 2015 Economic Study Strategic Transmission Analysis—Onshore Wind Integration Draft Results, PAC presentation (March 28, 2015); http://www.iso-ne.com/static-assets/documents/2016/03/a3_2015_economic_study_on_shore_wind_presentation.pdf.

The system simulations result in the lowest possible production costs, which include economic dispatch and unit commitment. This lowest production cost may not result in the dispatch with the lowest emissions.

ISO New England Inc. Transmission, Markets, and Services Tariff (ISO tariff), Section II, Open Access Transmission Tariff, Attachment K, “Regional System Planning Process” (April 13, 2016), http://www.iso-ne.com/regulatory/tariff/sect_2/oatt/sect_ii.pdf.

More information on the PAC is available at http://www.iso-ne.com/committees/planning/planning-advisory.

OATT, Attachment K, Section 4.1b.

A generator interconnection upgrade is an addition or modification to the New England transmission system for interconnecting a new or existing generating unit whose capability to provide energy or capacity is materially changing and increasing, whether or not the interconnection is for meeting the Network Capability Interconnection Standard or the Capacity Capability Interconnection Standard (both defined in the ISO’s OATT, Schedule 22, Large Generator Interconnection Procedures, available at http://www.iso-ne.com/participate/rules-procedures/tariff/oatt). An elective transmission upgrade is an upgrade to the New England transmission system voluntarily funded by one or more participants that have agreed to pay for all the costs of the upgrade. A market-efficiency transmission upgrade is a type of transmission system upgrade primarily designed to reduce the total net production cost to supply the system load, including the costs for electric energy, capacity, reserves, and losses, as well as costs associated with the bilateral prices for electric energy.

RENEW Northeast, Economic Study Proposal: Economic Impact of Maine Upgrades Identified in ISO New England’s Strategic Transmission Analysis for Wind Integration, email memo (April 1, 2015), http://www.iso-ne.com/static-assets/documents/2015/04/maine_upgrades_eco_study_request.pdf.

ISO New England, Strategic Transmission Analysis: Wind Integration Study, Planning Advisory Committee presentation (December 18, 2013), 
https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2013/dec182013/a4_wind_study.pdf. Strategic Transmission Analysis: Wind Integration Study—Stage 1—Maine, Regional Constraints, PAC presentation (May 21, 2014), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2014/may212014/a4_strategic_transmission_analysis_wind_power_update.pdf.

A capacity commitment period is the one-year period from June 1 through May 31 of the following year for which Forward Capacity Market obligations are assumed and payments are made.

The Final RSP15 Project List (May 2015) is available at http://www.iso-ne.com/static-assets/documents/2015/06/final_rsp15_project_list_may_2015.xls.

ISO New England, 2015 Economic Studies Strategic Transmission Analysis—Onshore Wind Integration Scope of Work—Revised Draft, PAC presentation (June 17, 2015), http://www.iso-ne.com/static-assets/documents/2015/06/a9_2015_economic_studies_on_shore_wind_integration_scope_of_work_revised_draft.pdf  and 2015 Economic Study—Onshore Wind Study, reference document (March 23, 2016), http://www.iso-ne.com/static-assets/documents/2016/03/a3_2015_economic_studies_on_shore_wind_reference.pdf.

The Maine interface transfer limits defined in the 2013-STA-WI formed the basis for the 2015 study’s simulations for increased transfer limits, which are higher than the limits associated with the completion of the MPRP.

“I.3.9” refers to the section of the ISO tariff that includes the requirements for market participants’ and transmission owners’ (TO) submissions of new or revised plans for adding to or changing any generation or demand resource or transmission facility 69 kV or larger that could have a significant effect on the stability, reliability, or operating characteristics of a TO’s or market participants transmission facility or system. It also contains the ISO’s requirements for reviewing and approving these applications. The ISO’s list of these projects, “Interconnection Requests for New England Control Area Generation, Elective Transmission Upgrade, and Transmission Service Requests,” is also known as the ISO interconnection queue. See http://www.iso-ne.com/static-assets/documents/2014/09/interconnection_request_queue.pdf.

ISO New England, 2015 Evaluation of Increasing the Keene Road Export Limit (Keene Road Economic Study) (August 2016), http://www.iso-ne.com/system-planning/system-plans-studies/rsp.

For all but Case 6, only “existing wind” as of April 1, 2015, was assumed outside Maine.

ISO New England, 2015—2024 Forecast Report of Capacity, Energy, Loads, and Transmission (May 1, 2015), http://www.iso-ne.com/static-assets/documents/2015/05/isone_fcst_data_2015.xls.

NERC, Transmission System Planning Performance Requirements, Standard TPL-001-4 (January 1, 2016), http://www.nerc.com/pa/Stand/Reliability%20Standards/TPL-001-4.pdf.

Cape Wind had an active status in the queue but was not included in the study.

EIA, 2015 Annual Energy Outlook (DOE, April 2015), http://www.eia.gov/forecasts/aeo/pdf/0383(2015).pdf.

ISO New England, Final 2015 Energy-Efficiency Forecast 2019–2024 (May 1, 2015), http://www.iso-ne.com/static-assets/documents/2015/04/iso_ne_final_2015_ee_forecast_2019_2024.pdf. A capacity supply obligation is a requirement for a resource to provide capacity, or a portion of capacity, to satisfy a portion of the ISO’s Installed Capacity Requirement acquired through a Forward Capacity Auction, a reconfiguration auction, or a CSO bilateral contract through which a market participant may transfer all of part of its CSO to another entity.

NREL, Eastern Renewable Generation Integration Study (US Department of Energy, 2015), http://www.nrel.gov/electricity/transmission/eastern_renewable.html.

Energy-only resources are generating units that are non-FCM settlement-only generators (and thus are not entitled to receive capacity credit) and other generators (per ISO’s Operating Procedure No. 14, Technical Requirements for Generators, Demand Resources, Asset-Related Demands, and Alternative Technology Regulation Resources [November 16, 2015], http://www.iso-ne.com/static-assets/documents/rules_proceds/operating/isone/op14/op14_rto_final.pdf) that produce less than 5 MW, but the ISO control room does not centrally dispatch them or monitor them in real time.

NREL, “Transmission Grid Integration: Eastern Wind Dataset” webpage (2015), http://www.nrel.gov/electricity/transmission/eastern_wind_methodology.html.

ISO New England, 2014 ISO New England Electric Generator Air Emissions Report (January 2016), http://www.iso-ne.com/static-assets/documents/2016/01/2014_emissions_report.pdf.

ISO New England, ”Summary of Steady-State Base Cases for TPL-001-4 Studies (n.d.),” http://www.iso-ne.com/static-assets/documents/2015/07/final_summary_of_steady_state_basecases_for_tpl_001_4.pdf.

The Final RSP15 Project List (May 2015) is available at http://www.iso-ne.com/static-assets/documents/2015/06/final_rsp15_project_list_may_2015.xls.

The LSE energy-expense metric does not include Auction Revenue Rights, which represent compensation derived from Financial Transmission Rights.

Interchange with neighboring areas is represented by a fixed interchange schedule with a zero cost for imports and zero revenues for exports.