Public Meeting Draft

2017 Regional System Plan

Released to the public for review. Do not quote or cite.

The information contained in this document is subject to modification. ISO New England and its employees and agents are not responsible for any reliance of this document by any other user or for any errors, omissions, or conclusions contained herein.

© ISO New England Inc.
System Planning
August 29, 2017

ISO-NE public USE

Preface

ISO New England Inc. (ISO) is the not-for-profit corporation responsible for the reliable and economical operation of New England’s electric power system. It also administers the region’s wholesale electricity markets and manages the comprehensive planning of the regional power system. The planning process includes the periodic preparation of a Regional System Plan (RSP) in accordance with the ISO’s Open Access Transmission Tariff (OATT) and other parts of the Transmission, Markets, and Services Tariff (the ISO tariff), approved by the Federal Energy Regulatory Commission (FERC). Regional System Plans meet the tariff requirements by summarizing planning activities that include the following:

- Forecasts of annual energy use and peak loads (i.e., the demand for electricity) for a 10-year planning horizon and the need for resources (i.e., capacity)

- Information about the amounts, locations, and characteristics of market responses (e.g., generation or demand resources or elective transmission upgrades) that can meet the defined system needs—systemwide and in specific areas

- Descriptions of transmission projects for the region that meet the identified needs, as summarized in an RSP Project List, which includes information on project status and cost estimates and is updated several times each year.

RSPs also must summarize the ISO’s coordination of its system plans with those of neighboring systems, the results of economic studies of the New England power system, and information that can be used for improving the design of the regional wholesale electricity markets. In addition to these requirements, RSPs identify other actions taken by the ISO, state officials, regional policymakers, participating transmission owners (PTOs), New England Power Pool (NEPOOL) members, market participants, and other stakeholders to meet or modify the needs of the system.

The regional system planning process in New England is open and transparent and reflects advisory input from regional stakeholders, particularly members of the Planning Advisory Committee (PAC), according to the requirements specified in the OATT. The PAC is open to all entities interested in regional system planning activities in New England. The ISO appreciates the robust input provided by stakeholders, which makes this report possible.

The 2017 Regional System Plan (RSP17) and the regional system planning process identify the region’s electricity needs and plans for meeting these needs for 2017 through 2026. RSP17 updates the RSP15 report by discussing study proposals, scopes of work, assumptions, draft and final study results, and other materials. RSP17 planning activities were reviewed at PAC meetings held from September 2015 through August 2017. The ISO also posted to its website PAC presentations, meeting minutes, reports, study base cases, databases, and other materials for stakeholder review and use. On August 3, 2017, the ISO and the PAC discussed stakeholder comments on an earlier draft of RSP17, [and the ISO held a public meeting on September 14, 2017, to discuss RSP17 and other planning issues facing the New England region.]

Through the planning process, the ISO demonstrates compliance with all planning criteria and regulatory requirements. [As required by the OATT Attachment K, the ISO New England Board of Directors has approved the 2017 Regional System Plan.]

# Contents

Preface	iii

Figures	ix

Tables	xi

Section 1
Executive Summary	1

1.1 Highlights and Key Results of the Regional System Plan	2

1.1.1 Forecasts of the Annual and Peak Use of Electric Energy, Energy Efficiency,
and Photovoltaic Capacity and Energy	2

1.1.2 Projections of the Systemwide Need for Capacity and Operating Reserves	3

1.1.3 Transmission System Needs, Solutions, and Cost Considerations	5

1.1.4 Interregional Planning Requirements and Activities	7

1.1.5 Fuel-Related Risks to System Reliability and Solutions	7

1.1.6 Existing and Pending Environmental Regulations, Emissions Analyses, and Other Studies	9

1.1.7 Integrating Renewable and Other Resources to Meet System Needs	11

1.1.8 Multistate, ISO, and State Initiatives that Affect System Planning	13

1.2 Key Findings and Conclusions	14

Section 2
Overview of RSP17, the Power System, and Regional System Planning	16

2.1 Overview of the System Planning Process and RSP17	16

2.1.1 Types of Transmission Upgrades	17

2.1.2 Transmission Planning Guides	19

2.1.3 Planning Studies Conducted for and Summarized in RSP17	20

2.1.4 Accounting for Uncertainty	21

2.1.5 Working with the Planning Advisory Committee and Other Committees	22

2.1.6 Providing Information to Stakeholders	23

2.1.7 Meeting All Requirements	23

2.2 Overview of the New England Electric Power System	24

2.3 Overview of the New England Wholesale Electricity Market Structure	26

2.4 Overview of System Subdivisions Used for Analyzing and Planning the System	27

Section 3
Forecasts of New England’s Peak Demand, Annual Use of Electric Energy, Energy Efficiency,
and Distributed Generation	31

3.1 ISO New England Gross Demand Forecasts	31

3.2 Energy-Efficiency Forecast for New England	34

3.3 Distributed Generation Forecast for New England	35

3.3.1 Distributed Generation Forecast Working Group	35

3.3.2 PV Nameplate Capacity Forecast	36

3.3.3 PV Energy Forecast	38

3.4 The Net Demand Forecast	38

3.5 Summary of Key Findings of the Demand, Energy-Efficiency, and PV Forecasts	41

Section 4
Resource Adequacy—Resources, Capacity, and Reserves	43

4.1 Determining Systemwide and Local-Area Capacity Needs	43

4.1.1 Systemwide Installed Capacity Requirements	43

4.1.2 Local Resource Requirements and Limits	45

4.1.3 Capacity Supply Obligations from the Forward Capacity Auctions	47

4.2 Determining FCM Capacity Zones	51

4.3 Analyzing Operable Capacity	52

4.4 Determining Operating Reserves and Regulation	53

4.4.1 Systemwide Operating-Reserve Requirements	54

4.4.2 Locational Reserve Needs for Major Import Areas	55

4.5 Existing and Future Resource Development in Areas of Need	59

4.5.1 Existing Generating Capacity by Subarea, Load Zone, and State	59

4.5.2 Summer Seasonal Claimed Capability of New England’s Generating Resources	61

4.5.3 Generation Retirement and Additions in New England	61

4.5.4 Generating Units in the ISO Interconnection Request Queue	62

4.6 Summary	64

Section 5
Transmission System Performance Needs Assessments and Upgrade Approvals	67

5.1 The Need for Transmission Reliability	67

5.2 Overview of New England’s Transmission System	68

5.3 FERC Order No. 1000 Discussion	68

5.4 Completed Major Projects	70

5.5 Key Study Area Update	70

5.5.1 Southwest Connecticut Key Study Area	71

5.5.2 Greater Hartford Central Connecticut Key Study Area	73

5.5.3 Pittsfield and Greenfield Key Study Area	73

5.5.4 Greater Boston Key Study Area	74

5.5.5 Southeastern Massachusetts and Rhode Island Key Study Area	75

5.5.6 Maine Key Study Area	76

5.5.7 New Hampshire and Vermont Key Study Area	77

5.5.8 Eastern Connecticut Key Study Area	79

5.6 General Need for Future Transmission	79

5.7 New England Asset Management	80

5.8 Local System Plan	80

5.9 RSP Project List and Projected Transmission Project Costs	80

5.9.1 Reliability Transmission Upgrades	81

5.9.2 Lack of Need for Market-Efficiency-Related Transmission Upgrades	83

5.9.3 Required Generator-Interconnection-Related Upgrades	87

5.9.4 Elective Transmission Upgrades	87

5.10 Summary	88

Section 6
Interregional Coordination	89

6.1 Eastern Interconnection Planning Collaborative Studies	89

6.2 Electric Reliability Organization Overview	90

6.3 IRC Activities	92

6.4 Northeast Power Coordinating Council Studies and Activities	93

6.5 Northeastern ISO/RTO Planning Coordination Protocol	93

6.6 Interregional Transfers	94

6.7 Summary	96

Section 7
Fuel-Security Risks to System Reliability and Solutions	97

7.1 Capacity and Electric Energy Production in the Region by Fuel Type	97

7.2 Natural Gas Infrastructure	99

7.3 Natural Gas and Oil Fuel Security and Risks to System Reliability	102

7.3.1 Fuel-Security Risks	102

7.3.2 Natural Gas Price Volatility	102

7.4 Addressing Fuel-Security and Cost Risks	105

7.4.1 Electric Power System and Natural Gas Sector Coordination	105

7.4.2 Fuel Security—Use of Oil, LNG, Compressed Natural Gas, and Efficiency Measures	106

7.4.3 Fuel-Security Analyses	107

7.4.4 Pipeline Improvements	108

7.5 Summary	110

Section 8
Impacts of Environmental Regulations and Siting Requirements on Generators and the Power System	111

8.1 Federal, Regional, and State Environmental Regulations Affecting Generators	111

8.1.1 Emerging Impacts of Clean Water Act Regulations on the Region’s Generators	112

8.1.2 Clean Air Act Requirements and Regional and Federal Greenhouse Gas Regulations	113

8.1.3 Cost of Compliance with Environmental Regulations	119

8.2 Update of Regional Nuclear Generation Licensing Renewals	120

8.3 Update on Hydroelectric Generation Relicensing	120

8.4 Conclusions	121

Section 9
Integration of Variable Energy Resources	122

9.1  Industry Recommendations for Facilitating the Integration of Wind and Solar Resources	122

9.2 Integration of Wind Resources	123

9.2.1 Wind Forecasting and Dispatch	123

9.2.2 Strategic Transmission Analysis—Wind Integration Study	124

9.3 Large-Scale Adoption of Photovoltaic Resources and Other Distributed Generation Resources	125

9.3.1 Operational Solar Forecasting	125

9.3.2 Potential Reliability Impacts of PV	126

9.3.3 Modeling of Hourly Load Reduction of Behind-the-Meter Photovoltaics
to Establish the Net Installed Capacity Requirement	127

9.3.4 Other Challenges of Integrating PV and Other Types of Distributed Energy Resources	127

9.3.5 Energy-Storage Resources	128

9.4 Economic Performance of the System and Other Studies	128

9.4.1 2015 Economic Studies	128

9.4.2 2016 Economic Study—Phase I	129

9.4.3 2016 Economic Study—Phase II	131

9.4.4 2017 Economic Study	133

9.5 Summary	133

Section 10
Multistate, ISO, and State Initiatives	135

10.1 Multistate Initiatives	135

10.1.1 Eastern Interconnection States Planning Council	135

10.1.2 Coordination among the New England States	135

10.1.3 Consumer Liaison Group	136

10.1.4 Southern New England States’ Request for Proposals	136

10.2 ISO Initiatives	136

10.2.1 Updates on Developing and Integrating Smart Grid and Other New Technologies	136

10.2.2 Transmission Planning Initiatives	139

10.2.3 ISO Market Initiatives	139

10.3 State Initiatives, Activities, and Policies	140

10.3.1 Summary of Renewable Portfolio Standards	140

10.3.2 Connecticut	141

10.3.3 Maine	141

10.3.4 Massachusetts	141

10.3.5 New Hampshire	142

10.3.6 Rhode Island	143

10.3.7 Vermont	143

10.4 Summary of Initiatives	143

Section 11
Key Findings and Conclusions	144

Acronyms and Abbreviations	146

# Figures

Figure 2-1: 	Key facts about New England’s electric power system and wholesale electricity markets.	25

Figure 2-2: 	RSP17 geographic scope of the New England electric power system.	28

Figure 2-3: 	Active-demand-resource dispatch zones in the ISO New England system.	30

Figure 3-1: 	The ISO’s actual summer peak loads (i.e., reconstituted to include the megawatt reductions
from OP 4 actions, FCM passive demand resources, and BTM PV) and the 50/50 and 90/10 forecasts, 1992 to 2016 (MW).	34

Figure 3-2: 	Cumulative New England PV forecast for each classification of PV, 2017 to 2026 (MW).	37

Figure 3-3: 	RSP17 Gross annual energy-use forecast; gross energy forecast minus BTM PV; gross energy forecast minus BTM PV and FCM #11 PDRs through 2020; and gross energy forecast minus
BTM PV, minus FCM PDRs, minus the energy-efficiency forecast for 2021 to 2026 (MW).	39

Figure 3-4: 	RSP17 Gross summer peak demand forecast (90/10); gross demand forecast minus BTM PV;
gross demand forecast minus BTM PV and FCM #11 PDRs through 2020; and gross demand
forecast minus BTM PV, minus FCM PDRs, minus the energy-efficiency forecast for
2021 to 2026 (MW).	39

Figure 4-1: 	Summary of new capacity and retirement requests for FCA #5 to FCA #11.	50

Figure 4-2: 	Actual and projected summer SCC generation retirements and additions, 2010 to 2020 (MW).	62

Figure 4-3: 	Capacity of generation-interconnection requests by RSP subarea, November 1997
to April 2017 (MW).	63

Figure 4-4: 	Resources in the ISO interconnection queue, by state and fuel type, as of April 1, 2017
(MW and %).	63

Figure 4-5: 	Resources in the ISO interconnection queue, by RSP subarea and fuel type, as of April 1, 2017 (MW).	64

Figure 5-1: 	Key study areas in New England.	71

Figure 7-1: 	New England’s summer seasonal claimed capability (MW, %) and electric energy production
(GWh, %) by fuel type for 2016.	98

Figure 7-2: 	Generating resource summer capability by fuel type based on the 2017 CELT Report and the interconnection queue, 2017, 2020, and 2026 (MW, %). 	99

Figure 7-3: 	Overview map of the natural gas infrastructure serving New England.	100

Figure 7-4: 	Sources of natural gas in the continental United States, 2015.	101

Figure 7-5: 	Natural gas pipeline network in the continental United States, September 2014.	101

Figure 7-6: 	Monthly average natural gas prices and real-time Hub LMPs compared with regional
natural gas prices, March 2003 to March 2017, ($/MWh; $/MMbtu). 	103

Figure 7-7: 	Natural gas market data, April 2014 to April 2017 ($/MMBtu).	104

Figure 7-8:  	Monthly fuel burn (both heavy and light oil) at all New England fossil-fuel stations, winter 2015/2016 and 2016/2017 (beginning of each month) (barrels)	106

Figure 7-9: 	Comparison of LNG deliveries for winter 2014/2015 through winter 2016/2017.	107

Figure 7-10: 	Proposed natural gas pipeline expansions benefiting New England, 2015.	108

Figure 8-1: 	Summer claimed capability and cooling technology type in New England, 2017 (MW).	113

Figure 8-2: 	New England system annual emissions of NOX, SO2, and CO2, 2006 to 2015 (ktons).	115

Figure 8-3: 	New England RGGI states’ quarterly CO2 emissions and allowance auctions, 2008 to 2016
(mtons, millions).	117

Figure 8-4: 	New England RGGI states’ quarterly CO2 allowance auction proceeds and clearing price,
2008 to 2016 (million $ and $).	118

Figure 8-5: 	Contribution of CO2 allowance costs to energy production costs, 2012 to 2017 ($/MWh).	119

Figure 9-1: 	Areas in Connecticut and Massachusetts where PV resources
are likely to trip off line because of low voltage in the event of a fault on the 345 kV
transmission system.	126

Figure 10-1: 	Existing and planned FACTS devices in New England.	138

# Tables

Table 3-1 	Summary of Annual Gross Electric Energy Use and Gross Peak Demand Forecast
for New England and the States, 2017/2018 and 2026/2027	32

Table 3-2  	Summary of PDR and EE Forecast Annual Electric Energy Savings and Peak Demand
Reductions for New England and the States, 2017 and 2026 (GWh, MW)	35

Table 3-3 	New England States’ Annual and Cumulative PV Nameplate Capacities, 2017 to 2026 (MWAC)	37

Table 3-4 	Cumulative New England PV Forecast for Each Classification of PV, 2017 to 2026 (MW)	38

Table 3-5 	Summary of BTM PV Forecast Annual Electric Energy Savings and Peak Demand Reductions
for New England and the States, 2017 and 2026 (GWh, MW)	38

Table 3-6 	Percentage Growth Rates of the Gross and Net Forecasts of Annual
and Peak Electric Energy Use, 2017 to 2026	40

Table 3-7 	State and Systemwide Net Forecasts of Annual and Peak Electric Energy Use, 2017 (MWh, MW)	40

Table 3-8 	Net Forecast of Demand in RSP Subareas, 2017 to 2026 (GWh, MW)	41

Table 4-1  	Actual and Representative New England Net Installed Capacity Requirements
and Resulting Reserves (MW, %)	45

Table 4-2 	Actual and Representative LSRs and MCLs (MW)	46

Table 4-3 	Summary of the FCA Obligations at the Conclusion of Each Auction (MW)	47

Table 4-4 	Capacity Supply Obligation for New Capacity Procured during the Forward Capacity
Auctions (MW)	48

Table 4-5  	Future Systemwide Needs (MW)	51

Table 4-6 	Projected New England Operable Capacity Analysis for Summer, 2018 to 2026,
Assuming 50/50 and 90/10 Loads (MW)	53

Table 4-7 	Representative Future Operating-Reserve Needs in Major New England Import Areas (MW)	57

Table 4-8 	2017 Generating Capacity by Subarea, State, and Load Zone (MW, %)	60

Table 4-9  	2017 Summer Seasonal Claimed Capability for ISO New England Generating Resources,
by Assumed Operating Classification, Systemwide and by RSP Subarea (MW)	61

Table 5-1 	Estimated Cost of Reliability Projects as of June 2017 Plan Update (Million $)	82

Table 5-2 	Actual and Forecast Regional Transmission Service Rates, 2016 to 2021	83

Table 5-3 	ISO New England Transmission System Day-Ahead, Real-Time, and Total Congestion Costs
and Credits, 2003 to 2016 ($)	85

Table 5-4 	Net Commitment-Period Compensation by Type and Year (Million $)	86

Table 6-1 	Assumed External Interface Import Capability, Summer 2017 to Summer 2026 (MW)	95

Table 7-1 	Comparison of 2014, 2015, 2016, and 2017 Winter Futures Prices ($/MMBtu, $/MWh)	105

Table 7-2  	Summary of Pipeline Improvements Benefiting New England	109

Table 8-1 	New England Operating Nuclear Power Plants	120

# Executive Summary

Over the past 20 years, the New England region has benefited from the successful implementation of wholesale electricity markets and transmission planning and development that have significantly enhanced system reliability and improved overall market efficiency. New England has the resource base and transmission system needed to meet consumer demand for power at competitive prices. The overall system is evolving to a cleaner, hybrid grid, with low system emissions and the widespread development of renewable resources, including onshore and offshore wind generation, energy efficiency (EE), and photovoltaics (PV). Over the planning horizon, additional imports of Canadian hydroelectricity (hydro) and new technologies, such as smart meters, microgrids, and energy storage will likely develop and continue the trend toward a cleaner and more complex system.

As the system evolves, New England faces fuel-security challenges the region is striving to address. Over the past several years, the ISO has studied the capability of the region’s natural gas pipeline system to meet the demands for both heating and electric power generation on a peak day. Inadequate access to pipeline capacity and limited contracting for liquefied natural gas (LNG) can constrain the supply to natural-gas-fired generators, which contributed close to 50% of the region’s electric energy production in 2016. Additionally, dual-fuel generators, which can burn either oil or natural gas, face increasing statutory and regulatory hurdles for obtaining permits to use oil when they cannot get natural gas for compliance with emissions restrictions. Moreover, the regional dependency on natural-gas-fired resources continues to increase with new gas-fired generators replacing the retirements of nuclear and oil- and coal-fired generators. The reliability concerns remain particularly critical during peak winter demand conditions. For these reasons, the ISO is continuing to examine fuel security in the region to ensure that fuel is sufficient to generate electricity for meeting energy-use needs.

The ISO has also engaged with the New England Power Pool (NEPOOL) and New England states to investigate how to better integrate markets and public policy (IMAPP). The region is seeking a means to accommodate state-sponsored resources into the Forward Capacity Market (FCM) over time, while also preserving competitive capacity price signals for unsponsored resources needed for regional resource adequacy. In response, the ISO has put forward a framework for competitive auctions with sponsored policy resources (CASPR). The CASPR proposal will be reviewed with regional stakeholders during the remainder of 2017.

Certain resource choices will require new infrastructure. For example, the region may need to develop transmission if states decide to meet environmental policy goals using additional Canadian hydro and northern New England wind for delivery to population centers in southern New England. The widespread use of these and other asynchronous resources, as opposed to traditional synchronized “spinning” resources, requires physical system improvements that must meet observability and controllability requirements necessary for the secure operation and planning of the system. The changing nature of demand, especially the large-scale application of energy-efficiency measures, further complicates operating and planning issues.

The ISO continues to work with stakeholders to address the state of the system, regional challenges, and plans for addressing future issues, as the system becomes less predictable; supply resources, less controllable; and system operations, more complex. For all RSP17 analyses, the ISO used a number of assumptions, discussed with the PAC, which are subject to uncertainty as the system evolves over the planning period and the markets are enhanced to account for public policies. Changes in these assumptions could affect the results and conclusions of RSP17 analyses and ultimately influence the development of transmission and generation and demand resources. While each RSP is a snapshot in time, the planning process is continuous and flexible, and the ISO updates the results of planning activities as needed, accounting for the status of ongoing projects, studies, and new initiatives.

## Highlights and Key Results of the Regional System Plan

This section discusses the highlights of RSP17 and the results of various system and regional strategic planning studies and other materials. The RSP17 sections indicated below contain more details and links to definitions of terms and full citation information.

### Forecasts of the Annual and Peak Use of Electric Energy, Energy Efficiency, and Photovoltaic Capacity and Energy (Section 3)

Historical loads, seasonal weather patterns, and economic and demographic factors drive the forecasts included in RSP17 of the gross peak and gross annual demand for electric energy—regionwide and in individual states and subareas. RSP17 also summarizes nameplate and energy projections of photovoltaic resources participating in the wholesale electricity markets as well as behind-the-meter (BTM) PV. In addition, RSP17 includes forecasts of energy-efficiency resources, which together with behind-the-meter PV, reduce the forecasts of gross peak demand and the gross annual use of electric energy. The resultant net demand forecasts are key inputs for determining the region’s resource-adequacy requirements for future years, evaluating the reliability and economic performance of the electric power system under various conditions, and planning needed transmission improvements.

Key Section 3 results are as follows:

- The 10-year net energy for load, accounting for both EE and PV, is projected to decrease from 126,786 gigawatt-hours (GWh) in 2017 to 119,680 GWh in 2026, which represents a decline of 0.6% per year. The RSP17 50/50 net summer peak forecast is 26,482 megawatts (MW) for 2017, which declines to 26,310 MW for 2026. The 90/10 net summer peak forecast, which represents more extreme summer heat waves, is 28,865 MW for 2017 and grows by 0.1% per year to 29,021 MW in 2026.

- The gross peak summer load forecast grows by 1% over the 10-year planning horizon. The gross 50/50 peak load is 29,146 MW in 2017 and 31,820 MW in 2026; the gross 90/10 peak load is 31,529 MW in 2017 and 34,531 MW in 2026. The net energy for load gross value grows at 0.9% from 140,583 GWh in 2017 to 152,593 GWh in 2026.

- The EE forecast reduces the growth rate of the 10-year gross winter peak demand from 0.6% to a net annual value of −0.7%. The projected decline of the 90/10 net winter peak load from 21,895 MW to 20,630 MW helps mitigate winter reliability concerns.

- Regional passive demand resources and energy efficiency are expected to grow from 2,089 MW in 2017 to 4,475 MW in 2026. New England states’ annual investments in EE programs are expected to be more than $1 billion per year for 2017 through 2026. These EE investments remain a major factor in the expansion of passive demand resources in the region, which are projected to grow at an average rate of 265 MW per year across the 10-year horizon.

- Photovoltaic resources reached 1,918 MWac (nameplate rating) by the end of 2016 and produced 1,581 GWh. These resources are expected to grow to 4,733 MWac nameplate rating by 2026 and are forecast to produce 6,218 GWh. These totals include PV resources participating in the ISO wholesale markets (i.e., FCM resources and “energy-only” resources that receive energy market revenues but do not participate in the FCM) and BTM PV, which affects the net load forecast. The estimated reductions in summer seasonal peak loads due to BTM PV resources are 575 MW in 2017 and 1,035 MW in 2026; BTM PV does not reduce winter peaks because the peaks typically occur after dusk.

### Projections of the Systemwide Need for Capacity and Operating Reserves (Section 4)

Despite forecasts of declining load, the region must procure resources (i.e., generation, demand resources, and import capacity) to provide the capacity needed to meet the regional net Installed Capacity Requirement (ICR), which is based on gross load and behind-the-meter PV load reductions. The representative net ICR is expected to grow from 34,300 MW in 2022 to 35,700 MW in 2026.

Resource retirements are expected to be the key driver for new resources. New generators, which to date have been responding to price signals from the ISO’s wholesale markets, will help meet future requirements. Encouraged by public policies, the growth of EE resources will also help meet future requirements, while BTM PV will help reduce future requirements.

The FCM sends market signals for resource development. The tenth Forward Capacity Auction (FCA #10) procured sufficient resources to meet demand, with more than 1,400 MW of new generating capacity entering the market. Fewer new resources cleared FCA #11, but existing resources, new passive demand resources, and smaller generation additions were sufficient to meet expected systemwide demand for 2020/2021. Given the lower net load forecast, FCA #11 resources will be sufficient to meet the region’s projected net ICRs through 2026. The region is projected to have a minimum of 1,717 MW more resources than its net ICR requirements throughout the planning horizon, provided the existing fleet of resources continues to operate. However, the region will likely still need to rely on operating procedures that provide load and capacity relief every season from 2018 through 2026, especially under extremely hot and humid conditions, severe winter weather, and during infrastructure-outage conditions of both electric power and natural gas facilities. The region also will likely face additional retirements of aging oil, and coal-fired generation. In the shorter term, new demand resources have tended to be available as much as a year in advance of their expected in-service date, but historically, some generation has been delayed due to permitting and construction challenges.

When built, the new capacity procured through the FCAs will help replace retired generators. As of June 1, 2017, another 1,525 MW of coal- and oil-fired generation had retired, and another 677 MW of nuclear generation is expected to retire in 2019. As these traditional, non-gas-fired resources retire, sufficient resources will be needed to replace them. Most new resources seeking to participate in the wholesale electricity markets are natural-gas-fired generating units or renewables (wind and solar). Since FCA #9, approximately 2,300 MW of gas-fired combined-cycle and combustion-turbine plants have cleared the auctions, and approximately half the projects in the ISO Interconnection Request Queue (queue) are natural gas resources. The increasing amount of natural-gas-only generation puts greater demand on natural gas storage and delivery infrastructure, increasing the region’s fuel-security concerns, especially at winter seasonal peak conditions.

Capacity zone configurations provide market signals that encourage the locational development of resources to address transmission constraints, contingency losses of generation or transmission, and zonal import or export constraints. The capacity zones for FCA #12, which remain the same as for FCA #11, will model Southeastern New England (SENE) (i.e., the combined Northeast Massachusetts [NEMA]/Southeast Massachusetts [SEMA]/Rhode Island [RI] area) as an import-constrained zone and Northern New England as an export-constrained zone. RSP17 results show FCA #11 procured sufficient resources to meet resource adequacy criteria (i.e., local-sourcing requirements; LSRs) in import-constrained zones through 2026. The region, however, is under risk for further resource retirements that could change the modeling of capacity zones. The ISO will review any such major changes with regional stakeholders to determine whether a change to the zones used in future auctions is warranted.

The most reliable and economic place for resource development remains in southern New England near load centers. Repowered generating units at existing sites are favorably located. In addition, FCA clearing prices for new resources may be locked in for up to seven years, creating greater financial certainty. Existing fast-start resources near load centers in the Greater Southwest Connecticut, Greater Connecticut, and Boston areas provide flexibility. Representative Forward Reserve Market (FRM) analyses indicate that sufficient operating reserves exist in Greater Boston, Greater Connecticut, and Greater Southwest Connecticut as the result of generation development and transmission improvements planned for these areas by 2018 and 2019.

The 76 active projects in the interconnection queue total 12,899 MW, which comprise 6,427 MW of natural gas, 5,397 MW of wind generation, and 77 MW of batteries, with other types of renewable resources making up most of the remaining amount. Two-thirds of the wind capacity consists of onshore wind projects located in Maine, and the remaining wind resources are primarily offshore projects located off the southeast coast of Massachusetts. Nearly all the proposed natural-gas-fired resources are located in the southern New England states of Connecticut, Massachusetts, and Rhode Island.

The processing of the interconnection requests in New England has substantially progressed. With the exception of the northern and western areas of Maine (which have weak transmission infrastructure and have experienced a backlog of mostly wind interconnection requests), substantially all the generator interconnection requests made through 2015 have completed the system impact study phase or have moved to the Interconnection Agreement and commercialization phases. The ISO will be introducing an approach for studying  groups of resources in the interconnection queue seeking to interconnect to the system (i.e., clustering) under certain circumstances. Once implemented, the clustering approach will facilitate the completion of interconnection studies in Maine and, in the future, other areas of the system should similar conditions evolve.

### Transmission System Needs, Solutions, and Cost Considerations (Section 5)

As a result of transmission expansion in New England, the region has enjoyed a high level of reliability and resiliency, reduced air emissions, and lower wholesale market costs. The overall need for major additional reliability-based transmission projects is expected to decline over the planning horizon. The low growth of net peak load means it no longer is a major driver of the need for new reliability-based transmission projects. The development of FCM resources in favorable system locations also defers the need for major new projects.

The ISO has been working with regional stakeholders to review the criteria and several key input assumptions used in assessing overall system needs in the regional transmission planning process. Revised reliability standards that more closely align regional criteria with the latest North American Electric Reliability Corporation (NERC) transmission planning standards are now in place. In addition, the ISO has implemented a new probabilistic methodology to determine the amount of generation assumed out of service in its base case analyses. In combination, these changes will tend to defer or eliminate many transmission reliability needs.

RSP17 does show the continuing need for certain transmission system upgrades. Approximately $4 billion of new transmission upgrades are reported in RSP17, many of which are in siting or under construction. Looking ahead, integrating large-scale renewable energy resources, addressing the dynamic characteristics of load and the expansion of distributed resources, upgrading and refurbishing aging infrastructure, adding interchange capability with neighboring systems, and complying with new NERC standards are potential drivers for transmission.

#### Revisions to Transmission Planning Criteria and Assumptions

Significant changes to criteria and assumptions used in long-term reliability assessments are underway. Planning Procedure No. 3 (PP 3) now reflects the evolution of the NERC transmission planning standards. Updates to the Transmission Planning Technical Guide document new methodologies regarding the study assumptions used for generator dispatch scenarios based on probabilistic planning analysis. The Federal Energy Regulatory Commission (FERC) Order No. 1000 preserves the status for incumbents of both proposed and planned projects on the ISO’s Regional System Plan project list as of May 18, 2015. Material changes were made to the ISO’s planning process going forward. The Transmission Planning Process Guide now addresses the requirements for the ISO to solicit proposals for reliability projects with a greater than three-year planning need and to issue requests for proposals (RFPs) for market-efficiency projects or if federal, state, and local public policies drive transmission needs. The Order No. 1000 process for planning for public policy was used for the first time in 2017.

#### Elective Transmission Upgrades and Market-Efficiency Transmission Upgrades

In 2015, the ISO improved the interconnection queue process for elective transmission upgrades (ETUs), which market participants fund. ETUs are in various stages of development, and their completion would improve the ISO’s ability to import power from neighboring systems or relieve congestion for the large-scale development of onshore wind resources, which are predominantly located in Maine.

To date, the ISO has not identified the need for market-efficiency transmission upgrades (METUs), primarily designed to reduce the total net production cost to supply the system load, because of the following:

- Reliability transmission upgrades have resulted in significant market-efficiency benefits, particularly when out-of-merit operating costs were reduced.

- The development of economic and fast-start resources in response to the ISO’s wholesale electricity markets has also helped reduce congestion and Net Commitment-Period Compensation (NCPC).

The system overall lacks congestion and the need for make-whole payments. However in 2016, the ISO performed an economic evaluation of the potential benefits of upgrading the Keene Road Export Interface in 2020, 2025, and 2030. The needs assessment showed that increasing the capability across this interface would provide minimal savings in productions costs. After discussing these findings with stakeholders, the ISO determined that the savings in production costs were not sufficient to move forward with the Order No. 1000 Competitive Solutions Process.

#### Project Updates

Since 2002, 730 transmission project components have been placed in service across the region; another 137 project components have a status of planned, proposed, or under construction. Overall, the estimated investment in New England to maintain reliability was $8.4 billion from 2002 to June 2017, and another $4.03 billion is planned over the planning horizon. Since the publication of the 2015 Regional System Plan, the following major projects have been completed or are near completion:

- The Maine Power Reliability Program (MPRP) included the addition of significant new 345 kV and 115 kV transmission lines and new 345 kV autotransformers at key locations in Maine. The majority of MPRP is in service with the exception of the 115 kV Lewiston Loop projects, which are anticipated to be in service by mid-2018.

- The New Hampshire/Vermont 2020 Upgrades included the addition of a new 345/115 kV autotransformer, a new 230/115 kV autotransformer, several new 115 kV transmission lines, upgrades and rebuilds of several existing 115 kV lines, and several reactive device additions and substation upgrades. Most of the New Hampshire/Vermont 2020 Upgrades are in service with the exception of a new 115 kV line from Madbury to Portsmouth, which is anticipated to be in service by the end of 2018, and the addition of reactive support at the Amherst station in NH, which is the subject of an ongoing reevaluation due to concerns with its implementation.

- The Interstate Reliability Project (IRP) component of the New England East–West Solution (NEEWS) included the addition of significant 345 kV facilities in central Massachusetts, eastern Connecticut, and northern Rhode Island. The IRP was placed in service in December 2015.

In addition, the ISO identified projects in Southwest Connecticut, Greater Hartford Central Connecticut, Pittsfield and Greenfield, Greater Boston, and Southeast Massachusetts/Rhode Island (SEMA/RI) to solve system needs. The identification of long-term needs of SEMA/RI has been initiated. These reliability upgrade projects will bolster the 345 kV and 115 kV facilities of the New England transmission system. The ISO still must modify the Maine, New Hampshire, Western and Central Massachusetts, and the Eastern Connecticut area studies to reflect the revised study assumptions and processes.

### Interregional Planning Requirements and Activities (Section 6)

Through the Northeastern ISO/RTO Planning Protocol, ISO New England coordinates interregional studies, including interconnection queue studies, and satisfies interregional planning requirements under Order No. 1000. ISO New England, the New York ISO (NYISO), and PJM presented system needs to the Interregional Planning Stakeholder Advisory Committee, but the ISO/RTOs and stakeholders have not identified the need for new ties with New England. Planning activities also occur under the NPCC, NERC, and the Eastern Interconnection Planning Collaborative (EIPC).

### Fuel-Related Risks to System Reliability and Solutions (Section 7)

Although the region is projected to have sufficient resources to meet capacity requirements and enough transmission facilities to meet reliability criteria, fuel security remains a primary issue the region must resolve to meet its energy-supply needs. The limited availability of the natural gas transportation infrastructure to supply gas to generating units can present fuel-security risks to the region, especially during winter operating periods, even as New England’s current reliance on natural gas as a primary fuel for generating units is projected to grow. The ISO is assessing the extent of the region’s top reliability risks and developing solutions to ensure that system reliability can be sustained during extreme cold winter conditions beyond 2018.

#### Regional Dependence on Natural Gas as the Primary Fuel

New England relies on natural gas as a primary fuel for generating electric energy and is decreasing its reliance on oil and coal. In 2016, the approximate percentages of the region’s generation capacity and electric energy production by fuel type were as follows:

•	Natural gas: 44.5% capacity and 48.8% electric energy

•	Oil: 21.6% capacity and 0.9% electric energy

•	Coal: 6.4% capacity and 2.4% electric energy

•	Nuclear: 13.1% capacity and 31.0% electric energy

•	Hydro, pumped storage, and renewable resources: 14.4% capacity and 16.9% electric energy

The high regional use of natural-gas-fired generation reflects the addition of new, efficient natural-gas-fired units over the past 16 years; the generally low price of natural gas; and the greater ease with which these new, efficient units can comply with emissions requirements. This change in the fuel mix reduces the economic dispatch of older, less efficient oil- and coal-fired units. The recent retirements of non-natural-gas-fired generation, including nuclear units, further increases the regional dependence on natural-gas-fired generation.

Natural-gas-fired generation’s proportion of the system capacity mix is expected to grow from 44.5 % in 2017 to approximately 50.9% by 2020 and 56.0% by 2026. Further retirements of coal and oil generators are expected after 2020 due to generally low natural gas prices, renewable energy additions, and pending environmental regulations. The Pilgrim nuclear plant in Massachusetts is scheduled for retirement in 2019, and uncertainty surrounds the future of 3,300 MW from the region's remaining nuclear plants. Therefore, the current situation where natural gas fuel prices typically set the marginal price for wholesale electricity is projected to continue over the planning horizon.

#### The Fuel-Security Risk

The region’s reliance on the natural gas fuel-delivery system, however, exposes the regional electric power system to potential reliability problems and an associated increased cost of electricity when natural gas prices are high. This is the result of limited gas pipeline capacity in New England, largely built to serve natural gas customers other than electric power generators. Pipelines can be constrained any time of the year, but cold-weather conditions and the subsequent heavy demand for space heating fueled by natural gas can exacerbate regional fuel-security issues when electric power imports from neighboring regions may not be readily available.

Liquefied natural gas deliveries are also subject to risk. LNG is a global commodity imported to New England by ocean tanker, so it must be contracted for months in advance—an option most generators elect not to pursue. The arrivals of any spot LNG cargoes depend on global prices and vary monthly and from year to year; they also supply the entire Northeast and beyond—not just New England generators. Additionally, severe weather could prevent the timely arrival of ships. Constraints on the regional gas supply (pipeline gas plus LNG) also result in higher spot prices for the limited amounts of natural gas capacity available to generators within the New England region.

Renewable resources play a valuable, but limited, role in offsetting natural gas consumption because they may not be available during extreme weather conditions or be able to respond to emergencies on the system. Although renewable resources can offset some natural gas use during the winter, their contribution is limited under adverse winter weather conditions. Wind speeds are variable, creating a need for natural-gas-fired generators that can ramp up and down quickly to balance fluctuations in supply or demand. Most PV is neither visible to nor dispatchable by the ISO, and none of it helps meet peak winter demand, which happens after the sun has set. Moreover, winter conditions, with snowfall and fewer daylight hours, also dampen solar output.

Environmental permitting for dual-fuel capability is becoming more difficult, and when allowed, the energy production for back-up oil units is restricted, as is the case for the existing oil fleet. Limited access to dual-fuel capability across the region exacerbates progress on fuel-security issues.

#### Working toward a Solution

For well over a decade, the ISO has worked closely with the natural gas industry to improve coordination between gas and electricity sector operations and communications. More recently, the ISO’s Winter Reliability Program has provided incentives to a small number of generators to secure contracts for winter deliveries of oil and LNG, although the 2017/2018 program will be the last because the pay-for-performance market design (see Section 10.3.3.2) becomes effective in June 2018. The types of fuel contracts used in the Winter Reliability Programs, as well as the building of on-site LNG or compressed natural gas (CNG) storage, are among the options generators could invest in to satisfy upcoming performance requirements in the capacity market. The greater development of renewable resources, energy efficiency, imports from neighboring regions, and continued investment in gas-efficiency measures are also part of the solution.

The recent expansion of natural gas pipelines are meant to serve local distribution company (LDC) loads but also somewhat help the electric power sector. Spectra Energy put most of the AIM project (245,000 dekatherms/day [Dth/d]) into service on November 1, 2016, and subsequently put the final piece (the Hudson River crossing, which increased the total capability to New England by 342,000 Dth/d) into service on January 7, 2017. The Connecticut Expansion project (72,000 Dth/d) on the Tennessee Pipeline is planning for commercial operation by late 2017, and the Atlantic Bridge project is expected to be in service no earlier than late 2017. The realization of other pipelines in various stages of planning and siting seems unlikely, although their development would improve the availability of natural gas to generating units.

The ISO is conducting a fuel-security study in 2017 to examine how anticipated generating resource and fuel-mix combinations in the 2025 timeframe could impact reliable winter operations of the power system. The ISO will present the results of the analysis during the fourth quarter of 2017 and will work with stakeholders to identify any needs for market or operational changes.

### Existing and Pending Environmental Regulations, Emissions Analyses, and Other Studies (Section 8)

Federal air, water, endangered species, and greenhouse gas standards could affect the economic performance of nuclear, renewable, and fossil-fired (coal, oil, and natural gas) generators by imposing operational constraints and additional capital costs for environmental controls. Other state and regional air, water, and carbon dioxide (CO2) standards could require certain generators to minimize adverse environmental impacts, such as to reduce emissions, through the extended operation of pollution control devices or reduced electric energy production. Various elements of the power system are also subject to state, regional, federal, and international environmental land-use, permitting, and siting regulations, many of which have protracted review periods that can complicate or delay planning, development, or the implementation of proposed transmission and generation improvements.

The ISO continues assessing the potential impact of existing and proposed US Environmental Protection Agency (EPA) and state regulations on the operation of existing fossil steam units and other types of generation in the region. Several regulations are currently subject to delay and change, especially those by EPA. Affected capacity, however, will likely face compliance or retirement decisions later this decade, extending into the early part of the next decade. Many regional and state environmental regulations are likely to have a greater potential impact on generating units than national requirements. The ISO will update stakeholders on the status of existing and pending regulations, as follows, as well as the amounts of capacity affected by these regulations:

•	Existing fossil and nuclear capacity in New England may need to modify their cooling water intake structures for mitigating impingement.

•	Effluent Limitation Guidelines under the Clean Water Act (CWA) could affect steam generators.

•	EPA’s more stringent ozone standard and implementation regulations on fine particulate matter could require operational changes and potential pollution control retrofits at several fossil-fueled generators across New England.

•	The remaining coal- and residual oil-fired generators subject to the Mercury and Air Toxics Standards can comply by using air toxic pollution controls or low-capacity-factor exemptions.

•	Regardless of the outcome of the Clean Power Plan and other federal greenhouse gas requirements, fossil-fueled generators in the region remain subject to the Regional Greenhouse Gas Initiative and individual state carbon reduction requirements, such as the Massachusetts Global Warming Solutions Act.

As the result of a court decision, Massachusetts issued a final environmental regulation under the Global Warming Solutions Act in August 2017. As part of the state decision-making process, the ISO filed comments requesting that Massachusetts account for market and reliability considerations in its final decision.

The ISO has calculated historical systemwide emissions for several years. From 2014 to 2015, total nitrogen oxide (NOX) system emissions decreased by 8%, and sulfur dioxide (SO2) system emissions decreased 22%, primarily as a result of the 23% reduction of coal-fired generation in 2015. CO2 system emissions increased 3%, primarily because Vermont Yankee Nuclear Power Station retired in December 2014, decreasing the production from nonemitting generators by 15% in 2015. Emitting generators, largely those fueled by natural gas, which increased production by 12%, filled the resulting energy gap. Also, oil-fired generation increased 10% in 2015 because of relatively high natural gas prices and constraints on natural gas availability for power generation during the winter months.

The remaining system fuel mix and individual state environmental regulations affecting unit operations will have an impact on future emission levels. Additional nonfossil retirements, or delays in the development of low-emitting resources, could require a greater reliance on older, less-efficient fossil generators that generate higher emissions. Alternately, increased reliance on generators firing lower-emitting fuels, continued investment in energy efficiency, and the development of wind and photovoltaic resources, along with more imports from neighboring systems and the use of new environmental controls could decrease regional emissions further. Increased access to natural gas would also reduce regional emissions due to decreased reliance on oil-and coal-burning generation, but this would require improved delivery of natural gas to New England’s generating resources when the natural gas pipelines are constrained or increased LNG storage.

Difficulties in obtaining siting and permitting approvals present risks to infrastructure development. As a result, the region may be subject to construction delays of natural gas pipelines, generation resources, and transmission facilities.

FERC is pursuing an ongoing integrated relicensing review for several hydroelectric projects located on the Connecticut River. In addition to energy production, relicensing must take into consideration the requirements for protecting fish and wildlife and the recommendations of state and federal fish and wildlife agencies. The ISO is monitoring such proceedings to assess the impacts of operational restrictions, including the need for minimum flows without bypass turbines or spillage (i.e., water allowed to pass through the dam without generating electricity) on the ability of hydroelectric generators to offer regulation and reserve services.

### Integrating Renewable and Other Resources to Meet System Needs (Section 9)

Regional and industry efforts are assisting in integrating renewable resources, demand resources, and smart grid technologies into the system. The region boasts the first offshore wind resource in the Western Hemisphere; the Deepwater facility located near Block Island consists of five wind turbines with a total nameplate capacity of 30 MW.

The implementation of wind forecasting and dispatch have improved the operation of the system, although more work is needed to incorporate the effects of PV in short-term load-forecasting tools used by system operators and to fully address the potential reliability impacts of growing penetrations of PV. The addition of a clustering approach in the ISO’s interconnection procedures will facilitate the addition of new resources, including wind generation projects.

The ISO actively participates in developing industry standards, including IEEE 1547—Standard for the Interconnection of Distributed Resources with Electric Power Systems, which ensures that increased amounts of PV can be reliably and economically interconnected to the system. This standard is being revised and is scheduled for completion by December 2017.

The ISO also has conducted studies that inform developers and policymakers on how renewable resource development affects system performance. The Strategic Transmission Analysis: Wind Integration Study, for example, developed conceptual additions to the transmission system that would enable onshore wind resources to reliably serve load.

Economic studies have examined various scenarios of changes in transfer capabilities, resource expansion, and retirement scenarios. The 2015 economic studies of the Keene Road area, onshore wind expansion, and offshore wind expansion provided information to stakeholders on the potential need for transmission upgrades that would facilitate the development of wind resources. The studies showed little need for transmission improvements in the Keene Road area, but significant transmission improvements would be required to fully integrate the large-scale development of onshore wind in northern New England. Also, offshore wind development near SEMA/RI is well located near load centers and could avoid major transmission improvements if it is judiciously interconnected to the system.

The 2016 Economic Study provides a common framework for future discussions on several issues facing the New England region and the need for physical infrastructure and improvements to the wholesale electric markets. The study shows the following:

- Natural gas will remain an important source of fuel for electric power generators.

- Similar to the results for the 2015 Economic Studies, the development of resources close to load centers, such as at existing generation sites, requires little transmission development. Conversely, significant transmission investment will be required to incorporate large amounts of remote renewable energy resources.

- Meeting carbon emission targets may prove challenging for the New England region without the widespread development of renewable resources, EE, and interconnections with neighboring systems.

- Decreasing amounts of traditional resources (e.g., coal, oil, nuclear) and increasing amounts of renewable resources will require significant technical and structural changes, for example:

  - The equipment must meet established performance requirements, such as power factor, voltage and frequency response capability, and voltage and frequency ride-through capability.

  - The large-scale development of asynchronous resources will require the addition of special controls on power system resources and new transmission equipment.

  - Observability, controllability, and interconnection performance are key technical issues that must be addressed for distributed resources and the large-scale development of wind generation resources.

  - Energy market revenues to resources will decrease at the same time that major capital investment in resources will be needed.

Efficient energy-storage technologies, such as pumped-storage hydro and distributed storage; demand response resources; and changes in tie schedules can provide systemwide flexibility and facilitate the integration of variable energy resources (VERs), which provide clean energy but increase the need for regulation, ramping, and reserves. The region’s first grid-scale battery system, a 16 MW facility at Yarmouth Station, was placed on line in 2016. The efficient processing of interconnection requests for inverter-based technologies (e.g., wind, solar, and battery storage) is dependent on the provision of appropriately detailed models and robust equipment design.

### Multistate, ISO, and State Initiatives that Affect System Planning (Section 10)

The ISO continuously works with a wide variety of policymakers and other regional and interregional stakeholders on initiatives that influence electric power system planning. These groups include the New England Conference of Public Utilities Commissioners (NECPUC), the New England States Committee on Electricity (NESCOE), the New England Governors’ Conference, the Consumer Liaison Group (CLG), and others. The planning process has evolved in response to compliance with FERC orders and other policy developments, especially under FERC Order No. 1000. For example, Renewable Portfolio Standards promote the development of wind energy, and economic studies inform policymakers of the potential benefits of transmission expansion to support delivery of the wind energy. In addition, the states have encouraged the development of energy storage. Massachusetts set energy-storage targets and released a solicitation for up to $10 million of new projects.

Energy-storage technology is developing rapidly and is expected to have increased levels of participation in the markets over the planning period as costs associated with energy storage continue to decline and levels of variable renewable resources in the markets continue to increase. ISO New England assisted stakeholders with integrating energy-storage facilities by clarifying market rules in documents and providing training. The ISO continues identifying and addressing other issues to prepare for the large-scale development of energy-storage technology.

Several additional technology developments and challenges affect the planning of the New England region. As the power system evolves into a hybrid grid, the widespread addition of variable wind resources connected to the transmission system must coordinate with smart grid resources connected to the distribution system. Distributed energy storage, microgrids, and distributed generation provide local distribution system reliability and flexibility but pose reliability issues because the ISO cannot observe or control them. Other transmission and distribution technologies involve integrating smart grid equipment, improving operator awareness and system modeling through the use of high-speed cloud computing and phasor measurement units (PMUs), and using high-voltage direct-current (HVDC) facilities and flexible alternating-current transmission system (FACTS) devices. The ISO is working to improve the forecasting and dispatch of resources, enhance markets, and create new systems and tools to improve operational and planning study capabilities and performance.

Market designs will also be needed to help as New England transitions from a capacity-limited system to an energy-limited system. Appropriate price formation is critical to resource retention, investment, and performance incentives. As states contract for new resources, the wholesale market rules will be reviewed and revised as necessary to ensure efficient price formation.

## Key Findings and Conclusions

The 2017 Regional System Plan identifies system needs and plans for meeting these needs for 2017 through 2026. RSP17 also discusses risks to the regional electric power system; the likelihood, timing, and potential consequences of these risks; and mitigating actions. Some of the highlights of RSP17, as discussed in Section 12, are as follows:

- Forecasts of the regional net peak and annual energy show flat to negative growth resulting from the additions of PV and EE, which are reflected in the planning processes. Net peak demand, thus, is less of a key driver of new infrastructure needs.

- Needed capacity and operating reserves are provided through the wholesale markets, but resource retirements and the successful integration of variable energy resources pose future challenges to the reliable and economic operation of the system. Studies of expected system conditions show that developing new resources near load centers, particularly in the Southeastern New England zone, would provide the greatest reliability benefit.

- Transmission expansion in New England has improved the overall level of reliability and resiliency, reduced air emissions, and lowered wholesale market costs by nearly eliminating congestion (total for 2016 was $38. 9 million) and Net Commitment-Period Compensation ($32.6 million for voltage and second-contingency NCPC in 2016) (of the $5.4 billion total wholesale electricity markets in 2016). Generator retirements, off-peak system needs, the growth of asynchronous resources, and changes to mandatory planning criteria promulgated by NERC and NPCC will drive the need for longer-term transmission projects.

- RSP17 complies with the intraregional and interregional planning processes required by the ISO’s Open Access Transmission Tariff. Revisions to the ISO planning processes now reflect Order No. 1000 requirements, probabilistic study assumptions, and changes to national and regional criteria. Coordinated planning activities with other systems will continue growing, particularly to provide access to a greater diversity of resources, including hydro imports and variable energy resources, and to meet environmental compliance obligations.

- The regional reliance on natural-gas-fired generation, coupled with natural gas pipeline constraints and uncertain LNG deliveries can pose reliability issues and lead to price spikes in the wholesale electricity markets. The ISO is quantifying this risk in its fuel-security study, which will be discussed with stakeholders in the last quarter of 2017.

- Environmental regulations, other public policies, and economic considerations, all will affect the future mix of regional resources, such as to influence the retirement of oil and coal generators and the addition of natural-gas-fired generation. Delays in EPA regulations and changes in regional and state regulations, however, create additional uncertainty in the shorter term. Generators needing to make major investments in environmental compliance measures may become uneconomical and retire, but others can recover their capital investment by locking into FCM prices for up to seven years. Carbon emissions targets will likely be the key regional environmental constraint on energy production.

- The region has significant potential for developing renewable resources and is actively addressing several key technical challenges to the successful integration of these resources. For example, interconnection queue processes that use clustering studies and new forecasting methods will improve the reliable and economical operation of the system with increasing amounts of wind resources. The addition of renewables and continued low natural gas prices, among other factors, could dampen energy market prices, which may encourage the retirement of traditional generating units. The large-scale development of wind resources in northern New England would require major transmission system improvements.

- New England is transforming to a sustainable, hybrid grid that supports the connection of more renewable energy and the transition to the smart grid, which will make more effective use of distributed energy resources. Issues of observability and controllability of variable and distributed energy resources will need to be addressed to realize the full benefits of energy storage, microgrids, and smart grid technologies. The rapid implementation of revised interconnection standards for distributed resources, including the IEEE 1547, is vital for ensuring overall system reliability and facilitating the economical development of renewable resources, such as PV.

- Federal and state policies and initiatives will continue to affect the planning process, such as those promoting EE, PV, and wind resources. The ISO remains a leader in technological innovation, as shown by the widespread use of phasor measurement units, extensive application of flexible alternating-current transmission systems, and the implementation of state-of-the-art forecasting methods for wind resources and PV.

- The nature of the New England electric power system is undergoing major change as the system evolves from a capacity-limited system to an energy-limited system.

Through an open process, regional stakeholders and the ISO are addressing these issues, which could include further infrastructure development, as well as changes to the wholesale electricity market design and the system planning process. Through current and planned activities, the region is working toward meeting all challenges for planning and operating the system in accordance with all requirements.

# Overview of RSP17, the Power System,
and Regional System Planning

As the Regional Transmission Organization (RTO) for New England, ISO New England (ISO) operates the region’s electric power system, administers the region’s competitive wholesale electricity markets, and conducts the regional system planning process, which includes coordinating planning efforts with neighboring areas. The main objectives of the ISO’s system planning process are as follows:

- Identify system needs and potential solutions for ensuring the short-term and long-term reliability of the system

- Facilitate the efficient operation of the markets through resource additions and transmission upgrades that serve to reliably move power from various internal and external sources to the region’s load centers

- Provide information to regional stakeholders, who can further develop system improvements

To meet these objectives and in compliance with all portions of the ISO’s Transmission, Markets, and Services Tariff (ISO tariff), including the Open Access Transmission Tariff (OATT), the 2017 Regional System Plan (RSP17) describes the ISO’s ongoing system resource and transmission planning activities covering the 10-year period to 2026.

This section provides an overview of RSP17 and the ISO’s regional system planning process required by the ISO’s tariff. For background, the section also provides highlights of the power system and the wholesale electricity market structure in New England. A summary of the various regional subdivisions the ISO uses in system planning studies is also provided.

Throughout RSP17, italicized terms indicate that a definition for the term is included within the text or footnotes; links to other documents that more fully define the more complex terms are provided. Links to relevant technical reports; presentations; and other, more detailed materials also are included throughout the report. All website addresses are current as of the time of publication. Appendix A is a list of acronyms and abbreviations used in RSP17.

## Overview of the System Planning Process and RSP17

For maintaining the reliability of the New England power system, while promoting the operation of efficient wholesale electricity markets, the ISO and its stakeholders analyze the system and its components as a whole. They account for the performance of these individual elements and the many varied and complex interactions that occur among the components that affect the overall performance of the system.

Using information on defined system needs, a variety of established signals from ISO-administered markets, and other factors, stakeholders responsible for developing needed resources can assess their options for satisfying these needs and commit to developing market resource projects. For example, stakeholders can build a new power plant to provide additional system capacity and produce electric energy. Similarly, market participants can provide active demand resources and passive demand resources (PDRs) to meet capacity needs and reduce the amount of electric energy used. They also can develop and independently fund transmission upgrades to interconnect a merchant transmission facility (MTF) to the ISO system These upgrades and supply and demand resource alternatives could result in modifying, offsetting, or deferring proposed regulated transmission upgrades.

To the extent that stakeholder responses to market signals are not forthcoming or adequate to meet identified system needs, the planning process requires the ISO either to acquire transmission solutions through a competitive solicitation or to work with incumbent transmission owners to develop their own transmission solutions, depending on the identified year of need. All transmission upgrades must meet reliability performance requirements.

### Types of Transmission Upgrades

Attachment N of the OATT, “Procedures for Regional System Plan Upgrades,” defines several categories of transmission upgrades that can be developed to address various types of defined system needs, such as reliability and market efficiency. Transmission upgrades resulting from system changes proposed by individual proponents include, for example, generator-interconnection-related upgrades and elective transmission upgrades (ETUs). Section 5.5 discusses specific transmission upgrades.

#### Reliability Transmission Upgrades

Reliability transmission upgrades (RTUs) are necessary to ensure the continued reliability of the New England transmission system, in compliance with applicable reliability standards. An RTU also may provide market-efficiency benefits. To identify the transmission system facilities required to maintain reliability and system performance, the ISO evaluates the following factors using reasonable assumptions for forecasted load and the availability of generation and transmission facilities:

- Known changes in available supply resources and transmission facilities, such as anticipated transmission enhancements, considering elective transmission upgrades and merchant transmission facilities (see Section 2.1.1.5); the addition of demand resources or new or previously unavailable generators; generator retirements; and maintenance schedules, forced outages, and other unavailability factors

- Forecasted load, which accounts for growth, reductions, and redistribution throughout the grid

- Acceptable stability response

- Acceptable short-circuit performance

- Acceptable voltage levels

- Adequate thermal capability

- Acceptable system operability and responses (e.g., automatic operations, voltage changes)

#### Market Efficiency Transmission Upgrades

Market efficiency transmission upgrades (METUs) are primarily designed to reduce the total net production cost to supply the system load. The ISO categorizes a proposed transmission upgrade as a METU when it determines that the net present value of the net savings in the total cost to supply system load with and without the METU is greater than the net present value of the carrying cost of the identified upgrade. Analyses can include historical information from market reports and special studies, for example, and they report on cumulative net present value annually over the study period.

#### Public Policy Transmission Upgrades

A public policy transmission upgrade (PPTU) is an addition or upgrade designed to meet transmission needs driven by public policy requirements. The planning process for PPTUs includes opportunities for input from the New England States Committee on Electricity (NESCOE; see Section 10.2.1) and the Planning Advisory Committee (PAC; see Section 2.1.5). The ISO has initiated the public policy planning process, as set out in Attachment K, in accordance with its compliance filing for FERC Order No. 1000 (see Section 5.3).

#### Generator Interconnection Upgrades and Generator-Interconnection-Related Upgrades

A generator interconnection upgrade is an addition or modification to the New England transmission system for interconnecting a new or existing generating unit whose capability to provide energy or capacity is materially changing and increasing, whether or not the interconnection is for meeting the Network Capability Interconnection Standard or the Capacity Capability Interconnection Standard. Costs of generator-interconnection-related upgrades typically are allocated to the generator owner in accordance with the OATT.

#### Elective Transmission Upgrades and Merchant Transmission Facilities

An elective transmission upgrade is an interconnection or upgrade to the pool transmission facilities (PTFs) that are part of the New England transmission system and subject to the ISO’s operational control pursuant to an operating agreement. ETUs are independently developed facilities funded by one or more entities that have agreed to pay for all the costs of the upgrade and thus assume the full market risk of development.

The ETU process is the mechanism available to integrate new merchant transmission facilities into the regional transmission system. The process provides an option for project sponsors to propose, develop, and fund transmission development within New England or connecting to neighboring systems. Such transmission may result in strengthening electrically weak portions of the regional transmission network, enhancing generator deliverability, or facilitating the integration of renewable resources.

The ETU interconnection procedures have requirements and obligations similar to those of generators, so that ETUs can establish and maintain a meaningful position in the ISO Interconnection Request Queue (the queue). The ETU interconnection service allows certain tie lines with neighboring areas to be designed to deliver capacity into New England and have these interconnection service rights preserved as the New England system changes over time. The market rules ensure that these resources can deliver capacity and energy into the wholesale power markets.

### Transmission Planning Guides

The ISO developed guides that document both the implementation of the regional planning process described in Attachment K of the OATT and the associated technical assumptions. The Transmission Planning Process Guide (Process Guide) contains details on the existing regional system planning process and how transmission planning studies are performed through the open regional stakeholder process. It discusses the development of needs assessments and solution studies, including the opportunities for stakeholder involvement. The guide includes more recent modifications required by FERC Order No. 1000 for the use of qualified transmission project sponsors (QTPSs), planning for public policy, and interregional planning. The Transmission Planning Technical Guide (Technical Guide) describes the current standards, criteria, and assumptions used in transmission planning studies of the regional power system. Both guides include stakeholder input.

### Planning Studies Conducted for and Summarized in RSP17

The ISO continually conducts numerous regional and local-area studies during all stages of planning for ensuring the reliability of the power system. FERC, interregional entities, the states, and others, also sponsor planning initiatives for improving the power system and interregional coordination. Throughout RSP17, the ISO’s major studies and initiatives, as well as those conducted by others, both individually and jointly with the ISO, are summarized consistent with the steps used in the planning process:

- Ten-year load forecasts through 2026 of peak demand and the annual use of electric energy

- Regional passive demand resources for 2017 to 2020 and an energy-efficiency (EE) forecast from 2021 to 2026

- Forecasts of photovoltaic (PV) development in the region and its effect on annual energy use and summer peak demand

- The development of a net forecast

- Analyses of the amount, operating characteristics, and locations of needed capacity and operating reserves

- Analyses of Forward Capacity Market and locational Forward Reserve Market resources that meet system needs

- Implications of generator retirements on transmission system requirements and potential locations for developing new resources

- Assessments of systemwide and local-area needs (i.e., needs assessments), and transmission solutions to meet these needs (i.e., solution studies)

- Planning coordination studies and initiatives affecting the planning of the system

- Northeastern ISO/RTO planning coordination studies

- Eastern Interconnection Planning Collaborative (EIPC) activities

- Other joint planning studies with neighboring regions

- Discussions of regional strategic planning needs and solutions to resource adequacy and the regional fuel-security issue

- Effects of generator compliance with environmental regulations on generator operating requirements and the need for remediation measures

  - Operating and planning for expansion of renewable resources, including the potential need for transmission development for wind generation and the identification of interconnection issues for distributed generation (DG) and distributed energy resources (DERs).

  - Studies of the economic and environmental performance of the system for various future resource- and transmission-expansion scenarios

- ISO development and integration of new technologies and enhancements to operating and planning procedures to improve system reliability

- Federal, state, and regional initiatives and governmental activities and policies affecting the planning process

All RSP analyses, including the following, reflect the material effects of the energy-efficiency forecast and the PV forecast:

- Resource adequacy assessments

- Transmission needs assessments

- Transmission solutions studies

- Proposed Plan Application (PPA) studies

- System impact studies

- Economic studies

- Interregional studies

### Accounting for Uncertainty

Regional system planning must account for the uncertainty in assumptions made about the next 10 years stemming from changing demand, fuel prices, technologies, market rules, planning processes, and environmental requirements; the development and retirement of resources; the physical conditions under which the system might be operating; and other relevant events. The following major factors may vary RSP17 results and conclusions and ultimately affect the development and timing of needed transmission facilities and generation, demand, and market resources:

- Forecasts of demand, energy efficiency, and distributed generation, which are dependent on the economy, new building and federal appliance-efficiency standards, state goals for the implementation of EE and DG programs, and other considerations

- Resource availability, which is dependent on physical and economic parameters that affect the performance, development, and retirement of resources

- Environmental regulations and compliance strategies, which can vary with changes in public policies, economic parameters, and technology development

- The deployment of new technologies, which may affect the physical ability and economic viability of new types of power system equipment and the efficiency of operating the power system

- Fuel price forecasts, which change with world markets and infrastructure development

- Market rules and public policies, which can alter the development of market resources

- Siting and construction delays and changes to the system

While each RSP represents a snapshot in time, the planning process is continuous; the ISO revisits the results as needed when new information becomes available. The ISO has been improving the information provided to stakeholders, especially the required timing of transmission projects.

### Working with the Planning Advisory Committee and Other Committees

To conduct the system planning process, the ISO holds an open and transparent stakeholder forum with the Planning Advisory Committee (PAC). PAC membership is open to all and currently includes representatives from state and federal governmental agencies; participating transmission owners (PTOs); ISO market participants; other New England Power Pool (NEPOOL) members; consulting companies; manufacturers; and other organizations, such as universities and environmental groups. The PAC has met 30 times from fall 2015 to summer 2017 to discuss draft scopes of work, assumptions, and draft and final study results on a wide range of issues. In addition, subgroups of the PAC have discussed the energy-efficiency forecast, the distributed generation forecast, environmental issues, and economic studies.

Other committees are involved in the system planning process. The Reliability Committee (RC) provides advisory input on planning procedures, final Proposed Plan Applications, regional transmission cost allocations, and other activities that affect the design and oversight of reliability standards for the power system. The Transmission Committee (TC) provides advisory input on the general tariff provisions of the OATT and amendments to the Transmission Owner Agreement. The Markets Committee provides advisory input on changes proposed by the ISO to Market Rule 1 and market procedures. Stakeholders who advise ISO New England or its neighboring ISO/RTOs on system planning matters have the opportunity to meet as a unified group through the Interregional Planning Stakeholder Advisory Committee (IPSAC; see Section 6.5).

### Providing Information to Stakeholders

In addition to publishing the Regional System Plan and specific needs assessments and solutions studies to provide information to stakeholders, the ISO issues the RSP Project List. The list includes the status of transmission upgrades during a project’s lifecycle and is updated several times per year (see Section 5.9). RSP17 incorporates information from the June 2017 list.

Additionally, the ISO posts on its website detailed information supplemental to the RSP process, such as the Regional Electricity Outlook (REO), Annual Markets Report (AMR), Wholesale Markets Project Plan (WMPP), presentations, and other reports. The ISO also makes available databases used in its analyses and related information required to perform simulations consistent with FERC policies and the ISO Information Policy requirements pertaining to both confidential information and critical energy infrastructure information (CEII) requirements. Stakeholders can use this information and data to conduct their own independent studies.

### Meeting All Requirements

In addition to complying with the ISO tariff, which reflects the requirements of FERC orders, RSP17 complies with North American Electric Reliability Corporation (NERC) and Northeast Power Coordinating Council (NPCC) criteria and standards, as well as ISO planning and operating procedures. RSP17 also conforms to transmission owner criteria, rules, standards, guides, and policies consistent with NERC, NPCC, and ISO criteria, standards, and procedures.

## Overview of the New England Electric Power System

New England’s electric power grid has been planned and operated as a unified system of its participating transmission owners and market participants. The New England system integrates resources with the transmission system to serve all regional load regardless of state boundaries. Most of the transmission lines are relatively short and networked as a grid. Therefore, the electrical performance in one part of the system affects all areas of the system. Figure 2-1 shows key facts about the New England regional electric power system.

Figure 2-1: Key facts about New England’s electric power system and wholesale electricity markets.

Sources: The 2017–2026 Forecast Report of Capacity, Energy, Loads, and Transmission (2017 CELT Report) (May 1, 2017), http://www.iso-ne.com/system-planning/system-plans-studies/celt#, the RSP Project List for June 2017; and ISO market analysis and settlements data. ISO-NE Internal Market Monitor, 2016 Annual Markets Report (May 30. 2017), https://www.iso-ne.com/static-assets/documents/2017/05/annual_markets_report_2016.pdf; “Key Grid and Market Stats,” website (2017), https://www.iso-ne.com/about/key-stats.

Notes: Settlement-only resources (SORs) are less than 5 MW but not centrally dispatched by the ISO control room and not monitored in real time. The 2,800 MW of ISO demand resources do not include behind-the-meter photovoltaic resources (BTM PV) and energy efficiency provided by other customer-based programs outside the ISO markets or are otherwise unknown to the ISO. The total load on August 2, 2006, would have been 28,770 MW had it not been reduced by approximately 640 MW, which included a 490 MW demand reduction in response to ISO Operating Procedure No. 4 (OP 4), Action during a Capacity Deficiency; a 45 MW reduction of other interruptible OP 4 loads; and a 107 MW reduction of load as a result of price-response programs, which are outside of OP 4 actions. (OP 4 guidelines contain 11 actions in total that can be implemented individually or in groups, depending on the severity of the situation.) More information on OP 4 is available at http://www.iso-ne.com/static-assets/documents/rules_proceds/operating/isone/op4/op4_rto_final.pdf.

RSP17 includes both a NERC and an NPCC term to describe the electric power system. The NERC term, bulk electric system (BES), includes transmission elements operated at 100 kilovolts (kV) or higher and real power and reactive power resources connected at 100 kV or higher. A BES does not include facilities used in the local distribution of electric energy. The NPCC term, bulk power system, refers to the interconnected electrical system within northeastern North America comprising  system elements on which faults or disturbances can have a significant adverse impact outside of the local area. RSP17 describes how the ISO meets NERC and NPCC requirements to ensure compliance with planning and operating standards and criteria.

## Overview of the New England Wholesale Electricity Market Structure

New England’s wholesale electricity markets facilitate the buying, selling, and transporting of wholesale electricity, as well as ensure proper system frequency and voltage, sufficient future capacity, seasonal and real-time reserve capacity, and system restoration capability after a blackout. Stakeholders also have the opportunity to hedge against the costs associated with transmission congestion. As shown in Figure 2-1, in 2016, approximately 400 market participants completed transactions in New England’s wholesale electricity markets totaling $5.4 billion. The wholesale electricity markets and market products in New England are as follows:

- Day-Ahead Energy Market—allows market participants to secure prices for electric energy the day before the operating day and hedge against price fluctuations that can occur in real time.

- Real-Time Energy Market—coordinates the dispatch of generation and demand resources to meet the instantaneous demand for electricity.

- Forward Capacity Market (FCM)—ensures the sufficiency of installed capacity, which includes demand resources, to meet the future demand for electricity by sending appropriate price signals to attract new investment, maintain existing investment, and encourage capacity to perform both where and when needed, including during shortage events.

- Financial Transmission Rights (FTRs)—allows participants to hedge against the economic impacts associated with transmission congestion and provides a financial instrument to arbitrage differences between expected and actual day-ahead congestion.

- Ancillary services

- Regulation Market—compensates resources that the ISO instructs to increase or decrease output moment by moment to balance the variations in demand and system frequency to meet industry standards.

- Forward Reserve Market (FRM)—compensates generators for the availability of their operational capacity not generating electric energy but able to be converted into electric energy within 10 or 30 minutes when needed to respond to system contingencies, such as unexpected outages.

- Real-time reserve pricing—compensates participants with on-line and fast-start generators for the increased values of their electric energy when the system or portions of the system are short of reserves. It also provides efficient price signals to generators when redispatch is needed to provide additional reserves to meet requirements.

- Voltage support—compensates resources for maintaining voltage-control capability, which allows system operators to maintain transmission voltages within acceptable limits.

One key feature of the region’s wholesale electricity markets is locational marginal pricing for electric energy, which reflects the variations in supply, demand, and transmission system limitations effectively at every location where electric energy enters or exits the wholesale power network. In New England, wholesale electricity prices are set at over 1,000 pricing points (i.e., pnodes) on the power grid. If the system were entirely unconstrained and had no losses, all locational marginal prices (LMPs) would be the same, reflecting only the cost of serving the next megawatt increment of load by the generator with the lowest-cost electric energy available, which would be able to flow to any point on the transmission system. LMPs would differ among the pnodes if each location’s marginal cost of congestion and marginal cost of line losses differed.

Transmission system constraints, which limit the flow of the least-cost generation and create the need to dispatch more costly generation, give rise to the congestion component of an LMP. Line losses are caused by physical resistance and subsequent heat loss in the transmission system as electricity travels through transformers, reactors, and other types of equipment, resulting in less power being withdrawn from the system than was injected. Line losses and their associated marginal costs are inherent to transmission lines and other grid infrastructure as electric energy flows from generators to loads. As with the marginal cost of congestion, the marginal cost of losses affects the amount of generation that must be dispatched. The ISO operates the system to minimize total system costs, while recognizing physical limitations of the system.

The ISO annually assesses the wholesale electricity markets to better understand problems to be addressed and to determine whether the market design or other measures warrant any changes. The ISO uses this information and the results of RSP studies to develop market design changes through an open stakeholder process.

## Overview of System Subdivisions Used for Analyzing and Planning the System

To assist in modeling, analyzing, and planning electricity resources in New England, the region and the system have been subdivided in various ways. These categories are included in the discussions throughout the RSP and are summarized below.

The ISO has established 13 subareas of the region’s electric power system. These subareas form a simplified model of load areas connected by the major transmission interfaces across the system. The simplified model illustrates possible physical limitations to the reliable and economic flow of power that can evolve over time as the system changes.

Figure 2-2 shows the ISO subareas and three external balancing authority areas. While transmission planning studies and the real-time operation of the system use more detailed models, the subarea representation shown in Figure 2-2 is suitable for some RSP17 studies of resource adequacy, operating-reserve requirements, production cost, and environmental emissions.

|  | Subarea Designation | Region or State |
| --- | --- | --- |
|  | BHE | Northeastern Maine |
|  | ME | Western and central Maine/ Saco Valley, New Hampshire |
|  | SME | Southeastern Maine |
|  | NH | Northern, eastern, and central New Hampshire/eastern Vermont and southwestern Maine |
|  | VT | Vermont/southwestern New Hampshire |
|  | Boston (all capitalized) | Greater Boston, including the North Shore |
|  | CMA/NEMA | Central Massachusetts/ northeastern Massachusetts |
|  | WMA | Western Massachusetts |
|  | SEMA | Southeastern Massachusetts/ Newport, Rhode Island |
|  | RI | Rhode Island/bordering Massachusetts |
|  | CT | Northern and eastern Connecticut |
|  | SWCT | Southwestern Connecticut |
|  | NOR | Norwalk/Stamford, Connecticut |
|  | NB, HQ, and NY | New Brunswick (Maritimes), Hydro­Québec, and New York external balancing authority areas |

Figure 2-2: RSP17 geographic scope of the New England electric power system.

Notes: Some RSP studies investigate conditions in Greater Connecticut, which combines the NOR, SWCT, and CT subareas. This area has similar boundaries to the State of Connecticut but is slightly smaller because of electrical system configurations near the border with western Massachusetts. Greater Southwest Connecticut includes the southwest and western portions of Connecticut and consists of the NOR and SWCT subareas. NB includes New Brunswick, Nova Scotia, and Prince Edward Island (i.e., the Maritime provinces) plus the area served by the Northern Maine Independent System Administrator (USA).

The system’s pricing points include individual generating units, load nodes, load zones (i.e., aggregations of load pnodes within a specific area), and the Hub. The Hub is a collection of 32 locations in central New England where little congestion is evident. It typically has a price intended to represent an uncongested price for electric energy, which is used as a price index and point of exchange for bilateral transactions in the energy market. The Hub also facilitates energy trading and enhances transparency and liquidity in the marketplace. In New England, generators are paid the LMP for electric energy at their respective nodes, and participants serving demand pay the price at their respective load zones.

New England is divided into eight electric energy load zones used for wholesale energy market settlement: Maine (ME), New Hampshire (NH), Vermont (VT), Rhode Island (RI), Connecticut (CT), Western/Central Massachusetts (WCMA), Northeast Massachusetts and Boston (NEMA), and Southeast Massachusetts (SEMA). Import-constrained load zones are areas within New England that do not have enough local resources and transmission-import capability to serve local demand reliably or economically. Export-constrained load zones are areas within New England where the available resources, after serving local load, exceed the areas’ transmission capability to export the excess electric energy. Reliability regions, which reflect the operating characteristics of, and the major constraints on, the New England transmission system, can have the same boundaries as load zones.

A capacity zone is a geographic subregion of the New England Balancing Authority Area that may represent load zones that are export constrained, import constrained, or contiguous—neither export nor import constrained. The Forward Capacity Auctions (FCAs) use capacity zones, which are subject to annual review. For both FCA #11 and FCA #12, three capacity zones are modeled, specifically:

- Southeastern New England (SENE) as an import-constrained zone, which includes the area within the Southeast New England interface, comprising the RSP ‘bubbles” (as shown in Figure 2-2) for SEMA, RI, and BOSTON

- Northern New England (NNE) as an export-constrained zone, which includes the area north of the North–South interface, comprising the RSP bubbles for BHE, ME, SME, NH, and VT

- Rest-of-Pool (ROP)

Other capacity zones the ISO considers to represent import- and export-constrained areas or contiguous areas are as follows:

- CT—the area within the Connecticut import interface, including the RSP bubbles for CT, SWCT, and NOR plus the Scitico substation served from western Massachusetts

- NEMA/Boston—the area within the Boston import interface, comprising the RSP bubble for BOSTON

- SEMA/RI—the area within the SEMA/RI import interface, comprising the RSP bubbles for SEMA and RI

- Maine—includes the area north of the ME-NH interface, comprising the RSP bubbles for BHE, ME, and SME

The region also currently has four reserve zones—Greater Connecticut; Greater Southwest Connecticut (SWCT); NEMA/Boston; and the rest of the system (Rest-of-System, ROS), which excludes the other, local reserve zones.

Additionally, the region is divided into 19 demand-resource dispatch zones, which are groups of nodes used to dispatch real-time demand-response (RTDR) resources smaller than 5 MW. These allow for a more granular dispatch of active demand resources at times, locations, and quantities needed to address potential system problems without unnecessarily calling on other active demand resources. Figure 2-3 shows the dispatch zones the ISO uses to dispatch FCM active demand resources.

Figure 2-3: Active-demand-resource dispatch zones in the ISO New England system.

# Forecasts of New England’s Peak Demand, Annual Use of Electric Energy, Energy Efficiency, and Distributed Generation

This section discusses the individual forecasts of gross demand, energy efficiency (EE), and photovoltaics (PV) for 2017 through 2026. Energy efficiency is considered a resource, and behind-the-meter (BTM) distributed generation is considered a reduction in demand, but for study purposes, their combined growth reduces the forecasts of gross peak demand and the gross annual use of energy. These resultant net demand forecasts provide key inputs for determining the region’s resource adequacy requirements for future years (see Section 4), evaluating the reliability and economic performance of the electric power system under various conditions (Section 9.4), and planning needed transmission improvements (Section 5). This section also discusses the application of the net peak demand and the net annual energy forecasts to planning studies.

The methodology for forecasting the gross demand, energy efficiency, and photovoltaic installations in RSP17 are generally similar to RSP15’s methodology. The historical loads and both the economic and demographic factors drive the forecasts of the gross peak and gross annual demand for electric energy, New England-wide and in individual states and subareas. Public policies are key inputs to the growth of energy-efficiency and photovoltaic resources for the 10-year RSP planning horizon. The EE forecast reflects participation in the ISO’s Forward Capacity Market. The RSP17 PV forecast reflects PV participation in the wholesale energy markets, updated policy information, and recent installation trends.

## ISO New England Gross Demand Forecasts

The ISO gross demand forecasts are estimates of the amount of electric energy the New England states will need annually and during seasonal peak hours. This year’s gross demand forecast horizon runs from 2017 through winter 2026/2027. Each forecast cycle updates the data for the region’s historical annual use of electric energy and peak loads, incorporating the most recent economic and demographic forecasts, and making adjustments for resettlement that include meter corrections.

The seasonal gross peak load and gross energy-use forecast, as published in the 2017–2026 Forecast Report of Capacity, Energy, Loads, and Transmission (2017 CELT Report) and used for planning studies, fully accounts for historical energy efficiency not part of the EE forecast and future federal appliance standards. The gross forecast does not reflect reductions in peak demand and energy use that will result from the passive demand resources (PDRs) that clear the Forward Capacity Auctions, the energy-efficiency forecast (described in Section 3.2), or the  behind-the-meter PV forecast (see Section 3.3). Other types of behind-the-meter distributed resources not participating in the FCM, however, are included in the gross load forecast as part of the historical growth of these types of resources.

The price of electricity and other economic and demographic factors drive the annual consumption of electric energy and the growth of the seasonal peak. Compared with the economic forecast in RSP15, the forecast in RSP17 shows less growth throughout the forecast horizon. The RSP17 forecast continues to use real gross state product (GSP) for energy forecasting, with federal efficiency standards subtracted from the energy forecast.

Table 3-1 summarizes the ISO’s forecasts of gross annual electric energy use and gross seasonal peak load (50/50 and 90/10) for New England overall and for each state. RSP17 forecasts of gross annual energy use, and both summer and winter gross seasonal peak conditions, are lower than those published in RSP15. Compared with the RSP15 forecast, the RSP17 50/50 load forecast for gross summer peak demand is 229 megawatts (MW) lower in 2017 and 682 MW lower in 2024.

Table 3-1
Summary of Annual Gross Electric Energy Use and Gross Peak Demand Forecast
for New England and the States, 2017/2018 and 2026/2027

| State(a) | Net Energy for Load (1,000 MWh) |  |  | Summer Peak Loads (MW) |  |  |  |  | Winter Peak Loads (MW) |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | 50/50 |  | 90/10 |  | CAGR(b) | 50/50 |  | 90/10 |  | CAGR(b) |
|  | 2017 | 2026 | CAGR(b) | 2017 | 2026 | 2017 | 2026 |  | 2017/18 | 2026/27 | 2017/18 | 2026/27 |  |
| CT | 34,128 | 36,018 | 0.6 | 7,546 | 7,960 | 8,220 | 8,696 | 0.6 | 5,740 | 5,892 | 5,928 | 6,080 | 0.3 |
| ME | 12,683 | 13,910 | 1.0 | 2,154 | 2,350 | 2,293 | 2,498 | 1.0 | 2,011 | 2,137 | 2,067 | 2,193 | 0.7 |
| MA | 65,274 | 72,227 | 1.1 | 13,693 | 15,255 | 14,732 | 16,462 | 1.2 | 10,661 | 11,428 | 10,987 | 11,753 | 0.8 |
| NH | 12,409 | 13,311 | 0.8 | 2,579 | 2,822 | 2,795 | 3,070 | 1.0 | 2,055 | 2,120 | 2,141 | 2,207 | 0.3 |
| RI | 9,229 | 9,836 | 0.7 | 2,058 | 2,253 | 2,312 | 2,553 | 1.1 | 1,453 | 1,504 | 1,479 | 1,530 | 0.4 |
| VT | 6,859 | 7,291 | 0.7 | 1,114 | 1,178 | 1,158 | 1,231 | 0.7 | 1,106 | 1,162 | 1,124 | 1,180 | 0.5 |
| ISO | 140,583 | 152,593 | 0.9 | 29,146 | 31,820 | 31,529 | 34,531 | 1.0 | 23,029 | 24,244 | 23,727 | 24,942 | 0.6 |

- A variety of factors cause state growth rates to differ from the overall growth rate for New England.

- “CAGR” stands for compound annual growth rate. CAGR values shown for the summer and winter peak loads are for the 90/10 forecasts.

Net energy for load (NEL) is the generation output within an area, accounting for electric energy imports from other areas and electric energy exports to other areas. It also accounts for system losses and excludes the electric energy used to operate pumped-storage hydroelectric plants. The compound annual growth rate (CAGR) for the ISO’s electric energy use is 0.9% for 2017 through 2026, 1.0% for the summer peak, and 0.6% for the winter peak. The systemwide load factor (i.e., the ratio of the average hourly load during a year to peak hourly load) based on the 50/50 forecast declines over the forecast horizon, from 55.1% in 2017 to 54.7% in 2026.

Figure 3-1 shows the ISO’s actual gross summer peak demand (i.e., the load reconstituted to include the megawatt reduction attributable to ISO New England Operating Procedure No. 4 [OP 4], Action during a Capacity Deficiency, and FCM passive demand resources), the 50/50 gross load forecast, and the 90/10 gross load forecast. The actual gross load has been near or has exceeded the 90/10 forecast six times over the last 25 years because of hot and humid weather conditions, and it has been near or above the 50/50 gross forecast 11 times during the same period.

Figure 3-1: The ISO’s actual summer peak loads (i.e., reconstituted to include the megawatt reductions from OP 4 actions, FCM passive demand resources, and BTM PV) and the 50/50 and 90/10 forecasts, 1992 to 2016 (MW).

Note: The forecasted load values are the first-year values of the CELT forecast for each year. For example, the forecasted loads for 2016 are the loads for the first year of the 2016 CELT Report.

## Energy-Efficiency Forecast for New England

The FCM provides the ISO with a comprehensive understanding of the savings in energy use over the FCM horizon. RSP17 uses qualified EE resources as a short-term projection of EE development for 2017 through 2020. (See Section 4.1.3 for the summary of new capacity supply obligations [CSOs] for passive demand resources, which may be different from the qualified EE resources due to market considerations.) The ISO’s regional energy-efficiency forecast, as summarized in this section for 2021 through 2026, is part of ongoing efforts to collect and analyze data in support of the long-term impacts of state-sponsored energy-efficiency programs on future demand. Individual program administrators and state regulatory agencies provide the ISO with the EE program performance and budget data used to create the forecast for 2021 to 2026. The ISO’s Energy-Efficiency Forecast Working Group assesses the forecast assumptions and offers input.

The final EE forecast for 2021 to 2026 projects the growth of annual savings in the average, total, and peak energy use for the region and each state. The results, which are based on an average annual program spending rate among the six states of $1.194 billion per year, show that the regional annual average savings in energy use attributable to new energy-efficiency measures (i.e., not cumulative from EE savings before 2021) is 1,923 gigawatt-hours (GWh). The forecast for the total savings in energy use from the growth of EE projected for 2021 to 2026 is 11,537 GWh. The states’ growth of annual average savings in energy use ranges from a low of 57 GWh in New Hampshire to a high of 1,148 GWh in Massachusetts.

Table 3-2 shows the growth of regional passive demand resources and EE for 2017 through 2026. The ISO’s FCM-qualified EE resources are for 2017 to 2020, and the EE forecast is for 2021 to 2026. Over the entire forecast period, the regional annual peak demand is estimated to decrease by an average of 265 MW as a result of passive demand resources and energy efficiency. The forecast for the total decrease in summer peak demand attributable to new PDRs and EE is 2,386 MW from 2017 to 2026. The states’ growth of the annual average savings in peak demand ranges from a low of 9 MW in New Hampshire to a high of 161 MW in Massachusetts.

Table 3-2 
Summary of PDR and EE Forecast Annual Electric Energy Savings and Peak Demand Reductions 
for New England and the States, 2017 and 2026 (GWh, MW)

| State | Annual Energy Savings (GWh) |  |  | Summer Peak Demand Reductions (MW) |  |  | Winter Peak Demand Reductions (MW) |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 2017 | 2026 | CAGR(a) | 2017 | 2026 | CAGR(a) | 2017 | 2026 | CAGR(a) |
| CT | 2,357 | 5,705 | 10.3 | 421 | 930 | 9.2 | 270 | 917 | 14.6 |
| ME | 1,199 | 1,901 | 5.3 | 184 | 240 | 3.0 | 171 | 215 | 2.6 |
| MA | 5,893 | 16,158 | 11.9 | 1,077 | 2,568 | 10.1 | 1,006 | 2,475 | 10.5 |
| NH | 542 | 1,046 | 7.6 | 97 | 177 | 7 | 79 | 143 | 6.8 |
| RI | 1,020 | 2,436 | 10.2 | 179 | 391 | 9.1 | 175 | 393 | 9.4 |
| VT | 892 | 1,330 | 4.5 | 132 | 169 | 2.8 | 131 | 169 | 2.9 |
| ISO | 11,903 | 28,575 | 10.2 | 2,089 | 4,475 | 8.8 | 1,832 | 4,312 | 10.0 |

- “CAGR” stands for compound annual growth rate.

## Distributed Generation Forecast for New England

Small-scale, distributed photovoltaic generation resources have been growing significantly in New England since 2012. BTM PV distributed generation reduces regional annual energy use and summer peak demand, as accounted for in the ISO’s PV nameplate capacity forecast and PV energy forecast.

### Distributed Generation Forecast Working Group

In 2013, the ISO established the Distributed Generation Forecast Working Group (DGFWG) to support the DG forecast process. This support entails the collection of policy information from state agency representatives with strong knowledge of DG programs and DG interconnection data from electric power distribution companies and DG program administrators.

Because PV facilities constitute the largest segment of DG resources throughout New England and have been growing rapidly in recent years, the ISO’s analysis of DG and the DG forecast focuses exclusively on the growth of photovoltaics. However, the ISO continues to monitor the growth of non-PV DG through the DGFWG to determine whether separate forecasts of these resources may be warranted.

### PV Nameplate Capacity Forecast

Using a policy-based approach, the ISO develops a nameplate PV forecast based on recent historical installation trends and updated state and federal policy information. Table 3-3 lists the state-by-state forecast of annual and cumulative PV nameplate capacities, after applying discount factors, through the 10-year planning horizon. These projections include all existing and future PV in the FCM, as well as PV that does and does not participate in the ISO’s wholesale energy markets and that reduces the load the ISO observes. To avoid double counting, the ISO classifies the forecast into three different types of PV, each of which receives a different treatment in system planning studies:

- FCM resources with capacity supply obligations

- Energy-only resources (EORs), which are generation resources that participate in the wholesale energy markets and receive energy market revenues but choose to not participate in the FCM

- Behind-the-meter resources (BTM PV)

System planning studies treat PV resources participating in the ISO wholesale markets as resources with sizes and locations visible to the ISO. PV resources with FCM capacity supply obligations are considered either generators or demand resources. Energy-only resources are registered in the ISO’s Customer Asset Management System (CAMS) and collect energy payments, but they do not necessarily supply the ISO with generator characteristics. Both FCM and energy-only resources are market resources that do not reduce the gross demand forecast.

Table 3-3
New England States’ Annual and Cumulative PV Nameplate Capacities, 2017 to 2026 (MWAC)

| Year | Annual Sum of States | Annual Total Capacities (MW, AC nameplate rating) |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | CT |  | MA |  | ME |  | NH | RI | VT |
| Through 2016 | 1,918.0 |  | 281.5 |  | 1,324.8 |  | 22.1 | 54.3 | 36.8 | 198.4 |
| 2017 | 497.9 |  | 132.8 |  | 273.9 |  | 6.8 | 18.1 | 41.3 | 25.0 |
| 2018 | 478.2 |  | 132.8 |  | 260.2 |  | 6.8 | 12.0 | 41.3 | 25.0 |
| 2019 | 371.8 |  | 132.8 |  | 164.4 |  | 6.8 | 7.4 | 35.3 | 25.0 |
| 2020 | 286.6 |  | 58.9 |  | 160.0 |  | 6.2 | 7.2 | 31.8 | 22.5 |
| 2021 | 249.6 |  | 44.7 |  | 155.6 |  | 5.8 | 7.0 | 15.2 | 21.3 |
| 2022 | 239.8 |  | 43.5 |  | 151.1 |  | 5.8 | 6.8 | 11.3 | 21.3 |
| 2023 | 233.6 |  | 42.2 |  | 146.7 |  | 5.8 | 6.6 | 11.1 | 21.3 |
| 2024 | 156.3 |  | 40.9 |  | 71.1 |  | 5.8 | 6.4 | 10.8 | 21.3 |
| 2025 | 152.4 |  | 39.6 |  | 68.9 |  | 5.8 | 6.2 | 10.6 | 21.3 |
| 2026 | 148.5 |  | 38.4 |  | 66.7 |  | 5.8 | 6.0 | 10.4 | 21.3 |
| Total | 4,732.7 |  | 988.2 |  | 2,843.3 |  | 83.7 | 138.2 | 255.9 | 423.4 |

System planning studies, including Installed Capacity Requirement (ICR) calculations (see Section 4.1.1), consider behind-the-meter PV as part of the demand forecast. BTM PV facilities do not participate in the ISO markets and are not registered in CAMS. For this reason, the ISO has an incomplete set of information on these resource characteristics, including their energy production data. Figure 3-2 illustrates the classification of the 2017 PV forecast into FCM, non-FCM energy-only resources, and BTM PV. Table 3-4 shows the data for this figure.

Figure 3-2: Cumulative New England PV forecast for each classification of PV, 2017 to 2026 (MW).

Notes: The FCM category reflects the PV nameplate of all or portions of the FCM-qualified resources. The FCM value is held constant for years beyond FCA #11 (see Section 4.1.3). The net load forecast reflects reductions of BTM PV.

Table 3-4
Cumulative New England PV Forecast for Each Classification of PV, 2017 to 2026 (MW)

| PV Category | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| FCM PV | 27.4 | 27.4 | 64.4 | 149.2 | 165.9 | 165.9 | 165.9 | 165.9 | 165.9 | 165.9 | 165.9 |
| Non-FCM, Energy-Only PV | 605.9 | 736.8 | 839.1 | 847.9 | 926.0 | 1,003.5 | 1,076.8 | 1,148.1 | 1,186.2 | 1,223.1 | 1,259.0 |
| Behind-the Meter PV | 1,284.6 | 1,651.7 | 1,990.6 | 2,268.8 | 2,460.6 | 2,632.7 | 2,799.1 | 2,961.5 | 3,079.7 | 3,195.2 | 3,307.8 |

### PV Energy Forecast

Using the nameplate PV forecast, historical installation rates, and performance based on a statistical sample of PV production data, the ISO estimates a PV energy forecast. Beginning with the 2016 forecast, the ISO has estimated BTM PV’s summer peak load reductions along with the growth of PV penetrations. Higher PV penetrations account for diminishing PV production overall because they cause peak loads to occur later in the afternoon when PV is less effective at reducing the load. Table 3-5 shows the values of regional annual energy savings and summer peak demand reductions from the 2017 forecast of BTM PV.

Table 3-5
Summary of BTM PV Forecast Annual Electric Energy Savings and Peak Demand Reductions 
for New England and the States, 2017 and 2026 (GWh, MW)

| State | Annual Energy Savings (GWh) |  |  | Summer Peak Demand Reductions (MW) |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | 2017 | 2026 | CAGR(a) | 2017 | 2026 | CAGR(a) |
| CT | 435 | 1,273 | 12.7 | 133 | 304 | 9.6 |
| ME | 33 | 107 | 14.0 | 10 | 26 | 11.0 |
| MA | 1,046 | 2,102 | 8.1 | 317 | 501 | 5.2 |
| NH | 74 | 164 | 9.2 | 22 | 39 | 6.3 |
| RI | 29 | 143 | 19.4 | 9 | 34 | 16.1 |
| VT | 278 | 549 | 7.9 | 84 | 131 | 5.1 |
| ISO | 1,894 | 4,338 | 9.6 | 575 | 1,035 | 6.7 |

(a) “CAGR” stands for compound annual growth rate.

## The Net Demand Forecast

The net forecast is the gross demand forecast lowered by the forecasted BTM PV load reductions, the existing FCM-qualified passive demand resources projected for 2017 to 2020, and the 2021 to 2026 energy-efficiency forecast. The net forecast is detailed in Figure 3-3, Figure 3-4, and Table 3-6 to Table 3-8. Figure 3-3 shows the gross annual energy-use forecast (NEL), minus the BTM PV forecast, and minus both the FCM-qualified passive demand resources projected for 2017–2020 and the results of the 2021–2026 energy-efficiency forecast. The results show declining long-run growth in electric energy use. Similarly, Figure 3-4 shows the amounts that BTM PV and EE reduce the gross summer peak load. Table 3-6 compares the gross energy and peak demand forecasts with the net forecasts. The net summer peak is projected to remain relatively flat over the forecast horizon. The net winter peak is flat (i.e., negative 0.7%) over the 10-year forecast. The BTM PV does not reduce the winter peak because the winter peak occurs after dark. Table 3-7 shows the net load forecast for each of the New England states, and Table 3-8 shows the net load forecast for each of the RSP subareas.

Figure 3-3: RSP17 Gross annual energy-use forecast (diamond); gross energy forecast minus BTM PV (circle); gross energy forecast minus BTM PV and FCM #11 PDRs through 2020 (triangle); and gross energy forecast minus BTM PV, minus FCM PDRs, minus the energy-efficiency forecast (square) for 2021 to 2026 (MW).

Figure 3-4: RSP17 Gross summer peak demand forecast (90/10) (diamond); gross demand forecast minus BTM PV (circle); gross demand forecast minus BTM PV and FCM #11 PDRs through 2020 (triangle); and gross demand forecast minus BTM PV, minus FCM PDRs, minus the energy-efficiency forecast (square) for 2021 to 2026 (MW).

Table 3-6
Percentage Growth Rates of the Gross and Net Forecasts
of Annual and Peak Electric Energy Use, 2017 to 2026

|  | Gross | Net(a) |
| --- | --- | --- |
| NEL | 0.9 | −0.6 |
| 50/50 and 90/10 Summer | 1.0 | −0.1/0.1 |
| 50/50 and 90/10 Winter | 0.6 | −0.7 |

(a)	The net forecast is the gross forecast minus BTM PV, minus FCM PV, minus qualified passive demand resources for 2017 to 2020, and minus energy-efficiency forecast results for 2021 to 2026.

Table 3-7
State and Systemwide Net Forecasts of Annual and Peak Electric Energy Use, 2017 (MWh, MW)

| Area | Energy (1,000 MWh) |  |  | Summer Peak Loads (MW) |  |  |  |  | Winter Peak Loads (MW) |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | 50/50 Load |  | 90/10 Load |  |  | 50/50 Load |  | 90/10 Load |  |  |
|  | 2017 | 2026 | CAGR | 2017 | 2026 | 2017 | 2026 | CAGR | 2017/18 | 2026/27 | 2017/18 | 2026/27 | CAGR |
| CT | 31,336 | 29,039 | −0.8 | 6,992 | 6,726 | 7,666 | 7,462 | -0.3 | 5,470 | 4,975 | 5,658 | 5,163 | −1.0 |
| ME | 11,451 | 11,902 | 0.4 | 1,960 | 2,085 | 2,099 | 2,233 | 0.7 | 1,840 | 1,922 | 1,896 | 1,978 | 0.5 |
| MA | 58,336 | 53,968 | −0.9 | 12,299 | 12,185 | 13,338 | 13,392 | 0.0 | 9,655 | 8,953 | 9,981 | 9,278 | −0.8 |
| NH | 11,793 | 12,101 | 0.3 | 2,460 | 2,606 | 2,676 | 2,854 | 0.7 | 1,976 | 1,977 | 2,062 | 2,064 | 0.0 |
| RI | 8,180 | 7,257 | −1.3 | 1,870 | 1,828 | 2,124 | 2,128 | 0.0 | 1,278 | 1,111 | 1,304 | 1,137 | −1.5 |
| VT | 5,690 | 5,412 | −0.6 | 898 | 877 | 942 | 930 | −0.1 | 975 | 993 | 993 | 1,011 | 0.2 |
| ISO(a, b) | 126,786 | 119,680 | −0.6 | 26,482 | 26,310 | 28,865 | 29,021 | 0.1 | 21,197 | 19,932 | 21,895 | 20,630 | −0.7 |

(a) 	The total load-zone projections are similar to the state load projections and are available at the ISO’s “2017 Forecast Data File,” https://www.iso-ne.com/static-assets/documents/2017/05/forecast_data_2017.xlsx; tab #2A-2C, “ISO-NE Control Area, States, RSP17 Subareas, and Standard Market Design (SMD) Load Zones Energy and Seasonal Peak Load Forecast.”

(b) 	Totals may not equal the sum because of rounding and may not exactly match the results for other tables in this section.

Table 3-8
Net Forecast of Demand in RSP Subareas, 2017 to 2026 (GWh, MW)(a)

| Area | Energy (1,000 MWh) |  |  | Summer Peak Loads (MW) |  |  |  |  | Winter Peak Loads (MW) |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | 50/50 Load |  | 90/10 Load |  |  | 50/50 Load |  | 90/10 Load |  |  |
|  | 2017 | 2026 | CAGR | 2017 | 2026 | 2017 | 2026 | CAGR | 2017/18 | 2026/27 | 2017/18 | 2026/27 | CAGR |
| BHE | 1,625 | 1,692 | 0.5 | 278 | 296 | 297 | 317 | 0.7 | 262 | 273 | 270 | 281 | 0.5 |
| ME | 5,583 | 5,799 | 0.4 | 918 | 974 | 983 | 1,043 | 0.7 | 932 | 975 | 961 | 1,004 | 0.5 |
| SME | 3,944 | 4,108 | 0.5 | 702 | 749 | 751 | 802 | 0.7 | 609 | 636 | 628 | 655 | 0.5 |
| NH | 9,982 | 10,237 | 0.3 | 2,072 | 2,195 | 2,251 | 2,401 | 0.7 | 1,660 | 1,665 | 1,731 | 1,736 | 0.0 |
| VT | 6,898 | 6,670 | -0.4 | 1,173 | 1,172 | 1,244 | 1,255 | 0.1 | 1,174 | 1,188 | 1,203 | 1,217 | 0.1 |
| BOSTON | 26,552 | 24,737 | -0.8 | 5,626 | 5,572 | 6,095 | 6,111 | 0.0 | 4,347 | 4,023 | 4,494 | 4,170 | −0.8 |
| CMA/NEMA | 7,787 | 7,285 | −0.7 | 1,648 | 1,656 | 1,787 | 1,820 | 0.2 | 1,286 | 1,201 | 1,330 | 1,245 | −0.7 |
| WMA | 9,424 | 8,546 | −1.1 | 1,912 | 1,864 | 2,077 | 2,055 | −0.1 | 1,631 | 1,507 | 1,686 | 1,561 | −0.8 |
| SEMA | 13,096 | 12,112 | −0.9 | 2,814 | 2,788 | 3,064 | 3,081 | 0.1 | 2,142 | 2,012 | 2,213 | 2,084 | −0.7 |
| RI | 10,963 | 9,838 | −1.2 | 2,435 | 2,405 | 2,728 | 2,752 | 0.1 | 1,786 | 1,614 | 1,830 | 1,657 | −1.1 |
| CT | 15,187 | 14,033 | −0.9 | 3,386 | 3,250 | 3,714 | 3,609 | −0.3 | 2,569 | 2,369 | 2,660 | 2,461 | −0.9 |
| SWCT | 10,367 | 9,570 | −0.9 | 2,313 | 2,216 | 2,536 | 2,458 | −0.3 | 1,810 | 1,639 | 1,872 | 1,700 | −1.1 |
| NOR | 5,377 | 5,050 | −0.7 | 1,203 | 1,171 | 1,318 | 1,295 | −0.2 | 931 | 844 | 963 | 876 | −1.0 |
| ISO total(a, b) | 126,786 | 119,680 | −0.6 | 26,482 | 26,310 | 28,865 | 29,021 | 0.1 | 21,197 | 19,932 | 21,895 | 20,630 | −0.7 |

(a) 	The total load-zone projections are similar to the state load projections and are available at the ISO’s “2017 Forecast Data File; https://www.iso-ne.com/static-assets/documents/2017/05/forecast_data_2017.xlsx, tabs #2A-2C, “ISO-NE Control Area, States, RSP Subareas, and SMD Load Zones.”

(b) 	Totals may not equal the sum because of rounding and may not exactly match the results for other tables in this section.

## Summary of Key Findings of the Demand, Energy-Efficiency, and PV Forecasts

The RSP17 forecasts of annual energy use and peak loads are key inputs in establishing the system needs discussed in Section 4 through Section 6. The key points of the forecast are as follows:

- The 10-year net energy for load, accounting for both EE and PV, is projected to decrease from 126,786 GWh in 2017 to 119,680 GWh in 2026, which represents a decline of 0.6% per year. The RSP17 50/50 net summer peak forecast is 26,482 MW for 2017, which declines to 26,310 MW for 2026. The 90/10 net summer peak forecast, which represents more extreme summer heat waves, is 28,865 MW for 2017 and grows by 0.1% per year to 29,021 MW in 2026.

- The EE forecast drives the reduction of the growth rate of the 10-year gross winter peak demand from 0.6% to a net annual value of −0.7%. The projected decline of the net peak load helps mitigate winter reliability concerns.

- Regional passive demand resources and energy efficiency are expected to grow from 2,089 MW in 2017 to 4,475 MW in 2026. New England states’ annual investments in EE programs are expected to be more than $1 billion per year for 2017 through 2026. These EE investments remain a major factor in the expansion of passive demand resources in the region, which are projected to grow at an average rate of 265 MW per year across the 10-year horizon.

- Photovoltaic resources reached 1,918 MWac in nameplate capacity by the end of 2016 and are expected to grow to 4,733 MWac by 2026. The estimated reductions in summer seasonal peak loads due to BTM PV resources are 575 MW in 2017 and 1,035 MW in 2026; BTM PV does not reduce winter peaks because they typically occur after dusk.

# Resource Adequacy—Resources, Capacity, and Reserves

The ISO’s system planning process identifies the amounts, locations, and types of resources the system needs for ensuring resource adequacy and how the region is meeting these needs in the short term through the Forward Capacity Market (FCM) and the locational Forward Reserve Market (FRM). The amount of capacity the system requires in a given year is determined through the Installed Capacity Requirement calculation, which accounts for uncertainties, contingencies, and resource performance under a wide range of existing and future system conditions. The procurement of resources providing operating reserves for the system and local areas addresses contingencies, such as unplanned outages. Collectively, the forecasts of future electricity demand (as discussed in Section 3), the ICR calculation, the procurement of resources providing capacity and reserves, and the operable capacity analyses that consider future scenarios of load forecasts and operating conditions are referred to as the resource adequacy process.

This section describes requirements for resource adequacy over the planning period; the analyses conducted to determine the systemwide and local-area needs for ensuring resource adequacy; and the region’s efforts to meet the need for resources through market initiatives, such as the FCM and FRM and energy-efficiency resources supported by the states. The forecasts of resources needed to satisfy FCM and the FRM requirements account for the ISO’s net demand forecast that fully considers EE and behind-the-meter generation. This section also discusses the results of the net operable-capacity assessments of the system under a variety of deterministic stressed-system conditions. Also addressed are existing and future generating resources, including the capacity supply obligations to the markets and the seasonal claimed capability (SCC) of existing resources and projects proposed through the ISO’s interconnection queue that can help meet the long-term needs of the system.

## Determining Systemwide and Local-Area Capacity Needs

The Installed Capacity Requirement forms the basis for determining the future systemwide capacity needs. The planning process also determines the need for capacity in local capacity zones, accounting for export and import capabilities (or limitations) of these local zones. The annual Forward Capacity Auction (FCA) and reconfiguration auctions are intended to procure the needed capacity, systemwide and for capacity zones. This section provides the results of the systemwide and local-area analyses for the planning period.

### Systemwide Installed Capacity Requirements

RSP17 discusses the established net ICR (NICR) values for the 2017/2018 through 2020/2021 capacity commitment periods (CCPs) and illustrates representative net ICR values for the 2022/2023 through 2026/2027 periods. The established net ICR values for the 2017/2018 through 2020/2021 capacity commitment periods reflect the latest ICR values approved by FERC and were developed using the 2016 CELT Report load data. The representative net ICR values, rounded to the nearest 100 MW, for 2022/2023 through 2026/2027 are calculated using the same assumptions used to develop the NICR for 2020/2021 except for the demand forecast net of BTM PV. The net demand forecast used to calculate the representative NICR values are based on the 2017 CELT forecast.

The representative NICR values do not indicate the definitive amount of capacity the region will purchase for that period but provide stakeholders with a general forecast of the likely resource needs of the region. The actual amount of capacity the region will purchase in an FCA and subsequent reconfiguration auctions will be based on the net Installed Capacity Requirements and the resource offers resulting from the use of demand curves. Specifically, beginning with FCA #11 for capacity commitment period 2020/2021, the ISO has developed systemwide and zonal demand curves using a marginal-reliability-impact (MRI)-based methodology to procure capacity.

Table 4-1 shows the actual and representative New England net ICRs for 2017/2018 to 2026/2027 and the resulting reserves expressed as a percentage of the 2017 CELT Report forecast of the 50/50 peak demands. The percentage resulting reserves associated with the actual net ICRs would be lower if these requirements were expressed as a percentage of the 2016 CELT 50/50 peak demands. The 50/50 peak forecast for these years is equal to the gross demand forecast minus reductions for behind-the-meter PV (see Section 3.4).

Table 4-1 
Actual and Representative New England Net Installed Capacity Requirements
and Resulting Reserves (MW, %)

| Commitment Periods | 2017 CELT Forecast 50/50 Peak (MW)(a) | Actual and Representative Future Net ICR (MW)(b) | Resulting Reserves (%)(c) |
| --- | --- | --- | --- |
| 2017/2018 | 28,571 | 33,138 | 16.0 |
| 2018/2019 | 28,764 | 33,421 | 16.2 |
| 2019/2020 | 28,970 | 33,755 | 16.5 |
| 2020/2021 | 29,191 | 34,075 | 16.7 |
| 2021/2022 | 29,436 | TBD(d) | - |
| 2022/2023 | 29,694 | 34,300 | 15.5 |
| 2023/2024 | 29,960 | 34,600 | 15.6 |
| 2024/2025 | 30,231 | 35,000 | 15.7 |
| 2025/2026 | 30,507 | 35,300 | 15.8 |
| 2026/2027 | 30,785 | 35,700 | 15.9 |

- The 2017 relevant CELT forecast 50/50 peak loads reflect the BTM load reductions from the PV forecast as described in Section 3.

- Net ICR values for 2017/2018 to 2020/2021 are the latest values approved by FERC. These net ICR values were developed using 2016 CELT Report loads.

- The resulting reserves percentage is calculated using the 2017 CELT Report loads. The resulting reserves percentage for 2017/2018 to 2020/2021, when calculated using their respective 2016 CELT Report loads, ranged from 15.0% to 15.1% (These values are not shown in the above table).

(d) 	As of the RSP17 publication date, the net ICR for 2021/2022 was under development and scheduled to be filed with FERC in November 2017.

As shown in Table 4-1, the region’s net ICR is expected to grow from 33,138 MW in 2017 to a representative value of 35,700 MW by 2026. This represents an average growth of approximately 285 MW per year, which is equivalent to approximately an annual compound growth rate of 0.83% per year. The net ICR average annual compound growth rate is similar to the 0.744% CAGR of the net peak demand after reflecting the BTM PV. As shown in the table, the resulting reserves increase because the contribution of capacity from FCM resources to meet the one-day-in-10 year loss-of-load expectation (LOLE) increases while the contribution of tie benefits from non-FCM resources to meet the LOLE requirement stays constant.

### Local Resource Requirements and Limits

While the ICR addresses New England’s total capacity requirement assuming the system overall has no transmission constraints, certain subareas are limited in their ability to import or export power. To address the impacts of these constraints on subarea reliability, before each FCM auction, the ISO determines the local sourcing requirement (LSR) and maximum capacity limit (MCL) for certain subareas within New England. An LSR is the minimum amount of capacity that must be electrically located within an import-constrained capacity zone to meet the net ICR. An MCL is the maximum amount of capacity that can be procured in an export-constrained capacity zone to meet the total net ICR for the New England region. Areas that meet certain objective criteria for capacity zone modeling are designated as capacity zones and either an LSR or an MCL are established for them for each FCM auction. These designations help ensure that the appropriate amount of capacity is procured within these capacity zones and contribute effectively to total system reliability. (See Section 4.2 for further discussion of capacity zones.)

The LSR and MCL values, associated with the respective capacity commitment period’s FCA, are included in Table 4-2 for the 2017/2018 through the 2020/2021 capacity commitment periods. Like the net ICR, the LSR and MCL for capacity zones and values for FCA #12 were under development at the time of the RSP17 publication and will be filed with FERC in November 2017. In May 2017, the ISO presented to the PAC the representative NICR and associated values, such as LSR and MCL, for 2022/2023 through 2026/2027 using the same probabilistic calculation techniques and assumptions (except for the load forecast, which is based on the 2017 CELT loads) used for determining the  2020/2021 net ICR values presented in Table 4-1.

Table 4-2
Actual and Representative LSRs and MCLs (MW)(a, b)

| Commitment Period |  | LSR (MW)(c) |  |  |  | MCL (MW)(c) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | CT | NEMA/ Boston | SEMA/RI | SENE | Maine | NNE |
| 2017/2018 | FCA #8 | 7,319 | 3,428 | N/A | N/A | 3,960 | N/A |
| 2018/2019 | FCA #9 | 7,331 | 3,572 | 7,479 | N/A | N/A | N/A |
| 2019/2020 | FCA #10 | N/A | N/A | N/A | 10,028 | N/A | N/A |
| 2020/2021 | FCA #11 | N/A | N/A | N/A | 9,810 | N/A | 8,980 |
| 2021/2022 | FCA #12 | N/A | N/A | N/A | TBD | N/A | TBD |
| 2022/2023 | FCA #13 | N/A | N/A | N/A | 10,200 | N/A | 8,950 |
| 2023/2024 | FCA #14 | N/A | N/A | N/A | 10,400 | N/A | 9,000 |
| 2024/2025 | FCA #15 | N/A | N/A | N/A | 10,550 | N/A | 9,050 |
| 2025/2026 | FCA #16 | N/A | N/A | N/A | 10,750 | N/A | 9,150 |
| 2026/2027 | FCA #17 | N/A | N/A | N/A | 10,900 | N/A | 9,250 |

(a) 	Source: “Summary of ICR, LSR, and MCL for FCM and the Transition Period,” table, in Summary of Historical ICR Values spreadsheet (December 13, 2016), https://www.iso-ne.com/static-assets/documents/2016/12/summary_of_historical_icr_values.xlsx. These are the latest values filed with FERC.

(b) 	LSR and MCL values were calculated only for capacity zones triggered to be modeled (see Section 4.2) in that capacity commitment period.

(c) 	See Section 2.4  for definitions of these capacity zones.

### Capacity Supply Obligations from the Forward Capacity Auctions

This section presents the results of the first through eleventh Forward Capacity Auctions, including the amount of capacity that generation, import, and demand resources in the region will supply.

#### Capacity Supply Obligations for the First Eleven FCAs

Table 4-3 shows the results of the eleven FCAs held to date for capacity commitment periods (CCPs) 2010/2011 (FCA #1) through 2020/2021 (FCA #11) and provides the capacity supply obligation totals at the conclusion of each auction. This table also includes some details on the types of CSOs procured, including self-supply obligation values that reflect bilateral capacity arrangements as well as import CSOs from neighboring balancing authority areas.

Table 4-3
Summary of the FCA Obligations at the Conclusion of Each Auction (MW)(a)

| Commitment Period | ICR | HQICC | Net ICR(b) | Capacity Supply Obligation | Self-Supply Obligation | Import Capacity Supply Obligation |
| --- | --- | --- | --- | --- | --- | --- |
| 2010/2011 | 33,705 | 1,400 | 32,305 | 34,077 | 1,593 | 934 |
| 2011/2012 | 33,439 | 911 | 32,528 | 37,283 | 1,696 | 2,298 |
| 2012/2013 | 32,879 | 914 | 31,965 | 36,996 | 1,935 | 1,900 |
| 2013/2014 | 33,043 | 916 | 32,127 | 37,501 | 2.698 | 1,993 |
| 2014/2015 | 34,154 | 954 | 33,200 | 36,918 | 3,176 | 2,011 |
| 2015/2016 | 34,498 | 1,042 | 33,456 | 36,309 | 4,164 | 1,924 |
| 2016/2017 | 34,023 | 1,055 | 32,968 | 36,220 | 4,662 | 1,830 |
| 2017/2018 | 34,923 | 1,068 | 33,855 | 33,702 | 3,330 | 1,237 |
| 2018/2019 | 35,142 | 953 | 34,189 | 34,695 | 1,287 | 1,449 |
| 2019/2020 | 35,126 | 975 | 34,151 | 35,567 | 1,586 | 1,450 |
| 2020/2021 | 35,034 | 959 | 34,075 | 35,835 | 1,550 | 1,235 |

  - Information regarding the results of annual reconfiguration auctions is available at http://www.iso-ne.com/markets/othrmkts_data/fcm/cal_results/index.html.

  - The net ICR equals the ICR minus the Hydro-Québec Interconnection Capability Credits. The ICR applies to the FCA, not the reconfiguration auction.

Table 4-4 illustrates, by resource type, the amounts of new capacity procured during all the FCAs conducted to date. Since RSP15, two FCM auctions were conducted, FCA #10 for capacity commitment period 2019/2020, and FCA #11 for CCP 2020/2021.

FCA #10 attracted significant competition among resources to provide reliability services in New England, with sufficient resources to meet demand in 2019/2020, at a lower price, and with more than 1,400 megawatts (MW) of new generating capacity. This new capacity will help replace the 1,525 MW of recently retired coal and oil units and the pending retirement of the 677 MW Pilgrim Nuclear Power Station that submitted a retirement request in FCA #10. To meet expected load, three large, new, dual-fuel power plants totaling 1,302 MW cleared the auction as well as offshore wind (27 MW) and solar projects (44 MW). In addition, 371 MW of demand-side resources, primarily state sponsored energy efficiency (330 MW), cleared in FCA #10.

Unlike FCA #10, few new resources cleared in FCA #11, but existing resources were still sufficient to meet expected demand for 2020/2021. Specifically, no major generators retired and no new large generators cleared the auction. Approximately 264 MW of new generating capacity, including 137 MW of wind and 66 MW of solar, and 640 MW of demand-side resources, including 515 MW of energy efficiency, cleared in FCA #11.

Table 4-4
Capacity Supply Obligation for New Capacity
Procured during the Forward Capacity Auctions (MW)(a, b)

| Capacity Resource | FCA #1 | FCA #2 | FCA #3 | FCA #4 | FCA #5 | FCA #6 | FCA #7 | FCA #8 | FCA #9 | FCA #10 | FCA #11 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Generation resources | 40 | 1,157 | 199 | 114 | 42 | 79 | 800 | 27 | 1,060 | 1,459 | 264 |
| Demand-resource total | 860 | 447 | 309 | 515 | 263 | 313 | 245 | 355 | 367 | 371 | 640 |
| Active demand resources | 576 | 185 | 98 | 257 | 42 | 66 | <1 | 14 | 81 | 20 | 85 |
| Passive demand resources | 284 | 262 | 211 | 258 | 221 | 247 | 245 | 341 | 286 | 350 | 554 |
| Import resources | 0 | 1,529 | 817 | 831 | 871 | 1,648 | 1,718 | 1,154 | 1,360 | 1,361 | 1,153 |

        - New RTEG capacity is not included in the table values because the FCA treated it as existing capacity. Repowered existing generating capacity (i.e., capacity that has undergone environmental upgrades), which is treated as new capacity in the FCA, has been removed as well. Refer to the full auction results at http://www.iso-ne.com/isoexpress/web/reports/auctions/-/tree/fcm-auction-results.

        - Full listings of all new and existing resources that qualified to participate in each of the FCAs is available in the Forward Capacity Obligations spreadsheets at https://www.iso-ne.com/isoexpress/web/reports/auctions/-/tree/fca-results. In addition, updated summaries of CSOs by resource type for each commitment period are provided monthly in the NEPOOL Participants Committee COO Reports at https://www.iso-ne.com/committees/participants/participants-committee.

#### Summary of New Capacity and Delist Bids

As part of the FCM rules, the ISO reviews each delist bid and retirement request to determine whether the capacity associated with the delist bid or retirement is needed for the reliability of the New England electric power system. All reviews are performed in accordance with Planning Procedure No. 10 (PP 10), Planning Procedure to Support the Forward Capacity Market.

Static and dynamic delist bids are priced requests to remove capacity from the market for a single year. Retirements and delist bid requests have influenced prices in the Forward Capacity Market and thereby provide incentives for new resources to be built.

More than 5,700 MW of generation and demand-response capacity has retired or will retire in less than five years. The ISO evaluates the effect of potential retirements on the system as well as the potential impact to the Forward Capacity Market. In general, new generation resources have been typically clearing within one to two auctions in response to major retirements on the system, while new demand resources have been clearing at relatively the same levels regardless of retirements. A trend starting with FCA #7 has been to install flexible, fast start generation, such as gas-fired combined-cycles plants (2,368 MW) and large gas-fired combustion turbines (618 MW). Figure 4-1 shows the amount of new generation and demand resources participating in the FCM and receiving CSOs and those resources, including demand resources, that chose to retire.

Figure 4-1: Summary of new capacity and retirement requests for FCA #5 to FCA #11.

Note: The new capacity and retirements may not actually occur in the indicated commitment period. Refer to Figure 4-2 for actual and projected generating capacity additions and retirements.

#### Representative Systemwide Resource Needs

The representative net ICR values for future years (Section 4.1.1) indicates the systemwide capacity needs. Table 4-5 compares these systemwide needs with the resources procured in FCA #11, accounting for the future levels of behind-the-meter PV (Section 3.3.3), and the future levels of passive demand resources (Section 3.2). The projection of systemwide capacity needs assumes that all resources with CSOs through FCA #11 are in commercial service by the start of the eleventh capacity commitment period commencing in June 2020 and that they remain in service through 2026/2027.

As shown in Table 4-5, New England will be approximately 1,717 MW long of resources in 2026, the last year of the study period, in meeting the NICR. This assumes that the projected load and capacity assumptions materialize, no additional retirements occur, and newly proposed resources are in service in accordance with their projected construction schedules. The ISO monitors closely the build out of all new, noncommercial resources in anticipation that some may be early or others late. To date, the tendency has been toward new demand resources being available as much as a year in advance of their expected in-service date while generation has been delayed due to permitting and transmission construction issues.

Table 4-5 
Future Systemwide Needs (MW)

| Year | 50/50 Peak Load(a) | Representative Net ICR (Need) | FCA #11 (Known Resources)(b) | EE Forecast (New Resources)(c) | Resource Surplus/Shortage(d) |
| --- | --- | --- | --- | --- | --- |
| 2022/2023 | 29,694 | 34,300 | 35,835 | 634 | 2,169 |
| 2023/2024 | 29,960 | 34,600 | 35,835 | 912 | 2,147 |
| 2024/2025 | 30,231 | 35,000 | 35,835 | 1,162 | 1,997 |
| 2025/2026 | 30,507 | 35,300 | 35,835 | 1,385 | 1,920 |
| 2026/2027 | 30,785 | 35,700 | 35,835 | 1,582 | 1,717 |

(a)	The 50/50 peak loads reflect forecasted behind-the-meter PV resources.

(b)	FCA #11 resource numbers are based on FCA #11 auction results, assuming no retirements and the same level of imports (i.e., most imports need to requalify for every auction). Details are available athttps://www.iso-ne.com/static-assets/documents/2017/03/ccp_2020_21_fca_11_cso_flow_diagram.pdf.

(c) 	EE cumulative forecast values are based on the 2017 EE forecast. Details are available at https://www.iso-ne.com/system-planning/system-forecasting/energy-efficiency-forecast

(d) 	Additional resources would be required if additional resources retire or less capacity imports obtain CSOs.

## Determining FCM Capacity Zones

For developing FCM capacity zones, the ISO annually identifies and evaluates all the boundaries and interface transfer capabilities that could be relevant to FCA capacity zone modeling. The review must focus on the actual constraints observed and expected on the New England system and directly considers submitted retirements and rejected delist bids. This review is designed to be responsive to system changes, such as new transmission facilities and new capacity resources. Primary auctions, reconfiguration auctions, and FCM settlements all use the capacity zones.

Determining capacity zones is a two-step process. Step one identifies potential zonal boundaries and associated transfer limits to be tested for modeling in the auction. Step two uses objective criteria to determine whether or not a zone should be modeled for the pertinent capacity commitment period. With respect to step two, the trigger to model an import-constrained zone is based on the quantity of existing resources in the zone, whereas the trigger to model an export-constrained zone is based on the quantity of existing and proposed new resources that could qualify in the zone. Zones that are neither import- or export-constrained are merged into the Rest-of-Pool capacity zone.

The FERC-approved methodology for determining capacity zones is focused on the review of system conditions for the capacity commitment period associated with the upcoming FCA. The final set of capacity zones up to FCA #12 will be filed with FERC November 2017 but were presented to stakeholders in March 2017. However, for FCA #13 and beyond, they will not be known until all the relevant system conditions for that capacity commitment period have been identified and evaluated. In particular, the zone-formation process must be responsive to retirements, rejected delist bids, and other system changes. Generally, zone determinations are made in the spring of each year and presented to PAC.

For FCA #11 and FCA #12, the same objective criteria applied in FCA #10 was used to determine the need for modeling the same or different capacity zones. For both FCA #11 and FCA #12, it was determined that three capacity zones will be modeled, specifically Southeastern New England (SENE), Northern New England (NNE), and Rest-of-Pool. The SENE zone was modeled because constraints continue to be observed in the transfer of power into the SENE area. These constraints were observed for the contingency loss of either generating resources or other transmission elements on or near the boundary formed by the combination of the load zones. The NNE zone was modeled in both FCA #11 and FCA #12 because of the significant amount of new capacity additions proposed in the northern part of the system during the qualification process, making the area more likely to be export constrained. Similar to previous FCAs, Connecticut was evaluated as a potential import-constrained zone but was merged with the ROP capacity zone because the transmission system has been improved significantly and the markets have responded for building new generation in the area. The Western Massachusetts load zone will continue to form the basis of the ROP capacity zone.

## Analyzing Operable Capacity

The ISO performs systemwide operable-capacity analyses to estimate the net capacity and determine the operable-capacity margin available under two scenarios (i.e., using the 50/50 and 90/10 forecasts of peak load). The analysis assumes that peak load conditions are reduced to fully reflect behind-the-meter PV (refer to Section 3.4). It also assumes that to meet the assumed peak demand plus operating-reserve requirements, the capacity in New England will only be equal to the net ICR, which relies on load and capacity relief from the implementation of OP 4 actions to meet the one-day-in-10 years LOLE. A negative margin for a specific scenario indicates the extent that possible mitigation actions would be required through predefined protocols, as prescribed in the ISO’s Operating Procedure No. 4, Action during a Capacity Deficiency, or Operating Procedure No. 7 (OP 7), Action in an Emergency.

Table 4-6 shows the results of the ISO’s systemwide operable capacity analysis for the 2018/2019 to 2026/2027 commitment periods. The analysis does not take into account operable capacity needs for RSP subareas. The results show that if the loads associated with the 50/50 forecast occurred, the ISO could expect New England to experience a positive operable-capacity margin ranging from approximately 200 MW to 500 MW during the study period.

Table 4-6
Projected New England Operable Capacity Analysis for Summer, 2018 to 2026,
Assuming 50/50 and 90/10 Loads (MW)

| Capacity Situation (Summer MW) |  | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 50/50 forecast | Load net of BTM PV(a) | 28,764 | 28,970 | 29,191 | 29,436 | 29,694 | 29,960 | 30,231 | 30,507 | 30,785 |
|  | Operating reserves(b) | 2,305 | 2,305 | 2,305 | 2,305 | 2,305 | 2,305 | 2,305 | 2,305 | 2,305 |
|  | Total requirement | 31,069 | 31,275 | 31,496 | 31,741 | 31,999 | 32,265 | 32,536 | 32,812 | 33,090 |
|  | Installed capacity (net ICR)(c) | 33,421 | 33,755 | 34,075 | N/A | 34,300 | 34,600 | 35,000 | 35,300 | 35,700 |
|  | Assumed unavailable capacity | −2,100 | −2,100 | −2,100 | −2,100 | −2,100 | −2,100 | −2,100 | −2,100 | −2,100 |
|  | Total net capacity(d) | 31,321 | 31,655 | 31,975 | N/A | 32,200 | 32,500 | 32,900 | 33,200 | 33,600 |
|  | Operable capacity margin(e)— 50/50 forecast | 252 | 380 | 479 | N/A | 201 | 235 | 364 | 388 | 510 |
| 90/10 forecast | Load net of BTM PV | 31,183 | 31,426 | 31,683 | 31,964 | 32,259 | 32,562 | 32,869 | 33,182 | 33,496 |
|  | Operating reserves(b) | 2,305 | 2,305 | 2,305 | 2,305 | 2,305 | 2,305 | 2,305 | 2,305 | 2,305 |
|  | Total requirement | 33,488 | 33,731 | 33,988 | 34,269 | 34,564 | 34,867 | 35,174 | 35,487 | 35,801 |
|  | Installed capacity (net ICR)(c) | 33,421 | 33,755 | 34,075 | N/A | 34,300 | 34,600 | 35,000 | 35,300 | 35,700 |
|  | Assumed unavailable capacity | −2,100 | −2,100 | −2,100 | −2,100 | −2,100 | −2,100 | −2,100 | −2,100 | −2,100 |
|  | Total net capacity(d) | 31,321 | 31,655 | 31,975 | N/A | 32,200 | 32,500 | 32,900 | 33,200 | 33,600 |
|  | Operable capacity margin(e)— 90/10 forecast | −2,167 | −2,076 | −2,013 | N/A | −2,364 | −2,367 | −2,274 | −2,287 | −2,201 |

(a)	These values are net of BTM PV, consistent with the other projections in this section. Because this table uses net ICR, the ISO does not subtract the EE forecast; EE is considered part of the resource mix meeting the ICR.

(b) 	The 2,305 MW value of operating reserves is based on the following assumptions: a first contingency of 1,400 MW plus a 20% increase in the 10-minute operating reserve to compensate for nonperformance of the reserve generating units (as discussed in Section 4.4.1) equal to 280 MW, and 30-minute reserves of 625 MW (one half of 1,250 MW).

(c)	Net ICR values for 2017/2018 to 2020/2021 are the latest values approved by FERC. These net ICR values were developed using 2016 CELT Report loads. The net ICR values for other years are consistent with the representative future net ICR values in -Table 4-5.

(d) 	The net capacity values are equal to the net ICR minus the assumed unavailable capacity.

(e) 	“Operable capacity margin” equals “total net capacity” minus “total requirement.”

Table 4-6 also shows that if the projected 90/10 peak loads occurred, New England could experience large negative operable-capacity margins from approximately 2,000 MW (2020) to a high of approximately 2,400 MW (2022 and 2023) during the study period. Due to the effects of increasing behind-the-meter PV on the load forecast, the negative operable-capacity margin decreases to approximately 2,200 MW by the end of the study period. Thus, throughout the study period, New England would have to rely on additional imports or load and capacity relief from OP 4 actions to meet the 90/10 peak demand.

## Determining Operating Reserves and Regulation

In addition to capacity resources being available to meet the region’s actual demand for electricity, as discussed in Section 4.1, the system needs a certain amount of resources that can provide operating reserves and system regulation. The overall mix of resources providing operating reserves must be able to respond quickly to system contingencies stemming from equipment outages. The ISO may also call on these resources to provide regulation service for maintaining system frequency and external transactions with neighboring balancing authority areas or to serve load during peak demand conditions. A suboptimal mix of resources overall, with limited amounts of flexible operating characteristics, could result in the system’s dependence on more costly resources to provide these services. In the worst case, reliability would be degraded.

Several types of resources in New England have the operating characteristics to respond to contingencies, provide regulation service, and serve peak demand. The generating units that provide operating reserves can respond to contingencies within 10 or 30 minutes and can either be synchronized or not synchronized to the power system. Synchronized (i.e., spinning) operating reserves are on-line resources that can increase output. Nonsynchronized (i.e., nonspinning) operating reserves are off-line, fast-start resources that can be electrically synchronized to the system quickly, reaching maximum output within 10 minutes or within 30 minutes. During real-time daily operations, the ISO determines operating-reserve requirements for the system as a whole and for major import-constrained areas.

This section discusses the need for operating reserves, both systemwide and in major import areas, and the use of specific types of fast-start resources to fill these needs. An overview of the Forward Reserve Market and a forecast of representative future operating-reserve requirements for Greater Southwest Connecticut, Greater Connecticut, and BOSTON are provided. This section also discusses the likely need for additional flexible resources identified by the studies and other actions supporting the strategic planning of the region, as discussed in Section 9.4.

### Systemwide Operating-Reserve Requirements

The ISO’s operating-reserve requirements, as established in Operating Procedure No. 8, Operating Reserve and Regulation (OP 8), are used to protect the system from the impacts associated with a loss of generating or transmission equipment within New England. A certain amount of the power system’s resources must be available to provide operating reserves to assist in addressing systemwide contingencies.

To comply with OP 8, the ISO must maintain sufficient reserves in its balancing authority area during normal conditions to be able to replace within 10 minutes the first-contingency loss (N–1) in the New England Reliability Balancing Authority Area multiplied by the contingency-reserve adjustment (CRA) factor for the most recent completed quarter. The current total 10-minute operating-reserve requirement reflecting the CRA factor is 1.2% of the first-contingency loss. In addition, OP 8 requires the ISO to maintain sufficient reserves to address the uncertainties associated with resource nonperformance, as well as load-forecast error. To meet this need, the ISO must be able to replace at least 50% of the next-largest contingency loss (N–1–1) within 30 minutes plus a replacement reserve requirement of 180 MW during Eastern Standard Time and 160 MW during Daylight Savings Time. The higher amount set for the winter period is to accommodate the additional peak-load ramping and fuel uncertainty usually experienced during this period.

Typically, the largest first-contingency loss is between 1,300 and 1,700 MW, and 50% of the next-largest contingency loss is between 600 and 850 MW. These resources typically consist of some combination of the two largest on-line generating units or imports on the Phase II interconnection with Québec.

In accordance with NERC and NPCC criteria for power system operation, ISO Operating Procedure No. 19 (OP 19), Transmission Operations, requires system power flows to stay within applicable emergency limits of the power system elements that remain after the loss of any other power system element (N−1). This N−1 limit may be a thermal, voltage, or stability limit of the transmission system. OP 19 further stipulates that within 30 minutes of the loss of the first-contingency element, the system must be able to return to a normal state that can withstand a second contingency. To implement these OP 19 requirements, and as set forth in OP 8, operating reserves must be distributed throughout the system. This requirement is designed to ensure that the ISO can activate all reserves without exceeding transmission system limitations and that the operation of the system remains in accordance with NERC, NPCC, and ISO New England criteria and guidelines.

### Locational Reserve Needs for Major Import Areas

To maintain system reliability further, the ISO maintains certain reserve levels within major importing subareas of the system. The amount and type of operating reserves needed within these subareas depend on many factors, including load levels, the projected peak load of the subarea, and the economic and physical operating characteristics of the generating units within the subarea. The systemwide commitment and economic dispatch of generation, system topology, system reliability constraints, special operational considerations, possible resource outages, and other system conditions are additional factors that can affect the required levels of reserve within subareas.

The ISO analyzes and determines how the generating resources within the subareas must be committed to meet the following day’s operational requirements and withstand possible contingencies, including the most critical contingencies that determine the transmission import capability into the subarea. If maximizing the use of transmission import capability to meet demand is more economical, the subarea will require more local operating reserves to protect for contingencies. If using import capability to meet demand is less economical, generation located outside the subarea could provide operating reserves, thus reducing operating-reserve support needed within the subarea.

Table 4-7 shows representative future operating-reserve requirements for Greater Southwest Connecticut, Greater Connecticut, and BOSTON. These estimated requirements are based on the same methodology used to calculate the requirements for the locational FRM. The estimates account for representative future system conditions for load, economic generation, generation availability, N−1 and N−1−1 transfer limits, and normal criteria contingencies for generation and transmission in each subarea. The analysis accounts for transmission upgrades consistent with the transmission-transfer capabilities presented to the PAC.

The representative values show a range to reflect the load and resource uncertainties associated with future system conditions. Table 4-7 also shows the existing amount of fast-start capability located in each subarea resulting from the fast-start resources offered into past FRM auctions. The total 10-minute operating-reserve values associated with the FRM reflect the contingency reserve adjustment, but this adjustment does not affect the amount of reserves distributed to locations (i.e., the reserve values for BOSTON, Greater Southwest Connecticut, and Greater Connecticut did not increase).

Table 4-7
Representative Future Operating-Reserve Needs in Major New England Import Areas (MW)

| Area/Improvement | Market Period(a) | Range of Fast-Start Resources Offered into the Past Five Forward Reserve Auctions (MW)(b) | Representative Future Locational Forward Reserve Market Requirements (MW) |  |
| --- | --- | --- | --- | --- |
|  |  |  | Summer(c) (Jun to Sep) | Winter(c) (Oct to May) |
| Greater Southwest Connecticut(d) | 2017 | 191–346 | 52(e) | To be updated |
|  | 2018 |  | 50–400 | 0–200 |
| Reflecting impact of CPV Towantic | 2019 |  | 50–400 0 with CPV in service | 0-150 0 with CPV in service |
| Reflecting impact of Bridgeport Harbor 5 | 2020 |  | 0 | 0 |
|  | 2021 |  | 0 | 0 |
| Greater Connecticut(f, g) | 2017 | 0–1,188(h) | 0(e) | To be updated |
|  | 2018 |  | 0–100 | 0 |
| Reflecting impact of CPV Towantic | 2019 |  | 0–100 0 with CPV in service | 0 |
| Reflecting impact of Bridgeport Harbor 5 | 2020 |  | 0 | 0 |
| Reflecting impact of Greater Hartford/Central Connecticut upgrades | 2021 |  | 0 | 0 |
| NEMA/Boston(g, i) | 2017 | 0–318 | 279(e) | To be updated |
| Reflecting impact of Footprint | 2018 |  | 200–650 0-50 with Footprint | 0 |
|  | 2019 |  | 0–50 | 0 |
| Reflecting impact of Greater Boston Upgrades | 2020 |  | 0 | 0 |
|  | 2021 |  | 0 | 0 |

- The market year is from June 1 through May 31 of the following year.

- These values are the range of the megawatts of resources offered into the past forward-reserve auctions. A summary of the forward-reserve offers for the past auctions is available at http://www.iso-ne.com/markets-operations/markets/reserves.

- “Summer” means June through September of a Capacity Commitment Period; “winter” means October of the associated year through May of the following year (e.g., the 2017 winter values are for October 2017 through May 2018). The representative values show a range to reflect uncertainties associated with the future system conditions. The operating limits shown below reflect those assumed at the time of the analysis.

- The assumed N−1 and N−1−1 values that reflect transmission import limits into Greater SWCT are 2,500 MW and 1,750 MW, respectively. The 2019 values for Greater Southwest Connecticut also show the forward-reserve needs, assuming that the 725 MW CPV Towantic generating station will be in service by June 2018.

- These values are actual locational forward-reserve requirements. The projections of the requirements for future years are based on assumed contingencies.

- For Greater Connecticut, the assumed import limits reflect an N−1 value of 2,950 MW and an N−1−1 value of 1,750 MW. With the Greater Hartford/Central Connecticut Upgrades assumed in service in 2020, the N−1 and N−1−1 import limits will increase to 3,400 and 2,200 MW, respectively.

- In some circumstances when transmission contingencies are more severe than generation contingencies, shedding some nonconsequential load (i.e., load shed that is not the direct result of the contingency) may be acceptable.

- These values include resources in Greater Southwest Connecticut.

- The assumed N−1 and N−1−1 values reflecting the transmission import limits into Boston are 4,850 MW and 4,175 MW, respectively, which reflect the impacts of the retirement of Salem Harbor units #1–#4 and the North Shore Upgrade. These limits will increase to 5,700 MW and 4,600 MW, respectively, after the Greater Boston Upgrades, which are assumed in service by June 2019. The operating-reserve values for BOSTON would be lower with transmission upgrades or without consideration of the common-mode failure of Mystic units #8 and #9 assumed to trip up to 1,400 MW because of exposure to a common-mode failure of the fuel supply to the units. The values also show the forward-reserve requirements assuming that Footprint Power, 674 MW, will be in service by 2017.

Because the local contingency needs in Greater Southwest Connecticut are nested within Connecticut, resources installed in the Greater Southwest Connecticut area also would satisfy the operating reserve need for resources located anywhere in Greater Connecticut.

#### Greater Southwest Connecticut

As shown in Table 4-7, Greater Southwest Connecticut is expected to require as much as 400 MW of operating reserves in the area before the CPV Towantic generating unit is in service. Consistent with ISO’s operating experience of recent years, the interface into Greater Southwest Connecticut could be heavily loaded because of economical transfers into the area. As a result of the heavy loading of the interface capability, more reserves must be carried locally within Greater Southwest Connecticut. The CPV Towantic and Bridgeport Harbor 5 generation, when in service, is expected to eliminate the local reserve need starting as early as 2019.

#### Greater Connecticut

Past RSPs and market signals had identified the need for in-merit and fast-start resources in Greater Connecticut to meet reliability needs and reduce out-of-merit market costs. As a result of resource development, Greater Connecticut is now projected to have adequate fast-start resources, and the economic performance of this area is expected to improve. Forward Reserve Market requirements in Greater Connecticut will depend on local economic generation. The operating-reserve needs are expected to be eliminated starting as early as 2019 once the CPV Towantic is completed. The installation of the Bridgeport 5 and the Greater Hartford/Central Connecticut transmission upgrades will further help eliminate locational reserve needs in Greater Connecticut beyond 2019.

#### BOSTON

The operating-reserve needs for the BOSTON subarea shown in Table 4-7 reflect the possible simultaneous contingency loss of Mystic units #8 and #9. The retirement of the Salem Harbor units in 2014 has reduced the ability to serve load economically within the BOSTON subarea. As a result, lower-cost generation is imported into BOSTON and local operating reserve is needed to protect against the larger of 1) the loss of the largest generation source within the subarea and a transmission line or 2) the loss of two transmission lines into the subarea. With the addition of Footprint Power (which increases local generation in this area), the local reserve needs are expected to decrease starting in 2018 (refer to Table 4-7, note i).

#### Summary of Operating-Reserve Needs in Major Subareas

New England must meet its overall operating-reserve needs and have sufficient reserves in subareas to meet reliability requirements. The need for operating reserves in local subareas has been decreasing, and the reduction is expected to continue. Future requirements may be completely eliminated starting as early as 2019, with the completion of proposed transmission upgrades, additional lower-cost generating resources in service in the subareas, and the expected installation of BTM PV. Any reduction in traditional baseload resources in these subareas would increase the operating-reserve need.

## Existing and Future Resource Development in Areas of Need

The development of resources can help meet the long-term needs of the system. This section reviews existing and future generating resources, including the capacity and claimed capability of existing resources, projects proposed through the ISO’s interconnection queue, and generator retirements.

### Existing Generating Capacity by Subarea, Load Zone, and State

Generating units located close to load centers typically reduce the need for transmission system improvements. Table 4-8 tabulates the existing generating amounts and locations by RSP subarea, load zone, and state. Some RSP subareas comprise multiple states or multiple load zones.

Table 4-8
2017 Generating Capacity by Subarea, State, and Load Zone (MW, %)(a, b)

| RSP Area | State | Load Zone | Summer |  |  | Winter |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Capacity Rating(b) (MW) | % of RSP Subarea | % of State | Capacity Rating(b) (MW) | % of RSP Subarea | % of State |
| BHE | Maine | ME | 854 | 100 | 27 | 1,050 | 100 | 30 |
| ME | Maine | ME | 851 | 100 | 27 | 956 | 100 | 27 |
| SME | Maine | ME | 1,470 | 100 | 46 | 1,544 | 100 | 43 |
|  | New Hampshire | ME | 0 | 0 | 0 | <1 | 0 | <1 |
|  |  |  | 1,470 | 100 | 46 | 1,545 | 100 | 44 |
| NH | Maine | NH | <1 | 0 | <1 | <1 | 0 | <1 |
|  | New Hampshire | NH | 4,179 | 99 | 100 | 4,430 | 99 | 100 |
|  | Vermont | NH | 0.3 | 0 | <1 | 1 | 0 | <1 |
|  |  | VT | 33 | 1 | 8 | 39 | 1 | 7 |
|  |  |  | 33 | 1 | 8 | 40 | 1 | 7 |
|  |  |  | 4,212 | 100 | 108 | 4,471 | 100 | 107 |
| VT | New Hampshire | NH | 1 | 0 | <1 | 3 | 1 | <1 |
|  |  | VT | 1 | 0 | <1 | 4 | 1 | <1 |
|  |  |  | 2 | 1 | 0 | 7 | 2 | <1 |
|  | Vermont | NH | 86 | 27 | 20 | 88 | 20 | 16 |
|  |  | VT | 234 | 73 | 54 | 350 | 79 | 63 |
|  |  |  | 321 | 99 | 74 | 438 | 98 | 79 |
|  |  |  | 323 | 100 | 74 | 445 | 100 | 79 |
| BOSTON | Massachusetts | NEMA | 2,564 | 100 | 23 | 3,065 | 100 | 23 |
|  |  | WCMA | 0 | 0 | <1 | 0 | 0 | 0 |
|  |  |  | 2,564 | 100 | 23 | 3,065 | 100 | 23 |
| CMA/NEMA | Massachusetts | WCMA | 176 | 100 | 2 | 172 | 100 | 1 |
| WMA | Massachusetts | WCMA | 3,657 | 98 | 33 | 3,855 | 98 | 28 |
|  | Vermont | WCMA | 77 | 2 | 18 | 76 | 2 | 14 |
|  |  |  | 3,735 | 100 | 51 | 3,931 | 100 | 42 |
| SEMA | Massachusetts | SEMA | 3,220 | 93 | 29 | 3,357 | 92 | 25 |
|  | Rhode Island | RI | 242 | 7 | 13 | 279 | 8 | 13 |
|  |  |  | 3,461 | 100 | 42 | 3,636 | 100 | 38 |
| RI | Massachusetts | SEMA | 1,471 | 47 | 13 | 3,109 | 63 | 23 |
|  | Rhode Island | RI | 1,664 | 53 | 87 | 1,846 | 37 | 87 |
|  |  |  | 3,135 | 100 | 101 | 4,955 | 100 | 110 |
| CT | Connecticut | CT | 5,917 | 100 | 71 | 6,153 | 100 | 69 |
| SWCT | Connecticut | CT | 2,305 | 100 | 27 | 2,586 | 100 | 29 |
| NOR | Connecticut | CT | 170 | 100 | 2 | 191 | 100 | 2 |
| Total |  |  | 29,174 |  |  | 33,157 |  |  |

(a) Totals may vary because of rounding.

(b) The values shown are seasonal claimed capability are based on the 2017 CELT.

### Summer Seasonal Claimed Capability of New England’s Generating Resources

Table 4-9 shows the megawatt amount of summer seasonal claimed capability of the generating resources, both systemwide and for each RSP subarea, categorized by the assumed operating classification of the resource design.

Table 4-9 
2017 Summer Seasonal Claimed Capability for ISO New England Generating Resources,
by Assumed Operating Classification, Systemwide and by RSP Subarea (MW)

| Area | Baseload(a) | Intermediate(b) | Peaking(c) | Variable(d) |
| --- | --- | --- | --- | --- |
| BHE | 122 | 653 | 0 | 79 |
| BOSTON | 675 | 1,631 | 240 | 18 |
| CMA/NEMA | 40 | 75 | 29 | 34 |
| CT | 3,903 | 1,464 | 550 | 0 |
| ME | 343 | 244 | 131 | 133 |
| NH | 2,842 | 1,241 | 83 | 46 |
| NOR | 0 | 0 | 170 | 0 |
| RI | 28 | 3,024 | 42 | 41 |
| SEMA | 1,901 | 1,340 | 142 | 78 |
| SME | 904 | 530 | 32 | 3 |
| SWCT | 535 | 1,000 | 769 | 1 |
| VT | 166 | 0 | 133 | 24 |
| WMA | 242 | 1,356 | 2,023 | 114 |
| Total(e) | 11,701 | 12,558 | 4,344 | 571 |

(a) 	Baseload units are assumed to run for long continuous hours at a constant output and have little flexibility. For operating classification purposes, bio/refuse, coal, fuel cell, pondage hydro, weekly hydro, nuclear, and thermal steam generators are assumed in the baseload category.

(b) 	Intermediate units have the ability to dispatch flexibly and can follow variations in the system load. Combined-cycle generators are assumed in the intermediate category.

(c)	Peaking generators can be dispatched to meet peak demand for relatively short periods. Internal combustion, gas turbine, and pumped-storage generators, as well as battery storage facilities, are assumed in the peaking category.

(d) 	Variable units produce energy subject to variations in “fuel” determined by weather. Run-of-river hydro, photovoltaic, and wind generators are assumed in the variable energy resource (VER) category; refer to Section 9.

(e) 	Totals may not equal the sum because of rounding.

### Generation Retirement and Additions in New England

Figure 4-2 shows the actual and projected annual New England generating unit retirements and additions in megawatts for 2010/2011 through 2020/2021, which covers the FCA #1 through FCA #11 periods. Approximately 4,100 MW of retirements occur from 2010/2011 through 2017/2018. The total for known generator retirements will reach approximately 4,800 MW by summer 2020, which includes approximately 680 MW of future retirements occurring by summer 2019. Significant generating resource additions occurred early in the eleven-year period, increasing again in 2018 with 1,701 MW of additions. Additional generating resources are expected beyond 2018, including 1,348 MW in 2019 and 104 MW in 2020. Total retirements and additions at the end of the 2010 through 2020 period will be nearly equal, with the generating unit additions outpacing retirements by only approximately 55 MW.

Figure 4-2: Actual and projected summer generation retirements and additions, 2010 to 2020 (MW).

Note: This table reflects both FCM and non-FCM capacity.

Since the region is expected to experience more generating resource additions than retirements by summer 2020, the ISO expects that resources will be adequate for meeting net Installed Capacity Requirements. The anticipated growth of PV and EE resources in the region and the 12,899 MW of generating resources actively seeking interconnection will further contribute to meeting demand. FCA #9 and #10 results (for 2018 and 2019, respectively) suggest that resources are responding to FCM market signals.

### Generating Units in the ISO Interconnection Request Queue

The interconnection requests in the ISO’s interconnection queue reflect the region’s interest in building new generation capacity. Figure 4-3 shows the capacity of the withdrawn, active, and commercial generation-interconnection requests in the queue by RSP subarea as of April 1, 2017. As shown, over 90% of the active project proposals are in the BHE, ME, SEMA, RI, CT, and SWCT subareas. Together, these six subareas have approximately 11,611 MW under study or development out of 12,899 MW of active projects for New England.

Figure 4-3: Capacity of generation-interconnection requests by RSP subarea, November 1997 to April 2017 (MW).

Notes: All capacities are based on the projects in the ISO interconnection queue as of April 1, 2017, that would interconnect with the ISO system. Projects involving only transmission or that did not increase an existing generator’s capacity were excluded. Projects with more than one listing in the queue, representing different interconnection configurations, were counted only once.

Since the first publication of the queue in November 1997, 131 generating projects (15,842 MW) out of 458 total generator applications (totaling 88,617 MW) have become commercial. Since the queue’s inception, 251 proposed projects totaling approximately 59,876 MW have been withdrawn, reflecting a megawatt attrition rate of 68%. The 76 active projects in the queue total 12,899 MW. Figure 4-4 shows the resources in the queue, by state and fuel type, as of April 1, 2017. Figure 4-5 shows the total megawatts of the same resources by RSP subarea.

Figure 4-4: Resources in the ISO interconnection queue, by state and fuel type, as of April 1, 2017 (MW and %).

Notes: The “Other Renewables” category includes 37 MW wood 795 MW, solar, 63 MW fuel cell, and 77 MW battery storage capacity. The totals for all categories reflect all queue projects that would interconnect with the system and not all projects in New England.

Figure 4-5: Resources in the ISO interconnection queue, by RSP subarea and fuel type, as of April 1, 2017 (MW).

The processing of the interconnection requests in New England has progressed. With the exception of the Maine portion of the system (which has experienced a backlog of mostly wind interconnection requests; see Sections 9.2), substantially all the interconnection requests made through 2015 have completed the system-impact study phase or have moved to the Interconnection Agreement and commercialization phases.

The ISO is working with stakeholders to improve the interconnection process. An example of a recent improvement is the development of a cluster study approach, which provides the means for considering multiple requests in the same study and allocating the costs of significant upgrades among the cluster participants. The goal is to reduce the time taken to complete system impact studies for new inverter-based generators and address the interconnection queue backlog, particularly for generators in weak areas of the system, such as Maine (see Section 9.2.2). The initiative also seeks to address the curtailment and performance issues in system operations for inverter-based generators and to meet the modeling and performance requirements that new NERC standards are introducing.

## Summary

Sufficient resources are projected for New England through 2026, assuming no retirements and the successful completion of all new resources that have cleared the FCM. The planning analysis accounts for new resource additions that have responded to market improvements and low net-load growth, which reflects behind-the-meter PV and an increase in the forecasts of energy-efficiency resources. Although the recent trend of generation resource retirements has abated, additional resources are likely to retire. The ISO is committed to procuring adequate demand and supply resources through the FCM and expects the region to install adequate resources to meet the physical capacity needs that the ICRs will define for future years.

To date, resource-adequacy studies show that the most reliable and economic place for developing new resources is in NEMA/Boston and SEMA/RI. This is due to recent and anticipated retirements of aging fossil generation and the projected load growth in this area. Transmission improvements are underway, and new capacity additions are projected, but may not be enough to keep pace with retirements.

By design, the level of the ICR specified for New England could necessitate the use of specific OP 4 actions because the ICR calculation relies on the load relief these actions provide to meet the system’s resource adequacy planning criterion. Several factors would affect the frequency and extent of OP 4 actions, including the amount of resources procured to meet capacity needs, their availability, and actual system loads. The results of operable-capacity studies show that, beginning in 2022, the need for load and capacity relief by OP 4 actions will be approximately 2,400 MW during extremely hot and humid summer peak-load conditions. This amount is likely achievable through OP 4 actions by depleting operating reserves, scheduling emergency transactions with neighboring systems, and implementing 5% voltage reductions; disconnecting customers would not be required.

This section explained that the region is expected to meet representative operating-reserve requirements for the system as currently planned. Fast-start resources with a short lead time for project construction can satisfy near-term operating-reserve requirements while providing operational flexibility to major load pockets and the system overall. Continuing to properly locate and size economical baseload resources within major load pockets decreases the amount of reserves required within the load pocket and reduces the reliance on transmission facilities. Transmission improvements have and can continue to allow for the increased use of reserves from outside these areas.

Preserving the reliable operation of the system will become increasingly challenging with potential retirements, the increased reliance on natural gas resources, and the penetration of variable energy resources. These factors are expected to trigger the need for reliable resources, especially flexible resources able to provide operating reserves and ramping capabilities. To help address this need, the ISO has procured additional 10-minute reserves and replacement operating reserve.

Some of the 12,899 MW of resources in the interconnection queue will likely be developed to meet future resource needs. Resources fueled by natural gas are being proposed near the load centers in southern New England. Proposed onshore wind resources are predominantly in northern New England, and offshore resources are being proposed off the southeastern New England coast. Overall, the region is expected to experience more generating resource additions than retirements by summer 2020, the ISO expects that adequate resources will be available to meet net Installed Capacity Requirements. New fast-start generation under construction and proposed to be developed close to load pockets, and particularly the SEMA/RI and NEMA/Boston areas, will improve system reliability. However, delays in the construction of these new generators or additional retirements would decrease the amount of regional resources and could adversely affect the ability of the system to meet net Installed Capacity Requirements.

Section 7 discusses the region’s immediate concerns about the availability of natural-gas-fired and oil-fired generating units and their fuel security to produce electrical energy, especially during winter peak periods, and ISO and stakeholder efforts to address these challenges over the long term.

# Transmission System Performance Needs Assessments and Upgrade Approvals

Since 2002, the ISO and regional stakeholders have made significant progress developing transmission solutions in New England that address existing and projected transmission system needs. Major transmission projects and other projects help maintain system reliability and enhance the region’s ability to support a robust, competitive wholesale power market by reliably moving power from various internal and external sources to the region’s load centers.

This section discusses the need for transmission reliability and provides an overview of the New England transmission system, updates on the performance of the system, and the status of several transmission planning studies. The progress of major transmission projects and various types of transmission upgrades in the region as of June 2017 are also provided. The transmission planning studies account for known plans for resource additions and attritions (see Section 4) and the material effects of the EE forecast and the PV forecast (see Section 3). Previous RSPs, various PAC presentations, and other ISO reports contain information regarding the detailed analyses associated with many of these efforts.

The Transmission Planning Process Guide details the existing regional system planning process and how transmission planning studies are performed, and the Transmission Planning Technical Guide references the current standards and details the current criteria and assumptions used in transmission planning studies.

## The Need for Transmission Reliability

A reliable, well-designed transmission system that provides regional transmission service is essential for complying with mandatory reliability standards (see Section 2.1.7) and supporting the secure dispatch and operation of generation that delivers numerous products and services. The numerous products and services of a reliable transmission system include the following:

- Capacity

- Electric energy

- Operating reserves

- Load-following

- Automatic generation control

- Immediate contingency response to sudden resource or transmission outages

A reliable transmission system also plays an important role in the following functions:

- Improving access to and the reliability of supply resources

- Regulating voltage and minimizing voltage fluctuations

- Stabilizing the grid after transient events

- Facilitating the efficient use of regional supply and demand resources

- Reducing the amount of reserves necessary for the secure operation of the system

- Facilitating the scheduling of equipment maintenance

- Assisting neighboring balancing authority areas, especially during major contingencies affecting their reliability, and ensuring the reliability of the interconnected system

## Overview of New England’s Transmission System

In New England, the power system provides electricity to diverse areas, ranging from rural agricultural to densely populated cities, and integrates widely dispersed and varied types of power supply resources. Geographically, approximately 20% of New England’s peak loads are in the northern states of Maine, New Hampshire, and Vermont, and 80% are in the southern states of Massachusetts, Connecticut, and Rhode Island. Although the land area in the northern states is larger than the land area in the southern states, the greater urban development in southern New England creates the relatively larger demand and corresponding transmission density. This means that while the demands on the New England transmission system can vary widely, the system must reliably operate under the wide-ranging conditions present in the region at all times—in compliance with mandatory reliability standards—to move power from various internal and external sources to the region’s load centers.

The New England transmission system consists of mostly 115 kV, 230 kV, and 345 kV transmission lines, which in northern New England generally are longer and fewer in number than in southern New England. The region has 13 interconnections with neighboring power systems in the United States and Eastern Canada. Nine interconnections are with New York (NYISO) (two 345 kV ties; one 230 kV tie; one 138 kV tie; three 115 kV ties; one 69 kV tie; and one 330 MW, ±150 kV high-voltage direct-current (HVDC) tie—the Cross-Sound Cable interconnection). New England and the Maritimes (New Brunswick Power Corporation) are connected through two 345 kV AC ties. New England also has two HVDC interconnections with Québec (Hydro-Québec). One is a 120 kV AC interconnection (Highgate in northern Vermont) with a 225 MW back-to-back converter station, which converts alternating current to direct current and then back to alternating current. The second is a ±450 kV HVDC line with terminal configurations allowing up to 2,000 MW to be delivered at Sandy Pond in Massachusetts (i.e., Phase II).

## FERC Order No. 1000 Discussion

In May 2015, ISO New England implemented changes to the regional and interregional transmission planning process to comply with the directives in FERC Order No. 1000. The order establishes new electric transmission planning and cost allocation requirements for public utility transmission providers across the country. (Refer to Section 6.5 for a discussion of interregional aspects of Order No. 1000.) In addition, the order’s objectives include the following:

- Introduce competition into the development of regulated transmission solutions by removing arrangements that protect the right of first refusal (ROFR) for incumbent transmission providers

- Create a mechanism for transmission development to address public policies that drive transmission

While the order preserves the status of both proposed and planned projects on the ISO’s Regional System Plan project list as of May 18, 2015, it changed the ISO’s planning process going forward. The changes added the requirement to solicit proposals for reliability projects that have a planning need longer than three years beyond the completion of the needs assessment and to implement a process for identifying and evaluating federal, state, and local public policies that create the need for additional transmission. These changes have been incorporated into the Transmission Planning Process Guide.

Since the effective date of the order, the ISO has completed several area needs assessments or has conducted an update to an already completed needs assessment. The results of all the needs assessments show that that time-sensitive and a few non-time-sensitive needs exist. Thus, the solutions study process has been used first to solve the time-sensitive needs, and the Competitive Solutions Process for the few non-time-sensitive needs has been placed on hold until the time-sensitive needs are addressed through the solutions study process. After the solutions have been identified for the time-sensitive needs, the ISO will begin a new needs assessment, which will include the preferred solutions for the time-sensitive needs and identify any remaining needs. The ISO will continue to review the implementation of the competitive process in New England and across the country.

ISO New England began its first public policy process in January 2017 through a public notification to the PAC. The notification solicited stakeholder input to the New England States Committee on Electricity regarding state and federal public policy requirements and to the ISO for local (e.g., municipal and county) public policy requirements identified as driving transmission needs in New England In response to the notification, members of the PAC provided input to ISO New England and NESCOE. On May 1, 2017, NESCOE submitted a statement to the ISO that, at this time, no federal or state public policy requirements drive the need for a regionally developed transmission solution. In June, the ISO provided its decision to stakeholders that it will not pursue a public policy transmission study.

## Completed Major Projects

Since the publication of the 2015 Regional System Plan, the following major projects have been completed or are near completion:

- The Maine Power Reliability Program (MPRP) included the addition of significant new 345 kV and 115 kV transmission lines and new 345 kV autotransformers at key locations in Maine. The majority of MPRP is in service with the exception of the 115 kV Lewiston Loop projects, which are anticipated to be in service by mid-2018.

- The New Hampshire/Vermont 2020 Upgrades included the addition of a new 345/115 kV autotransformer, a new 230/115 kV autotransformer, several new 115 kV transmission lines, upgrades and rebuilds of several existing 115 kV lines, and several reactive device additions and substation upgrades. The majority of the New Hampshire/Vermont 2020 Upgrades are in service with the exception of a new 115 kV line from Madbury to Portsmouth, which is anticipated to be in service by the end of 2018, and the addition of reactive support at the Amherst station in New Hampshire, which is the subject of an ongoing reevaluation.

- The Interstate Reliability Project (IRP) component of the New England East–West Solution (NEEWS) included the addition of significant 345 kV facilities in central Massachusetts, eastern Connecticut and northern Rhode Island. The IRP was placed in service in December 2015.

Study efforts continue throughout New England to address remaining issues discussed in the next section.

## Key Study Area Update

Historically, the two most significant issues facing the northern New England area have been to maintain the general performance of the long 345 kV corridors, particularly through Maine, and to ensure sufficient system reliability to meet demand. The region faces thermal and voltage performance issues and stability concerns. The system of long 115 kV lines, with weak sources and high real- and reactive-power losses, is exceeding its ability to integrate generation and efficiently and effectively serve load. Also, in many instances, the underlying systems of 34.5 kV, 46 kV, and 69 kV lines are exceeding their capabilities, and some are being upgraded, placing greater demands on an already stressed 115 kV system.

The most significant concerns in the southern New England area involve maintaining the reliability of supply to serve load and developing the transmission infrastructure due to the retirement of generation throughout this area. In many areas, an aging low-capacity 115 kV system has been overtaxed and is no longer able to serve load and support generation reliably. Ongoing planning and power system upgrades will ensure the system can meet its current level of demand and prepare for future power system conditions.

To address the issues in New England, study efforts have been progressing on a wide range of system concerns and have been grouped into several key study areas shown in Figure 5-1 and detailed below.

Figure 5-1: Key study areas in New England.

### Southwest Connecticut Key Study Area

The Southwest Connecticut (SWCT) study area is located inside the Southwest Connecticut import interface. It borders the New England to New York interface along the Connecticut state border. The SWCT study area is divided into five study subareas: Frost Bridge–Naugatuck Valley, Housatonic Valley/Norwalk–Plumtree, Bridgeport, New Haven–Southington, and Glenbrook–Stamford.

The SWCT study area has gone through three study efforts over the past 10 years. These study efforts are identified by the study horizon years of 2018, 2022, and 2025. The 2018 needs assessment of this area identified interdependent and independent subarea needs, which were addressed by the Glenbrook–South End cable and the Mill River–Quinnipiac 8300 line reconfiguration. Both projects have been placed in service.

Due to changes in net demand forecasts, changes in topology resulting from the approval of Glenbrook–South End cable and Mill River–Quinnipiac 8300 line reconfiguration and the results of FCA #7 that included the retirement of Bridgeport Harbor 2 and the retirement notification of Norwalk Harbor, a new needs assessment was undertaken. This study effort was referred to as the 2022 SWCT Needs Assessment and reflected the latest transmission planning assumptions. The needs assessment was presented to the PAC in February 2014, and the report was posted in June 2014.

The SWCT area is primarily an import area and depends on the transmission lines connecting the area to the rest of the system to serve load. Most of the issues in this study area are load-serving issues caused by the loss of key transmission elements under N-1 and N-1-1 contingency conditions. The result of the 2022 needs assessment still showed needs present in all subareas with the exception of the Glenbrook–Stamford subarea. A 2022 SWCT solutions study solved the needs from the 2022 SWCT Needs Assessment; the preferred solution components were presented to the PAC in July 2014, and the solutions study report was completed in February 2015. All the identified preferred solution components were on the 115 kV system and included rebuilding and reconductoring lines, installing new lines, rebuilding two stations, and adding reactive support to maintain voltage. Several of the projects within the SWCT suite of projects are already in service, and all the components of the preferred solutions are expected to be in service by April 2019. The major components of the preferred solutions for addressing the needs are listed in the latest version of the RSP Project List (see Section 5.9).

Because the CPV Towantic and Wallingford 6 and 7 projects received capacity supply obligations in FCA #9, and a proposed unit at Bridgeport Harbor received a CSO in FCA #10, a new 2025 study effort for the SWCT area evaluated the validity of the previously developed 2022 transmission solutions for the area and whether any new needs exist. The 2025 Update results showed three transmission solutions were no longer required and were canceled. New needs were identified in the Norwalk–Plumtree subarea. However, these new needs were resolved with two of the previously identified 2022 SWCT solution components; therefore, no additional solutions were necessary.

### Greater Hartford Central Connecticut Key Study Area

The Greater Hartford Central Connecticut (GHCC) study area is located between the Connecticut Import interface and the SWCT import interface, while only parts of the study area are within the Western Connecticut import area. The GHCC study area represents about 35% of Connecticut load and is divided into four study subareas: Greater Hartford, Northwest Connecticut, Middletown, and Manchester/Barbour Hill.

The GHCC study area is primarily an import area and depends on the transmission lines connecting the area to the rest of the system to serve load. Most of the issues seen in the study area are load-serving issues caused by the loss of key transmission elements under N-1 and N-1-1 contingency conditions. The needs assessment for this study, referred to as the 2022 GHCC Needs Assessment, shows that system needs exist in all four subareas, attributed to load-serving issues and the need for increased import capability into western Connecticut.  An updated GHCC solutions study was completed to solve the needs from the 2022 GHCC Needs Assessment; the preferred solution components were presented to the PAC in July 2014, and the solutions study report was completed in February 2015. The preferred solution components included adding two new autotransformers and 115 kV upgrades, such as reconductoring lines; installing new lines; separating double-circuit towers (DCTs); rebuilding two stations; and adding reactive support to maintain voltage. Several of the projects within the GHCC suite of projects are already in service, and all the components of the preferred solutions are expected to be in service by December 2018. The major components of the preferred solutions for addressing the needs are included in the latest version of the RSP Project List (see Section 5.9).

### Pittsfield and Greenfield Key Study Area

The Pittsfield and Greenfield study area extends from the city of Pittsfield north to the Vermont border, east to Greenfield and south to Amherst (MA).

The Pittsfield and Greenfield study area has gone through two study efforts over the past 10 years, identified by the study horizon years of 2013/2018 and 2022. The results of the 2013/2018 needs assessment showed various needs throughout the study area, and the 2013/2018 solutions study identified preferred solutions to solve the needs. Like the SWCT study, a new needs assessment was started due to changes in net demand forecasts, changes in topology resulting from the approval of new projects, and the results of FCA #7. The result of the 2022 needs assessment continued to show various needs throughout the study area.

An updated 2022 solutions study was completed to solve the needs from the 2022 needs assessment; the preferred solution components were presented to the PAC in April 2015, and the solutions study report was completed in October 2015. The preferred solution components included rebuilding a station, adding a new autotransformer, adding reactive support to maintain voltage on the 345 kV system, rebuilding and reconductoring lines, installing a new line, separating double-circuit towers, and adding reactive support to maintain voltage on the 115 kV system. Several of the projects within the Pittsfield and Greenfield suite of projects are already in service, and all the components of the preferred solutions are expected to be in service by December 2019. The major components of the preferred solutions for addressing the needs are included in the latest version of the RSP Project List (see Section 5.9).

### Greater Boston Key Study Area

The Greater Boston study area is defined as the communities north and east of Interstate 495 north to the New Hampshire border, the city of Boston, and the suburbs south of Boston. The Greater Boston study area is divided into seven subareas:

- 345 kV and 115 kV Northern Ties to Greater Boston

- Woburn and Lexington Area

- Downtown Boston 115 kV Cables

- Sudbury, Marlboro, and Northborough Area

- Holbrook and W. Walpole Area

- Boston, Golden Hills and Wakefield Junction Area

- 115 kV Lines Near Tewksbury

The Greater Boston study area has gone through two study efforts over the past 10 years. The first needs assessment, with a study horizon of 2013 and 2018, was published in 2010. Because the study area changed significantly, a second needs assessment, with a study horizon of 2018 and 2023, was published in 2015. The changes that prompted the updates can be categorized into four topics: load forecast and demand resources, resource additions and retirements, transmission system topology, and system modeling.

The needs assessments showed thermal and voltage needs under peak load conditions in the Greater Boston study area, high-voltage needs in the Greater Boston study area under minimum load conditions, and, as part of the short-circuit analysis, overdutied breakers in the downtown Boston subarea. The Greater Boston solutions study solved the needs from the latest needs assessment, the preferred solution components were presented to the PAC in February 2015, and the solutions study report was completed in August 2015. The major components of the preferred solutions for addressing the needs includes multiple new 345 kV facilities, new 115 kV facilities, and upgrades to existing equipment within the study area. The Greater Boston suite of projects also included the addition of a +/-200 MVAR static synchronous compensator (STATCOM) in Maine based on the stability testing performed for the preferred solution. Several of the projects within the Greater Boston suite of projects are already in service, and all the components of the preferred solutions are expected to be in service by December 2019. The details for the different solution components are included in the latest version of the RSP Project List (see Section 5.9).

### Southeastern Massachusetts and Rhode Island Key Study Area

The Southeastern Massachusetts and Rhode Island (SEMA/RI) study area focuses on the SEMA and the RI load zones, which encompass the areas within Massachusetts located south of Boston and the entire state of Rhode Island. The SEMA/RI study area is divided into six subareas: Farnum, West Medway–West Walpole, South Shore, Industrial Park, Somerset–Newport, and Cape Cod.

The major goals of the SEMA/RI study were to determine any long-term system needs required to integrally serve the broad SEMA and Rhode Island areas. Several PAC presentations detailed needs in the study area, but a needs assessment was never completed due to the retirement announcements of Brayton Point in late 2013 and Pilgrim Nuclear Power Station (Pilgrim) in late 2015. After the Pilgrim retirement announcement, the SEMA/RI study was restarted in late 2015 with a study horizon of 2026. The 2026 needs assessment was presented to PAC in March 2016, and the report was published in May 2016. The needs assessment results continued to show various time-sensitive needs on the 115 kV system in all the SEMA/RI subareas. A 2026 solutions study solved the time-sensitive needs from the 2026 needs assessment; the preferred solution components were presented to the PAC in December 2016, and the solutions study report was completed in March 2017. Most of the preferred solution components were identified on the 115 kV system and included adding a new switching station, reconductoring lines, installing new lines, separating double-circuit towers, and adding reactive support to maintain voltage. One 345 kV project required the separation of a DCT. The major components of the preferred solutions for addressing the needs are included in the latest version of the RSP Project List. The project to replace the wave trap on the 114 line at the Tremont station has been cancelled because the work was previously performed as part of other station work.

The Aquidneck Island area, which is part of the Somerset–Newport subarea, underwent an advanced needs assessment and solutions study in early 2015, The needs assessment results showed thermal overloads on the 115/69 kV autotransformer and 69 kV lines serving the area. The preferred solution components included the rebuild of a station and 69 kV lines and the conversion of 69 kV equipment to 115 kV. The major components of the preferred solutions for addressing the needs are included in the latest version of the RSP Project List (see Section 5.9).

The SEMA/RI study area will undergo another needs assessment beginning in mid-2017 to identify remaining needs, if any. This needs assessment will consider the preferred solutions, which were developed to solve time-sensitive needs found in the SEMA/RI 2026 needs assessment.

In late 2016, a SEMA/RI minimum-load needs assessment began to evaluate the reliability performance and identify reliability-based transmission needs in the SEMA/RI study area under minimum load conditions. The SEMA/RI minimum-load needs assessment was presented to PAC in November 2016. An updated presentation was made to PAC in March 2017, and the draft needs assessment report was completed in June 2017.

### Maine Key Study Area

In 2013, as a follow up to the Maine Power Reliability Program, a 2023 needs assessment studied the Maine transmission system. The 2023 needs assessment was presented to PAC in September 2014, and the report was published in December 2016. The results of the 2023 needs assessment show various time-sensitive needs on the 115 kV system.

Due to a large mill retirement, significant transmission system upgrades added to the study area since the 2023 needs assessment was completed, and further review and analysis of the needs results, an addendum analysis report to the 2023 Maine needs assessment was completed. The results of the addendum to the 2023 needs assessment continued to show various time-sensitive needs on the 115 kV system and high-voltage needs on the 345 kV system at minimum load levels. A 2023 solutions study developed alternatives to address the identified time-sensitive needs from the 2023 needs assessment, which the ISO presented to PAC. In early 2017, the 2023 solutions study was suspended, however, for the following reasons:

- Changes to Planning Procedure No. 3 (PP 3), Reliability Standards for the New England Area Pool Transmission Facilities

- Incorporation of probabilistic planning methods to establish the local dispatch used in needs assessment studies

- Addition of resources as a result of FCA #11

- Retirement delist bids for FCA #12

- Updated load, energy-efficiency and photovoltaic forecasts

- Results of changes to NPCC classification of the bulk power system (BPS)

Taking into account all these changes, a new needs assessment for the Maine study area will begin in mid-2017.

### New Hampshire and Vermont Key Study Area

As a follow up to the New Hampshire/Vermont 2020 Upgrades, the latest NH/VT needs assessment was completed using a study horizon of 2023. The 2023 needs assessment included updated load and resource assumptions and the retirement of the Vermont Yankee Nuclear Plant. The 2023 needs assessment was presented to PAC in March 2014, and the report was published in August 2014.

The results of the 2023 needs assessment show various time-sensitive thermal and voltage needs on the 115 kV system in New Hampshire and Vermont and high-voltage needs on the 345 kV system at minimum load levels in New Hampshire. For the Vermont study area, solution components for the needs identified in the 2023 needs assessment were developed in a 2023 solutions study, the preferred components were presented to the PAC in September 2014, and the solutions study report was completed in November 2014. The preferred solution components were for the 115 kV system and included rebuilding a new switching station, rebuilding a line, and adding reactive support to maintain voltage.

An addendum report to the 2023 needs assessment was published in October 2015 to address topology changes. The results continued to show time-sensitive thermal and voltage needs on the 115 kV system and high-voltage needs on the 345 kV system at minimum load levels in New Hampshire. A New Hampshire 2023 solutions study was initiated, and potential solutions to address the time-sensitive needs from the 2023 needs assessment were developed and presented to PAC.

The ISO has cancelled the Amherst substation project (RSP ID 1269) and the Eversource portion of the load transfer project (RSP ID 1300) from the New Hampshire/Vermont 2020 Upgrades. The Amherst project was cancelled due to concerns with the feasibility of its implementation. This project consists of adding a 345 kV breaker and two 25 MVAR capacitor banks to the substation. The Eversource portion of the load-transfer project was cancelled because the 2023 NH/VT needs assessment found that it was not adequate to address the related needs. The Eversource portion of this project consists of a load transfer at Pemigewasset to Laconia for certain system conditions. Time-sensitive needs related to these projects are documented in the 2023 needs assessment addendum report, and alternatives to these projects were explored as part of the potential solutions presented to PAC. In early 2017, the 2023 solutions study was suspended for the same reasons the Maine 2023 solutions study was suspended, as listed above. Taking into account all these changes, a new needs assessment for the New Hampshire area will begin in mid-2017.

### Eastern Connecticut Key Study Area

The Eastern Connecticut (ECT) study area is the area in the eastern part of Connecticut not covered by the SWCT or GHCC studies. The ECT study area is located outside the western Connecticut import interface and inside the Connecticut import/export interface. The study area also borders part of the New England east–west and west–east interfaces mainly along the Rhode Island border.

The ECT study area is a large load pocket served from the Killingly, Card, and Montville stations and a 115 kV line from Rhode Island. A needs assessment with a study horizon of 2022 was presented to the PAC in May and June 2013, and the report was published in June 2015. The results of the 2022 needs assessment showed various time-sensitive needs on the 115 kV and 69 kV portions of the system.

A 2022 ECT solutions study began to address the time-sensitive needs found in the 2022 needs assessment, and solution alternatives were presented to PAC in September 2016. In early 2017, the 2022 solutions study was suspended due to the same reasons the Maine and New Hampshire 2023 solutions studies were suspended, as listed above. Taking into account all these changes, a new needs assessment will begin in mid-2017.

  - General Need for Future Transmission

Since 2002, 714 project components have been placed in service across the region to fortify the transmission system. In addition, 153 project components have a status of planned, proposed, or under construction. Overall, the estimated investment in New England to maintain reliability has been $12.4 billion since 2002. With these system upgrades in place, combined with the changes in assumptions to needs assessments described previously, the need for additional reliability-based transmission upgrades, as shown by the steady-state studies of peak load, is expected to decline over the planning horizon. Conversely, generation retirements and studies reviewing system performance, accounting for the integration of nonsynchronous resources and improved load modeling, may drive the need for some additional reliability-based transmission upgrades.

## New England Asset Management

Because of the general age of the transmission system in New England, many assets are reaching their end of life and are requiring significant refurbishment. These activities are spread across the system and are being addressed either individually or as part of an ongoing solutions assessment. The New England Asset Management Key Study Area is a repository to store all asset-condition-related PAC presentations.

The ISO announced at the October 2015 PAC meeting during the Regional System Plan transmission projects update that the RSP Project List would not capture asset-condition projects beyond the May 18, 2015, effective date of Order No. 1000. The decision was based on the fact that Section 4.1(a) of Attachment K of the OATT does not identify the asset-condition classification as a trigger for a needs assessment, and the equipment owner, not the ISO, must identify asset-condition issues.

In 2016, the ISO created a New England Asset-Condition Update List to capture all asset-condition PAC presentations that occurred after May 18, 2015. The ISO updates the new Asset-Condition Update List three times per year along with the RSP Project List.

## Local System Plan

The Local System Plan (LSP) process is described in Appendix 1 to Attachment K of the Open Access Transmission Tariff. In general, LSP projects are needed to maintain the reliability of the non-pool transmission facility (PTF) system. While LSP projects are designed to serve the needs of the non-PTF, they typically involve PTF components. Under FERC Order No. 1000, projects eligible for regionalization of costs should be subject to a competitive solicitation, unless they are excluded by FERC. LSP projects are considered non-regionalized and therefore fall under the FERC exclusion. Currently, Appendix 1 does not have a list of excluded-from-competition type PTF projects or a mechanism for a competitive solicitation. Until this concern is resolved, as of the May 18, 2015, Order No. 1000, effective date, the ISO is no longer places LSP projects on the RSP Project List. Information regarding LSP projects is provided to stakeholders through the Transmission Owner Planning Advisory Committee (TOPAC) meetings.

## RSP Project List and Projected Transmission Project Costs

The RSP Project List is a summary of needed transmission projects for the region and includes information on project type, the primary owner, the transmission upgrades and their status, and the estimated cost of the PTF portion of the project. The RSP Project List includes the status of reliability transmission upgrades, market-efficiency transmission upgrades, elective transmission upgrades, and generator-interconnection transmission upgrades (described in Section 2.1.1). The list also will include public policy transmission upgrades. The ISO updates this list at least three times per year. Additional information on the project classifications included in the RSP Project List is available in the Transmission Planning Process Guide.

The ISO regularly updates the PAC on RTU and METU (and eventually PPTU) study schedules, scopes of work, assumptions, draft and final results, and project costs. Projects are considered part of the Regional System Plan consistent with their status and are subject to transmission cost allocation for the region. RSP17 incorporates information from the June 2017 RSP Project List.

This section discusses RTUs underway and their costs and the status of the ETUs in the region. It also explains why no market-efficiency-related transmission upgrades have been needed and provides information on several transmission upgrades developed and paid for by generator developers.

### Reliability Transmission Upgrades

As of June 2017, the total estimated cost of transmission upgrades—proposed, planned, and under construction—was approximately $4.0 billion, as shown in Table 5-1.

Table 5-1
Estimated Cost of Reliability Projects as of June 2017 Plan Update (Million $)

| Projects | Project Costs (millions of $)(a) |
| --- | --- |
| Major projects |  |
| Maine Power Reliability Program | 1,459 |
| Greater Hartford and Central Connecticut | 337 |
| New England East–West Solution (NEEWS) | 1,581 |
| NEEWS (Greater Springfield Reliability Project)—$676.0 million |  |
| NEEWS (Rhode Island Reliability Project)—$362.3 million |  |
| NEEWS (Interstate Reliability Project)—$482.3 million |  |
| NEEWS (other)—$59.6 million |  |
| Southeast Massachusetts/Rhode Island Reliability Project | 309 |
| Pittsfield-Greenfield Project | 191 |
| Greater Boston—North, South, Central, Western Suburbs | 827 |
| New Hampshire Solution—Southern, Central, Seacoast, Northern | 328 |
| Vermont Solution—Southeastern, Connecticut River | 96 |
| Southwest Connecticut | 415 |
| Subtotal(b) | 5,543 |
| Other projects(c) | 6,817 |
| New projects(d) | 43 |
| Total(b) | 12,403 |
| Minus “concept” projects | 0 |
| Minus “in-service” projects | −8,426 |
| Aggregate estimate of active projects in the plan(b) | 3,977 |

(a) 	Transmission owners provided all estimated costs, which may not meet the guidelines described in Planning Procedure No. 4, Procedure for Pool-Supported PTF Cost Review, Attachment D, “Project Cost Estimating Guidelines” (May 6, 2016), https://www.iso-ne.com/static-assets/documents/rules_proceds/isone_plan/pp04_0/pp4_0.pdf.

(b) 	Totals may not sum due to rounding.

(c) 	The "Other Projects" category is the sum of all other project costs in the RSP Project List not explicitly listed above. The cost estimates for projects in the “Major Projects” category move to the “Other Projects” category once they are completed.

(d) 	The cost for the “New Projects” category reflects updated costs from the June 2017 project list update compared with the March 2017 update.

The PTO Administrative Committee provides annual informational filings to FERC on the current regional transmission service rates and annual updates to the ISO and NEPOOL on projected regional transmission rates, as shown in Table 5-2.

Table 5-2
Actual and Forecast Regional Transmission Service Rates, 2016 to 2021(a)

|  | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 |
| --- | --- | --- | --- | --- | --- | --- |
|  | Actual(b) |  | Forecast(c) |  |  |  |
| Estimated additions in service and CWIP ($ millions)(d) | N/A | N/A | 1,098 | 1,059 | 589 | 446 |
| Forecasted revenue requirement ($ millions) | 159 | 162 | 165 | 155 | 93 | 68 |
| Total revenue requirement | 2,069 | 2,195 | 2,360 | 2,515 | 2,608 | 2,676 |
| Year-prior 12 CP (kW)(e) | 19,871,253 | 19,605,055 | 19,605,055 | 19,605,055 | 19,605,055 | 19,605,055 |
| RNS rate increase from prior year ($/kW-year) | 5.40 | 7.86 | 8 | 8 | 5 | 4 |
| RNS rate ($/kW-year) | 104.10 | 111.96 | 120 | 128 | 133 | 137 |
| RNS rate forecast using a 55.5% load factor) ($/kWh) | 0.021 | 0.023 | 0.025 | 0.026 | 0.027 | 0.028 |
| TOUT service rate ($/kWh) | 0.01188 | 0.01278 | 0.014 | 0.015 | 0.015 | 0.016 |

(a) 	The figures may not agree because of rounding.

(b) 	2016 PTO Administrative Committee (PTO-AC)  Informational Filing, 2017 PTO-AC Informational Filing.

(c)	Source: RNS Rates: PTF Forecast, PTO-AC  Rates Working Group presentation at the NEPOOL RC /TC  Summer Meeting (July 18–19, 2017), https://www.iso-ne.com/static-assets/documents/2017/07/2017_07_18_tc_a02_forcst.pptx. The 2018–2021 rate forecast reflects PTO Administrative Committee estimated data and assumptions and is preliminary and for illustrative purposes only. Therefore, such estimates, assumptions, and rates are expected to change as current data become available.

(d)	“CWIP” refers to construction work in progress.

(e)	“12 CP” refers to the average of all the monthly regional network loads (per the OATT, Section 21.2) for the 12 months of the calendar year on which the rate is based.

### Lack of Need for Market-Efficiency-Related Transmission Upgrades

To date, the ISO has not identified the need for market-efficiency transmission upgrades (METUs), primarily designed to reduce the total net production cost to supply the system load, because of the following:

- Reliability transmission upgrades have resulted in significant market-efficiency benefits, particularly when out-of-merit operating costs were reduced.

- The development of economic resources and fast-start resources in response to the ISO’s wholesale electricity markets has also helped eliminate congestion and Net Commitment-Period Compensation (NCPC).

In 2016, the ISO performed an economic evaluation of the potential benefits of upgrading the Keene Road Export Interface. The needs assessment showed that increasing the capability across this interface would provide minimal savings in productions costs. After discussing these findings with stakeholders, the ISO determined that the savings in production costs were not sufficient to move forward with the Competitive Solutions Process.

This section summarizes the historical systemwide congestion and NCPC. Economic studies are analyzing future system performance that may identify future need for METUs, (see Section 9.4.1).

#### Transmission Congestion

As shown in Table 5-3, recent experience has demonstrated that the regional transmission system has little congestion among the New England load zones relative to the Hub. At approximately $39 million in 2016, the total day-ahead and real-time congestion costs remain low, and mitigation by additional transmission upgrades is not warranted. Planned reliability transmission upgrades could reduce congestion costs further, as well as reduce transmission system losses.

Table 5-3
ISO New England Transmission System Day-Ahead, Real-Time,
and Total Congestion Costs and Credits, 2003 to 2016 ($)

| Year | Day-Ahead Congestion(a, b) | Real-Time Congestion(a, c) | Total Congestion(a, d) |
| --- | --- | --- | --- |
| 2003 | −$85,964,588 | −$1,385,442 | −$87,350,030 |
| 2004 | −$82,384,177 | $2,833,577 | −$79,550,600 |
| 2005 | −$273,449,871 | $6,814,010 | −$266,635,861 |
| 2006 | −$192,419,271 | $12,683,233 | −$179,736,038 |
| 2007 | −$130,145,862 | $17,721,136 | −$112,424,726 |
| 2008 | −$125,358,187 | $4,295,716 | −$121,062,471 |
| 2009 | −$26,681,125 | $1,593,273 | −$25,087,852 |
| 2010 | −$37,321,849 | −$622,287 | −$37,944,136 |
| 2011 | −$17,957,036 | −$246,892 | −$18,203,928 |
| 2012 | −$29,326,997 | −$174,471 | −$29,501,468 |
| 2013 | −$46,186,914 | −$175,059 | −$46,361,973 |
| 2014 | −$34,218,158 | $2,153,173 | −$32,064,985 |
| 2015 | −$30,168,691 | −$1,038,608 | −$31,207,299 |
| 2016 | −$34,272,410 | −$4,599,343 | −$38,871,754 |

(a) 	Negative numbers indicate charges to load; positive numbers indicate credits to load.

(b) 	Day-ahead congestion charges = the amount billed to load minus payments to the generators.

(c) 	Real-time congestion refers to deviations from day-ahead charges. Additional outages, problems, and non-day-ahead load issues that cause additional generator dispatch within the congested zone results in a credit to load. Less generation within the zone results in a real-time charge to load.

(d) 	Total congestion refers to money the ISO uses to pay FTR holders.

The highest mean annual positive difference in the congestion component of the LMPs was $0.69/MWh at the BOSTON RSP subareas relative to the Hub. The small congestion component of the locational marginal prices suggests that the system has little congestion. Portions of the system remote from load centers, especially northern Maine, have high negative loss components. The MPRP added 345 kV facilities, and recently, shunt reactive compensation, which will reduce losses in Maine.

#### Transmission Improvements to Load and Generation Pockets Addressing Reliability Issues

The performance of the transmission system is highly dependent on embedded generators operating to maintain reliability in several smaller areas of the system. Consistent with ISO operating requirements, the generators may be required to provide second-contingency protection or voltage support to avoid overloads of transmission system elements. Reliability may be threatened when only a few generating units are available to provide system support, especially when considering normal levels of unplanned or scheduled outages of generators or transmission facilities. This transmission system dependence on local-area generating units typically can result in reliability payments associated with out-of-merit unit commitments. The total cost for these reliability payments are a small portion of the overall wholesale electricity market costs in New England of $5.4 billion in 2016.

Some areas currently depend on out-of-merit generating units to some degree to maintain reliability, or have been dependent on these units until recently. The NCPC in the Boston area totaled approximately $28.4 million for 2016, approximately 88% of the New England total. After the upgrades being pursued as part of the Greater Boston projects are placed in service, the need to run units out of merit (and subsequent NCPC) is expected to decline (see Sections 5.5.4).

Generating units in load pockets may receive second-contingency or voltage-control payments for must-run situations. Table 5-4 shows the NCPC by type and year. The 2009, 2010, 2011, and 2012 figures showed a significant decrease from the preceding years, averaging less than $17 million per year. The 2013, 2014, 2015, and 2016 figures show a modest increase, averaging approximately $43 million per year. At $32.6 million, 2016 represents the lowest total of the most recent four-year period. Because reliability transmission upgrades improve the economic performance of the system, upgrading transmission solely to reduce NCPC is not often justifiable.

Table 5-4
Net Commitment-Period Compensation by Type and Year (Million $)

| Year | Second Contingency(a) | Voltage | Total(b) |
| --- | --- | --- | --- |
| 2003(c) | 36.0 | 14.4 | 50.4 |
| 2004 | 43.9 | 68.0 | 111.9 |
| 2005 | 133.7 | 75.1 | 208.8 |
| 2006 | 179.9 | 19.0 | 199.0 |
| 2007 | 169.5 | 46.0 | 215.5 |
| 2008 | 182.9 | 29.4 | 212.3 |
| 2009 | 17.5 | 5.0 | 22.5 |
| 2010 | 3.9 | 5.1 | 9.0 |
| 2011 | 6.0 | 5.8 | 11.9 |
| 2012 | 8.8 | 14.9 | 23.6 |
| 2013 | 38.0 | 16.6 | 54.6 |
| 2014 | 32.4 | 6.2 | 38.5 |
| 2015 | 42.7 | 5.4 | 48.1 |
| 2016 | 31.1 | 1.4 | 32.6 |

(a) NCPC for first-contingency commitment and distribution support is not included.

(b) Numbers may not add precisely due to rounding.

(c) NCPC under Standard Market Design began in March 2003.

In 2016, the ISO filed revisions to Market Rule 1 that calculate NCPC. These revisions ensure better consistency with subhourly settlement rules and improve incentives for market participants to follow the ISO’s operating instructions.

Transmission solutions continue to be put in place where proposed generating or demand resources have not relieved transmission system performance concerns. The ISO is studying many of these areas, and while transmission projects are still being planned for some areas, other areas already have projects under construction and in service to mitigate dependence on generating units. Reliability transmission upgrades were used to address these system performance concerns, which contributed to a substantial reduction in out-of-merit operating costs.

### Required Generator-Interconnection-Related Upgrades

No significant transmission system upgrades resulted from the interconnection of generators. Most of the generator-interconnection-related upgrades are fairly local to the point of interconnection of the generator. The RSP Project List identifies the PTF upgrades (see Section 4.5.3).

### Elective Transmission Upgrades

A number of new elective transmission upgrades have been added to the ISO Interconnection Request Queue. Many of these are focused on delivering zero or low-carbon resources to or within New England. As of April 1, 2017, 15 projects have active interconnection requests as elective transmission upgrades:

- Queue Project (QP)-498: 400 MW, 150 kV HVDC tie; New York Power Authority (NYPA) 230/115 kV substation to VELCO 345 kV New Haven substation

- QP-499: 1,090 MW, 300 kV HVDC/AC tie; HQ Des Cantons substation to Public Service of New Hampshire (PSNH) Deerfield substation

- QP-500: Keene Road ETU, Emera Keene Road substation

- QP-501: 1,000 MW HVDC tie—import only, HQ 735 kV substation to VELCO 345 kV Coolidge substation

- QP-506: 1,000 MW internal HVDC—north to south flow, Northern Maine Independent System Administrator (NMISA) to NSTAR 345 kV K Street substation

- QP-507: 75 MW AC tie—bidirectional; NMISA Mullen substation to Emera Keene Road substation

- QP-508: 600 MW HVDC tie from New York to western Massachusetts—bidirectional; NY Alps substation to Western Massachusetts Electric Company (WMECO) 345 kV Berkshire substation

- QP-569: 1,200 MW internal HVDC-north to south flow, from Emera 345 kV Orrington substation to NSTAR 345 kV K Street substation

- QP-571: 850 MW internal 345 kV AC transmission line between the Wyman area and the Iberdrola 345 kV Larrabee Road substation

- QP-585: 900 MW HVDC bidirectional from New Brunswick to eastern Massachusetts, connecting to the Eversource 345 kV Mystic substation

- QP-589: 500 MW internal 345 kV AC transmission line between the Wyman area and a new Iberdrola 345 kV Pittsfield substation

- QP-590: 1,200 MW internal 345 kV AC transmission line between the northern Maine area and a new Iberdrola 345 kV Pittsfield substation

- QP-591: 400 MW internal 345 kV AC transmission line addition in Maine

- QP-625: 1,600 MW internal 345 kV AC transmission line connection to the National Grid 345 kV Brayton Point substation

- QP-627: 1,200 MW HVDC tie north-south flow from Quebec to Northern New Hampshire at the National Grid 230 kV Comerford substation

## Summary

Significant transmission projects have been placed in service across New England since 2002. These projects help maintain system reliability, enhance the region’s ability to support a robust, competitive wholesale power market by reliably moving power from various internal and external sources to the region’s load centers, and ensure the system can meet its current level of demand and prepare for future load growth.

As of summer 2017, MPRP, the New Hampshire/Vermont 2020 Upgrades, and the NEEWS suite of projects are complete or nearing completion. In addition, SWCT, GHCC, Pittsfield and Greenfield, Greater Boston, and SEMA/RI have identified projects to solve needs found in their study areas. These reliability upgrade projects will bolster the 345 kV and 115 kV facilities of the New England transmission system. Study work remains to be done in the Maine, New Hampshire, Vermont, and the Eastern Connecticut areas.

Since May 2015, ISO New England began implementing changes to the regional and interregional transmission planning process to comply with the directives in FERC Order No. 1000. As of summer 2017, the ISO has not yet identified any regional non-time-sensitive system need that requires a request for proposals (RFP) soliciting competitive bids to solve the need. The public policy process began in January 2017 and concluded in June with a finding that a public policy transmission study will not be pursued in this public policy planning cycle.

Many new elective transmission upgrades have been proposed, which focus on delivering zero or low-carbon resources to New England. As of June 1, 2017, four projects are under study as elective transmission upgrades, and three have received their proposed plan application approval.

All transmission projects are developed to meet the reliability requirements of the entire region and are fully coordinated regionally and interregionally. Most projects on the RSP Project List remain subject to regional cost allocation. With transmission expansion in the region, the ISO meets all required transmission planning requirements, and little congestion is currently evident on the system.

A total of 730 project components have been placed in service across the region since 2002. In addition, another 137 project components have a status of planned, proposed, or under construction. Overall, the estimated investment in New England to maintain reliability has been $12.4 billion since 2002. With these system upgrades in place, combined with the changes in assumptions to needs assessments, the need for additional reliability-based transmission upgrades is expected to decline over the planning horizon.

# Interregional Coordination

Interconnections with neighboring systems allow for the exchange of capacity and energy. The tie lines facilitate access to a diversity of resources; compliance with environmental obligations; and the more economic, interregional operation of the system. Quantifying these benefits, identifying potential needs for additional interconnections, and coordinating the planning of the interconnected system are becoming increasingly important.

The ISO coordinates its planning activities with neighboring systems and across the Eastern Interconnection. Consistent with the mandatory reliability requirements of the North American Electric Reliability Corporation (NERC), the ISO must identify and resolve interregional planning issues, as identified in needs assessments and solutions studies. With other entities within and outside the region, including neighboring areas, the ISO conducts studies that aim to, for example, improve production cost models, share simulation results, investigate the challenges to and possibilities for integrating renewable resources, and address other common issues affecting the planning of the overall system.

The ISO also participates in numerous interregional planning activities with the US Department of Energy (DOE), the Northeast Power Coordinating Council, and other planning authority areas in the United States and Canada. The overriding purpose of these projects is to enhance the widespread reliability of the interregional electric power system.

This section discusses the main collaborative efforts the ISO is undertaking with neighboring areas to analyze the interconnection-wide system, study and address interregional transfers and seams issues, and improve competitive electricity markets in North America.

## Eastern Interconnection Planning Collaborative Studies

The electric power planning authorities of the Eastern Interconnection, including ISO New England, formed the Eastern Interconnection Planning Collaborative (EIPC) in 2009 to address their portion of North American planning issues, combine the existing regional transmission expansion plans, and analyze the interconnection-wide system. During 2015, EIPC initiated the first year of its new two-year planning cycle, again developing and studying “roll-up” cases, which combined each region’s electric power system plan into a comprehensive model of the Eastern Interconnection. This work effort expanded the roll-up cases to include models for 2025 summer and winter peak scenarios, which were rigorously tested under reference and transfer conditions using NERC criteria. The final report of the roll-up cases was posted in March 2016. Based on stakeholder input, no additional scenario testing was conducted beyond the 2025 summer and winter base conditions.

EIPC entities responsible for system planning are currently developing a production cost model of the Eastern Interconnection being reviewed interconnection-wide—the first such review of its kind. With stakeholder input, EIPC will consider potential production costing analyses to be conducted in the future.

EIPC also is currently exploring which types of analyses and reporting complement the existing regional planning processes to assure comprehensive coordination of Eastern Interconnection-wide transmission planning.

## Electric Reliability Organization Overview

As the RTO for New England, the ISO is responsible for ensuring that its operations and planning comply with applicable NERC standards. In addition, the ISO participates in regional and interregional studies required for compliance.

Through its committee structure, NERC, which is the FERC-designated Electric Reliability Organization (ERO), regularly publishes reports that assess the reliability of the North American electric power system. Annual long-term reliability assessments evaluate the future adequacy of the power system in the United States and Canada for a 10-year period. The reports project electricity supply and demand, evaluate resource and transmission system adequacy, and discuss key issues and trends that could affect reliability. Summer and winter assessments evaluate the adequacy of electricity supplies in the United States and Canada for the upcoming peak demand periods in these seasons. Special regional, interregional, or interconnection-wide assessments are conducted as needed.

In December 2016, NERC issued its annual Long-Term Reliability Assessment (LTRA), analyzing reliability conditions across the North American continent. This report describes transmission additions, generation projections, and reserve capability by reliability council area. The 2016 LTRA identified focus areas, as summarized below, that require consideration to reduce risks to the North American BES:

- Single-fuel dependency: Over the last decade, several assessment areas have significantly increased their dependence on natural gas, which has increased vulnerabilities in serving load, particularly during extreme weather conditions.

- Nuclear uncertainty: Low natural gas prices continue to affect the competitiveness of nuclear generation and are a key contributing factor to nuclear generation’s difficulty in remaining economic with competing fuel sources. Potential nuclear retirements create uncertainty around local transmission adequacy and the ability to plan for future resource and demand needs due to their large baseload contribution.

- Essential reliability services: The addition of a large number of variable energy resources onto the BES has resulted in the need for operational flexibility to accommodate demand while also effectively managing the resource portfolio. As variable energy resources are becoming more significant, NERC is developing sufficiency guidelines to establish requisite levels of primary frequency response (PFR), voltage support, and ramping capability, for example, for VERs, which are needed for the continued reliable operation of the BES.

- Distributed energy resources: Increasing installations of DERs modify how distribution and transmission systems interact with each other. Many utilities currently lack sufficient visibility and operational control of these resources, increasing the risk to BES reliability. (Refer to Sections 2.1.3 and 9.1.)

The NERC LTRA offers several recommendations, including the following, to alleviate the potential impacts of the reliability issues identified above:

- As natural-gas-fired resources continue to increase, system planners and operators should evaluate the potential effects of an increased reliance on natural gas as it pertains to BES reliability. Natural gas provides “just-in-time” fuel; therefore, firm transportation and maintaining dual-fuel capability can significantly reduce the risk of common-mode failure and wider-spread reliability challenges. As part of future transmission and resource planning studies, planning entities will need to more fully understand how impacts to the natural gas transportation system can in turn impact electric reliability. Regulatory action may be needed to better coordinate electric power and gas industries.

- NERC should continue to monitor the potential effects of nuclear retirements on overall resource adequacy as well as potential mitigating factors, such as state regulatory measures that provide incentives for nuclear facilities to remain operational.

- Regulators and legislators should evaluate the changes occurring on the BES irrespective of the final rulings on pending regulation, such as the Clean Power Plan (CPP) (see Section 8.1.2.4). Policymakers should closely monitor and evaluate the measures being taken to address the evolving resource-adequacy trends.

- Regulators and legislators should consider the uncertainties in resource retirements and changes in the resource mix projected by resource planners and the interconnection-wide impacts, including generation retirements, curtailments, and transmission constraints that can manifest if essential reliability services are not maintained.

To study the implications of a shift in the resource mix resulting primarily from the retirement of conventional resources and the integration of new resources, NERC formed the Essential Reliability Services Task Force (ERSTF). The ERSTF studied the three reliability blocks: frequency support, voltage support, and net demand ramping variability. Among the recommendations made in the ERSTF report were the following:

- All new resources should have the capability to support voltage and frequency.

- Since DERs will increasingly affect the net distribution load observed by the BES, NERC should establish a working group to examine the forecasting, visibility, control, and participation of DERs as an active part of the BES. With prudent planning, operating and engineering practices, and policy oriented to support reliability, DERs should be able to be reliably integrated into BES operation. Refer to Section 9.1 for more information about the interconnection requirements for DERs.

- The reliability of the system can be maintained or improved as the resource mix evolves, provided that sufficient amounts of ERSs are available. This can be achieved by sharing of experiences and lessons learned around the industry.

In 2016, the ERSTF transitioned to a working group (now known as Essential Reliability Services Working Group [ERSWG]) and was charged with examining methodologies to determine sufficient levels of each ERS. In addition, this working group formed a task force under their purview to address challenges and potential risks from increasing DERs.

NERC recognizes that a changing resource mix with significant increases in energy-limited resources, changes in off-peak demand, and other factors can affect resource adequacy. As a result, NERC is incorporating more probabilistic approaches into the LTRA as well as other ongoing analyses that will provide further insights into how to best establish adequate reserve margins amidst a BES undergoing unprecedented changes.

NERC remains concerned with the potential reliability impacts from environmental regulations, which include restricted operations and retirements (see Section 8.1). NERC plans to conduct a reliability assessment once the US Environmental Protection Agency (EPA) finalizes Section 111(d) of the Clean Air Act (CAA) (see Section 8.1.2).

## IRC Activities

Created in April 2003, the ISO/RTO Council (IRC) is an industry group consisting of the nine functioning ISOs and RTOs in North America. These ISOs and RTOs serve two-thirds of the electricity customers in the United States and more than 50% of Canada‘s population. The IRC works collaboratively to develop effective processes, tools, and standard methods for improving competitive electricity markets across much of North America. Each ISO/RTO manages efficient, robust markets that provide competitive and reliable electricity service, consistent with its individual market and reliability criteria.

While the IRC members have different authorities, they have many planning responsibilities in common because of their similar missions. As part of the ISO/RTO authorization to operate, each ISO/RTO independently and fairly administers an open, transparent planning process among its participants. These activities include exchanging information, treating participants comparably, resolving disputes, coordinating infrastructure improvements regionally and interregionally, conducting economic planning studies, and allocating costs. This ensures a level playing field for infrastructure development driven efficiently by competition and meeting all reliability requirements.

The IRC has coordinated a number of reports, filings, and presentations with national government agencies. The IRC has worked with EPA, the states, and all interested parties on proposed carbon dioxide (CO2) regulations that respect electric power system reliability and are compatible with the efficient dispatch of the electric power grid. Additionally, the IRC has submitted FERC filings on issues of common concern for its members, such as FERC’s notice of proposed rulemaking on electric storage resources and distributed energy resource aggregations in organized wholesale electric markets (see Section 9.3). IRC members also have coordinated on a number of technical issues, including the use of software and the sharing of planning techniques, such as the modeling of distributed energy resources.

## Northeast Power Coordinating Council Studies and Activities

The Northeast Power Coordinating Council is one of eight regional entities located throughout the United States, Canada, and portions of Mexico responsible for enhancing and promoting the reliable and efficient operation of the interconnected bulk power system. NERC has authorized NPCC to create regional standards to enhance the reliability of the international, interconnected BES in northeastern North America. As a member of NPCC, the ISO fully participates in NPCC-coordinated interregional studies with its neighboring areas.

NPCC assesses seasonal reliability and, periodically, the reliability of the planned BPS. It also evaluates annual long-range resource adequacy. All studies are well coordinated across neighboring area boundaries and include the development of common databases that can serve as the basis for internal studies by the ISO. ISO New England assessments demonstrate full compliance with NERC and NPCC requirements for meeting resource adequacy and transmission planning criteria and standards.

## Northeastern ISO/RTO Planning Coordination Protocol

Each ISO/RTO develops individual system reliability plans, production cost studies, and interconnection studies, mindful of significant interregional impacts. To facilitate interregional coordination and communication among all interested parties, the Joint ISO/RTO Planning Committee (JIPC) and the Interregional Planning Stakeholder Advisory Committee (IPSAC) were established. The JIPC has successfully implemented the Northeastern ISO/RTO Planning Coordination Protocol and the subsequent Amended and Restated Northeastern ISO/RTO Planning Protocol, which has further improved interregional planning among neighboring areas as part of regional compliance with FERC Order No. 1000. The IPSAC provided stakeholder input to the JIPC.

Regarding interregional planning, Order No. 1000 requires all transmission providers to develop further procedures with neighboring regions to provide for the following:

- Sharing information regarding the respective needs of each region and potential solutions to these needs

- Identifying and jointly evaluating interregional transmission facilities that may be more efficient or cost-effective solutions to these regional needs

In addition to the Amended Planning Protocol, ISO New England, NYISO, and PJM, with input from their regional stakeholders and IPSAC, jointly developed other documents that FERC has determined comply with the interregional planning principles required by Order No. 1000. The three regions developed the Northeast Coordinated System Plan 2015 (NCSP15) and other IPSAC meeting materials, and they participate in a number of activities, in accordance with these requirements, which demonstrate continued, collaborative interregional planning.

NCSP15 summarizes the 2014 and 2015 interregional planning activities under the responsibilities of the JIPC and references other interregional activities, such as work associated with the North American Electric Reliability Corporation, ReliaiblityFirst, and the Northeast Regional Reliability Council. NCSP15 and IPSAC materials show that the regions have enhanced the timely exchange of needed databases and models required to perform planning studies and have coordinated interregional studies for resource adequacy, transmission planning, economic performance, and other issues.

Recent planning activities among ISO New England, NYISO, and PJM, discussed with IPSAC, include the interregional planning process, regional needs, and projects meeting regional needs. The information helps stakeholders identify potential interregional solutions to regional problems that may be more efficient or cost effective. Additional IPSAC discussions included interconnection queue studies with potential interregional impacts and how the JIPC has coordinated these studies. To date, the ISO/RTOs have not identified new interregional transmission projects that would be more effective or cost efficient in meeting the needs of multiple regions than proposed regional system improvements.

The ISO/RTOs have also enhanced the timelines and procedures for interregional planning. These entities will continue to share system information for conducting joint and individual planning studies. Input from the IPSAC and JIPC will provide additional perspectives in addressing current and future challenges, and stakeholder input will continue to provide valuable contributions in future planning cycles.

## Interregional Transfers

Interconnections with neighboring regions provide opportunities for exchanging capacity, energy, reserves, and mutual assistance during capacity-shortage conditions. Capacity imports help New England meet its Installed Capacity Requirements and promote competition in the FCM. The tie-reliability benefits from the interconnections also can lower the ICR. Additionally, imports provide resource diversity and can lower regional generation emissions, especially imports of hydro.

The ISO’s planning studies use the energy and capacity import capabilities shown in Table 6-1 (and described in Section 5.2) of the 13 interconnections New England has with neighboring power systems in the United States and Eastern Canada.

Table 6-1
Assumed External Interface Import Capability, Summer 2017 to Summer 2026 (MW)(a)

| Interconnection | Import Type | Assumed Import Capability |
| --- | --- | --- |
| New York–New England AC | Energy(b) | 1,400 |
|  | Capacity | 1,400 |
| Cross-Sound Cable | Energy(c) | 330 |
|  | Capacity | 0 |
| Maritimes–New England | Energy(d) | 1,000 |
|  | Capacity | 700 |
| Québec–New England (Highgate)(e) | Energy | 217 |
|  | Capacity | 200 |
| Québec–New England (Phase II) | Energy(f) | 2,000 |
|  | Capacity | 1,400 |

(a) 	Limits are for the summer period. These limits may not include possible simultaneous impacts and should not be considered as “firm.”

(b) 	The AC import capabilities do not include the Cross-Sound Cable and the Northport–Norwalk Cable. Simultaneously importing into New England and Connecticut can lower the New York to New England AC capability.

(c) 	Import capability on the Cross-Sound Cable is dependent on the level of local generation in Connecticut.

(d) 	The electrical limit of the Maritimes (New Brunswick)–New England tie is 1,000 MW. When adjusted for the ability to deliver capacity to the greater New England control area, the New Brunswick–New England transfer capability becomes 700 MW.

(e) 	The capability listing for the Highgate facility is for the New England AC side of the Highgate terminal.

(f) 	The Hydro-Québec Phase II interconnection is a DC tie with equipment ratings of 2,000 MW. Because of the need to protect for the loss of this line at the full import level in the PJM and NY systems, ISO New England has assumed its transfer capability to be 1,400 MW for calculating capacity and reliability. This assumption is based on the results of loss-of-source analyses conducted by PJM and NY. The procedure and daily limits are shown at the ISO’s “Operations Report: Single-Source Contingency,” webpage (2017), http://www.iso-ne.com/isoexpress/web/reports/operations/-/tree/single-src-cont.

Historically, New England experienced net capacity and energy imports. The ISO expects this trend to continue, given the amount of import capacity supply obligations resulting from the FCAs (see Section 4.1.3) and the number of tie-line projects in the ISO’s interconnection queue (Section 4.5.4), which could provide additional opportunities for importing energy from neighboring power systems.

The summer import capacity supply obligations for FCA #8 (for the 2017/2018 capacity commitment period) through FCA #11 (for the 2020/2021 period) range from 1,235 MW (in FCA #11) to 1,450 MW (in FCA #10), with New York providing more than half of the CSOs. The tie-reliability benefits used in calculating the ICR ranges from 1,870 MW to 1,990 MW during that same period, with over half provided by Québec.

During the past five years, the annual net energy imports have increased from 12,648 GWh in 2012 to over 20,000 GWh in 2014 through 2016. The resulting percentage of the total New England net energy for load is approximately 10% to 17%.

New England imported 22,963 GWh of energy (i.e., gross imports without accounting for exports) during 2016. Over half the energy imports were from Québec, which is predominantly a hydro system. Avoided New England emissions associated with energy imported from Québec were estimated using the 2015 New England system average emission rates. The estimated avoided emissions were 2.14 ktons of nitrogen oxides (NOx), 1.04 ktons of SO2, and 4,565 ktons of CO2.

## Summary

The ISO coordinates planning activities with the Northeast Power Coordinating Council and throughout North America through NERC studies, as well as joint system assessments and studies of planned projects and planning activities with neighboring systems. The JIPC, IRC, and EIPC also have all coordinated interregional activities and discussion, such as of the effects of environmental regulations and the development of renewable resources.

The ISO has achieved full compliance with all required planning standards and has successfully implemented the Northeastern ISO/RTO Planning Protocol, which has further improved interregional planning among neighboring areas. It will continue this effort as part of ongoing regional compliance with FERC Order No. 1000. Stakeholder input has been provided through the IPSAC.

Interconnections with neighboring systems provide access to capacity and energy and reduce emissions within the New England area. The interconnections have improved regional reliability and the economic operation of the system. The ISO uses the energy and capacity import capabilities of the interconnections in its planning studies.

# Fuel-Security Risks to System Reliability and Solutions

New England has several fuel-related risks, as follows, that affect the reliability of the power system:

- The region relies heavily on natural-gas-fired capacity, and serious and growing reliability issues have emerged regarding the need for fuel for natural-gas-fired generation because of constraints of the natural gas delivery system and the amount of liquefied natural gas (LNG) the region uses.

- The lack of firm fuel contracts by natural gas generators has limited the availability of natural gas transport to generators and funding for natural gas infrastructure expansion.

- Gas units with dual-fuel capability can have limited on-site fuel storage, and some resources need an extended time to switch and replenish fuels.

- Infrequently operated and older oil and coal resources experience diminished operating performance and face energy-production constraints, with oil units potentially experiencing issues with fuel availability, delivery, environmental restrictions, and other challenges caused by the sporadic operation of the units.

- New England also faces the retirement of non-gas-fired generation, which will likely increase the region’s reliance on natural-gas-fired generation.

The ISO and other entities have been conducting many studies on these overarching and overlapping strategic risks and broad planning issues, the extent of these issues, and potential solutions. Some of the more specific topics analyzed have been as follows:

- Winter operating experience, which shows the region’s exposure to high natural gas prices, the reliability risks of limited fuel supplies, and the results of regional actions to address these issues

- The interactions between the natural gas and electric power systems, which quantify the need for improving fuel security to the region

Improvements to the wholesale electricity markets (see Section 10.3.3) also will help secure a reliable supply of electric energy to the region.

This section discusses the electric power system’s reliance on natural-gas-fired generation, the associated reliability risks, the winter operating experience, and both short-term and long-term actions the region is taking to address these risks.

## Capacity and Electric Energy Production in the Region by Fuel Type

New England’s capacity and electric energy production in 2016 indicates that the region is highly dependent on natural-gas-fired generation. As shown in Figure 7-1, approximately 45% of the region’s capacity in 2016 was natural-gas-fired generation. This is approximately twice as large as oil-fired capacity, which was the next-largest type of generation resource in the region. Figure 7-1 also shows that natural gas power plants contributed 49% to the region’s electric energy production in 2016. Nuclear generation supplied 31% of the electric energy, but each of the other types of generating resources produced less than 8%. (Refer to Section 6.6 for a discussion on the role of imports that supply the region.)

Figure 7-1: New England’s summer seasonal claimed capability (MW, %) and electric energy production (GWh, %) by fuel type for 2016.

Note: The capacity and energy statistics exclude the capacity and energy associated with imports and behind-the-meter generation not registered in the region’s wholesale energy markets. In 2016, the NEL, accounting for both EE and BTM PV, was 124,369 GWh, pumped storage consumed an additional of 1,959 GWh, and the net imports into the region were 20,769 GWh, which represents 17% of the 2016 system net energy for load. (Numbers may not add in the figure due to rounding.)

Sources: The capacity data are the same as 2016 CELT Report data (https://www.iso-ne.com/static-assets/documents/2016/05/2016_celt_report.xls). The energy data are based on the March 1, 2017, 90-day resettlement of total electric energy production for 2016.

The region will continue to rely on natural-gas-fired generation and the addition of variable renewable resources in its fuel mix. Recent FCM auction results (see Section 4.1.3) have shown the retirement of coal- and oil-fired generators in the region as well as the loss of two nuclear plants. As additional generators retire, units in the ISO interconnection queue, which primarily are natural-gas-fired generation and wind resources (see Section 4.4.5.4), will likely replace them. The region experienced the addition of wind-powered generation and PV resources, and future growth is expected due to an increase in state renewable targets and funding to promote their development (see Section 10.4.1). Figure 7-2 shows the expected regional resource capacity mix for 2017, 2020, and 2026. As indicated, natural-gas-fired generation in the capacity mix is expected to grow from approximately 45% in summer 2017 to 56% in 2026.

Figure 7-2: Generating resource summer capability by fuel type based on the 2017 CELT Report and the interconnection queue, 2017, 2020, and 2026 (MW, %).

Note: The figure does not include interchange with neighboring regions (see Section 6.6). It also does not include active demand resources, EE, and BTM PV (see Section 3). PV resources forecasted to participate in the ISO capacity and energy markets are shown as part of the hydro/renewables category. The wind is derated to 13.2% of nameplate capacity (based on an average ratio of summer SCC to nameplate for existing wind units), and PV is derated to between 33.5% and 37.5% of nameplate depending on the in-service year.

## Natural Gas Infrastructure

New England’s natural gas supply and delivery infrastructure, and its limitations, have become an area of focus for improving the region’s fuel availability. Natural-gas-fired generators receive fuel supply from six interstate pipelines currently serving New England:

- Three originate from the south and west:

  - Algonquin Gas Transmission (AGT) Pipeline

  - Tennessee Gas Pipeline (TGP)

  - Iroquois Gas Transmission System (IGTS)

- The Portland Natural Gas Transmission System (PNGTS) originates in the northwest portion of New Hampshire.

- The Maritimes and Northeast (M&N) Pipeline originates in the Canadian Maritime provinces.

- The Granite State Gas Transmission (GSGT) System is in Maine and New Hampshire and does not bring gas from outside New England into the region.

Three LNG import terminals also serve New England, two onshore and one offshore:

- Distrigas LNG in Everett, Massachusetts and New Brunswick’s Canaport LNG onshore terminals

- Northeast Gateway LNG offshore terminals

The Distrigas terminal is connected with the AGT and TGP pipelines and the local gas distribution company (National Grid)—the gas utility that serves residential, commercial, and industrial customers. The Canaport terminal sends natural gas through the Brunswick pipeline, which directly connects to the M&N Pipeline. The M&N Pipeline also has the option of delivering natural gas to New England from the offshore natural gas production fields of the Sable Offshore Energy Project (SOEP) and Deep Panuke located offshore from Nova Scotia, Canada. Figure 7-3 shows the major existing natural gas infrastructure serving New England.

Figure 7-3: Overview map of the natural gas infrastructure serving New England.

Source: ICF International (ICF)

Notes: Several pipelines shown in the map indirectly serve New England: Emera New Brunswick owns and operates the Brunswick Pipeline. A subsidiary of Gaz Metro and TransCanada Pipeline owns the Trans Québec and Maritimes (TQM) Pipeline, which supplies Canadian gas into the PNGTS at Pittsburg, NH.

Figure 7-4 shows the sources of natural gas, including Utica and Marcellus shale gas, and Figure 7-5 shows the natural gas pipeline network in the lower 48 states. Comparing these figures shows that New England has relatively few pipelines that can access plentiful supplies of Marcellus and Utica shale gas.

Figure 7-4: Sources of natural gas in the continental United States, 2015.

Source: US DOE, Energy Information Agency (EIA).

Figure 7-5: Natural gas pipeline network in the continental United States, September 2014.

Source: Interstate Natural Gas Association of America (INGAA), http://www.ingaa.org/File.aspx?id=22553&v=a776386.

## Natural Gas and Oil Fuel Security and Risks to System Reliability

Because natural gas plants make up such a large part of the New England generating fleet, the availability of this fuel has an immediate effect on power grid reliability. For example, the planned or unplanned outage of a major gas pipeline at any time of year may affect many thousands of megawatts of generation. Additionally, when gas-fired generators are unavailable to run or are derated, the ISO needs to commit significant amounts of additional generating resources to maintain system reliability. However, many of the oil and coal plants called on to run require a long time to start and ramp up, may have performance problems related to their age, and may not have enough fuel to run as long as needed. Oil- and coal-fired generation may also need to limit their run times to comply with environmental restrictions (see Section 8).

The energy-production limitations create challenges to operating the system reliably and economically. In addition, many of these resources are retiring, limiting the amount of replacement capacity the ISO can call on during stressed system conditions (see Section 4.1.3).

### Fuel-Security Risks

The fuel-security risk occurs mostly during the winter but can occur any time of the year. During the last several years, a number of factors have been affecting the ability of natural gas plants to get the fuel they need to perform:

- Constrained infrastructure: The existing pipeline system in New England is reaching maximum capacity more often, especially in winter. The priority for a pipeline’s capacity goes to customers who have signed long-term firm contracts. In New England, these customers have been the local gas distribution companies.

- Interruptible fuel arrangements: Most natural gas plants procure, day to day, pipeline supply and transportation that the LDCs will not be using. As more people and businesses in New England convert to natural gas to take advantage of inexpensive shale gas, LDCs have had less pipeline capacity to release to the secondary markets. More competition also is taking place among the increasing numbers of gas-fired generators, which means generators risk not being able to obtain pipeline transportation for the gas needed to fuel their plants.

- Higher variable-cost peaking alternatives: Some generators can use LNG supplies when the region’s pipelines are fully congested. However, LNG tends to be more expensive than the typical price of gas emanating from the Marcellus shale.

- Limited fuel storage: Unlike generators that use others types of fuel, many natural gas plants in the region have limited or no onsite gas storage, making them even more vulnerable to the pipeline supply problems. Dual-fuel units can switch to using oil when necessary, but only about 40% of the region’s gas-capable units currently have this ability. More so, limitations in onsite liquid fuel storage may constrain the operation of these generation units.

### Natural Gas Price Volatility

As shown in Figure 7-6, New England’s heavy reliance on natural-gas-fired generation has resulted in natural gas fuel prices setting or closely following the associated price for wholesale electricity. The daily volatility in natural gas fuel prices was at its greatest in winter 2013/2014 and winter 2014/2015. Gas prices were more stable, however, during winter 2015/2016 and winter 2016/2017, likely attributable to more mild winters and the winter reliability programs.

Figure 7-6: Monthly average natural gas prices and real-time Hub LMPs compared with regional natural gas prices, March 2003 to March 2017, ($/MWh; $/MMbtu).

Note: Underlying natural gas data furnished by the Intercontinental Exchange (ICE). The regional natural gas price is the average Massachusetts price, which is the volume-weighted average of pricing points for Algonquin, Tennessee, and Dracut.

Figure 7-7 shows wholesale electricity and natural gas market data for New England trading hubs and the Marcellus price. Although the development of Marcellus shale is a growing source of natural gas, pipeline limitations into and within New England typically cause price separation between New England and Marcellus supplies. LNG supplies New England locally and can mitigate higher New England prices by providing supply during peak demand periods, but the higher unit cost of this supply still results in higher electric energy prices in New England than near the wellhead in Marcellus.

Figure 7-7: Natural gas market data, April 2014 to April 2017 ($/MMBtu).

Source: SNL Financial (accessed May 12, 2017), http://www.snl.com/.

As shown in Table 7-1, the natural gas futures prices for January and February 2016 were lower compared with the previous winters’ prices primarily because mild weather conditions reduced demand, which led to the greater availability of pipeline gas. The prices rose again slightly in winter 2016/2017. LNG vaporization at Canaport, Distrigas, and Excelerate LNG (offshore buoy), continue to provide gas supplies directly to the northeastern part of the natural gas system, which has improved regional gas grid reliability.

Table 7-1
Comparison of 2014, 2015, 2016, and 2017 Winter Futures Prices ($/MMBtu, $/MWh)(a)

|  | Location | 2014 Futures(b) | 2015 Futures(c) | 2016 Futures(d) | 2017 Futures(e) |
| --- | --- | --- | --- | --- | --- |
| Natural gas ($/MMBtu)(f) | Algonquin (New England) | 11.76 | 21.45 | 9.69 | 7.71 |
|  | Transco Zone 6 non-NY (Mid-Atlantic) | 4.78 | 9.09 | 6.21 | 6.26 |
|  | Dominion South (Marcellus) | 3.66 | 2.85 | 1.97 | 2.14 |
|  | Southern California border | 3.95 | 4.30 | 2.85 | 3.79 |
|  | Henry Hub | 3.87 | 4.08 | 2.77 | 3.55 |
| Power ($/MWh)(g) | Massachusetts hub | 99.88 | 183.88 | 89.28 | 78.93 |
|  | PJM western hub | 44.90 | 72.60 | 50.56 | 55.80 |
|  | Northwest (Mid-Columbia trading point)(h) | 37.73 | 35.75 | 24.88 | 32.05 |
|  | Southern California (SP-15)(i) | 42.25(j) | 46.13 | 33.76 | 41.18 |

(a) 	Sources: Derived ICE and Nymex data and FERC, 2014–2015, 2015–2016, and 2016–2017  Winter Energy Market Assessment Presentation (October 16, 2014), (October 15, 2015), and (October 20, 2016); http://www.ferc.gov/market-oversight/reports-analyses/mkt-views/2014/10-16-14-A-3.pdf,  https://www.ferc.gov/market-oversight/reports-analyses/mkt-views/2015/10-15-15-A-3.pdf, and https://www.ferc.gov/market-oversight/reports-analyses/mkt-views/2016/10-20-16-A-3.pdf.

(b) 	January and February 2014 futures pricing is as of October 1, 2013.

(c)	January and February 2015 futures pricing is as of October 1, 2014.

(d)	January and February 2016 futures pricing as of October 1, 2015.

(e)	January and February 2017 futures pricing as of October 1, 2016. Futures location pricing is derived from CME Group/NYMEX and OTC Global Holdings futures for the above locations.

(f)	Gas prices ($/MMBtu) shown are regional futures prices (the sum of the Henry Hub future contract price plus the regional basis futures).

(g) 	Power prices ($/MWh) shown are peak financial swap prices.

(h)	The Mid-Columbia electric trading point is a center point along the Columbia River on the border between Washington and Oregon states.

(i) 	SP-15 refers to California Independent System Operator’s (CAISO’s) zone covering southern California.

(j) 	The futures pricing for SP-15 2014 is as of October 31, 2013.

## Addressing Fuel-Security and Cost Risks

A number of solutions to the fuel-security and cost-volatility risk are underway. These measures include improved coordination between the electric power system and natural gas sector, winter reliability programs, revised wholesale electricity market rules (see Section 10.3.3) and pipeline infrastructure expansion and enhancements. Fuel stored as oil, LNG, and compressed natural gas also improve the fuel security of the region.

### Electric Power System and Natural Gas Sector Coordination

The implementation of operating procedures and an increase in communications between electric power and natural gas system operators over the past several years have improved the coordination between the natural gas and electric power systems and have prevented certain operational risks. ISO efforts have included examining data from various sources to estimate the availability of natural gas for electric energy purposes, analyzing capacity scenarios across different seasons using information gathered from fuel surveys and pipelines, and establishing operating plans to deal with different system conditions.

The ISO continues to work with the natural gas industry to address the challenges of the increasing interdependency between the gas and electric power industries. Ways in which the gas sector could assist with reliability efforts include having gas suppliers provide generators with additional opportunities to obtain fuel outside normal business hours, having pipelines offer more flexible scheduling by modifying the nomination process, offering additional nonratable transportation services, physically improving infrastructure, and continually improving real-time information exchange on the status of the pipeline system. The additional flexibility of pipeline operations could facilitate more variable electric power system operations, including using fast-start generation, regulation, ramping, and reserves.

### Fuel Security—Use of Oil, LNG, Compressed Natural Gas, and Efficiency Measures

Figure 7-8 displays a comparison of the total number of barrels of fuel oil (both heavy and light oil) burned at all regional fossil stations in 2015/2016 compared with the amount burned in 2016/2017. The overall amount of fuel oil burned was approximately 19% higher in 2016/2017 than in the prior winter. The regional electric power sector consumed approximately 136,754 barrels (bbls) in December 2016, approximately 55,895 bbls in January 2017, and approximately 78,677 bbls during February 2017, bringing the three-month total of fuel oil used to approximately 271,325 bbls.

Figure 7-8:  Monthly fuel burn (both heavy and light oil) at all New England fossil-fuel stations, winter 2015/2016 and 2016/2017 (beginning of each month) (barrels)

Note: All values were taken from fuel surveys submitted to the ISO on the first day of each month.

During winters 2015/2016 and 2016/2017, oil was a reliable fuel source and capped the effects that high natural gas prices had on the wholesale electric system markets. In general, oil consumption during the winter months increases, which relieves stress on the natural gas fuel supply for New England generators. Specifically, natural gas prices above $6.00/MBtu at Algonquin Gates and TGP Dracut (refer to Figure 7-7, above) were indicative of when natural gas supplies to generators were tight during winter 2016/2017.

Figure 7-9 shows the increase in LNG supplies delivered to the region for the past two winters. Winter 2014/2015 had almost double the amount of LNG supplies at approximately 32 billion cubic feet (Bcf) compared with approximately 16 Bcf in the prior winter. The ISO has observed on the regional pipeline electronic bulletin boards an increased LNG send out, which is a result of the recently improved availability of spot-market gas within the Northeast and contracts made in advance of the winter. LNG deliveries help address the regional fuel security issue.

Figure 7-9: Comparison of LNG deliveries for winter 2014/2015 through winter 2016/2017.

Source: EIA, U.S. Liquefied Natural Gas Imports by Point of Entry, https://www.eia.gov/dnav/ng/ng_move_poe1_a_epg0_iml_mmcf_m.htm.

The use of compressed natural gas (CNG) also offers an option for storing natural gas. CNG can be used instead of ultralow sulfur diesel (ULSD) fuel as a backup fuel for dual-fuel peaking generating units where the primary fuel is pipeline gas. CNG has lower air emissions than ULSD without the need to “retune” the gas turbine (GT) to run on liquids. CNG also facilitates the coordination between the electrical dispatch of generating units and their gas-nomination times with the natural gas pipelines for regularly scheduled gas deliveries.

The natural gas industry actively seeks to improve its use of existing infrastructure. In 2015, the nine northeastern states (six New England states plus New York, New Jersey, and Pennsylvania) invested $544 million in gas efficiency measures, which represents 39% of the total US investment.

### Fuel-Security Analyses

ISO New England has had long-standing concerns about the region’s dependence of New England’s natural gas infrastructure. This dependency is likely to increase in the coming years as older oil, coal and nuclear generators retire. To quantify the risks to the region as well as evaluate the effectiveness of various solutions, in 2017, the ISO began to assess potential reliability consequences of various future gas pipeline scenarios for 2025. By calculating the generation mix required to meet demand each day, calculating the associated fuel usage, and then comparing the needed fuel with the capacity of the region’s pipelines, the ISO may be able to better predict potential reliability consequences of a physically limited natural gas fuel supply. The ISO plans to present its 2017 fuel security analysis to stakeholders in late 2017.

### Pipeline Improvements

The ISO continues to monitor upgrades to natural gas infrastructure to maintain operational awareness of the changing capacity of the natural gas system. Interstate pipeline companies serving the Northeast region (including the Mid-Atlantic region) have added numerous interconnections from the Marcellus gas production area’s large and small producers, and annual natural gas production volumes in the Northeast are projected to rise from 3.92 trillion cubic feet (Tcf) in 2013 to 6.66 Tcf in 2024. Figure 7-10 shows the proposed natural gas pipeline expansions that could benefit New England.

Figure 7-10: Proposed natural gas pipeline expansions benefiting New England, 2015.

Source: EIA, New England natural gas pipeline capacity increases for the first time since 2010 (December 6, 2016).

At present, of the 19 proposed pipeline-expansion projects under development across the Northeast, seven projects, as shown in Table 7-2, would specifically bring either new or incremental pipeline capacity to New England and regional access to additional natural gas supplies.

Table 7-2
 Summary of Pipeline Improvements Benefiting New England

| Project (Developer) | Additional Capacity Dekatherms per day (Dth/d) | Location | Regulatory Status |
| --- | --- | --- | --- |
| Algonquin Incremental Market (AIM) (Enbridge/Spectra Energy)(a) | 342,000 | CT and MA | FERC granted approval, March 2015; full in-service date, January 2017 |
| Connecticut Expansion Project (Kinder Morgan/Tennessee Gas Pipeline) | 72,000 | Primarily CT, some NY and MA | FERC issued final approval, March 2016; estimated November 2017 in-service date |
| Continent-to-Coast (C2C) Expansion Project (PNGTS, TransCanada, Iroquois) | 168,000 – 300,000 | Québec, NY, and ME | Estimated November 2017 in-service date |
| Atlantic Bridge Project (Enbridge/Spectra Energy/ Algonquin and Maritimes) | 133,000 Involves incremental expansion on the AGT and M&N pipelines to serve emerging gas markets in northern New England and the Canadian Maritimes | CT, RI, MA, NH, and ME | FERC issued final approval, January 2017; expected to be in service no earlier than late 2017. |
| Iroquois South to North Project(b) (Iroquois Gas Transmission System) | Up to 650,000 Reverse flow on Iroquois northward to US/Canada border. Would export Marcellus production using interconnects with Dominion in Canajoharie, NY, Algonquin in Brookfield, CT, and the proposed Constitution Pipeline in Wright, NY | CT, NY | Developer delayed estimated in-service date until 2020 |
| Iroquois Wright Interconnect Project (Iroquois Gas Transmission System) | Up to 650,000 Adds new interconnection point with Constitution Pipeline, modifies existing compressor station with new transfer capacity and compressors | Mid-state NY | FERC issued final approval, December 2, 2014; in August 2016, FERC authorized extension until December 2018 to construct due to NY Dept. of Environmental Conservation permitting delay |
| Portland Natural Gas Transmission | Up to 32,000 Increase import/export capacity from 178,000 to 210,000 from Pittsburg, NH, to Westbrook, ME | NH, ME | FERC application filed, December 2016 Part of C2C Expansion Project |

(a) As of February 2017, Spectra Energy became Enbridge.

(b) The Iroquois South to North Project will be able to operate either north or south to New England. If it operates north, the gas may be used by customers in Canada, or it may be routed back south to New England over the Portland Gas Pipelne.

Sources:  FERC, Northeast Gas Association, ICF International, and RBN.

Unlike the electric power industry, which builds infrastructure in anticipation of demand, interstate natural gas pipeline companies require gas shippers and customers to enter into long-term firm commitments before the infrastructure can be developed. Although the natural gas pipelines serving the region are at or near capacity, they will not be expanded until customers make firm commitments. In fact, FERC, which must approve interstate pipeline projects, bases its decision that a pipeline project is in the public convenience and a necessity in large part on the existence of firm contractual commitments. The ISO will continue to monitor when any power generators within New England sign a firm contract for any portion of these regional upgrades that will improve fuel assurance.

The recent and planned expansion and other upgrades to the regional and interregional natural gas infrastructure are initial steps for expanding access to natural gas sources, helping New England meet its increasing demand for gas to generate electric power. More expansion will most likely be required, however.

## Summary

The operational challenges experienced during winter periods highlight the need for the ISO to manage energy production limitations of electric power generators, especially natural-gas-fired generators. The constrained ability of natural gas pipelines to deliver fuel to generating units results in the need for oil and coal generators to produce electricity. Siting and permitting new dual-fuel facilities that have sufficient operating flexibility when access to natural gas is limited remains challenging. Similarly, siting new gas pipelines can be a long and difficult process and will not address short-term needs. Fuel constraints physically challenge the reliable operation of the system and result in increased prices for electricity whenever natural gas is in shorter supply to the region, especially during the winter months.

Making natural gas scheduling more flexible will improve generator response to system conditions and enhance system reliability. Improvements to the regional and interregional natural gas infrastructure also would help. Fuel-security could be further improved in a number of ways:

- Firm contracts with natural gas pipelines would support the building of new natural gas pipeline capacity.

- Firm contracts with natural gas suppliers, including LNG operators, would improve the availability of natural gas for electric power generation.

- The use of existing and new dual-fuel capability at generating plants would provide alternative supplies of fuel when natural gas supplies are limited.

- Adequate on-site storage of liquid fuels would increase generation reliability at dual-fuel power plants.

- Compressed natural gas and LNG offer options for storing natural gas near peaking generating units.

- Increased efficient use of natural gas and electricity would allow greater use of available pipeline capacity by generators.

The ISO’s 2017 fuel-security study should enhance understanding about the 2025 anticipated generating resource fuel-mix combinations and the impact to reliable winter operations of the power system.

# Impacts of Environmental Regulations and Siting Requirements on Generators and the Power System

Various elements of the power system are subject to federal, regional, and state environmental laws and regulations controlling pollution, emissions, or discharges. Siting and environmental permitting requirements for new or  existing transmission and generation are often complex and may involve multiple federal and state regulatory entities, all of which can delay or jeopardize the planning, development, or the implementation of proposed transmission and generation improvements. Compliance with environmental requirements may involve major capital investments for new projects, remediation measures, or changes in generator operations.

This section summarizes environmental regulations affecting generators and relicensing timelines for hydroelectric generators and nuclear units. The section also summarizes regional emissions for 2015, the latest available data.

## Federal, Regional, and State Environmental Regulations Affecting Generators

Compliance obligations for generators from existing and pending federal, state, and regional environmental requirements differ by resource age, economics, location, fuel type, and readiness of commercially available control technologies. As generator retirements have progressed and the median age of larger generation units has fallen to 28 years in 2017, existing and new fossil generators generally have operated more advanced pollution control technologies that reduce emissions and discharges. Federal air, water, endangered species, and carbon dioxide (CO2) standards, however, could affect the economic performance of nuclear and fossil-fired generators by imposing operational constraints or lead to capital costs for installing environmental remediation measures.

Certain federal environmental requirements are highly uncertain at present. Significant programmatic or budgetary changes at the US Environmental Protection Agency (EPA) and US Fish and Wildlife Service (FWS) are under consideration or implementation. A number of major environmental regulations are being challenged in court, and the level of uncertainty may complicate permitting for new and existing generators and transmission facilities.

Pursuant to various executive orders and legislation, EPA is reconsidering several major air and water quality rules in the following areas that affect various classes of existing and new generators:

- Surface water withdrawals (for cooling water use and consumption)

- Wastewater discharges into surface water

- Mercury, acid gas, and other toxic air emissions

- Ozone (O3) transport and fine particulate matter (PM2.5) and sulfur dioxide (SO2) emissions

- Greenhouse gases (GHGs)/CO2 emissions

System reliability could suffer if the aggregate impact and timing of all these requirements limit generator energy production, reduce capacity output, or contribute to unit retirements. However, EPA has provided compliance options in several major recent rules, recognizing the reliability value that low-capacity fossil steam generators provide in maintaining system fuel diversity. Recent EPA and US Department of Energy (DOE) Energy Information Administration modeling indicate that several major regulations have declining importance on national (and by implication regional) grid reliability (see Section 7.3). Compliance deadlines for many of these requirements began in 2015 and continue through 2022.

State and regional air, water, and carbon dioxide standards could emerge as more stringent compliance requirements for generators. New England states are developing and implementing state air and water quality requirements for generators. This includes the continued drive for regulated entities (i.e., local distribution companies; LDCs) to attain greenhouse gas reduction targets under the Regional Greenhouse Gas Initiative (RGGI) (see Section 8.1.2.5) or the implementation of other state-specific generator emissions caps.

### Emerging Impacts of Clean Water Act Regulations on the Region’s Generators

EPA and state regulators are implementing several Clean Water Act (CWA) regulations affecting electric power generators, including the final § 316(b) Cooling Water Intake Structures (CWIS) Rule and the proposed § 304 Effluent Limitation Guidelines (ELGs). Both the CWIS Rule and the ELG requirements are currently being challenged in court, which may lead to changes or or delays in compliance obligations for generators.

In New England, 6.85 GW of existing fossil thermal electric capacity rely on larger once-through cooling systems subject to the CWIS Rule and could incur additional compliance costs (operational changes or retrofits) during periodic water permit reviews. Another 4.40 GW of existing capacity have partially compliant cooling systems, and 2.92 GW of existing capacity (mainly newer facilities with combined-cycle units) have already-compliant recirculating cooling systems. These rules also require new thermal electric energy capacity to install dry, hybrid, or closed-cycle cooling systems and control or eliminate certain wastewater discharges under new discharge requirements.

EPA and New England states are implementing the final CWA CWIS Rule requirements to mitigate the adverse impacts to aquatic life of once-through cooling systems with a design intake flow of at least 2 million gallons per day (MGD). According to US Geological Survey (USGS) data summarized in Figure 8-1, 12.9 GW of existing steam electric generators (nuclear, coal, oil, natural gas, and bio/refuse) in New England withdraw cooling water using once-through systems engineered with a design intake flow of 2 MGD or greater. Electric generators equipped with such once-through cooling water systems are required to use the best technology available to reduce fish impingement (i.e., when fish or wildlife are trapped against the intake structure due to the velocity of a facility’s water withdrawals) and entrainment (i.e., when very small organisms, such as fish eggs and larvae, are drawn through a facility’s intake screens with the cooling water). While EPA anticipated most retrofits occurring between 2018 and 2022, regional delays with several existing water permit reviews could push this schedule beyond 2022.

Figure 8-1: Summer claimed capability and cooling technology type in New England, 2017 (MW).

Note: Thermal cooling system data are available for 24.3 GW of existing system capacity in New England (excluding hydro, wind and photovoltaic). 10.5 GW use open once-through thermal cooling systems, 7.4 GW use recirculating (induced draft) cooling systems, 5.0 GW use dry/hybrid cooling systems, and 1.4 GW report no cooling water systems. Cooling system data were unavailable for 1.2 GW. Resources <25 MW and resources retired in 2017 (such as Brayton Point), are excluded.

Sources: Energy Information Administration, 2015 Thermoelectric cooling water data, webpage (accessed March 2017), https://www.eia.gov/electricity/data/water/; ISO-NE 2017. CELT Report) (May 1, 2017), http://www.iso-ne.com/system-planning/system-plans-studies/celt#.

### Clean Air Act Requirements and Regional and Federal Greenhouse Gas Regulations

Many Clean Air Act (CAA) actions affect New England’s fossil-fuel power generators and the region’s air emissions. As air-quality rules have been implemented across the region, their impact is reflected in decreasing power generation emission trends. Regional and federal greenhouse gas regulations also present a range of environmental and economic implications.

EPA finalized a more stringent ozone standard in October 2015, which may require operational changes and potential pollution control retrofits for larger fossil fuel generators’ capacity across southern New England once implemented after 2017. The 2015 ozone standard would trigger more stringent technology-based performance standards for new or modified fossil fuel generators. In April 2017, the D.C. Circuit Court of Appeals granted EPA’s motion to continue oral arguments and indefinitely delay any decisions on challenges to the 2015 ozone standard.

#### Implementation of Mercury and Air Toxics Standards

Of the 5.6 GW of remaining coal- and oil-fired steam thermal electric generators subject to the Mercury and Air Toxics Standards (MATS), 72% are residual oil-fired and qualify as limited-use units, as defined by the standard. This subcategory of units has less-stringent compliance obligations than non-limited-use units. In April 2017, the D.C. Circuit Court of Appeals granted EPA’s motion to continue oral arguments in litigation involving the MATS supplemental finding, but affected generators must continue complying with MATS. In addition, many state air toxics regulations remain in force, however, and air toxics controls will continue to operate for most units in New England.

Mercury emissions from coal-fired steam generators declined 75% from 2005 to 2015 due to the cobenefits of controlling other air pollutants (SO2 and nitrogen oxides; NOX) and the increased use of mercury-specific pollution-control technologies. Most of the region’s coal- and residual oil-fired steam generators greater than 25 MW in capacity are already complying with the standard’s emissions limits for acid gases, toxic metals, and mercury based on maximum achievable control technologies (MACTs). Or, they are subject to the less-stringent requirements for limited-use units based on low individual unit capacity factors. With several coal-fired generator retirements, residual oil-fired steam generation in New England has the most remaining generating capacity affected by MATS. The capacity factor exceptions threshold for limited-use units will likely become more important to system reliability in future years because the affected generators could limit their energy production during critical periods.

#### Clean Air Act Regional Air Pollution Reduction

State and federal air regulators are expected to address deteriorating air quality trends across southern New England (particularly due to ozone and fine particulate matter), possibly resulting in more stringent emissions limits for fossil generators. Ozone and fine particulate matter generated far upwind of New England has hampered considerable regulatory efforts to improve local air quality.

#### Regional Emissions Trends

The ISO tracks the system emissions, rates, and trends for NOX, SOX, and CO2 to help gauge the potential effects of future environmental regulations on the system and in response to historical requests from the states for emissions data. The ISO’s most recent air emissions report, the 2015 ISO New England Electric Generator Air Emissions Report, provides detailed historical trends and emissions rate data using methodologies developed with input from stakeholders.

A shift in the fuel mix powering the region directly contributes to the changing regional emissions. Since 2006, the annual total NOX emissions have decreased by 56%; SO2, by 91%; and CO2, by 22%. The reductions in emissions resulted primarily from the regional shift away from electrical energy production by older oil- and coal-fired generation to efficient natural-gas-fired generation and increasing reliance on imports (see Section 7.1). Other factors that lowered emissions include the high capacity factors achieved by nuclear generators; the growth of both energy efficiency and renewable resources with low or zero emissions; the addition of environmental controls to generators, which reduce the production of pollutants; and transmission improvements, which decrease the dispatch and commitment of high-polluting generators. Figure 8-2 shows the regional annual emissions for New England.

Figure 8-2: New England system annual emissions of NOX, SO2, and CO2, 2006 to 2015 (ktons).

Source: 2015 ISO New England Electric Generator Air Emissions Report (January 2017), https://www.iso-ne.com/static-assets/documents/2017/01/2015_emissions_report.pdf.

From 2014 to 2015, total NOX system emissions decreased by 8% and SO2 system emissions decreased 22%, while CO2 system emissions increased 3%. One of the key factors contributing to the changes between 2014 and 2015 was the ongoing retirement of coal-fired resources. Coal-fired generation fell by about 23% in 2015. In addition, the production from nonemitting generators in 2015 decreased 15% due to the retirement of Vermont Yankee Nuclear Power Station in December 2014. Emitting generators, largely those fueled by natural gas, filled the resulting energy gap, which increased production by 12%. Oil-fired generation increased 10% in 2015, and SO2 system emissions are highly concentrated among the 10 remaining residual oil-fired resources lacking any SO2 pollution controls. A significant increase in the use of such uncontrolled residual oil-fired resources could conflict with SO2 air quality standards in the future.

#### Clean Power Plan and CO2 Emissions

Federal greenhouse gas policy and regulation are in a state of flux, and at the time of publication, the outcomes for generators of pending regulatory actions and litigation remain unclear.

In August 2015, EPA finalized the Clean Power Plan (CPP), for existing fossil-fuel-fired power plants under Section 111(d) of the Clean Air Act. The final CPP requires affected fossil power plants to reduce CO2 emissions 32% nationwide by 2030 from a 2005 baseline, with the initial reductions due by an interim 2022 deadline and additional milestones before the final 2030 deadline. On February 9, 2016, the US Supreme Court stayed the implementation of the CPP, pending completion of litigation, which was held in abeyance in April 2017 by the D.C. Circuit Court of Appeals. In March 2017, an executive order directed EPA to review the CPP and 111(b) Standards of Performance for Greenhouse Gas Emissions for Power Plants and suspend, revise, or rescind the final rules and associated guidance and memoranda, subject to all applicable legal requirements.

Regardless of the outcome of the CPP litigation and any subsequent EPA actions on greenhouse gas emissions, the New England states are expected to proceed with various initiatives affecting fossil generators to reduce CO2 emissions. The New England states’ CO2 emissions in 2016 (26.7 million short tons) are already below all the aggregate regional 2022–2030 CPP caps. The greater use of lower-emitting fuels, energy efficiency, wind and photovoltaic resources, and imports from neighboring systems and added environmental controls could decrease regional emissions further.

#### Implications of Regional Greenhouse Gas Regulations

The New England states have various greenhouse gas reduction targets that generally require reductions between 75% to 95% below 1990 baseline levels by 2050. To help achieve these targets, fossil fuel generators in New England larger than 25 MW have been subject to a CO2 cap under the Regional Greenhouse Gas Initiative since 2009.

CO2 emissions from RGGI-affected generators in the entire nine-state RGGI program have declined since 2009, with 2016 RGGI emissions (79.2 million short tons) 8.4 % below the 2016 emissions cap (86.5 million short tons). The RGGI states are conducting a comprehensive program review that may include the adoption of a more stringent, post-2020 emissions cap (see Section 9.4). Figure 8-3 shows the total New England allowances for each of the auctions and the total CO2 emissions from the New England sources.

Figure 8-3: New England RGGI states’ quarterly CO2 emissions and allowance auctions, 2008 to 2016 (mtons, millions).

Source: RGGI (May 11, 2017), http://www.rggi.org/rggi.

As Figure 8-4 shows, auction prices increased from 2014 through 2015 before they declined in 2016 with the US Supreme Court’s February 2016 stay of CPP implementation, as mentioned above. Auction reports indicate that affected generators remain active participants, acquiring most of the allowances offered during the current control period.

Figure 8-4: New England RGGI states’ quarterly CO2 allowance auction proceeds and clearing price, 2008 to 2016 (million $ and $).

Source: RGGI, (March 11, 2016), http://www.rggi.org/rggi.

The 2016 RGGI program review was designed in part to evaluate adjustments needed to permit participating RGGI states to meet future CPP requirements by developing a joint state plan, leveraging expected post-2020 emissions (assuming the RGGI cap continued declining at 2.5% from 2015 to 2020). After the CPP was suspended in February 2016, the RGGI states considered other program design details during the 2016–2017 program review:

- Timing of policy implementation (whether to adopt post-2020 reduction targets out to 2030)

- Adjustment of banked allowances (account for banked allowances accrued from 2014 to 2020)

- Reserve price (modify the floor auction price)

- Emissions containment reserve (ECR) (withdraw allowance from auction at set price)

- Cost-containment reserve (CCR) (modify trigger price and change size of the reserve)

- Offsets (modify eligible projects on individual state basis)

The 2016 program review as of this writing has not yet finalized changes to the RGGI model rule, but the schedule announced by the RGGI states calls for adopting any rule changes before the 2018–2020 control period.

### Cost of Compliance with Environmental Regulations

Compliance costs for generating units differ by age, economics, location, and readiness of commercially available control technologies. As the median age of the fossil generation fleet declines, existing generating units, particularly those employing combined-cycle technologies—both oil- or natural-gas-fired—operate best-available pollution control technologies for air emissions and water discharges. The key driver of emission costs for New England generators is the RGGI marketplace for CO2 credits. In 2016, CO2 prices declined by 13%, which according to the EIA, coincided with the suspension of the Clean Power Plan in February 2016. In 2016, CO2 allowance compliance costs for RGGI were the major environmental variable cost of generation for natural gas, coal, and No. 6 oil (i.e., residual fuel oil used to produce electric power) at $2.36, $5.33, and $4.73/MWh, respectively. Figure 8-5 highlights that CO2 allowance costs have a relatively small impact on generation production costs and consequently do not have a noticeable impact on the economic merit order of generation.

Figure 8-5: Contribution of CO2 allowance costs to energy production costs, 2012 to 2017 ($/MWh).

Notes: The line series for each fuel category illustrates the quarterly estimated production cost using the average heat rate for generators of a representative technology type. The height of the shaded band above each line series represents the average additional energy production costs attributable to CO2 emissions costs in each category.

Source: ISO New England Internal Market Monitor, 2016 Annual Markets Report, https://www.iso-ne.com/static-assets/documents/2017/05/annual_markets_report_2016.pdf, p.42.

## Update of Regional Nuclear Generation Licensing Renewals

New England currently has four nuclear generating generators: two in Waterford, Connecticut (Millstone), and one each in Seabrook, New Hampshire, and Plymouth, Massachusetts (Pilgrim). Pilgrim has announced its retirement effective May 2019. All remaining nuclear generators require an operating license, which is subject to renewals or extensions, as summarized in Table 8-1.

Table 8-1
New England Operating Nuclear Power Plants

| Unit Name | Operating (OP)/ Renewed License Dates | License Expiration Date | Reactor Type | Electrical Output (MWe)(a) | Reactor Vendor/Type |
| --- | --- | --- | --- | --- | --- |
| Millstone 2 | September 26, 1975/ November 28, 2005 | July 31, 2035 | Pressurized water | 884 | Combustion Engineering (vendor) |
| Millstone 3 | January 31, 1986/ November 28, 2005 | November 25, 2045 | Pressurized water | 1,227 | Westinghouse/ four-loop |
| Seabrook | OP: March 15, 1990 | March 15, 2030 | Pressurized water | 1,295 | Westinghouse/ four-loop |

        - “MWe” stands for electrical megawatts. Nameplate electrical output from the Nuclear Regulatory Commission’s (NRC) website, http://www.nrc.gov/info-finder/reactor/.

The Nuclear Regulatory Commission finalized a replacement rulemaking, the Continued Storage Rule, in November 2014, revising the general environmental impacts of spent nuclear fuel storage operations at closed reactors sites nationwide, including 11 sites in New England.

## Update on Hydroelectric Generation Relicensing

Conventional hydroelectric generators are among the oldest generators on the system, which include 1,418 MW, or 4.6%, of the regional summer claimed capability and represent 6,010 GWh, or 6.7%, of all generation in 2016. In addition to providing capacity and electric energy, hydroelectric units traditionally have been well suited to provide regulation and reserves, but they may lose some of their ability to operate flexibly as part of their relicensing requirements.

The licenses for approximately 1,291 MW of existing hydroelectric generators, including 1,172 MW of pumped-storage capacity, will expire between 2014 and 2022. FERC is pursuing an integrated relicensing review for several hydroelectric projects located on the Connecticut River, which is ongoing. Relicensing must take into consideration the requirements for adequately and equitably protecting and mitigating damage to fish and wildlife (and their habitats) and the recommendations of state and federal fish and wildlife agencies. The ISO is monitoring such proceedings to assess the impacts of operational restrictions, including the maintenance of minimum flows without bypass turbines or spillage (i.e., water allowed to pass through the dam without generating electricity), on the ability of hydroelectric generators to offer regulation and reserve services.

## Conclusions

Existing and pending federal, regional, and state environmental regulations may require many generators to consider adding air-pollution control devices; modifying or reducing water use and wastewater discharges; and, in some cases, limiting operations. The actual compliance timelines and costs will depend on the timing and substance of the final regulations and site-specific circumstances of the electric generating facilities. Some generators may decide they are uneconomical and retire before making major investments in environmental compliance measures, but others can recover their capital investment by locking into FCM prices for up to seven years.

Regional generator air emissions remain relatively low compared with historical levels, resulting from the greater use of natural gas generation. Higher emissions, however, occur during the winter months because of the burning of oil by generators when natural gas is more expensive or in limited supply. A combination of retirements of larger thermal generators and the decreased use of most remaining thermal capacity has lowered water use and consumption for power generation compared with historical levels.

# Integration of Variable Energy Resources

The integration of large amounts of variable energy resources (VERs), including wind, photovoltaics, and energy storage poses new challenges to the electric power system. To address these challenges, the ISO has been conducting a number of studies, gathering operational data and observations, and participating in other projects assessing the development and integration of VERs.

## Industry Recommendations for Facilitating the Integration of Wind and Solar Resources

The research activities of the US Department of Energy's National Renewable Energy Laboratory (NREL) include the development of data and tools for analyzing wind and PV resources and studies that identify key integration issues. The ISO uses NREL-developed data sets critical for modeling hypothetical wind and PV resources in planning studies. NREL studies found that to accommodate higher amounts of wind and solar power on the electric power grid, utilities will need to ramp up and ramp down conventional generators more frequently than with less wind and solar on the grid. Studies also show the need for transmission development required to integrate remote wind resources. The ISO will continue to track industry research and monitor the effects that increased amounts of VERs have on system performance, including ramping.

IEEE Standard 1547 is the Standard for Interconnection and Interoperability of Distributed Energy Resources with Associated Electric Power Systems Interfaces. Its requirements apply to interconnection of DERs, including synchronous machines, induction machines, and power inverters/converters. The criteria and requirements are applicable to all DER technologies interconnected to electric power systems at typical primary and secondary distribution voltages. These standards were originally designed for relatively small penetrations of DERs and do not require resources, such as distributed PV, to be able to “ride through” a fault on the transmission system. This is because the original standard was written to meet distribution system requirements, and the lack of ride through capabilities did not have a material effect on transmission system performance for small penetrations of DERs.

IEEE Standard 1547, originally approved in 2003, was amended in 2014. Another proposed revision should become effective by the end of 2017. This upcoming revision will reflect performance requirements appropriate for large penetrations of distributed generation and represents a very important step forward for the industry’s definition of performance requirements and expectations for DERs. The revised standard will identify required performance capabilities for voltage and frequency response and voltage and frequency ride-through. Power quality, islanding performance, and interoperability on distribution networks will also be covered. In addition, the standard will recognize applications of “smart inverters” that would allow distributed resources to provide ancillary services, such as voltage support. Adoption of the new features in IEEE Standard 1547 will improve transmission and distribution reliability and facilitate the successful integration and operation of additional DERs that could not otherwise be physically allowed to interconnect to the system.

In February 2017, the NERC Essential Reliability Services Working Group issued the Distributed Energy Resources Report on Connection Modeling and Reliability Considerations (see Section 6.2). The report examined the transformation of the North American electric power system to one with a resource mix that relies less on coal and nuclear and  more on natural gas, wind, solar, distributed generation, and demand-response resources in the context of monitoring grid reliability and resiliency. The report discussed the potential reliability risks and mitigation approaches for increased levels of distributed energy resources on the BPS. It also identified voltage- and frequency-response capability and voltage- and frequency-ride-through capability as important considerations for both distribution and BPS reliability. Transmission and distribution entities will need to coordinate efforts to determine the appropriate use and modeling of future DER capabilities.

## Integration of Wind Resources

New England has significant potential for developing wind resources. The region has developed approximately 1,300 MW (nameplate), and almost 5,400 MW (nameplate) was in the interconnection queue as of April 1, 2017. As the amount of wind generation grows, operational forecasts of this variable energy resource take on increasing importance.

### Wind Forecasting and Dispatch

On January 15, 2014, the ISO began incorporating wind forecasting into ISO processes, scheduling, and dispatch services. In addition to the ISO’s use of the wind forecast, wind-resource operators can download the forecast of expected output for their individual units, which can help them build a strategy for bidding in the Day-Ahead Energy Market. The ISO also created displays that improve operators’ situational awareness and is now maintaining historical wind data for future use by the forecast service and in auditing and other analyses.

In May 2016, the dispatch of wind resources was more closely coordinated with the short-term outage-scheduling process, and the ISO began publishing an aggregate week-ahead wind power forecast (similar to the publishing of the week-ahead load forecasts). This assists market participants in incorporating this information into their decision-making processes and market strategies.

Congestion management in New England was also enhanced in May 2016 when the ISO implemented “do-not-exceed” (DNE) dispatch changes to the market rules, subjecting wind and hydro VERs that traditionally had been non-dispatchable to economic dispatch and participation in price formation in real time. Thus, when transmission limits start to bind, the dispatch can now reflect the energy supply offers of wind and hydro resources, which can be dispatched down and set the price when marginal. Compared with the manual curtailment of resources, which does not reflect the congestion price, DNE dispatch reflects the lower value of energy in an export-constrained area. The DNE dispatch changes enhance reliable system operation by eliminating much of the need for the manual curtailment of these resources. These improved price signals will better inform future decisions about siting of resources.

Additional revisions to the market rules, referred to as the “resource dispatchability changes,” broaden the range of resources required to be subject to economic dispatch. The resource dispatchability changes further improve price formation, which will provide more accurate locational signals to developers when considering where to locate new resources.

### Strategic Transmission Analysis—Wind Integration Study

In 2014 and 2015, the ISO conducted Strategic Transmission Assessments of the integration of new wind resources in Maine and in Vermont. The study found that transmission system improvements are necessary to address a combination of local and regional transmission constraints and address BPS performance concerns. Small amounts of additional 115 kV-connected wind resources planned in Maine for the Wyman Hydro and Rumford regions could likely be accommodated without a major new transmission line to the local regions. However, the Keene Road and Bangor regions cannot support much additional wind capacity beyond the amount studied without major new transmission facilities. Large wind generation projects proposed in western Maine would also require major new transmission additions.

Northern Vermont would require new reactive support to accommodate additional wind resources and would still be thermally constrained below the amount of wind studied but less so in the winter than in other seasons. Central Vermont showed no constraints to the amount of wind in the queue studied (165 MW), and the study determined that this area would be capable of integrating about 231 MW of wind. Southern Vermont showed only minor constraints. Some risk of curtailment remains at higher wind production levels in the northern and southern regions if only modest upgrades are applied. Major upgrades would be necessary to eliminate the maximum wind-condition restrictions; however, no curtailment would be required at typical wind levels.

As a general matter, the interconnection process is working well throughout the New England transmission system, with interconnection studies being completed within expected timeframes. This, however, has not been the case for studies associated with interconnection requests for resources seeking to interconnect in the northern and western Maine parts of the system where a significant backlog of interconnection requests of proposed new resources, mostly wind generation, persists.

The primary obstacle to interconnection for these resources is a physical one of limited transmission infrastructure. The northern and western Maine areas of the system are comprised of a transmission network built to serve low levels of area load, and a number of generators are already connected, leaving this part of the transmission system at its performance limit with no remaining margin. Interconnecting the quantity of proposed resources in northern and western Maine requires significant new transmission infrastructure. The backlog in this area of the system, however, would likely persist with the continued application of the serial queue study process. Each interconnection request involves lengthy and complex study work to identify the significant transmission infrastructure, and individual projects are not able or willing on an individual basis to make the scale of system upgrade investments warranted.

The ISO has developed and will file with FERC a set of clustering revisions to the interconnection procedures for resolving the queue backlog in Maine and elsewhere on the New England transmission system should similar conditions arise (see Section 4.5.4). The development of the proposed methodology was informed by extensive research, including a review of cluster study approaches that other ISOs and RTOs in North America have implemented, including specific “targeted” study approaches for addressing situations similar to those observed in Maine, as well as stakeholders’ experiences with these processes. In parallel with this review, the ISO also initiated a strategic infrastructure study—the Maine Resource Integration Study—under the OATT Attachment K planning process to identify the transmission upgrades necessary for interconnecting proposed resources in Maine. This work informed the proposed clustering revisions and will form the basis for the ISO’s first cluster system impact study after the clustering revisions are approved.

## Large-Scale Adoption of Photovoltaic Resources and Other Distributed Generation Resources

New England has witnessed significant growth in the development of solar photovoltaic resources over the past few years, and continued growth of PV is anticipated (see Section 3.3). PV technology holds promise as a nonemitting source of electric energy that can be reliably and economically integrated into the electric power system, albeit with some challenges.

Regional PV installations are predominantly small (i.e., less than 10 MW) and state-jurisdictionally interconnected to the distribution system. State policies largely influence the spatial distribution of PV, such that states with more-supportive PV policies (e.g., Massachusetts) are experiencing the most growth of the resource. Existing amounts of PV have not caused noticeable effects on system operation, but impacts are anticipated as penetrations grow. The ISO has engaged in a number of initiatives to examine and prepare for the potential effects of large-scale PV development in the region.

### Operational Solar Forecasting

Because the ISO cannot observe or dispatch most PV in the region, these projects act as a modifier of system load that must be accurately forecasted in the short term to support the efficient administration of the day-ahead market and the reliable operation of the system. As PV penetrations continue to grow and displace energy production from other resources, PV power production is introducing increased variability and uncertainty to the system and eventually will affect  system operations (e.g., result in the need for increased reserve, regulation, and ramping). As such, new forecasting techniques are required to account for PV generation appropriately. The ISO has begun efforts to improve load forecasting to address these challenges.

To assist in its PV forecasting efforts for both system planning and system operations, the ISO is participating in a collaborative pilot study with the Vermont Electric Company (VELCO) as part of its Vermont Weather Analytics Center (VTWAC) project. This collaboration has allowed the ISO to leverage VELCO’s comprehensive information regarding historical PV production in Vermont to validate its method of estimating historical PV production using a more limited amount of data available across the region. Work completed thus far has demonstrated that the results of the ISO’s estimation technique applied in Vermont closely match that of the comprehensive data made available by VELCO.

### Potential Reliability Impacts of PV

Because of the differences between the state-jurisdictional interconnection standards that apply to most PV facilities and the FERC-jurisdictional standards that apply to larger, conventional generators, PV exhibits different electrical characteristics during system conditions typical of grid disturbances (e.g., low-voltage conditions during an unexpected outage of a large generator or transmission facility). The ISO asked the region’s utilities about their interconnection standards, and the responses indicated that most PV units meet the existing IEEE 1547 standards (see Section 9.1). The ISO participated in an Electric Power Research Institute (EPRI) evaluation of the potential reliability impacts of large amounts of distributed generation, such as PV.

A high-level screening conducted by the ISO showed the potential loss of PV resulting from faults on the transmission system. The following maps in Figure 9-1, of Connecticut and Massachusetts, show the areas where PV facilities are likely to trip off line because of low voltage in the event of a fault on the 345 kV transmission system. This could result in thermal or stability problems and could cause the need for additional transmission upgrades. As PV penetrations grow, the severity of this potential problem could also grow. NERC is also studying these concerns at the national level (see Section 6.2).

Figure 9-1: Areas (in blue), in Connecticut (left) and Massachusetts (right), where PV resources are likely to trip off line because of low voltage in the event of a fault on the 345 kV transmission system.

Notes: The key refers to per-unit voltage. Also see Impacts of Transmission System Contingencies on Distributed Generation—Overview, PAC presentation (December 16, 2013), http://www.iso-ne.com/static-assets/documents/committees/comm_wkgrps/othr/distributed_generation_frcst/2013mtrls/dec162013/dg_transmission_impacts.pdf.

A sensitivity analysis also was conducted, which indicates that low voltage will be more widespread when local generation is not operating, for example, on a spring day with light load and high wind and solar generation. The above example highlights the criticality of new DG meeting the voltage and frequency performance expectations of the pending revision of the IEEE 1547 standard.

The ISO is working with the New England states, distribution utilities, and IEEE and other international experts to ensure that the future interconnection standards for PV (and other inverter-interfaced DG resources) better coordinate with broader system reliability requirements. The ISO has participated actively in revising the IEEE standards with the aim of clearly identifying the performance requirements for new DG and improving the coordination of distribution system needs and meeting the performance requirements for the transmission system without imposing barriers to the development of distributed generation. Allowance for smart inverter technologies in revisions to IEEE 1547 provides opportunities for additional DERs to reliably interconnect to the distribution system.

The ISO also will continue to actively track the growth of PV in the region and evaluate its potential impacts on the efficient administration of the wholesale electricity markets and reliable operation and planning of the region’s electric power system. Because many other regions of North America also are witnessing the large-scale adoption of PV, the ISO also is engaging with other ISO/RTOs to share relevant methods and experience (see Section 6.3).

### Modeling of Hourly Load Reduction of Behind-the-Meter Photovoltaics to Establish the Net Installed Capacity Requirement

Since 2015, calculations of the net Installed Capacity Requirement (see Section 4.1) have reflected the effects of behind-the-meter PV on gross demand. The modeling of the BTM PV was based on the average seasonal production for the peak reliability hours (2:00 p.m. to 6:00 p.m. during the summer), which was appropriate given the limited amount of data available to the ISO.

BTM-PV load reductions can now be reflected on an hourly basis in NICR calculations as a result of improved data bases of BTM PV production. The new method could reduce the NICR for FCA #12 by approximately 335 MW. Stakeholder discussions are underway to provide input to the ISO before it submits the FERC filing of the NICR for FCA #12, scheduled for November 2017.

### Other Challenges of Integrating PV and Other Types of Distributed Energy Resources

The growth in PV presents some challenges for grid operators and planners. Challenges for the ISO include the following:

- Difficulty obtaining and managing the amount of data concerning PV resources, including their size, location, and operational characteristics

- A current inability to observe and control most PV resources in real time

- A need to better understand the impacts on system operations of the increasing amounts of PV, including ramping, reserve, and regulation requirements

At present, the ISO’s demand-forecast method considers demand history as an input, which captures the growth and production non-PV DERs. To date, the region has not witnessed the large-scale growth of other types of DERs, which would present challenges similar to PV. The ISO continues to monitor this situation and actively examines its processes for improving its demand forecasts.

The ISO’s work with the regional stakeholders will help position the region to best integrate rapidly growing DER resources in a way that maintains reliability and allows the states to realize the public policy benefits they have identified as the basis for their DER programs.

### Energy-Storage Resources

Recently, the ISO has received requests to interconnect new energy storage devices to the New England system. New England has a long history of allowing electric storage and DERs to participate in its markets. A significant amount of pumped-storage hydroelectric facilities has participated in the New England markets since the inception of the wholesale markets in 1999, and the region has a long-standing model that allows DERs to participate in both the capacity market and as price takers in the Real-Time Energy Market (as settlement-only resources). The dispatchable asset-related demand (DARD) model is also available in the region, which allows load and behind-the-meter DERs to participate in the wholesale electric energy and reserve markets. Additionally, the system’s alternative-technology regulation resource (ATRR) construct enables energy-storage devices (and other DERs) to participate in the Regulation Market in a manner that acknowledges the physical capabilities of these potentially limited-energy devices.

The ISO has successfully processed interconnection requests for electric-storage resources using the existing interconnection procedures and agreements. Most new proposals for electric-storage resources make use of inverter-based technologies, and for the ISO to process the interconnection requests for these technologies efficiently, the requests must include appropriately robust equipment design. The power system models must perform well in the network study analysis and the equipment must meet established performance requirements, such as power-factor, ride-through, and frequency requirements.

## Economic Performance of the System and Other Studies

Economic studies provide metrics depicting various system-expansion scenarios and the pros and cons associated with selected possible future scenarios. These scenarios could assess system performance at a higher level, such as possible additional imports from Canada, resource retirements, and resource additions but do not assess scenarios and the performance of individual asset owners. The key metrics developed include estimates of production costs, transmission congestion, electric energy costs for New England consumers, and a number of others. These metrics suggest the most economical locations for resource development and the least economical locations for resource retirements.

### 2015 Economic Studies

The ISO received three economic study requests in 2015 to assess the following topics:

- Onshore wind development in the Keene Road area of northern Maine and the effects of upgrading the Keene Road Interface.

- Onshore wind development in Maine and the effects of implementing the conceptual improvements identified in the Strategic Transmission Analysis: Wind Integration Study.

- Offshore wind development and the effects of adding transmission improvements that relieve potential bottlenecks

Approximately 320 MW of wind resources were located in the Keene Road area, and over 90 MW of additional future development were proposed for interconnecting to the 115 kV system in the area. The first economic study developed metrics to quantify the effects of curtailments expected on the post MPRP system (see Section 5.4). The effect of potential improvements in the Keene Road area were then evaluated to quantify the possible benefits associated with market-efficiency transmission upgrades (see Sections 2.1.1.2) that could allow the wind resources to operate without the current level of constraints. Additional analysis beyond the economic study was then conducted, and the ISO determined that METUs were not justified (see Section 5.9.2).

The second economic study investigated scenarios of wind-resource development and showed the effect of the conceptual transmission system expansion in Maine. As discussed in Section 9.2.2, the Strategic Transmission Analysis: Wind Integration Study identified a number of conceptual transmission upgrades that could relieve constraints to existing and planned onshore wind development throughout Maine. This study may inform stakeholders on the cost and benefits of pursuing these transmission upgrades.

When less than 1,149 MW of wind are in Maine—with 334 MW located north of Orrington South transmission interface—an increase in transmission interface limits in Maine resulted in production cost savings of less than $5 million annually. With more than 2,084 MW of wind resources in Maine—and more than 1,185 MW north of Orrington South, the annual savings increased to the $38 to $75 million range. Increased imports from New Brunswick increased the production cost savings up to $78 million. As the Maine corridor was upgraded to accommodate higher levels of wind resources, the downstream North–South interface was constrained in more hours.

The third 2015 economic study examined offshore wind development near Rhode Island and Southeast Massachusetts. The analysis included the effects of imports from Canada over new interconnections and the development of onshore wind generation in northern New England. The study also considered the retirement of older nuclear, coal-fired, and oil-fired generating units.

The results of this study suggest that offshore wind deployment could bring sizable economic and environmental benefits to New England. The addition of offshore wind also caused two major interfaces, the North–South and SEMA/RI import interfaces, to be less constrained. This study also highlighted that Kent County, Brayton Point, and Barnstable appear to be favorable interconnection points for low production cost resources. However, interconnection studies consistent with the ISO‘s administration of the interconnection queue would need to be conducted before any final determination could be made for points of interconnection.

### 2016 Economic Study—Phase I

Phase I of the 2016 ISO New England Economic Study was conducted at the request of the New England Power Pool. The study,  2016 NEPOOL Scenario Analysis—Implications of Public Policy on ISO New England Market Design, System Reliability and Operability, Resource Costs and Revenues, and Emissions, examines six resource-expansion scenarios of the regional power system and provides information about the potential effects of these different future changes on resource adequacy, operating and capital costs, and options for meeting environmental policy goals. The study provides a common framework for NEPOOL participants, regional electricity market stakeholders, policymakers, and consumers to identify and discuss these reliability, economic, and environmental concerns issues and to discuss possible solutions. The scope of work, assumptions, and draft results reflect input from the PAC during 12 meetings held from April 2016 through February 2017. Results, however, were presented such that stakeholders may make their own assumptions on capital costs for new resources and transmission development costs. Some of the major results and conclusions are as follows:

- Although increased renewable production reduces the use of natural gas, natural-gas-fired units remain on the margin most of the time and are a major source of fuel for electric power generation production.

- New resources will require sources of revenue in addition to the wholesale energy market to remain economically viable. Natural gas units show the greatest revenue shortfall compared with their annual carrying charges as a result of their production costs being higher than the $0/MWh costs of renewables, which decreases their net revenues from the wholesale energy market. Renewable resources, however, also show significant revenue shortfalls as compared with their annual fixed costs.

- Locating new resources with relatively low production costs near load centers in southern New England reduces systemwide congestion and the need for transmission expansion, which increases with the remote development of renewable resources in northern New England.

  - Scenarios with the remote development of resources in northern New England result in the megawatt flow across transmission interfaces reaching their limit, which causes the LMP at the sending end being lower than at the receiving end in the constrained cases.

  - The constrained cases show that renewable production by remote wind, hydro, and imports need to reduce or “spill” output to respect transmission constraints, which increases the overall production cost, load-serving entity (LSE) energy expenses, and system emissions.

- Meeting carbon emission targets may prove challenging for the New England region without the widespread development of renewable resources, EE, and interconnections with neighboring systems.

- Transitioning New England to a system with decreasing amounts of traditional resources (e.g., coal, oil, nuclear) and increasing amounts of renewable resources will prove physically and economically challenging. Observability, controllability, and interconnection performance are key technical issues that must be addressed for distributed resources and the large-scale development of wind generation resources.

- Efficient storage technologies, such as pumped storage and distributed storage, and changes in tie schedules can provide systemwide flexibility and facilitate the integration of variable resources. Proper types and placement of flexible resources show the potential for relieving congestion and reducing requirements for regulation, ramping, and reserves. Increasing the development of energy storage technologies used for energy price arbitrage makes them less economic because storage equalizes LMPs across all hours.

As part of the 2016 Economic Study, the ISO met with the PAC to discuss many of the challenges of integrating renewable resources. Transitioning New England to a hybrid system with decreasing amounts of traditional resources (e.g., coal, oil, nuclear) and increasing amounts of renewable resources will require significant technical and structural changes, for example:

- The equipment must meet established performance requirements, such as power factor, voltage and frequency-response capability, and voltage and frequency ride-through capability.

- The large-scale development of asynchronous resources (such as HVDC ties, photovoltaics, and wind) will require the addition of special controls on power system resources and new transmission equipment, especially to compensate for the loss of traditional resources that provide inertia and short-circuit availability. The needs are exacerbated by the changing nature of demand, especially the large-scale use of energy-efficiency measures, which further increases the complexity of operating and planning the system by increasing exposure to light load conditions.

- Advanced software will facilitate future analysis of the system, especially to conduct probabilistic simulations that consider variable energy resource production.

### 2016 Economic Study—Phase II

Supplemental studies of the Phase I NEPOOL Scenario Analysis assess several market and operational issues. For each of the Phase I scenarios, the Phase II Scenario Analysis examines the following:

- Representative Forward Capacity Auction clearing prices

- The ability of the natural gas system to supply fuel to generators

- Changes in the amounts of regulation, ramping, and reserves

The FCA analysis considered energy market revenues from the Phase I simulations and then determined FCA clearing prices and revenues consistent with market rules. Because resources could retire and develop in the intervening years, the FCA pricing results do not capture the effect of transitions in the resource mix. All resources in the scenarios were considered “existing resources,” and the results provide relative FCA clearing prices across scenarios rather than absolute FCA prices. Key results of the FCA analysis are as follows:

- Scenarios with retirements and new entry approximately meeting net ICR result in the highest FCA prices, which are slightly above the net cost of new entry (CONE) (i.e., the prices are the same as for existing-resource offers.

- The scenario with no retirements and no major new resources beyond FCA #10 has lower FCA prices.

- The scenario with retirements with substantial new clean and distributed resources results in the lowest FCA prices because the scenario added large quantities of CSOs in excess of net ICR.

- All scenarios show the need for additional revenue streams outside the wholesale electricity markets for capacity and energy. Scenarios that added renewables resulted in the greatest revenue shortfalls for all resource types given the higher cost of new entry for renewables and depressed energy market revenues.

The second Phase II study examined natural gas system deliverability issues by considering six scenarios for natural gas supply to the region compared with the seasonal fuel requirements of natural-gas-fired generation, recognizing that the local distribution company loads must be served first. The analysis examined the ability of the spare capacity of the natural gas system to serve the installed seasonal claimed capability of natural-gas-fired generation and the amount of gas-fired generation dispatched in the production simulations. But the study did not consider maintenance conditions or forced outages on the natural gas system, which would reduce its capability to serve gas-fired generation across scenarios.

Even for maximum assumed natural gas supply to the region, the results show insufficient spare natural gas system capacity to satisfy the installed capacity of all natural-gas-fired generating units across the six resource-expansion scenarios for the 2024/2025 and 2029/2030 winters. Although not all natural-gas-fired generating units will necessarily run during the winter peak, the results show vulnerability to electric power system contingencies, such as reductions in non-natural-gas-fired resources (e.g., nuclear units) and disruptions of electric energy imports, all of which could require the additional use of natural-gas-fired units. The study also concludes the region will need to rely on the large-scale addition of energy efficiency and resources that use fuels other than natural gas, such as renewable resources, to supplement the natural gas supply to meet electric system energy needs during the winter operating season.

Phase II results also showed that, assuming its full capability, the existing pipeline capacity has sufficient spare natural gas system capacity to serve the natural-gas-fired generating units and their energy requirements for the six resource- expansion scenarios during the summers of 2025 and 2030. The analysis accounts for the reduction in LDC consumption during the summer operating period but did not consider pipeline maintenance conditions that typically occur during the summer.

The third Phase II study is examining intrahour ramping, regulation, and reserve requirements of the system for the six scenarios. The requirements will be quantified through simulation results, which are expected by late 2017.

### 2017 Economic Study

The ISO received one request for an economic study in 2017. The study will examine three combinations of large-scale renewable wind, PV, and EE resources, as well as plug-in electric vehicles and distributed storage. The study will show several economic metrics typically provided in economic studies:

- Total energy production by resource/fuel type

- Systemwide production costs

- Average locational marginal prices

- Load-serving entity energy expenses and congestion

- High order-of-magnitude cost estimates for transmission development

- Relative annual resource costs for the addition of new resources

- Environmental emissions

- “Spillage” of renewable resource energy production due excess production systemwide or  transmission constraints that bottle economical resources

## Summary

The ISO continues to enable the reliable integration of wind and distributed resources. The implementation of wind forecasting and dispatch have improved the operation of the system. Additional work remains on incorporating the effects of PV in improved short-term load-forecasting tools for use by system operators and fully addressing the potential reliability risks and benefits posed by growing penetrations of PV.

The Strategic Transmission Analysis: Wind Integration Study developed conceptual additions to the transmission system that would enable onshore wind resources to reliably serve load. Clustering the ISO’s interconnection queue facilitates the addition of wind resources. The equipment must meet established performance requirements, such as power factor, voltage and frequency-response capability, and voltage and frequency ride-through capability. Revisions to the interconnection standards for distributed resources will improve reliability and increase the amount of PV that can be interconnected to the system. The large-scale development of asynchronous resources will require the addition of special controls on power system resources and new transmission equipment.

Economic studies have examined various scenarios of changes in transfer capabilities, resource expansion, and retirement scenarios. The 2015 economic studies of the Keene Road area, onshore wind expansion, and offshore wind expansion provided information on the potential need for transmission upgrades that would facilitate the development of wind resources. The 2016 Economic Studies provide a common framework for future discussions on several issues facing the New England region and the need for physical infrastructure and improvements to the wholesale electric markets.

PV and wind generation reduce energy prices, lower regional emissions, and present several technical challenges. The ISO continues to work with stakeholders to address these effects, including the need for any enhancements to the markets.

# Multistate, ISO, and State Initiatives

State and multistate initiatives and policies have a significant impact on the wholesale electricity markets and transmission developed to meet system needs, specifically influencing the timing, type, and location of resources and transmission infrastructure. Federal initiatives, by FERC, DOE, and the White House, address reliability and security issues. Initiatives and policies by each of the six New England states address energy infrastructure, renewable energy, and environmental concerns. ISO initiatives focus on new technologies and enhancing operating and planning procedures.

## Multistate Initiatives

This section discusses activities at the multistate level that affect the regional power system.

### Eastern Interconnection States Planning Council

The New England states are active participants in the interconnection-wide planning for the Eastern Interconnection. The Eastern Interconnection States Planning Council (EISPC) is an organization of 39 states and eight Canadian provinces in the Eastern Interconnection electric transmission grid, including representatives from New England, responsible for participating with the planning authorities that are part of the EIPC. Initially funded by a DOE Funding Opportunity Announcement, the EISPC comprises public utilities commissions (PUCs), governors' offices, energy offices, and other key government representatives and provides input to the EIPC study effort. The EISPC has begun functioning as part of the National Council on Electricity Policy (NCEP), which has been recently reinvigorated by the National Association of Regulatory Utility Commissioners (NARUC). As a planning authority, the ISO participates in EIPC and has provided support to the EISPC, as appropriate. Section 6.1 discusses some EIPC studies.

### Coordination among the New England States

The New England states have worked together continually to identify, discuss, and address energy issues of common interest. Even with this history of cooperation, each state has a unique set of energy policy objectives and goals.

Each of the New England states is actively involved in the ISO’s regional planning process, individually and through the New England States Committee on Electricity (NESCOE). NESCOE serves as one forum for representatives from the states to participate in the ISO's decision-making processes, including those dealing with resource adequacy and system planning and infrastructure expansion.

In addition to NESCOE, the ISO works collaboratively with the New England Conference of Public Utilities Commissioners (NECPUC), the New England governors’ offices, and the states’ consumer advocates. The ISO provides monthly updates to the states on regional stakeholder discussions regarding the regional planning process and the wholesale electricity markets.

### Consumer Liaison Group

The ISO and regional electricity market stakeholders created the Consumer Liaison Group (CLG) in 2009 as an additional means to facilitate the consideration of consumer interests in determining the needs and solutions for the region’s power system. With representatives from state offices of consumer advocates and attorneys general, large industrial and commercial consumers, chambers of commerce, and others, the CLG meets quarterly to address various electricity issues affecting consumers. With the input of CLG members, a Coordinating Committee guides CLG meeting agendas and ideas for special guest speakers and discussion topics.

In 2016, the CLG’s discussions focused on issues relating to distributed energy resources, advanced technology and cybersecurity, energy infrastructure, and the New England states’ clean energy initiatives. On March 1, 2017, the CLG Coordinating Committee and the ISO issued the 2016 Report of the Consumer Liaison Group, which summarizes the activities of the CLG in 2016. It also provides an update on ISO activities and initiatives, as well as wholesale electricity costs and retail electricity rates.

### Southern New England States’ Request for Proposals

In November 2015, the three southern New England states—Massachusetts, Connecticut and Rhode Island—issued an RFP for clean energy resources and electric transmission developers to deliver additional supplies of renewable energy and large-scale hydropower to the New England power system. Bids submitted by the January 28, 2016, deadline were considered by an evaluation team that made its final selection on October 24, 2016. The three states collectively selected projects that represent approximately 460 MW of clean energy for the New England market. None of the projects included associated transmission to deliver the clean energy supplies to New England load centers. The projects selected advanced to the contract negotiation stage with the three states’ electric distribution companies (EDCs), and are subject to review by each state’s utility commission.

## ISO Initiatives

The ISO is involved in a number of initiatives aimed at developing and integrating new technologies, and enhancing operating and planning procedures to enhance system reliability.

### Updates on Developing and Integrating Smart Grid and Other New Technologies

The ISO strives to keep up to date with new technologies that can have an impact on the region’s electric power grid. As policymakers set targets and allocate public funds for developing smart grid initiatives and renewable resource generation, the ISO analyzes the effects of these technologies on system operations and reliability. Several of the technology developments and challenges affecting the planning of the New England region involve integrating smart grid equipment, improving operator awareness and system modeling through the use of phasor measurement units (PMUs), and using HVDC facilities and flexible alternating-current transmission system (FACTS) devices.

#### Research Participation and Technical Support

The ISO currently participates in several research projects sponsored by DOE, the Power System Engineering Research Center (PSERC), and the Electric Power Research Institute that support the successful integration of advanced technologies. Additionally, the ISO is providing technical and other support for the development of demand-response-related and other market-related standards by the North American Energy Standards Board (NAESB). The ISO staff and stakeholders remain professionally active in the Institute of Electrical and Electronics Engineers (IEEE), a society that serves to educate its members and the public at large, as well as develops standards for the interconnection and operation of smart grid technologies.

#### Operational Efficiencies through Advanced Technology

To satisfy an increasing number of required transmission plan studies and enhance the ISO’s ability, speed, and costs of using more detailed and sophisticated system models and scenarios, the ISO uses cloud computing. The initiative—the first of its kind for large-scale power system simulation studies in the industry—is already yielding successful early results. In addition, various projects to create new systems and tools for greater operational and planning efficiencies and performance are also underway. The ISO remains a leader in the application of phasor measurement units, which include projects related to voltage stability, control room visualization, and power system modeling. The ISO uses PMUs for detecting oscillation sources, which identifies potential control system issues in power system equipment.

Where appropriate and cost effective, the application of power electronics to the power system through high-voltage direct-current and flexible alternating-current transmission system technologies can address performance concerns on the transmission system. HVDC and FACTS use a combination of solid-state switches and computerized automation that enables nearly instantaneous customized control of real or reactive power flows—far faster than traditional electromechanical switches. As part of its planning process, the ISO has reaffirmed the need for specific FACTS devices, several of which are old. Figure 10-1 shows retired, refurbished, and planned HVDC and FACTS devices in New England.

Figure 10-1: Existing and planned FACTS devices in New England.

Notes: (a) The acronyms and abbreviations in the key refer to the following terms: HVDC = high voltage, direct current. VSC = voltage source converter. SVC = static voltage ampere reactive (V) compensator. STATCOM = static synchronous compensator. DVAR = dynamic voltage ampere reactive. (b) Plans call for replacing the DVAR at Stony Hill and Bates Rock with a synchronous condenser at Stony Hill.

Another initiative is the ISO’s monitoring of local energy-storage technologies, such as batteries and quick-responding automated demand response, and other smart grid technologies to anticipate their potential effect on regional system performance. Distribution utilities and local customers must address issues posed by the integration of variable energy resource on the distribution system, such as voltage regulation and power quality, and may need to apply local storage and smart grid technologies to improve electrical performance. The ISO is also a leader in simulating detailed models of HVDC, FACTS, and wind and PV resources and accounting for potential adverse interactions resulting from the widespread use of inverter-based technologies. These types of simulations increase the complexity of system studies, which must accurately model control and protection systems and their interactions.

### Transmission Planning Initiatives

The ISO has developed methods to better represent and make assumptions about system conditions for probability and statistical analyses of load levels and generator availability. Work continues to improve the modeling of VERs. Ongoing and future efforts through the stakeholder process will review data sources and identify or specify new simulation tools, which will extend beyond 2017.

The ISO has updated the Transmission Planning Process Guide to reflect the new methodology. The ISO has also updated the Process Guide to reflect FERC Order No. 1000’s required changes to the planning process. Refer to Sections 2.1.2 and 5.3.

### ISO Market Initiatives

The ISO maintains system reliability and economic efficiency through the region’s competitive wholesale electricity markets and short- and long-term projects that enhance the markets. The FCM Performance Incentives project, Price-Responsive Demand project, and the Competitive Auctions with Sponsored Policy Resources project represent several key market projects at the ISO.

#### Price-Responsive Demand Project

FERC Order No. 745, Demand-Response Compensation in Organized Wholesale Energy Markets, requires organized wholesale energy markets to pay demand-response providers the market price for electric energy for reducing consumption below expected levels, when doing so lowers costs to consumers and helps balance real-time supply and demand. To comply with the order, the ISO modified its existing demand-response programs and is implementing various market-rule changes for fully integrating demand response and further improving overall market efficiency. The ISO also has proposed modifications to the market rules to allow demand-response resources that participate in the energy market to also provide reserves, similar to other supply resources. Demand-response resources will be fully integrated into the wholesale energy, reserves, and capacity markets on June 1, 2018.

#### Forward Capacity Market Incentives

Recent enhancements to the FCM are designed to better meet operational needs. The FCA clearing prices for new resources may be locked in for seven years, creating financial stability. The introduction of priced retirement delist bids in FCA #10 (which replaced nonpriced retirements) has helped ensure that resources leave the marketplace when it is economically appropriate. FCA #9 introduced the systemwide sloped demand curve, and in FCA #11, MRI-based system and zonal sloped demand curves (see Section 4.1.1) were introduced to more economically procure needed resources.

Starting in 2018, the existing FCM shortage-event penalty structure will be replaced with a new two-settlement market design intended to create strong financial incentives for all capacity suppliers, without exception, to maximize performance and availability during scarcity conditions (i.e., during operating reserve deficiencies). This pay-for-performance market improvement will ensure that supply resources face appropriate market-based incentives and have the financial capability to undertake cost-effective investments that improve resource performance and system reliability.

#### Competitive Auctions with Sponsored Policy Resources

The ISO has also engaged with NEPOOL and the New England states to investigate the better integration of markets and public policy (IMAPP). The ISO has put forward a framework for competitive auctions with sponsored policy resources (CASPR), which is designed to maintain competitively based forward capacity price signals while, over time, accommodating the entry into the FCM of new resources sponsored by public entities. The CASPR proposal will be reviewed with regional stakeholders during the remainder of 2017.

An ISO discussion paper details the ISO’s proposal to address concerns about sponsored new resources’ participation in the FCM and the potential effects, including depressed prices or excess capacity. The ISO’s proposed solution would accomplish the following:

- Introduce a new two-stage, two-settlement process by adding a secondary market known as a substitution auction after the primary capacity auction is completed

- Provide financial incentives for existing, high-cost capacity resources to transfer their capacity obligations to sponsored new resources, then permanently exit the capacity market—akin to a “severance payment”

- Keep the market technology neutral

The ISO looks forward to continuing its discussions with stakeholders on this design with the objective of modifying the capacity market rules to address these goals, possibly by FCA #13 in February 2019.

## State Initiatives, Activities, and Policies

The New England states have worked together continually to identify, discuss, and address energy issues of common interest. Even with this history of cooperation, each state has a unique set of energy policy objectives and goals. This section summarizes actions taken by the individual New England states pertaining to regional system planning, including several recently implemented laws, policies, and initiatives.

### Summary of Renewable Portfolio Standards

All six New England states have targets for the proportion of electric energy that load-serving entities must provide using renewable resources. Options for meeting, or exceeding, these Renewable Portfolio Standard (RPS) targets include developing the renewable resources in the ISO queue, importing qualifying renewable resource energy from adjacent balancing authority areas, building new renewable resources in New England not yet in the queue, developing behind-the-meter projects, and using eligible renewable fuels in existing generators. In addition, load-serving entities can make state-established alternative compliance payments if their qualified renewable resources fall short of providing sufficient renewable energy credits to meet the RPSs.

State RPS targets for 2020 range from 10% to 59% and have driven new proposals for renewable energy (as discussed in Section 10.2.3 above). This trend is expected to continue as state targets increase incrementally between now and 2020. The wide range of RPS percentages results from the different definitions of renewable resources in the region. All states have, or are considering, RPS targets that extend to 2030 and beyond.

### Connecticut

Connecticut state law requires the Connecticut Department of Energy and Environmental Protection (DEEP) to prepare a Comprehensive Energy Strategy (CES) every three years. The CES is an assessment of future energy needs in the state and strategies for reducing costs to ratepayers, ensuring reliable power system operations, and mitigating the public health and environmental impacts of Connecticut’s energy use. The major topics to be reviewed in the 2017 CES include securing cheaper, cleaner, more reliable energy options in the electricity, buildings, and transportation sectors.

DEEP has been implementing energy legislation passed in 2015 titled An Act Concerning Affordable and Reliable Energy. The statute gives the Commissioner of DEEP the authority to issue multiple solicitations for a wide variety of resources and direct the state’s electric distribution companies  to enter into long-term contracts for any combination of these resources, provided the benefits to electric ratepayers outweigh the costs. The legislation required DEEP to evaluate the costs and benefits of the proposals it received concurrently to ensure it selected the projects most beneficial to Connecticut ratepayers.

In accordance with Connecticut’s participation in the three-state Clean Energy RFP, any relevant contracts executed by Connecticut’s EDCs are required to be filed with the Public Utilities Regulatory Authority (PURA) for review and approval.

### Maine

Over the past few years, the Maine Public Utilities Commission (ME PUC) analyzed whether to enter an energy-cost-reduction contract to procure natural gas pipeline capacity and considered specific bids from gas pipeline developers. A study funded by the PUC concluded that the $75 million cost to Maine from entering into a firm natural gas transportation contract would outweigh the benefits if the state were to act alone. In July 2016, the ME PUC unanimously approved a plan that allows the state, through utility billing, to pay to expand gas pipeline capacity in the region when the benefits outweigh the cost, which the ME PUC determined can be accomplished if other states in the region enter into similar contracts.

### Massachusetts

In May 2016, the Supreme Judicial Court’s decision in Kain et al. v. Massachusetts Department of Environmental Protection (Kain) affirmed the state’s obligations under the 2008 Global Warming Solutions Act (GWSA) and requires the commonwealth to create and implement regulations to meet its mandates for reducing carbon emissions. Following the Kain decision, the governor issued Executive Order No. 569, which calls for an integrated strategy for combatting climate change and included a directive for the Massachusetts Department of Environmental Protection (MA DEP) to issue regulations to meet the 2020 emissions limit under the GWSA. These regulations, released August 11, 2017, include, among other things, clean energy standards and seek to reduce sulfur hexafluoride emissions from gas-insulated switchgear, methane emissions from natural gas distribution systems, and CO2 from electricity generating facilities.

In 2016, a comprehensive energy bill was passed into law, which requires the state’s electric distribution companies solicit long-term contracts (15 to 20 years in duration) for offshore wind and clean energy. In the first half of 2017, pursuant to this legislation, the Massachusetts Department of Public Utilities (MA DPU) approved the release of requests for proposals for offshore wind and clean energy bids. In 2018, the EDCs will submit to the DPU the contracts resulting from the RFP. The DPU will determine whether the winning bids each contract is a cost-effective mechanism for procuring reliable renewable energy on a long-term basis, and if so, it will approve the contract.

In June 2017, in accordance with  legislation passed in 2016, Governor Baker announced a 200 MWh energy-storage target to be achieved by January 1, 2020. The target, set by the Department of Energy Resources (DOER), builds on the Energy-Storage Initiative (ESI), a $10 million commitment to analyze opportunities to support energy-storage companies in Massachusetts and develop policy options to encourage energy storage deployment.

### New Hampshire

In 2017, the legislature passed, and the Governor signed, legislation that established a new committee to study transmission, distribution, generation and other costs in the state’s electricity system. In addition, the New Hampshire Public Utilities Commission (NH PUC), in accordance with the 2014 State Energy Strategy and supporting legislation, opened a docket to study grid modernization. It also opened separate dockets to consider an energy-efficiency resource standard and develop an alternative net-metering tariff.

In 2016, the NH PUC opened a docket to examine a petition by a New Hampshire electric utility to purchase natural gas capacity on the proposed Access Northeast pipeline. The capacity purchased was to be resold to New England gas-fired generators for lowering electric energy prices and enhancing power system reliability. The NH PUC dismissed the utility’s petition in October 2016 for being inconsistent with New Hampshire’s restructuring law.

### Rhode Island

In March 2017, Rhode Island Governor Gina Raimondo announced a strategic goal for a tenfold increase in clean energy in the state by the end of 2020. The goal is to have 1,000 MW of clean energy operating or under contract in Rhode Island by 2020. Rhode Island had approximately 100 MW of clean energy installed in the state in 2016, the baseline year for this goal. According to the governor’s office, the goal will include energy from a broad portfolio of clean energy resources, including wind (onshore and offshore) and solar. The governor’s announcement follows the commissioning of the nation’s first offshore wind farm in Rhode Island state waters—the Block Island Wind Farm.

In 2017, the state also extended its Renewable Energy Growth Program, which was set to expire in 2019, for an additional 10 years with the goal of installing 40 MW of distributed generation in each of the 10 years.

### Vermont

The Vermont Department of Public Service (VT DPS) and Public Utilities Commission (VT PUC) have largely been focused on implementing several significant laws the legislature enacted the past few years.

In 2015, Vermont established a Renewable Energy Standard (RES) program, which took effect on January 1, 2017. The RES requires three tiers of compliance for state electric utilities. The first tier requires utilities to obtain 55% of annual electricity sales from renewable resources in 2017, rising to 75% by 2032. The second tier requires 1% of utility sales to come from small, distributed renewable resources (less than 5 MW in size) in 2017, rising to 10% by 2032. The third tier requires 2% of utility sales (Btu equivalency) to come from projects that reduce customer fossil fuel consumption starting in 2017, rising to 12% in 2032. Such projects could include promoting weatherization, energy storage technologies, electric vehicles, and other such infrastructure.

## Summary of Initiatives

The ISO’s planning activities are closely coordinated among the six New England states, with neighboring systems, across the Eastern Interconnection, and nationally. Each New England state has a unique set of energy policy objectives and goals and continues to implement laws, policies, and initiatives that affect the regional system planning in New England.

In response to state policy initiatives, the region is examining improvements to the wholesale electricity markets. The goal of these improvements is to accommodate New England states’ energy and environmental policies at the lowest reasonable cost without unduly diminishing the benefits of competitive organized markets.

# Key Findings and Conclusions

In accordance with all requirements in the Open Access Transmission Tariff, ISO New England’s 2017 Regional System Plan discusses the electric power system’s needs and the amounts, locations, and types of resource development that can meet these needs from 2017 through 2026. RSP17 also discusses the status of transmission system assessments, transmission system planning studies, and projects needed for meeting reliability requirements and improving the economic performance of the system. Other discussions include interregional planning requirements and risks to the regional electric power system; the likelihood, timing, and potential consequences of these risks; and mitigating actions. Some of the other highlights of RSP17 include strategic planning challenges expected over the 10-year planning horizon and how the region is analyzing and addressing these challenges.

This section summarizes the key findings of RSP17 and conclusions about the outlook for New England’s electric power system over the next 10 years:

- Forecasts of the regional net peak and annual energy show flat to negative growth resulting from the additions of PV and EE, which are reflected in the planning processes. Net peak demand, thus, is less of a key driver of new infrastructure needs.

- Needed capacity and operating reserves are provided through the wholesale markets, but resource retirements and the successful integration of variable energy resources pose future challenges to the reliable and economic operation of the system. Studies of expected system conditions show that developing new resources near load centers, particularly in the Southeastern New England zone, would provide the greatest reliability benefit.

- Transmission expansion in New England has improved the overall level of reliability and resiliency, reduced air emissions, and lowered wholesale market costs by effectively eliminating congestion and Net Commitment-Period Compensation. Generator retirements, off-peak system needs, the growth of asynchronous resources, and changes to mandatory planning criteria promulgated by NERC and NPCC will drive the need for longer-term transmission projects.

- RSP17 complies with the intraregional and interregional planning processes required by the ISO’s Open Access Transmission Tariff. Revisions to the ISO planning processes now reflect Order No. 1000 requirements, probabilistic study assumptions, and changes to national and regional criteria. Coordinated planning activities with other systems will continue growing, particularly to provide access to a greater diversity of resources, including hydro imports and VERs, and to meet environmental compliance obligations.

- The regional reliance on natural-gas-fired generation, coupled with natural gas pipeline constraints and uncertain LNG deliveries can pose reliability issues and lead to price spikes in the wholesale electricity markets. The ISO is quantifying this risk in its fuel-security study, which will be discussed with stakeholders in the last quarter of 2017.

- Environmental regulations, other public policies, and economic considerations, all will affect the future mix of regional resources, such as to influence the retirement of oil and coal generators and the addition of natural-gas-fired generation. Delays in EPA regulations and changes in regional and state regulations, however, create additional uncertainty in the shorter term. Generators needing to make major investments in environmental compliance measures may become uneconomical and retire, but others can recover their capital investment by locking in FCM prices for up to seven years. Carbon emissions targets will likely be the key regional environmental constraint on energy production.

- The region has significant potential for developing renewable resources and is actively addressing several key technical challenges to the successful integration of these resources. For example, interconnection queue processes that use clustering and new forecasting methods have been updated to improve the reliable and economical operation of the system with increasing amounts of wind resources. The addition of renewables, however, suppresses energy market prices and may further encourage the retirement of traditional generating units. The large-scale development of wind resources in northern New England would require significant additional transmission system improvements.

- New England is transforming to a sustainable, hybrid grid that supports the connection of more renewable energy and the transition to the smart grid, which will make more effective use of distributed energy resources. Issues of observability and controllability of variable and distributed resources will need to be addressed to realize the full benefits of energy storage, microgrids, and smart grid technologies. The rapid implementation of revised interconnection standards for distributed resources, including the IEEE 1547, is vital for ensuring overall system reliability and facilitating the economical development of renewable resources, such as PV.

- Federal and state policies and initiatives will continue to affect the planning process, such as the effect of policies promoting EE, PV, and wind resources. The ISO remains a leader in technological innovation, as shown by the widespread use of phasor measurement units, extensive application of flexible alternating-current transmission systems, and the implementation of state-of-the-art forecasting methods for wind resources and PV.

- The nature of the New England electric power system is undergoing major change as the system evolves from a capacity-limited system to an energy-limited system.

Through an open process, regional stakeholders and the ISO are addressing these issues, which could include further infrastructure development, as well as changes to the wholesale electricity market design and the system planning process. Through current and planned activities, the region is working toward meeting all challenges for planning and operating the system in accordance with all requirements.

# Acronyms and Abbreviations

| Acronym/Abbreviation | Description |
| --- | --- |
| $/kW-mo; $/kW-m | dollar(s) per kilowatt-month |
| $/kW-yr | dollar(s) per kilowatt-year |
| $/MMBtu | dollar(s) per million British thermal units |
| $/MWh | dollar(s) per megawatt-hour |
| 12 CP | average of all the monthly regional network loads (per the OATT, Section 21.2) for the 12 months of the calendar year on which the rate is based |
| 50/50 | refers to a 50/50 peak load—a peak load with a 50% chance of being exceeded because of weather conditions, expected to occur in the summer in New England at a weighted New England-wide temperature of 90.2°F, and in the winter, 7.0°F |
| 90/10 | refers to a 90/10 peak load—a peak load with a 10% chance of being exceeded because of weather conditions, expected to occur in the summer in New England at a weighted New England-wide temperature of 94.2°F, and in the winter 1.6°F |
| AC; ac | alternating current |
| ACEEE | American Council for an Energy-Efficient Economy |
| ADR | active demand resource |
| AEO | Annual Energy Outlook (EIA) |
| AGT | Algonquin Gas Transmission |
| AIM | Algonquin Incremental Market (Enbridge Energy project) |
| AMRXY | 20XY Annual Markets Report |
| ARIPPA | Anthracite Region Independent Power Producers Association |
| ATRR | alternative technology regulation resource |
| Bangor Hydro | 1) Bangor Hydro Electric Company 2) active-demand-resource dispatch zone |
| bbl | blue barrel |
| Bcf; Bcf/d | billion cubic feet; billion cubic feet per day |
| BES | bulk electric system (NERC) |
| BHE | 1) RSP subarea of northeastern Maine 2) Bangor Hydro Electric Company |
| Boston | active-demand-resource dispatch zone (sentence capitalization) |
| BOSTON, BOST | RSP subarea of Greater Boston, including the North Shore (all capitalized) |
| BPS | bulk power system (NPCC) |
| BTM | behind the meter |
| Btu | British thermal unit |
| C2C | Continent-to-Coast Expansion Project (PNGTS, TransCanada, Iroquois) |
| CAA | Clean Air Act (US) |
| CAGR | compound annual growth rate |
| CAISO | California Independent System Operator |
| CAMS | Customer Asset-Management System |
| CASPR | competitive auction with sponsored policy resources |
| CC | combined cycle |
| CCP | capacity commitment period |
| CCR | cost-containment reserve |
| CCRP | Central Connecticut Reliability Project |
| CEII | critical energy infrastructure information |
| CELT | capacity, energy, loads, and transmission |
| 2016 CELT Report | 2016–2025 Forecast Report of Capacity, Energy, Loads, and Transmission |
| 2017 CELT Report | 2017–2026 Forecast Report of Capacity, Energy, Loads, and Transmission |
| Central MA | Central Massachusetts active-demand-resource dispatch zone |
| CES | Comprehensive Energy Strategy (CT) |
| CFR | Code of Federal Regulations |
| CHP | combined heat and power |
| Cir. | Circuit (court) |
| CLG | Consumer Liaison Group |
| CMA/NEMA | RSP subarea comprising central Massachusetts and northeastern Massachusetts |
| CMP | Central Maine Power (Company) |
| CNG | compressed natural gas |
| CNRIS | Capacity Network Resource Interconnection Service |
| CO2 | carbon dioxide |
| CONE | cost of new entry |
| COO | chief operating officer |
| CPP | Clean Power Plan (US EPA) |
| CRA | contingency reserve adjustment (factor) |
| CSC | Cross-Sound Cable |
| CSO | capacity supply obligation |
| CT | 1) State of Connecticut 2) RSP subarea that includes northern and eastern Connecticut 3) Connecticut load zone 4) capacity zone area within the Connecticut import interface, including the RSP bubbles for CT, SWCT, and NOR plus the Scitico substation served from western Massachusetts |
| CWA | Clean Water Act (US) |
| CWIP | construction work in progress |
| CWIS | cooling water intake structure |
| DARD | dispatchable asset-related demand |
| DC | direct current |
| D.C. | District of Columbia |
| D.C. Cir. | District of Columbia Circuit (US Court of Appeals) |
| DCT | double-circuit tower |
| DEEP | Department of Energy and Environmental Protection (CT) |
| DER | distributed energy resource |
| DG | distributed generation |
| DGFWG | Distributed Generation Forecast Working Group |
| DOC | Microsoft Word file |
| DOE | Department of Energy (US) |
| DOER | Department of Energy Resources (MA) |
| DNE | do not exceed |
| DPU | Department of Public Utilities (MA) |
| DRCR | demand response capacity resource |
| Dth/d | dekatherms per day |
| DVAR | dynamic voltage ampere reactive |
| Eastern CT | Eastern Connecticut active-demand-resource dispatch zone |
| ECR | emissions containment reserve |
| ECT | eastern Connecticut |
| EDC | electric distribution company |
| EE | energy efficiency |
| EEF | energy-efficiency forecast |
| EERS | Energy-Efficiency Resource Standard (NH PUC) |
| EIA | Energy Information Administration (US DOE) |
| EIPC | Eastern Interconnection Planning Collaborative |
| EISPC | Eastern Interconnection States Planning Council |
| ELG | Effluent Limit Guidelines (for Electric Steam Generation) (US EPA) |
| EOR | energy-only resource |
| EPA | Environmental Protection Agency (US) |
| EPRI | Electric Power Research Institute |
| ERO | Electric Reliability Organization |
| ERSTF | Essential Reliability Services Task Force (NERC) |
| ERSWG | Essential Reliability Services Working Group (NERC) |
| ESI | Energy-Storage Initiative (MA DOER) |
| ETU | elective transmission upgrade |
| F.3d | Federal Reporter, third series |
| FACTS | Flexible Alternating-Current Transmission System |
| FCA | Forward Capacity Auction |
| FCA #N | nth Forward Capacity Auction |
| FCM | Forward Capacity Market |
| Fed. Reg. | Federal Register |
| FERC | Federal Energy Regulatory Commission |
| FR | Federal Register |
| FRM | Forward Reserve Market |
| FTR | Financial Transmission Right |
| FWS | US Fish and Wildlife Service (US Department of the Interior) |
| GHCC | Greater Hartford/Central Connecticut (part of NEEWS) |
| GHG | greenhouse gas |
| Greater Connecticut; Greater CT | 1) RSP study area that includes the RSP subareas of NOR, SWCT, and CT 2) capacity zone 3) reserve zone |
| Greater Southwest Connecticut; Greater Southwest CT; Greater SWCT | 1) RSP study area that includes the southwestern and western portions of Connecticut and comprises the SWCT and NOR subareas 2) reserve zone |
| GRI | Greater Rhode Island |
| GSGT | Granite State Gas Transmission |
| GSP | gross state product |
| GSRP | Greater Springfield Reliability Project |
| GT | gas turbine |
| GW | gigawatt |
| GWh | gigawatt-hour(s) |
| GWSA | Global Warming Solutions Act (MA) |
| HQ | Hydro-Québec Balancing Authority Area |
| HQICC | Hydro-Québec Installed Capability Credit |
| (the) Hub | ISO New England energy trading hub |
| HV | high voltage |
| HVDC | high voltage, direct current |
| hydro | hydroelectricity |
| ICE | Intercontinental Exchange, Inc. |
| ICF | ICF International, Inc. |
| ICR | Installed Capacity Requirement |
| IEEE | Institute of Electrical and Electronics Engineers |
| IGTS | Iroquois Gas Transmission System |
| IMAPP | intergrating markets and public policy |
| INGAA | Interstate Natural Gas Association of America |
| IPM | Integrated Performance Model (RGGI) |
| IPSAC | Inter-Area Planning Stakeholder Advisory Committee |
| IRC | ISO/RTO Council |
| IRP | Interstate Reliability Project |
| ISO | Independent System Operator |
| (the) ISO | Independent System Operator of New England; ISO New England |
| ISO/RTO | Independent System Operator/Regional Transmission Organization |
| ISO tariff | ISO New England’s Transmission, Markets, and Services Tariff |
| JIPC | Joint ISO/RTO Planning Committee |
| ktons | kilotons |
| kV | kilovolt(s) |
| kW | kilowatt |
| kWh | kilowatt-hour |
| lb | pound |
| LDC | local distribution company |
| LLC | limited liability company |
| LMP | locational marginal price |
| LNG | liquefied natural gas |
| LOLE | loss-of-load expectation |
| Lower SEMA | Lower Southeast Massachusetts active-demand-resource dispatch zone |
| LSE | load-serving entity |
| LSP | Local System Plan |
| LSR | local sourcing requirement |
| LTRA | Long-Term Reliability Assessment (NERC) |
| M&N | Maritimes and Northeast Pipeline |
| MA | Massachusetts |
| MACT | maximum achievable control technology |
| MA DEP | Massachusetts Department of Environmental Protection |
| MA DPU | Massachusetts Department of Public Utilities |
| Maine | active-demand-resource dispatch zone |
| MATS | Mercury and Air Toxics Standard (US EPA) |
| Mcf | 1,000 cubic feet |
| MCL | maximum capacity limit |
| MDth/d | thousand dekatherms per day |
| ME | 1) State of Maine 2) RSP subarea that includes western and central Maine and Saco Valley, New Hampshire 3) Maine load zone 4) Maine capacity zone, including the area north of the ME-NH interface and comprising the RSP bubbles for BHE, ME, and SME 5) Maine active-demand-resource dispatch zone |
| ME PUC | Maine Public Utilities Commission |
| METU | market efficiency transmission upgrade |
| MGD | millions gallons per day |
| MMBtu | million British thermal units |
| MPRP | Maine Power Reliability Program |
| MRI | marginal-reliability-impact |
| MTF | merchant transmission facility |
| mtons | million tons |
| MVAR | megavolt-ampere reactive |
| MW | megawatt(s) |
| MWAC | the megawatts converted from the direct-current electricity produced by the photovoltaic panels to alternative current, which typically is supplied to utility customers |
| MWDC | the megawatts generated by photovoltaic panels, which produce direct-current electricity |
| MWe | electrical megawatts (of nuclear power plants) |
| MWh | megawatt-hour(s) |
| N-1 | first-contingency loss |
| N-1-1 | second-contingency loss |
| N/A | not applicable |
| NAESB | North American Energy Standards Board |
| NARUC | National Association of Regulatory Utility Commissioners |
| NB | 1) Province of New Brunswick 2) New Brunswick (Maritimes) balancing authority area |
| NCEP | National Council for Electricity Policy |
| NCPC | Net Commitment-Period Compensation |
| NCSPXY | Northeast Coordinated System Plan 20XY |
| n.d. | no date |
| NECPUC | New England Conference of Public Utilities Commissioners |
| NED | Northeast Energy Direct project |
| NEEWS | New England East–West Solution |
| NEL | net energy for load |
| NEMA | 1) RSP subarea for northeast Massachusetts 2) Northeast Massachusetts load zone |
| NEMA/Boston | 1) combined load zone that includes northeast Massachusetts and the Boston area 2) capacity zone, including the area within the Boston import interface and comprising the RSP bubble for BOSTON 3) reserve zone |
| NEPOOL | New England Power Pool |
| NERC | North American Electric Reliability Corporation |
| NESCOE | New England States Committee on Electricity |
| New Hampshire | active-demand-resource dispatch zone |
| NH | 1) State of New Hampshire 2) RSP subarea comprising northern, eastern, and central New Hampshire; eastern Vermont; and southwestern Maine 3) New Hampshire load zone 4) New Hampshire active-demand-resource dispatch zone |
| NH PUC | New Hampshire Public Utilities Commission |
| NICR | net Installed Capacity Requirement |
| NMISA | Northern Maine Independent System Administrator, Inc. |
| NNE | 1) northern New England 2) export-constrained capacity zone, which includes the area north of the North–South interface and comprises the RSP bubbles for BHE, ME, SME, NH, and VT |
| No. | number |
| NOR | RSP subarea that includes Norwalk and Stamford, Connecticut |
| Northern CT | Northern Connecticut active-demand-resource dispatch zone |
| Northshore | active-demand-resource dispatch zone |
| Northwest Vermont | active-demand-resource dispatch zone |
| Norwalk-Stamford | active-demand-resource dispatch zone |
| NOX | nitrogen oxide(s) |
| NPCC | Northeast Power Coordinating Council, Inc. |
| NRC | Nuclear Regulatory Commission (US) |
| NREL | National Renewable Energy Laboratory (US DOE) |
| NRIS | Network Resource Interconnection Service |
| NY | 1) State of New York 2) New York Balancing Authority Area |
| NYISO | New York Independent System Operator |
| NYPA | New York Power Authority |
| O3 | ozone |
| OATT | Open Access Transmission Tariff |
| OP 4 | ISO Operating Procedure No. 4, Action during a Capacity Deficiency |
| OP 7 | ISO Operating Procedure No. 7, Action in an Emergency |
| OP 8 | ISO Operating Procedure No. 8, Operating Reserve and Regulation |
| OP 14 | ISO Operating Procedure No. 14, Technical Requirements for Generators, Demand Resources, Asset-Related Demands, and Alternative Technology Regulation Resources |
| OP 19 | ISO Operating Procedure No. 19, Transmission Operations |
| PAC | Planning Advisory Committee |
| PDR | passive demand resource |
| PFR | primary frequency response |
| PG | Pittsfield–Greenfield |
| PJM | PJM Interconnection LLC; the RTO for all or parts of Delaware, Illinois, Indiana, Kentucky, Maryland, Michigan, New Jersey, North Carolina, Ohio, Pennsylvania, Tennessee, Virginia, and the District of Columbia |
| PM | particulate matter |
| PM2.5 | fine particulate matter |
| PMU | phasor measurement unit |
| PNGTS | Portland Natural Gas Transmission System |
| pnode | pricing node |
| Portland, ME | Portland, Maine, active-demand-resource dispatch zone |
| PP 3 | ISO Planning Procedure No. 10, Reliability Standards for the New England Area Pool Transmission Facilities |
| PP 10 | ISO Planning Procedure No. 10, Planning Procedure to Support the Forward Capacity Market |
| PPA | Proposed Plan Application |
| PPTU | public policy transmission upgrade |
| PSERC | Power System Engineering Research Center (US DOE) |
| PSNH | Public Service of New Hampshire |
| PTF | pool transmission facility |
| PTO | participating transmission owner |
| PTO-AC | Participating Transmission Owner-Administrative Committee |
| PUC | Public Utilities Commission (ME, NH, RI, VT) |
| PURA | Public Utilities Regulatory Authority (CT) |
| PV | photovoltaic |
| QP | queue project |
| QTPS | qualified transmission project sponsor |
| queue (the) | ISO Interconnection Request Queue |
| RC | Reliability Committee |
| REO | Regional Energy Outlook |
| RES | Renewable Energy Standard (RI, VT) |
| RFP | request for proposals |
| RGGI | Regional Greenhouse Gas Initiative |
| RI | 1) State of Rhode Island 2) RSP subarea that includes the part of Rhode Island bordering Massachusetts 3) Rhode Island load zone 4) Rhode Island active-demand-resource dispatch zone |
| RIRP | Rhode Island Reliability Project |
| RNS | Regional Network Service |
| ROFR | right of first refusal |
| ROP | Rest-of-Pool capacity zone |
| ROS | Rest-of-System reserve zone, which excludes the other, local reserve zones |
| RPS | Renewable Portfolio Standard |
| RSP | Regional System Plan |
| RSPXY | 20XY Regional System Plan |
| RTDR | real-time demand response |
| RTEG | real-time emergency generation |
| RTO | Regional Transmission Organization |
| RTU | reliability transmission upgrade |
| SB | Senate Bill |
| SBC | systems benefits charge |
| SCC | seasonal claimed capability |
| Seacoast | active-demand-resource dispatch zone |
| SEMA | 1) RSP subarea comprising southeastern Massachusetts and Newport, Rhode Island 2) Southeastern Massachusetts load zone 3) active-demand-resource dispatch zone |
| SEMA/RI | Southeastern Massachusetts/Rhode Island capacity zone, the area within the SEMA/RI import interface, comprising the RSP “bubbles” for SEMA and RI |
| SENE | Southeastern New England import-constrained capacity zone, which includes the area within the Southeast New England interface, comprising the RSP ‘bubbles” for SEMA, RI, and BOSTON |
| SMD | Standard Market Design |
| SME | RSP subarea for southeastern Maine |
| SO2 | sulfur dioxide |
| SOEP | Sable Offshore Energy Project |
| SOR | settlement-only resource |
| SP-15 | CAISO zone covering southern California |
| SPI | Strategic Planning Initiative |
| Springfield, MA | Springfield, Massachusetts, active-demand-resource dispatch zone |
| SSCC | summer seasonal claimed capability |
| STATCOM | static synchronous compensator |
| SVC | static voltage ampere reactive (VAR; V) compensator |
| SWCT | RSP subarea for southwestern Connecticut |
| TBD | to be determined |
| TC | Transmission Committee |
| tcf | trillion cubic feet |
| Technical Guide | ISO New England’s Transmission Planning Technical Guide |
| TGP | Tennessee Gas Pipeline |
| TOPAC | Transmission Owner Planning Advisory Committee |
| TOUT | through-or-out service |
| TQM | Trans-Québec and Maritimes Pipeline |
| ULSD | ultra-low-sulfur diesel |
| US | United States |
| USA | United States of America |
| USC | United States Code |
| USGS | US Geological Survey |
| VAR | voltage-ampere reactive |
| VELCO | Vermont Electric Power Company |
| VER | variable energy resource |
| Vermont | active-demand-resource dispatch zone |
| VSC | voltage source converter |
| VT | 1) State of Vermont 2) RSP subarea that includes Vermont and southwestern New Hampshire 3) Vermont load zone 4) Vermont active-demand-resource dispatch zone |
| VT DPS | Vemont Department of Public Service |
| VTWAC | Vermont Weather Analytics Center |
| WCMA | Western/Central Massachusetts load zone |
| Western CT | Western Connecticut active-demand-resource dispatch zone |
| Western MA | Western Massachusetts active-demand-resource dispatch zone |
| WMA | RSP subarea for western Massachusetts |
| WMECO | Western Massachusetts Electric Company |
| WMPP | Wholesale Markets Project Plan |
| XLS | Microsoft Excel file |
| yr | year |

The ISO considers a hybrid grid to be a power system where large generators and other power resources connected to the regional transmission system meet electricity needs, in combination with thousands of small resources connected “behind the meter” (BTM) directly to retail customer sites or local distribution utilities. This type of grid must include fast, flexible power plants ready to balance the variable output of energy from wind and solar resources, which in New England will likely be natural-gas-fired generators in the near term because of their ability to turn on and off quickly.

State sponsorships of resources reflect policies supporting renewable resources and long-term contracts not available to other types of resources. See the ISO’s “New England’s Capacity Markets and a Renewable Energy Future,” discussion paper (June 3, 2015), https://www.iso-ne.com/static-assets/documents/2015/06/iso_ne_capacity_mkt_discussion_paper_06_03_2015.pdf.

ISO New England, “Competitive Auctions with Subsidized Policy Resources,” discussion paper (April 2017), https://www.iso-ne.com/static-assets/documents/2017/04/caspr_discussion_paper_april_14_2017.pdf. Note that the resources had initially been described as “subsidized” and not “sponsored.”

Asynchronous resources include inverter-based technologies, such as photovoltaics, wind, battery storage, and imports over high-voltage direct-current (HVDC) facilities.

The actual load has been near or above the 50/50 forecast 11 times during the last 25 years because of weather conditions; six of these 11 times, the load has been near or has exceeded the 90/10 forecast.

The mix of capacity resources could change. Updates are included in the ISO’s monthly chief operating officer (COO) report to the NEPOOL Participants Committee; http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/prtcpnts/mtrls/index.html.

ISO New England, Planning Procedure No. 3, Reliability Standards for the New England Area Pool Transmission Facilities (February 10, 2017), https://www.iso-ne.com/static-assets/documents/2017/02/pp3_rev7.pdf.

ISO New England, Transmission Planning Technical Guide (March 24, 2017), https://www.iso-ne.com/static-assets/documents/2017/03/planning_technical_guide_3_24_2017.pdf. Additional information about NPCC is available at https://www.npcc.org/default.aspx.

FERC, “Order No. 1000—Transmission Planning and Cost Allocation,” website (October 26, 2016), https://www.ferc.gov/industries/electric/indus-act/trans-plan.asp.

ISO New England, Transmission Planning Process Guide (April 6, 2017), https://www.iso-ne.com/static-assets/documents/2017/04/transmission_planning_process_guide_4_6_2017.pdf.

NCPC is a make-whole (i.e., uplift) payment to a supply resource that responded to the ISO’s dispatch instructions but did not fully recover its start-up and operating costs in either the Day-Ahead or Real-Time Energy Markets.

ISO New England, 2015 Regional System Plan (November 5, 2015), https://www.iso-ne.com/static-assets/documents/2015/11/rsp15_final_110515.docx.

The Northeastern ISO/RTO Planning Coordination Protocol (2012) is available at https://www.iso-ne.com/static-assets/documents/committees/comm_wkgrps/othr/ipsac/rto_plan_prot/planning_protocol.pdf.

PJM is the RTO for all or parts of Delaware, Illinois, Indiana, Kentucky, Maryland, Michigan, New Jersey, North Carolina, Ohio, Pennsylvania, Tennessee, Virginia, West Virginia, and the District of Columbia.

The percentages reflect the mix of native generation resources in the region. During 2016, net energy imports (i.e., gross imports minus gross exports) equaled 20,769 GWh, which represents 17% of the 2016 system net energy for load of 124,372 GWh. See New England 2017 Regional System Plan (RSP17) Load, Energy and Capacity Resource Overview (April 2017), https://www.iso-ne.com/static-assets/documents/2017/05/rsp17_load_energy_capacity_resource_overview.pdf.

As of February 2017, Spectra Energy became Enbridge.

“ISO New England Study on Regional Fuel Security is Underway,” public statement (May 2017), https://www.iso-ne.com/static-assets/documents/2017/05/20170522_fuel_security_study_update_final.pdf.

EPA, National Ambient Air Quality Standards for Ozone, final rule, 80 FR 65292 (October 26, 2015), http://www.gpo.gov/fdsys/pkg/FR-2015-10-26/pdf/2015-26594.pdf; and Fine Particulate Matter National Ambient Air Quality Standards: State Implementation Plan Requirements, final rule, 81 FR 58010 (August 24, 2016).

EPA, National Emissions Standards for Hazardous Air Pollutants From Coal- and Oil-Fired Electric Utility Steam Generating Units and Standards of Performance for Fossil-Fuel-Fired Electric Utility, Industrial-Commercial-Institutional, and Small Industrial-Commercial-Institutional Steam Generating Units, final rule, 77 FR 9304 (February 16, 2012), https://www.federalregister.gov/d/2012-806.

EPA, Carbon Pollution Emission Guidelines for Existing Stationary Sources: Electric Utility Generating Units, final rule, 80 FR 64662 (October 23, 2015), https://www.federalregister.gov/d/2015-22842; and Standards of Performance for Greenhouse Gas Emissions From New, Modified, and Reconstructed Stationary Sources: Electric Utility Generating Units, final rule, 80 FR 64509 (October 23, 2015), https://www.federalregister.gov/d/2015-22837. More information about the Regional Greenhouse Gas Initiative CO2 budget trading programs of Connecticut, Delaware, Maine, Maryland, Massachusetts, New Hampshire, New York, Rhode Island, and Vermont is available at http://www.rggi.org/. An Act Establishing the Global Warming Solutions Act (Chapter 298 of the Massachusetts Acts of 2008; S.2540) (August 7, 2008), http://www.mass.gov/legis/laws/seslaw08/sl080298.htm.

State of Massachusetts, Adopt new 310 CMR 7.74: Reducing CO2 Emissions from Electricity Generating Facilities, final regulation, (August 11, 2017), http://www.mass.gov/eea/docs/dep/air/climate/3dregf-electricity.pdf and http://www.mass.gov/eea/agencies/massdep/air/climate/section3d-comments.html.

ISO New England, Comments on the Massachusetts Department of Environmental Protection’s proposed regulations on the Global Warming Solutions Act (February 20, 2017), https://www.iso-ne.com/static-assets/documents/2017/02/iso_dep_comments_022017.pdf.

The Mount Tom and Salem Harbor unit #3 retirements, mild weather, and the relatively inexpensive price of natural gas reduced the energy production by coal units.

An abstract of 1547-2003—IEEE Standard for Interconnecting Distributed Resources with Electric Power Systems is available at http://ieeexplore.ieee.org/document/1225051/?reload=true (2017).

ISO New England, Strategic Transmission Analysis: Wind Integration Study (December 18, 2013), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2013/dec182013/a4_wind_study.pdf.

ISO New England, 2015 Economic Study— Evaluation of Increasing the Keene Road Export Limit (September 2, 2016), https://www.iso-ne.com/static-assets/documents/2016/09/2015_economic_study_keene_road_increased_export_limits_fina.docx; 2015 Economic Study—Evaluation of Offshore Wind Deployment (September 2, 2016), https://www.iso-ne.com/static-assets/documents/2016/09/2015_economic_study_offshore_wind_development_final.docx; 2015 Economic Study— Strategic Transmission Analysis—Onshore Wind Integration (September 2, 2016), https://www.iso-ne.com/static-assets/documents/2016/09/2015_economic_study_onshore_wind_integration_final.docx.

Draft 2016 Economic Study: NEPOOL Scenario Analysis (July 24, 2017,  https://www.iso-ne.com/static-assets/documents/2017/07/draft_2016_phase1_nepool_scenario_analysis_report.docx.

Likewise, the markets and market changes may help meet future system needs by providing incentives for the development of new resources. Market changes are subject to a different stakeholder process and are described in the ISO’s Annual Markets Report (AMR) (accessible at http://www.iso-ne.com/markets-operations/market-monitoring-mitigation/internal-monitor) and Wholesale Markets Project Plan (WMPP) (http://www.iso-ne.com/markets-operations/markets-development/wholesale-markets-project-plan).

ISO New England Inc. Transmission, Markets, and Services Tariff (ISO tariff) (2017), http://www.iso-ne.com/regulatory/tariff/index.html, including Section II. ISO New England Open Access Transmission Tariff, https://www.iso-ne.com/participate/rules-procedures/tariff/oatt.

Demand response occurs through resources that can reduce the demand of end-use customers. Demand-response resources may offer demand reductions into the ISO’s energy markets, and some may participate in the ISO’s capacity markets. Some capacity “active” demand resources (ADRs) offer to reduce load quickly in response to price signals in the ISO’s markets. Other capacity “passive” demand resources (PDRs) are nondispatchable and may reduce the total amount of electrical energy consumed during peak times or seasons through installed measures (e.g., products, equipment, systems, services, practices, or strategies) on end-use-customer facilities (e.g., energy efficiency, load management, and distributed generation). Some “behind-the meter” (on-site) distributed generation (DG) is located with net metering (see more on DG below). Net metering allows power customers who generate their own electricity, such as from wind or solar power, to feed their unused electricity back into the grid.

A merchant transmission facility is an independently developed and funded facility subject to the operational control of the ISO, pursuant to an operating agreement specific to each facility.

See the OATT, Section II.B, Attachment N, “Procedures for Regional System Plan Upgrades,”
http://www.iso-ne.com/static-assets/documents/regulatory/tariff/sect_2/oatt/sect_ii.pdf.

FERC, ISO New England Inc. Order on Compliance Filings (May 17, 2013), https://www.iso-ne.com/static-assets/documents/regulatory/ferc/orders/2013/may/er13_193_er13_196_5_17_13_order_on_order_1000_compliance_filings.pdf. Also see “Order No. 1000—Transmission Planning and Cost Allocation,” FERC webpage (2016), http://www.ferc.gov/industries/electric/indus-act/trans-plan.asp.

The Network-Capability Interconnection Standard is an energy-only standard that includes the minimum criteria required to permit a generator to connect to the transmission system so that it has no adverse impacts on the reliability, stability, or operation of the system, including the degradation of transfer capability for interfaces affected by the generating facility. The Capacity-Capability Interconnection Standard is a capacity and energy standard that includes the same criteria as the Network-Capability Interconnection Standard but also includes criteria to ensure intrazonal deliverability by avoiding the redispatch of other capacity network resources. The OATT, Section 22, defines the standards; http://www.iso-ne.com/static-assets/documents/regulatory/tariff/sect_2/sch22/sch_22_lgip.pdf. Also see Schedule 23 for small generator interconnections and applications for new interconnections; https://www.iso-ne.com/static-assets/documents/regulatory/tariff/sect_2/sch23/sch_23_sgip.pdf.

Pool transmission facilities are the facilities rated 69 kilovolts (kV) or above owned by the participating transmission owners, over which the ISO has operating authority in accordance with the terms set forth in the Transmission Operating Agreements. Refer to the OATT, Section II.49, 109, for additional specifications, http://www.iso-ne.com/static-assets/documents/regulatory/tariff/sect_2/oatt/sect_ii.pdf. See Schedule 25 of the OATT for additional information on ETUs.

The filing for the addition or modification to the transmission upgrade must be in accordance with the OATT, Section II.47.2, on a date after the RSP Project List (as of the date of that application) already has documented the addition or modification, other than as an elective transmission upgrade. (See Section 2.1.6 for more on the RSP Project List.)

An internal ETU is a transmission facility with interconnection points located solely within the New England Control Area; it would receive a right to interconnect to the system subject to meeting all the requirements specified in an Interconnection Agreement (e.g., completing the upgrades required to accommodate the requested interconnection). An external ETU is a transmission facility that will interconnect the New England Control Area with another control area. External ETUs can receive Capacity Network Resource Interconnection Service (CNRIS) for capacity or Network Resource Interconnection Service (NRIS) for energy if they complete all the required milestones. For more information, refer to Elective Transmission Upgrade Project, Reliability Committee presentation (October 21, 2014), https://www.iso-ne.com/static-assets/documents/2014/10/a7_etu_conforming_changes_rev1.pdf.

The ISO’s  Interconnection Request Queue lists the status of requests for the interconnection of new or uprated (i.e., increased capacity) generating facilities to the ISO New England-administered transmission system; see Section 4.5.4. It also includes elective transmission upgrades and transmission service requests.

OATT, Attachment K, http://www.iso-ne.com/static-assets/documents/regulatory/tariff/sect_2/oatt/sect_ii.pdf.

Transmission Planning Process Guide (April 6, 2017), http://www.iso-ne.com/system-planning/transmission-planning/transmission-planning-guides.

Any entity that intends to submit a proposal in response to an ISO-identified need for a reliability transmission upgrade, market-efficiency transmission upgrade, public policy transmission upgrade, or a backstop transmission solution must first be recognized by the ISO as a qualified transmission project sponsor, in accordance with the OATT, Attachment K, Section 4B.

Transmission Planning Technical Guide, (March 24, 2017), http://www.iso-ne.com/system-planning/transmission-planning/transmission-planning-guides.

A critical load level is the load level at which a system problem could occur and therefore a solution would be needed. Refer to the OATT, Attachment K, Section 4.1 and 4.2 for complete definitions for needs assessments and solutions studies; https://www.iso-ne.com/static-assets/documents/regulatory/tariff/sect_2/oatt/sect_ii.pdf.

The Eastern Interconnection is one of two major AC power grids in North America spanning from central Canada eastward to the Atlantic coast (excluding Québec), south to Florida, and west to the foot of the Rocky Mountains (excluding most of Texas—the portion in the Electric Reliability Corporation of Texas) that, during normal system conditions, interconnects transmission and distribution infrastructure and operates at a synchronized frequency of 60 Hz average. The Eastern Interconnection is tied to the Western Interconnection, the Texas Interconnection, and the Quebec Interconnection generally through numerous HVDC transmission lines.

A distributed generation resource is generation provided by a relatively small, on-site installation directly connected to a distribution facility or retail customer facility to serve load at the point of consumption rather than the regional power system (i.e., it is behind the meter). Distributed energy resources are sources and aggregated sources of electric power not directly connected to a bulk power system. DERs include generators and energy-storage technologies capable of exporting active power to an electric power system. A distributed generator is a type of distributed energy resource.

Any stakeholder can designate a representative to the PAC by providing written notice to the ISO. PAC materials (2007–2017) are available at http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/index.html. PAC agendas; minutes; materials; draft reports, including stakeholder questions and ISO responses; and final reports are posted on the ISO website.

NEPOOL members serve as ISO stakeholders and market participants. More information on NEPOOL participants is available at http://www.iso-ne.com/participate/governing-agreements/nepool-agreement.

A Transmission Operating Agreement is an agreement between a Regional Transmission Operator and a transmission-providing utility whereby the RTO pays the utility for its transmission system costs in exchange for control of the transmission.

Market Rule 1 (ISO tariff, Section III) (2017), http://www.iso-ne.com/regulatory/tariff/sect_3/index.html.

The current list is available at http://www.iso-ne.com/system-planning/system-plans-studies/rsp (filters: Regional System Plan document type; XLS file type).

Recent and archived RSP materials are available at http://www.iso-ne.com/trans/rsp/index.html. The latest and archived editions of the REO, AMR, and WMPP are available at https://www.iso-ne.com/about/regional-electricity-outlook, http://www.iso-ne.com/markets/mkt_anlys_rpts/annl_mkt_rpts/, and http://www.iso-ne.com/markets-operations/markets-development/wholesale-markets-project-plan. The needs assessments and solutions studies presented to the PAC and posted on the ISO website can be obtained by contacting ISO Customer Service at 413-540-4220.

Stakeholders also can obtain publicly available models of the transmission system network through the FERC 715 process, which requires transmitting utilities that operate facilities rated at or above 100 kV to submit information to FERC annually; see http://www.ferc.gov/docs-filing/forms/form-715/overview.asp. ISO New England Information Policy (ISO tariff, Attachment D) (2014) contains the requirements for controlling the disclosure of CEII and confidential information; see http://www.iso-ne.com/static-assets/documents/regulatory/tariff/attach_d/attachment_d.pdf.

ISO New England, “Rules and Procedures” webpage, http://www.iso-ne.com/participate/rules-procedures. FERC, Preventing Undue Discrimination and Preference in Transmission Service, 18 CFR Parts 35 and 37, Order No. 890 (February 16, 2007), http://www.ferc.gov/whats-new/comm-meet/2007/021507/E-1.pdf. NERC Reliability Standards (2016), http://www.nerc.com/pa/Stand/Pages/ReliabilityStandards.aspx. NPCC Regional Standards (2017), https://www.npcc.org/Standards/default.aspx.

“Transmission Operating Agreements” webpage, http://www.iso-ne.com/regulatory/toa/index.html.

The ISO is not responsible for portions of northern and eastern Maine. The Northern Maine Independent System Administrator, Inc. (NMISA) is a nonprofit entity responsible for the administration of the northern Maine transmission system and electric power markets in Aroostook and Washington counties. The 2017 peak load forecast for NMISA is approximately 136 MW. NMISA, Seven-Year Outlook: An Assessment of the Adequacy of Generation and Transmission Facilities on the Northern Maine Transmission System (April 2017), p. 3, http://nmisa.com/docs/041917-Final-2017-Seven-Year-Outlook.pdf.

Real power or active power is the rate at which energy is expended to do work, measured in kilowatts or magawatts. Reactive power supports the magnetic and electric fields necessary to operate power system equipment in an alternating current power system. It is measured in volt-ampere reactive (VAR) and megavolt-ampere reactive (MVAR) units.

For more information on New England wholesale electricity markets, see the ISO’s 2016 Annual Markets Report (AMR16) (May 30, 2017), https://www.iso-ne.com/static-assets/documents/2017/05/annual_markets_report_2016.pdf.

Installed capacity is the megawatt capability of a generating unit, dispatchable load, external resource or transaction, or demand resource that qualifies as a participant in the ISO’s Forward Capacity Market according to the market rules. Additional information is available at http://www.iso-ne.com/markets-operations/markets/forward-capacity-market.

Regulation is the capability of specially equipped generators to increase or decrease their generation output every four seconds in response to signals they receive from the ISO to control slight changes on the system.

According to NERC, NPCC, and ISO criteria, a contingency is the sudden loss of a generation or transmission resource. A system’s first contingency (N−1) is when the power element (facility) with the largest impact on system reliability is lost. A second contingency (N−1−1) takes place after a first contingency has occurred and is the loss of the facility that, at that time, has the largest impact on the system. A forced outage is a type of unplanned outage or unexpected removal from service of a generating unit, transmission facility, or other facility or portion of a facility because of an emergency failure or the discovery of a problem that needs to be repaired as soon as crews, equipment, or corrective dispatch actions can perform the work.

Fast-start resources can be electrically synchronized to the system quickly and reach claimed capability (i.e., a generator’s maximum production or output) within 10 to 30 minutes to respond to a contingency and serve demand.

See the ISO’s Wholesale Markets Project Plans at https://www.iso-ne.com/markets-operations/markets-development/wholesale-markets-project-plan.

The ISO tariff allows loads that meet specified requirements to request and receive nodal pricing.

See Market Rule 1, Section III.2.7, of the ISO tariff, http://www.iso-ne.com/participate/rules-procedures/tariff/market-rule-1.

RTDRs are demand resources that must curtail electrical usage within 30 minutes of receiving a dispatch instruction from the ISO. Real-time emergency generation is distributed generation the ISO calls on to operate during certain voltage-reduction or more severe actions but must limit its operation to 600 MW to comply with the generation’s federal, state, or local air quality permit(s), as well as the ISO’s market rules. RTEG operations result in curtailing load on the grid, as the distributed energy provided by the emergency generator begins serving demand. RTDRs will become demand-response capacity resources and active demand capacity resources after June 1, 2018, at which point RTEGs will no longer be eligible (see Section 10.3.3.1).

The ISO’s Capacity, Energy, Load, and Transmission (CELT) Reports and associated documentation contain more details on the short-run and long-run forecast methodologies, models, and inputs; weather normalization; regional, state, subarea, and load-zone forecasts of annual electric energy use and peak loads; high- and low-forecast bandwidths; and retail electricity prices. They are available at the “CELT Reports,” webpage, https://www.iso-ne.com/system-planning/system-plans-studies/celt. Also see the 2017 CELT Report at the same link and the ISO NE Seasonal Peaks since 1980 (April 25, 2017), which can be accessed at https://www.iso-ne.com/static-assets/documents/2014/10/seasonal_peak_data_summary.xls.

Compared with distributed PV, non-PV distributed generation has been growing much more modestly and somewhat consistently with its historical growth trend. August 2016 Distributed Generation Survey Results, Distributed Generation Forecast Working Group (DGFWG) presentation (December 16, 2016), https://www.iso-ne.com/static-assets/documents/2016/12/august2016_dgsurveyresults_20161216.pdf.

Draft 2017 CELT ISO-NE Annual Energy and Summer Peak Forecast, PAC presentation (March 22, 2017), https://www.iso-ne.com/static-assets/documents/2017/03/a2_new_england_energy_efficiency_pv_and_load_forecast_update.pdf.

The 50/50 “reference” case peak loads have a 50% chance of being exceeded because of weather conditions. For the reference case, the summer peak load is expected to occur at a weighted New England-wide temperature of 90.2°F, and the winter peak load is expected to occur at 7.0°F. The 90/10 “extreme” case peak loads have a 10% chance of being exceeded because of weather. For the extreme case, the summer peak is expected to occur at a temperature of 94.2°F, and the winter peak is expected to occur at a temperature of 1.6°F.

Preliminary ISO-NE Annual Energy and Seasonal Peak Forecast 2015-2024, PAC presentation (February 18, 2015), http://www.iso-ne.com/static-assets/documents/2015/02/a5_new_england_load_forecast_update.pdf (Preliminary Forecast 2015–2024).

The generation output includes output from settlement-only resources (SORs), which are less than 5 MW but not centrally dispatched by the ISO control room and not monitored in real time. NEL = Total ISO generator energy production + imports – exports – pumped storage load.

The compound annual growth rate (CAGR) is calculated as follows:

OP 4 actions implemented during a capacity deficiency include the dispatch of active demand resources. Operating Procedure No. 4, Action during a Capacity Deficiency (August 12, 2014), http://www.iso-ne.com/static-assets/documents/rules_proceds/operating/isone/op4/op4_rto_final.pdf.

Weather conditions during the actual peak summer loads were slightly below the expected 90/10 weather conditions for 1994, 1999, 2001, and 2002, and weather conditions were slightly above the expected 90/10 weather during the 2006, 2011, and 2013 peaks. A spreadsheet containing historical annual peak loads and associated weather conditions since 1980 is available at http://www.iso-ne.com/isoexpress/web/reports/load-and-demand/-/tree/net-ener-peak-load.

A capacity supply obligation is a requirement for a resource to provide capacity to meet NPCC’s and the ISO’s bulk power system reliability planning criteria. A CSO is acquired through a Forward Capacity Auction, a reconfiguration auction, or a CSO bilateral contract through which a market participant may transfer all or part of its CSO to another entity (see Section 4.1). FCM reconfiguration auctions take place before and during the capacity commitment period to allow participants to buy and sell capacity obligations and adjust their positions.

State-sponsored EE programs consist of various efforts designed to reduce energy consumption. These efforts generally are funded by multiple sources, including a system benefits charge (SBC) that electricity providers apply to customer bills, the Regional Greenhouse Gas Initiative (RGGI) auction revenues (see Section 8.1.2.5), and state EE policy funds. More information on the methodology used to develop the EE forecast is available at the ISO’s “Energy-Efficiency Forecast Working Group,” webpage, http://www.iso-ne.com/committees/planning/energy-efficiency-forecast. ISO New England Energy-Efficiency Forecast for 2021–2026 (May 1, 2017), https://www.iso-ne.com/static-assets/documents/2017/05/final_eef_2017_v2.pdf.

The DGFWG, chaired by a representative of the ISO, is not a formal NEPOOL committee or subcommittee. More information on the DGFWG, including the group’s scope of work (September 25, 2013) is available at http://www.iso-ne.com/static-assets/documents/committees/comm_wkgrps/othr/distributed_generation_frcst/2013mtrls/sep302013/draft_dgfwg_scope_of_work.pdf.

Existing and future DG with obligations in the FCM are considered resources and contribute to meeting New England’s ICR. Load reductions from the remainder of existing DG (i.e., installations that do not participate in the wholesale markets) are embedded in the historical loads used to develop the ISO’s 10-year load forecast. Compared with distributed PV, non-PV distributed generation has been growing much more modestly and similar to historical trends. More information is available in the August 2016 Distributed Generation Survey Results, Distributed Generation Forecast Working Group presentation (December 16, 2016), https://www.iso-ne.com/static-assets/documents/2016/12/august2016_dgsurveyresults_20161216.pdf.

A full explanation of the methodology used for the PV forecast is available at https://www.iso-ne.com/static-assets/documents/2017/05/2017_solar_forecast_details_final.pdf.

The forecast reflects distributed generation PV, which includes projects that are typically 5 MW or less in nameplate capacity; therefore, the forecast does not include policy drivers for larger-scale projects, which are generally accounted for as part of ISO’s interconnection process and participate in wholesale markets.

Settlement-only resources and non-FCM generators, as defined in Operating Procedure No. 14 (OP 14), Technical Requirements for Generators, Demand Resources, Asset-Related Demands, and Alternative Technology Regulation Resources, are included in this market type. Refer to OP 14 (January 17, 2017), at http://www.iso-ne.com/static-assets/documents/rules_proceds/operating/isone/op14/op14_rto_final.pdf.

ISO’s detailed analysis and resulting methodology is available as an appendix in “2016 Final PV Forecast,” available at https://www.iso-ne.com/static-assets/documents/2016/09/2016_solar_forecast_details_final.pdf.

Deterministic analyses are snapshots of assumed specific conditions that do not quantify the likelihood that these conditions will actually materialize. The results are based on analyzing the assumed set of conditions representing a specific scenario.

Established ICR values refer to the FERC-approved values. Representative net ICR values are the representative ICRs for the region, minus the tie-reliability benefits associated with the Hydro-Québec Interconnection Capability Credits (HQICCs). (As defined in the ISO’s tariff, the HQICC is a monthly value that reflects the annual installed capacity benefits of the HQ Interconnection, as determined by the ISO using a standard methodology on file with FERC.) The ISO calculates representative net ICR values solely to inform New England stakeholders; it does not file these values with FERC for approval. The values for FCA #12 for the 2021/2022 capacity commitment period are scheduled to be filed with FERC in November 2017. For additional information about ICRs, see the ISO’s “Installed Capacity Requirements,” webpage at http://www.iso-ne.com/system-planning/resource-planning/installed-capacity-requirements.

ISO New England, 2016–2025 Forecast Report of Capacity, Energy, Loads, and Transmission (May 2016), https://www.iso-ne.com/static-assets/documents/2016/05/2016_celt_report.xls.

Based on the representative net ICR values presented to the PAC in May 2017, https://www.iso-ne.com/static-assets/documents/2017/05/a6_representative_icr_values_2022_2026.pdf.

ISO New England, 2017–2026 Forecast Report of Capacity, Energy, Loads, and Transmission (May 2017), https://www.iso-ne.com/static-assets/documents/2017/05/2017_celt_report.xls.

ISO New England Inc. and New England Power Pool Participants Committee, 155 FERC ¶ 61,319 (2016). In its order, FERC accepted the new demand curve design as well as a transition mechanism for the systemwide capacity demand curve. The transition curve is a hybrid of the previous linear demand curve design and the new MRI-based design. While systemwide capacity demand curves were developed for FCA #9 and FCA #10, a linear methodology was used to develop the demand curves for these auctions.

Resulting reserves are the amount of capacity in excess of the forecast 50/50 peak load. Percentage resulting reserves = [{(Net ICR − 50/50 peak load) ÷ 50/50 peak load} × 100].

The LOLE analysis is a probabilistic analysis used to identify the amount of installed capacity (in MW) the system needs to meet the NPCC and ISO resource adequacy planning criterion to not disconnect firm load more than one day in 10 years.

LSRs and MCLs are based on network models using transmission facilities that will be in service no later than the first day of the relevant capacity commitment period.

The ICR requirements for 2017/2018 through the 2020/2021 are available in the FERC filings at http://www.iso-ne.com/regulatory/ferc/filings/2013/nov/er14-328-000_11-5-13__icr_2017-2018_.pdf, http://www.iso-ne.com/static-assets/documents/2014/11/er15-___-000_11-6-14_2018-2019_icr_filing.pdf, https://www.iso-ne.com/static-assets/documents/2015/11/icr_values_2019-2020_ccp.pdf, and https://www.iso-ne.com/static-assets/documents/2016/11/icr_filing_for_2020-2021_ccp.pdf.

A dual-fuel unit is a gas generator that can switch to burning oil. The three generators include Burrillville Energy Center (485 MW), Bridgeport Harbor 5 (484 MW), and Canal 3 (333 MW). Two of the three are in the former Southeast Massachusetts/Rhode Island capacity zone, where a capacity shortfall materialized in FCA #9 for the 2018/2019 capacity commitment period.

Due to changes in EPA rules, real-time emergency generators (RTEGs) have exited the FCM or have modified their facilities such that they can operate as real-time demand response (RTDR) or demand-response capacity resources  (DRCRs) after June 1, 2018, when a new price-responsive demand structure will go into effect in the New England wholesale electricity markets (see Section 10.3.3.1).

A delist bid is a submission in an FCA for an existing FCM resource indicating that the resource wants to opt of the auction before the deadline for qualifying its existing capacity and does not want a CSO below a certain price. The ISO reviews all delist bids for reliability impacts, and beginning with FCA #11, the way in which retirement requests were submitted changed. Specifically, a resource that wants to retire, in full or part, must submit a priced retirement delist bid quantifying its exit price, which in turn must be approved by the internal market monitor. Like a nonpriced retirement request, a priced retirement delist bid is irrevocable and subject to an ISO review for reliability impacts. Reliability determinations for retirement requests are available at http://www.iso-ne.com/system-planning/resource-planning/nonprice-retirement.

Planning Procedure No. 10, Planning Procedure to Support the Forward Capacity Market, (January 13, 2015), http://www.iso-ne.com/static-assets/documents/rules_proceds/isone_plan/pp10/pp10.pdf.

A static delist bid is submitted for a resource before an FCA—and that cannot be changed during the auction—requesting for the resource to opt out of receiving a CSO at a certain price and reflecting either the cost of the resource or a reduction in ratings as a result of ambient air conditions. A dynamic delist bid is submitted during the auction and indicates that a resource wants to opt out of receiving a CSO below a certain price.

Capacity retirements to date and future retirements include Salem Harbor Station (749 MW, retired 2011 and 2014); Norwalk Harbor Station (342 MW, retired 2013); Mount Tom Station (143 MW, retired 2014); Vermont Yankee (604 MW, retired 2014); Brayton Point Station (1,535 MW, retired 2017); Pilgrim Nuclear Power Station (677 MW, to be retired in 2019); approximately 190 MW of smaller generating resources; and approximately 1,100 MW of active demand-response resources. Bridgeport Harbor Unit 3 (383 MW) has announced its retirement effective FCA #12 (2021). Other FCA #12 retirements will be known by November 2017.

The delisting includes retirement, permanent, static, and dynamic delist bids. A permanent delist bid prohibits a resource from participating in any future FCA or assuming any CSO unless it qualifies for and clears as a new resource in a subsequent FCA.

Forward Capacity Auction 12 Transmission Transfer Capabilities & Capacity Zone Development PAC presentation (March 22, 2017), https://smd.iso-ne.com/operations-services/ceii/pac/2017/03/a8_fca_12_zonal_boundary_determination.pdf.

Forward Capacity Auction #12 Transmission Transfer Capabilities and Capacity Zone Development, PAC presentation (March 22, 2017), https://smd.iso-ne.com/operations-services/ceii/pac/2017/03/a8_fca_12_zonal_boundary_determination.pdf and Zonal Modeling for FCA #12, Power Supply Planning Committee Meeting (May 18, 2017), https://www.iso-ne.com/static-assets/documents/2017/05/a5-fca-12-zone-formation-pspc.pdf .

Tie benefits are an example of capacity relief obtainable from implementation of OP 4.

Operating Procedure No. 4, Action during a Capacity Deficiency (May 11, 2017), and Operating Procedure No. 7, Action in an Emergency (May 11, 2017), http://www.iso-ne.com/participate/rules-procedures/operating-procedures.

ISO Operating Procedure No. 8, Operating Reserve and Regulation (January 17, 2017), https://www.iso-ne.com/static-assets/documents/rules_proceds/operating/isone/op8/op8_rto_final.pdf.

Ramping up and ramping down refer to generators’ increasing or decreasing output to meet changing load levels, such as in the early morning, which typically involves ramping up, and in the late evening, which typically involves ramping down.

ISO Operating Procedure No. 19, Transmission Operations (April 14, 2017), http://www.iso-ne.com/rules_proceds/operating/isone/op19/op19_rto_final.pdf.

While the estimates for operating-reserve requirements are based on expected future operating conditions, annual market requirements are based on historical data that reflect the actual previous seasonal system conditions, as adjusted for transmission topology changes and resource retirements and additions. The ISO calculates market requirements immediately before each locational FRM procurement period.

See footnote above (in Section 4.2) on FCA #12 Transmission-Transfer Capabilities and Capacity Zone Development, https://smd.iso-ne.com/operations-services/ceii/pac/2017/03/a8_fca_12_zonal_boundary_determination.pdf.

Market Rule 1, Standard Market Design (ISO tariff, Section III) (2017), defines the types of reserves that can meet these requirements; http://www.iso-ne.com/regulatory/tariff/sect_3/index.html.

Economic-merit order (i.e., in merit or in merit order) is when the resources with the lowest-price offers are committed and dispatched first, and increasingly higher-priced resources are brought on line as demand increases. Out-of-merit dispatch occurs when resources are run less economically to respect system reliability requirements.

In some circumstances, when transmission contingencies are more severe than generation contingencies, shedding some load may be acceptable.

The ISO provides monthly updates on the status of active generation interconnection requests, NEPOOL Participant Committee COO Report for Monthly Updates (Monthly COO Report). See the April 2017 monthly COO Report in the https://www.iso-ne.com/static-assets/documents/2017/04/april-2017-coo-report.pdf.

The SME subarea in Maine and the NOR subarea in Connecticut have no megawatts proposed in the active queue.

In addition to the monthly COO reports, information on the queue is available at http://www.iso-ne.com/system-planning/transmission-planning/interconnection-request-queue. The projects proposed but discontinued faced problems associated with financing, licensing, insufficient market incentives, or other issues.

“Interconnection Requests that Are Being Considered in the Maine Resource Integration Study,” PAC memorandum (January 23, 2017), https://www.iso-ne.com/static-assets/documents/2017/01/2017_01_23_memo_pac_mri.pdf.

A FERC filing has been postponed until later in 2017.

Higher tie-reliability benefits and reductions in the net ICR would increase the frequency and depth of OP 4 actions.

Further details about individual transmission projects can be found by referring to the latest RSP Project List available at https://www.iso-ne.com/system-planning/system-plans-studies/rsp.

Past RSPs are available at http://www.iso-ne.com/trans/rsp/index.html. PAC materials and reports are available at http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/index.html.

ISO New England, Transmission Planning Process Guide, (April 6, 2017) and Transmission Planning Technical Guide (March 24, 2017), http://www.iso-ne.com/system-planning/transmission-planning/transmission-planning-guides.

One exception is that Aroostook and Washington Counties in Maine receive electric service from New Brunswick.

Information on public policy transmission upgrades is available at https://www.iso-ne.com/system-planning/system-plans-studies/public-policy-transmission-upgrades.

The area reliability studies are Southeastern Massachusetts and Rhode Island (refer to Section 5.5.5), Eastern Connecticut (Section 5.5.8), Maine (Section 5.5.6), and New Hampshire Section 5.5.7).

A time-sensitive need is a reliability criteria violation that needs to be solved within three years of the completion of the relevant needs assessment (posting of the final needs assessment report). Developing solutions for time-sensitive needs follows the solutions study process, as detailed in Section 4.2 of Attachment K of the OATT. A non-time-sensitive need is a criteria violation that needs to be solved but not necessarily sooner than within three years from the completion of the relevant needs assessment. These solutions follow the competitive solutions process, as detailed in Section 4.3 of Attachment K of the OATT. Because load growth has flattened, as discussed in Section 3, with system load in year one of the planning horizon now being very close to the load in year 10, the passage of time, which historically corresponded to load growth, has become less of a driver for new reliability issues on the transmission system.

The temporary hold is put in place because implementing solutions for the time-sensitive needs may resolve non-time-sensitive needs, eliminating the need to implement multiple solutions for the same problem and their associated costs. Solving the time-sensitive needs could also change the options for redispatch in the area system topology, which would require new upgrade proposals.

The SEMA/RI study area, for which a March 2017 reliability study identified a preferred solution for time-sensitive needs, will undergo another needs assessment beginning in mid-2017 to identify remaining needs, if any (see Section 6.5.5).

ISO New England, “Public Notification for Public Policy Requirements Submittals,” (January 11, 2017), https://www.iso-ne.com/static-assets/documents/2017/01/a10_2017_public_policy_transmission_upgrde_process_announcement.pdf.

ISO New England, “2017 Stakeholder Public Policy Requirements Submittals,” compilation (March 1, 2017), https://www.iso-ne.com/static-assets/documents/2017/03/2017_public_policy_requirements_stakeholder_submittals_combined.pdf.

NESCOE, “NESCOE Submission Regarding Transmission Needs Driven by State and Federal Public Policy Requirements,” (May 1, 2017), https://www.iso-ne.com/static-assets/documents/2017/05/nescoe_submission_public_policy_transmission_upgrades.pdf.

2017 Public Policy Transmission Upgrade Process, PAC presentation (June 21, 2017), https://www.iso-ne.com/static-assets/documents/2017/06/a3_public_policy_transmission_upgrade_process_june_2017.pdf.

The Western and Central Massachusetts key study area was created to store all material for a new study in this area, which will be initiated in 2017. Therefore, this RSP does not discuss this new key study area. The Pittsfield and Greenfield key study area will be retained, but all new study work in the Pittsfield and Greenfield area will be saved in the Western and Central Massachusetts key study area.

Southwest Connecticut Key Study Area, webpage (2017), https://www.iso-ne.com/system-planning/key-study-areas/swct.

Southwest Connecticut 2022 Needs Assessment II (February 19, 2014), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2014/feb192014/a9_swct_needs_assessment_2.pdf. Southwest Connecticut Area Transmission 2022 Needs Assessment (June 2014), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/reports/2014/final_swct_2022_needs.pdf.

Southwest Connecticut 2022 Preferred Solution Selection (July 15, 2014), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2014/jul152014/a9_swct_2022_preferred_solutions.pdf. Southwest Connecticut Area Transmission 2022 Solutions Study (February 12, 2015), https://smd.iso-ne.com/planning/ceii/studies/ct/final_swct_2022_solutions_study.pdf.

The Bunker Hill substation rebuild (RSP Project List #1571) and looping the 1990 (Frost Bridge–Baldwin–Stevenson) line into Bunker Hill (RSP Project List #1569) are no longer necessary due to the Towantic interconnection substation being functionally similar. The separation of the 3827 (Beseck–East Devon)/1610 (Southington–Mix Ave.–June St.) double-circuit tower (RSP Project List #1579), previously recommended to alleviate overloads on 88003A/89003B lines, is no longer necessary with the additional generation in the SWCT area.

The addition of a second 115 kV circuit breaker in series with the 29T breaker at Plumtree (RSP Project List #1562) has already been placed in service and the relocation of the 37.8 capacitor bank at Plumtree (RSP Project List #1565) is under construction and is expected to be in service by December 2017.

Greater Hartford Key Study Area, webpage (2-17), https://www.iso-ne.com/system-planning/key-study-areas/greater-hartford.

Greater Hartford and Central Connecticut Area Transmission 2022 Needs Assessment (May 2014), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/reports/2014/ghcc_needs_assessment_report_rev2.zip.

Greater Hartford and Central Connecticut Area Solutions Study II (July 2014), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2014/jul152014/a8_ghcc_area_solutions_2.zip. Greater Hartford and Central Connecticut Area Transmission 2022 Solutions Study (February 2015), https://smd.iso-ne.com/planning/ceii/reports/final_ghcc_solutions_study_report.pdf.

Pittsfield and Greenfield Key Study Area, webpage (2017), https://www.iso-ne.com/system-planning/key-study-areas/pittsfield-greenfield.

Pittsfield Greenfield 2022 Solutions Study (April 2015), https://smd.iso-ne.com/planning/ceii/reports/2010s/archive/a8_pittsfield_greenfield_2022_solutions_study_rev2.pdf. Pittsfield-Greenfield Area (PG Area) 2022 Solutions Study (October 2015), https://smd.iso-ne.com/operations-services/ceii/pac/2015/10/2022_pittsfield_greenfield_area_solutions_study_report_final.pdf.

Greater Boston Key Study Area, webpage (2017), https://www.iso-ne.com/system-planning/key-study-areas/greater-boston.

Greater Boston Area Transmission Needs Assessment (July 2010), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/reports/2012/boston_needs_report.ZIP.

The Greater Boston Area Transmission needs assessment for the 2018 and 2023 study horizon was originally published January 20, 2015. A summary of minor updates is available at https://www.iso-ne.com/static-assets/documents/2016/07/summary_of_corrections_made_to_greater_boston_needs_assessment_report_final.pdf. The updated needs assessment for the 2018 and 2023 study horizon (July 26, 2016) is available at https://smd.iso-ne.com/planning/ceii/reports/2010s/greater_boston_updated_needs_assessment_report_final.pdf.

Greater Boston Preferred Solution, (February 2015), https://www.iso-ne.com/static-assets/documents/2015/02/a2_isone_greater_boston_preferred_solution_non_ceii.pdf. Greater Boston Area Transmission Solutions Study (August 2015), https://smd.iso-ne.com/operations-services/ceii/pac/2015/08/final_greater_boston_transmission_solution_study_reports.zip.

Southeastern Massachusetts and Rhode Island Key Study Area, webpage (2017), https://www.iso-ne.com/system-planning/key-study-areas/sema-ri.

These subareas were used for the needs assessment. Under the solutions study effort, as the solutions were developed, some of the solution alternatives solved needs across the subarea designations created during the needs assessment phase. Due to this finding, the SEMA/RI study area was partitioned into new groups for the Solutions Study. Group 1 comprises portions of Farnum, West Medway-West Walpole, South Shore, and Somerset-Newport subareas. Group 2 comprises the Industrial Park and Somerset-Newport subareas. Group 3 comprises a portion of the Farnum subarea. Group 4 comprises a portion of the West Medway-West Walpole subarea. Group 5 comprises a portion of the South Shore subarea. Group 6 is equivalent to the Cape Cod subarea.

Southeastern Massachusetts and Rhode Island Area Needs Assessment (N-1) (October 2012), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2012/oct172012/sema_ri.pdf. Southeastern Massachusetts and Rhode Island (SEMA/RI) Area Needs Assessment (N-1) (February 2014), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2014/feb192014/a8_sema_ri_needs_assessment.pdf. Southeastern Massachusetts and Rhode Island Area Needs Assessment (N-1-1) (July 2014), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2014/jul152014/a5_sema_ri_area_needs_2_n_1_1_rev1.pdf.

Southeastern Massachusetts and Rhode Island 2026 Needs Assessment (March 2016), https://smd.iso-ne.com/operations-services/ceii/pac/2016/05/final_sema_ri_2026_needs_assessment_presentation_rev2.pdf.

Southeastern Massachusetts and Rhode Island Area 2026 Needs Assessment (May 2016), https://smd.iso-ne.com/operations-services/ceii/pac/2016/05/final_sema_ri_needs_assessment_report.pdf.

Southeastern Massachusetts and Rhode Island 2026 Preliminary Preferred Solution (December 2016), https://smd.iso-ne.com/operations-services/ceii/pac/2016/12/a3_sema_ri_2026_preliminary_preferred_solutions.pdf. Southeastern Massachusetts and Rhode Island Area 2026 Solutions Study (March 2017), https://smd.iso-ne.com/operations-services/ceii/pac/2017/02/final_sema_ri_2026_solutions_study_report_rev1.pdf.

Newport RI (Aquidneck Island) Transmission Area Improvements – Needs and Preferred Solution (April 2015), https://smd.iso-ne.com/planning/ceii/reports/2010s/archive/a7_newport_aquidneck_island_transmission_area_improvements_presentation.pdf.

Southeastern Massachusetts and Rhode Island Minimum Load Needs Assessment, (November 2016), https://smd.iso-ne.com/operations-services/ceii/pac/2016/11/a2_sema_ri_2025_min_load_needs_assessment_
final.pdf.

Southeastern Massachusetts and Rhode Island  Updated Minimum Load Needs Assessment, (March 2017), https://smd.iso-ne.com/operations-services/ceii/pac/2017/03/a9_sema_ri_min_load_needs_assessment_
presentation.pdf and Southeastern Massachusetts and Rhode Island Area 2026 Minimum Load Needs Assessment, (June 2017), https://smd.iso-ne.com/operations-services/ceii/pac/2017/06/ceii_draft_sema_ri_min_load_needs_assessment_
report.docx.

Maine Key Study Area, webpage (2017), https://www.iso-ne.com/system-planning/key-study-areas/maine.

Maine Transmission System 2023 Needs Assessment Steady State Results (September 2014), https://smd.iso-ne.com/operations-services/ceii/pac/2014/a3_maine_2023_needs_assessment_results.pdf. Maine Transmission System 2023 Needs Assessment and TPL-001-4 Compliance Study Report (December 2014), https://smd.iso-ne.com/operations-services/ceii/pac/2014/final_maine_2023_needs_assessment_tpl_001_4_compliance_report.pdf.

Final Addendum Analysis Report to the 2023 Maine  Transmission System Needs Assessment (April 2016), https://smd.iso-ne.com/operations-services/ceii/pac/2016/04/2023-final-me-addendum-report_20160428.pdf.

Maine 2023 Solutions Study Update (January 2017), https://smd.iso-ne.com/operations-services/ceii/pac/2017/01/a4_maine_2023_solution_study_update.pdf.

ISO New England Planning Procedure No. 3, Reliability Standards for the New England Area Pool Transmission Facilities (February 10, 2017), https://www.iso-ne.com/static-assets/documents/2017/02/pp3_rev7.pdf.

As of June 1, 2017, the latest PAC update on incorporating probabilistic planning methods was discussed during the chair’s remarks at the May 2017 meeting.

Updates to System Studies Memorandum (February 24, 2017), https://www.iso-ne.com/static-assets/documents/2017/02/updates_to_system_study_memo.pdf.

Updates to System Studies - Incorporating Changes in Criteria and Assumptions into Ongoing Assessments (March 2017), https://www.iso-ne.com/static-assets/documents/2017/03/a4_updates_to_system_studies.pdf.

New Hampshire and Vermont Key Study Area, webpage (2017), https://www.iso-ne.com/system-planning/key-study-areas/vt-nh.

New Hampshire/Vermont 2023 Needs Assessment Update (March 2014), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2014/mar172014/a7_nh_vt_2023_needs_assessment.pdf.

New Hampshire/Vermont Transmission System 2023 Needs Assessment Report (August 2104), https://smd.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/reports/2014/final_2023_nhvt_transmission_system_needs_assessment.pdf.

Vermont 2023 Solutions Study (September 2014), https://smd.iso-ne.com/operations-services/ceii/pac/2014/a4_vermont_2023_solution_study.pdf. Vermont Transmission System 2023 Solutions Study Report (November 2014), https://smd.iso-ne.com/operations-services/ceii/pac/2014/vermont_2023_solutions_report_final.pdf.

Final Addendum Analysis Report to the 2023 New Hampshire/Vermont (NH/VT) Transmission System Needs Assessment (October 2015), https://smd.iso-ne.com/operations-services/ceii/pac/2015/10/2023_final_nhvt_transmission_needs_assessment_addendum_report.pdf.

New Hampshire 2023 Solutions Study Update (October 2016), https://smd.iso-ne.com/operations-services/ceii/pac/2016/10/a5_new_hampshire_2023_solutions_study_update.pdf.

Eastern Connecticut Key Study Area, webpage (2017), https://www.iso-ne.com/system-planning/key-study-areas/eastern-connecticut.

Eastern Connecticut 2022 Needs Assessment I (May 2013), https://smd.iso-ne.com/operations-services/ceii/pac/2013/eastern_ct_study_n_1_n_1_1_needs_final.pptx.

Eastern Connecticut 2022 Needs Assessment II (July 2014), https://smd.iso-ne.com/operations-services/ceii/pac/2013/eastern_ct_study_needs_cll_short_circuit_final.pptx.

Eastern Connecticut Area Transmission 2022 Needs Assessment (June 2015), https://smd.iso-ne.com/planning/ceii/reports/2010s/final_eastern_ct_2022_needs_assessment_report.pdf.

Eastern Connecticut 2022 Solutions Study Update (September 2016), https://smd.iso-ne.com/operations-services/ceii/pac/2016/09/a3_eastern_connecticut_2022_solution_study_update.pdf.

This total includes seven projects in 2002, 26 projects in 2003, 30 projects in 2004, 51 projects in 2005, 55 projects in 2006, 36 projects in 2007, 64 projects in 2008, 38 projects in 2009, 37 projects in 2010, 44 projects in 2011, 61 projects in 2012, 91 projects in 2013, 67 projects in 2014, 69 projects in 2015, 34 projects in 2016, and 4 additional projects through March 2017. The March 2017 RSP Project List shows that 42 more projects are due in service by the end of 2017.

The data is based on the June 2017 Regional System Plan Project List.

New England Asset Management Key Study Area, webpage (2017), https://www.iso-ne.com/system-planning/key-study-areas/new-england-asset-management/?load.more=1.

A PAC presentation is required for all asset-condition-related work where the cost estimate is greater than or equal to $5 million.

Regional System Plan Transmission Projects October 2015 Update (October 2015), https://www.iso-ne.com/static-assets/documents/2015/10/a3_draft_rsp15_project_list_presentation.pdf. The Asset-Condition Update List is available at https://www.iso-ne.com/system-planning/system-plans-studies/rsp.

Regional System Plan Transmission Projects October 2015 Update, https://www.iso-ne.com/static-assets/documents/2015/10/a3_draft_rsp15_project_list_presentation.pdf. Links to the most recent Local System Plans are included on the ISO’s RSP Project List at https://www.iso-ne.com/system-planning/system-plans-studies/rsp. Also refer to the Transmission Owner Planning Advisory Committee web page at https://www.iso-ne.com/committees/planning/topac.

The RSP Project List is available at https://www.iso-ne.com/system-planning/system-plans-studies/rsp.

PAC materials and meeting minutes are available at http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/index.html. The RSP Project List (XLS file) is available at http://www.iso-ne.com/system-planning/system-plans-studies/rsp.

Regional transmission service is comprised of regional network service (RNS) and through-or-out (TOUT) service. RNS is the transmission service the ISO provides over the PTFs, described in the OATT, Part II.B, that network customers use to serve load within the New England Control Area. The ISO’s TOUT service over the PTFs allows a real-time market transaction to be exported out of or “wheeled through” the New England area, including services used for network resources or regional network load not physically interconnected with a PTF. The PTO Administrative Committee is expected to make a supplemental filing on or before February 28, 2015, that will update New England Power Company’s transmission revenue requirement, which will revise the 2014 regional transmission service rates. See FERC, letter order to National Grid, Docket No. ER14-1686-000 (June 6, 2014), http://www.ferc.gov/CalendarFiles/20140606132455-ER14-1686-000.pdf.

NCPC is a payment to a supply resource that responded to the ISO’s dispatch instructions but did not fully recover its start-up and operating costs in either the Day-Ahead or Real-Time Energy Markets.

Keene Road Market Efficiency Transmission Upgrades Final Needs Assessment, PAC presentation (December 19, 2016), https://www.iso-ne.com/static-assets/documents/2016/12/2016_keene_rd_metu_needs_assessment_final_1.pdf.

Keene Road Market Efficiency Transmission Upgrade (March 2017), https://www.iso-ne.com/static-assets/documents/2017/03/a3_keene_rd_metu_presentation.pdf.

Locational Marginal Prices and Interface Flows, 2016 Historical Market and Operational Data, PAC presentation, slide 8 (April 19, 2017), https://www.iso-ne.com/static-assets/documents/2017/04/a8_2016_interface_flows_and_other_system_perfromance_summaries.pdf.

ISO New England Inc. and New England Power Pool,, Part 1 of Two-Part Filing of NCPC Rule Revisions for Subhourly Settlement and  Part 2 of Two-Part Filing of NCPC Rule Revisions for Subhourly Settlement; Docket No. ER17-___-000, FERC filing (December 27, 2016), https://www.iso-ne.com/static-assets/documents/2016/12/part_1_of_two-part_filing_ncpc_revisions_shs.pdf and https://www.iso-ne.com/static-assets/documents/2016/12/part_2_of_two-part_filing_of_ncpc_revisions_shs.pdf .

More information about NERC is available at http://www.nerc.com/.

Additional information on the EIPC is available at http://www.eipconline.com/.

EIPC, 2015 Report for 2025 Summer and Winter Roll-Up Integration Cases (March 24, 2016) is available at http://www.eipconline.com/non-doe-documents.html.

See NERC’s “Reliability Assessment and Performance Analysis,” webpage (2016), http://www.nerc.com/pa/RAPA/Pages/default.aspx.

NERC, 2016 Long-Term Reliability Assessment (December 2016), http://www.nerc.com/pa/RAPA/ra/Reliability%20Assessments%20DL/2016%20Long-Term%20Reliability%20Assessment.pdf.

NERC, Essential Reliability Services Task Force Measures Framework Report (November 2015), https://www.google.com/url?sa=t&rct=j&q=&esrc=s&source=web&cd=1&cad=rja&uact=8&ved=0ahUKEwj16Oi2mKrUAhVGvRoKHWA3BbkQFggmMAA&url=http%3A%2F%2Fwww.nerc.com%2Fcomm%2FOther%2FessntlrlbltysrvcstskfrcDL%2FERSTF%2520Framework%2520Report%2520-%2520Final.pdf&usg=AFQjCNEV_k9d-grrdno85cjAD5EBCxsBzA.

IRC, “Reports and Filings,” webpage (2015), http://www.isorto.org/Reports/default.

ISO/RTO Council, Comments of the ISO/RTO Council on Notice of Proposed Rulemaking Regarding Electric Storage Resources and Distributed Energy Resource Aggregations in Organized Wholesale Electric Markets (February 13, 2017), http://www.isorto.org/Documents/Report/20170213_Final_IRC_Comments_on_ESR_and_DER_RM16-23-000.pdf.

The NPCC region covers nearly 1.2 million square miles populated by more than 55 million people. NPCC in the United States includes the six New England states and the state of New York. NPCC Canada includes the provinces of Ontario, Québec, and the Maritime provinces of New Brunswick and Nova Scotia. As full members, New Brunswick and Nova Scotia also ensure that NPCC reliability issues are addressed for Prince Edward Island.

ISO New England, “Interregional Planning Stakeholder Advisory Committee,” webpage (2017), https://www.iso-ne.com/committees/planning/ipsac.

ISO New England, NYISO, and PJM, 2015 Northeast Coordinated System Plan (April 11, 2016), https://www.iso-ne.com/static-assets/documents/2016/04/2015_ncsp_041116_final.docx.

Locational Marginal Prices and Interface Flows, PAC presentation (April 19, 2017), https://www.iso-ne.com/static-assets/documents/2017/04/a8_2016_interface_flows_and_other_system_perfromance_summaries.pdf.

Energy imports were 1,848 GWh over Highgate and 10,373 GWh over Phase II.

2015 ISO New England Electric Generator Air Emissions Report (January 2017), https://www.iso-ne.com/static-assets/documents/2017/01/2015_emissions_report.pdf.

By 2019, more than 4,200 MW of generation will be retired, including Salem Harbor Station (749 MW); Vermont Yankee (604 MW); Norwalk Harbor Station (342 MW); Brayton Point Station (1,535 MW); Mount Tom Station (143 MW); Pilgrim Nuclear Power Station (677 MW); and approximately 1,100 MW of active demand-response resources.

The Neptune LNG facility was not included because the Maritime Administration approved the company’s request to suspend its deepwater port license as of June 26, 2013, for a five-year period. Neptune has the right to restart port operations before June 26, 2018, with six months’ prior notice to the Maritime Administration and if certain conditions established in Neptune’s Suspension Plan have been satisfied.

LNG storage facilities can, on short notice, vaporize gas for injection into the New England pipelines and thus help the region meet peak demand. These facilities may require advance contracting, however, to assure adequate onsite liquid storage.

”Bbls” refers to “blue barrels,” the traditional name of the units of oil purchased at 42 gallons/bbls.

American Council for an Energy Efficient Economy (ACEEE), “2016 State Energy Efficiency Scorecard,” (September 2016), http://aceee.org/research-report/u1606. In addition, methane emissions from natural gas systems in Massachusetts have declined by 67% since 1990, according to the MA Department of Environmental Protection’s recent greenhouse gas (GHG) inventory report (MA DEP, GHG Emissions Inventory, 1990–2014 (March 2017), http://www.mass.gov/eea/docs/dep/air/climate/gwsa-appc.xls.

EPA, Evaluation of Existing Regulations, 82 FR 17793, request for comment (April 13, 2017), https://www.federalregister.gov/d/2017-07500, implementing Executive Order 13777 of February 24, 2017, Enforcing the Regulatory Reform Agenda (March 1, 2017), https://www.federalregister.gov/d/2017-04107.

RGGI is a mandatory, market-based effort to reduce CO2 emissions across nine New England and Mid-Atlantic states through a multistate CO2 emissions budget cap-and-trade program. For a state-specific CO2 cap, see Massachusetts 310 CMR 7.74, Reducing Greenhouse Gas Emissions From Electricity Generating Facilities, proposed rule (December 16, 2016), http://www.mass.gov/eea/docs/dep/air/climate/7-74-facility-limits-12-15-16.docx.

EPA, National Pollutant Discharge Elimination System—Final Regulations to Establish Requirements for Cooling Water Intake Structures at Existing Facilities and Amend Requirements at Phase I Facilities, final rule, 79 FR 48299 (August 15, 2014); applies to existing and new cooling water intake structures at power plants and manufacturers. EPA, Effluent Limitation Guidelines and Standards for the Stream Electric Power Generating Point Source Category, final rule, 80 FR 67837 (November 3, 2015). The main pollutants of concern for these discharges include metals (mercury, arsenic, and selenium), nitrogen, and total dissolved solids generated by the operation of air pollution control devices (i.e., scrubbers).

Cooling Water Intake Structure Coalition v. EPA, No. 14-4645 (2nd Circuit US Court of Appeals) and Southwestern Electric Power Co. v. EPA, No. 15-60821 (5th Circuit US Court of Appeals).

Timothy H. Diehl and Mellissa A. Harris, Withdrawal and Consumption of Water by Thermoelectric Power Plants in the United States, 2010, US Geological Survey Scientific Investigations Report 2014–5184 (US Geological Survey, 2014), http://dx.doi.org/10.3133/sir20145184.

A range of different technologies may satisfy this requirement, depending on the circumstances at each facility.

US EPA, Clean Air Act, 42 USC §7401 et seq. (1970), http://www2.epa.gov/laws-regulations/summary-clean-air-act.

EPA, National Ambient Air Quality Standards for Ozone, final rule, 80 Fed. Reg. 65292 (October 26, 2015), https://www.federalregister.gov/articles/2015/10/26/2015-26594/national-ambient-air-quality-standards-for-ozone.

EPA,   National Ambient Air Quality Standards for Particulate Matter, final rule, 78 FR 3086 (January 15, 2013); National Ambient Air Quality Standards for Sulfur Dioxide, final rule, 75 FR 35520 (June 22, 2010).

April 11, 2017, order in Murray Energy Corp. v. EPA, No. 15-1385, continuing oral arguments scheduled for April 19, 2017, and requiring a status report every 90 days from EPA. EPA indicated in its April 7, 2017, motion to continue oral argument that EPA officials appointed by the new administration are reviewing the 2015 ozone National Ambient Air Quality Standards Rule to determine whether it should reconsider the rule or some part of it. On June 6, 2017, the EPA administrator notified state governors of a one-year delay in making non-attainment-area designations for the 2015 ozone standard, from October 2017 to October 2018.

April 27, 2017, order in Anthracite Region Independent Power Producers Association (ARIPPA) v. EPA, No. 15-1180 (D.C. Cir).

Zhang, Y, Jacob, D.J. et al, “Observed decrease in atmospheric mercury explained by global decline in anthropogenic emissions,” Proceedings of the National Academy of Sciences, (digital object identifier: 10.1073/pnas 1516312113) (January 19, 2016), vol. 113, no. 3, 526–531.

EPA, National Emission Standards for Hazardous Air Pollutants: Coal- and Oil-Fired Electric Utility Steam Generating Units, final rule, 77 FR 9304 (February 16, 2012). EPA developed standards under Section 112(d) to reduce hazardous air pollutant emissions from this source category.

2015 ISO New England Electric Generator Air Emissions Report (January 2017), https://www.iso-ne.com/static-assets/documents/2017/01/2015_emissions_report.pdf.

EPA, Air Monitoring Program Data (accessed March 24, 2017). This cluster of 10 residual oil-fired resources accounted for 34% of 2014 SO2 emissions (3,321 out of 9,658 short tons) and 60% of 2015 SO2 emissions (4,532 out of 7,470 short tons), reflecting an absence of advanced SO2 pollution controls compared with remaining coal-fired resources.

EPA, Standards of Performance for Greenhouse Gas Emissions From New, Modified, and Reconstructed Stationary Sources: Electric Utility Generating Units, final rule, 80 FR 64509 (October 23, 2015), https://www.federalregister.gov/d/2015-22837.

RGGI, Inc., “Program Overview,” webpage (n.d.), http://www.rggi.org/design/overview. The RGGI CO2 budget (cap) is equal to the total number of CO2 allowances issued by RGGI states in a given year. A CO2 allowance represents a limited authorization to emit one short ton of CO2 from a regulated source, as issued by a participating state. In 2017, the cap is 84.3 million short tons of CO2/yr, declining 2.5% until 2020 with two interim adjustments in the overall cap for the nine-state region to account for banked CO2 allowances (approximately 234 million CO2 allowances in circulation as of February 2017). RGGI Market Monitor, Report on the Secondary Market for RGGI CO2 Allowances: Fourth Quarter 2016 (May 2017) https://www.rggi.org/docs/Market/MM_Secondary_Market_Report_2016_Q4.pdf.

RGGI, Inc., The RGGI Program Overview, https://www.rggi.org/design/overview; EPA, Air Markets Program data (emissions data), https://ampd.epa.gov/ampd/. The New England RGGI states’ emissions declined to 26.7 million short tons in 2016.

RGGI, Inc., http://www.rggi.org/design/program-review. Other changes may include an emissions-containment reserve, which would further tighten the emissions cap automatically in future years by decreasing allowances available for auction if auction prices fell below a predetermined price point or points.

RGGI, Inc., Report on the Secondary Market for RGGI CO2 Allowances Fourth Quarter 2016 (February 28, 2017). The RGGI market monitor determined that of the 234 million CO2 allowances in circulation at the end of December 2016, RGGI-affected entities held 142 million CO2 allowances (61% of the total in circulation).

RGGI, Inc., Key Topics for 2016 Program Review Stakeholder Discussions (November 17, 2015), https://www.rggi.org/docs/ProgramReview/2016/11-17-15/Key_Discussion_Items_11_17_15.pdf. The RGGI states noted the expected 2020 RGGI cap would be approximately 78 million short tons but could fluctuate if cost-containment reserve allowances are released or if offset allowances are awarded. In comparison, the CPP total mass goals for the nine RGGI states is approximately 79 million short tons in 2030 for existing sources and roughly 80 million short tons in 2030 for new and existing sources.

RGGI, Inc., “2016 Program Review,” webpage (n.d.), http://rggi.org/design/2016-program-review.

The Analysis Group, Considerations Related to Trading for the RGGI States under the EPA’s Clean Power Plan Report (July 12, 2016), fn13, http://www.analysisgroup.com/news-and-events/news/energy-report--considerations-related-to-trading-for-the-rggi-states-under-the-epa-s-clean-power-plan/.

Energy Information Administration, “Regional Greenhouse Gas Initiative Auction Prices Decline,” website article (June 24, 2016), https://www.eia.gov/todayinenergy/detail.php?id=26812.

ISO New England, Internal Market Monitor, 2016 Annual Markets Report (May 30, 2017), https://www.iso-ne.com/static-assets/documents/2017/05/annual_markets_report_2016.pdf, p. 16.

Nuclear Regulatory Commission, Continued Storage of Spent Nuclear Fuel, final rule, 79 Fed. Reg. 56238 (September 19, 2014). The rulemaking replaces NRC’s Waste Confidence Rule (governing onsite storage of spent nuclear fuel) struck down in 2012 (New York v. NRC, 681 F.3d 471 (D.C. Cir. 2012).

ISO-NE, 2017-2026 Forecast Report of Capacity, Energy, Loads and Transmission (CELT), Tab 2.1, “Generator List SCC for affected coal-, oil-, gas/oil steam units, excluding all Brayton Point SCC capacity.” https://www.iso-ne.com/static-assets/documents/2017/05/2017_celt_report.xls.

FERC issues initial and renewal hydroelectric project licenses for 30 to 50 years typically, although it may issue temporary annual licenses to continue an expired license during a relicensing review. FERC, “Applications for New Hydropower Licenses and Relicensing,” (June 7, 2017), http://www.ferc.gov/industries/hydropower/gen-info/licensing.asp. ISO New England, 2017 CELT, Tab 2.1, “Generator List with Existing and Expected SCC,” showings the seasonal rating of generating units; https://www.iso-ne.com/static-assets/documents/2017/05/2017_celt_report.xls.

FERC, Modification to Integrated Licensing Process Schedule, TransCanada Hydro Northeast, Inc., and Firstlight Hydro Generating Company (December 21, 2012); Connecticut River Joint Commission, Relicensing of Connecticut River Dams (accessed February 18, 2014). Adjustments in relicensing studies timeline were necessitated by the closure of Vermont Yankee in December 2014, as certain environmental baseline conditions could have changed during the relicensing study period. FERC agreed to extend project licenses by one year, to allow study of post-closure conditions.

Information on NREL is available at https://www.nrel.gov/research/publications.html.

IEEE Standard 1547 establishes criteria and requirements for the interconnection of distributed resources with electric power systems. This document provides a uniform standard for the performance, operation, testing, safety considerations, and maintenance of the interconnection. See “IEEE 1547 Standard for Interconnecting Distributed Resources with Electric Power Systems,” webpage (2015), http://grouper.ieee.org/groups/scc21/1547/1547_index.html.

Ride-through capabilities reduce unwanted trips of DERs for contingency events on the transmission and distribution systems.

NERC, Distributed Energy Resources Connection Modeling and Reliability Considerations (February 2017), http://www.nerc.com/comm/Other/essntlrlbltysrvcstskfrcDL/Distributed_Energy_Resources_Report.pdf.

Block Island is the only offshore wind plant at 29 MW; the remaining 1,271 MW is onshore wind.

See the ISO’s “Do Not Exceed Dispatch Project” webpage (2017), https://www.iso-ne.com/participate/support/customer-readiness-outlook/do-not-exceed-dispatch.

FERC, Order Accepting Proposed Tariff Revisions, 157 FERC ¶ 61,189 (December 9, 2016), https://www.iso-ne.com/static-assets/documents/2016/12/er17-68-000_12-9-16_order_accept_resource_dispatchability_revisions.pdf.

Operational Load Forecast Improvement Effort, Participants Committee presentation (April 7, 2017), https://www.iso-ne.com/static-assets/documents/2017/04/npc_20170407_addl.pdf (pages 156-169).

EPRI, Recommended Settings for Voltage and Frequency Ride-Through of Distributed Energy Resources (May 8, 2015), http://www.epri.com/abstracts/Pages/ProductAbstract.aspx?ProductId=000000003002006203.

These IEEE 1547 and interconnection requirements are for low/high-voltage ride through, low/high-frequency ride through, ramp rates, and others.

DG Interconnection Issues, PAC presentation (July 7, 2015), http://www.iso-ne.com/static-assets/documents/2015/07/a2_dg_interconnection_issues_update.pdf.

The use of active demand resources will change as of June, 1, 2018, and include demand-response capacity resources, active demand capacity resources, and price-responsive demand resources (see Section 10.3.3.1).

2015 Economic Study—Evaluation of Increasing the Keene Road Export Limit;  2015 Economic Study—Evaluation of Offshore Wind Deployment; and 2015 Economic Study—Strategic Transmission Analysis—Onshore Wind Integration (all posted September 2, 2016), accessible at https://www.iso-ne.com/committees/planning/planning-advisory/?document-type=Economic Studies&file-type=DOC&file-type=DOCX (using  “Economic Studies” and “DOC” filters).

Draft 2016 Economic Study: NEPOOL Scenario Analysis Report: Implications of Public Policies on ISO New England Market Design, System Reliability and Operability, Resource Costs and Revenues, and Emissions (July 25, 2017), https://www.iso-ne.com/static-assets/documents/2017/07/draft_2016_phase1_nepool_scenario_analysis_report.docx. The ISO anticipated posting the final report in fall 2017. [Update with link to final report, if posted]

EPRI, Grid Impacts and Challenges Arising from the Integration of Inverter-Based Variable Resources, PAC presentation (October 19, 2016), https://www.iso-ne.com/static-assets/documents/2016/10/a3_integration_and_planning_of_large_amounts_of_inverter_based_resources.pptx.

Light load conditions can present high-voltage issues and trigger over-generation situations.

Analysis Group, Capacity Market Impacts and Implications of Alternative Resource Expansion Scenarios: An Element of the ISO New England 2016 Economic Analysis (July 3, 2017), https://www.iso-ne.com/static-assets/documents/2017/07/final_analysis_group_2016_economic_analysis_capacity_market_impacts.pdf. The final results for the ramping, regulation, and reserve study is scheduled for December 2017.

The CONE is a pricing threshold derived from the capacity clearing prices established in an FCA used to (1) establish the starting price for each FCA, (2) set thresholds for reviewing delist bids to deter the exercise of market power, (3) set initial pricing for reconfiguration auctions when the ISO or a market participant that does not meet its commercial operation date submits demand bids or supply offers, and (4) determine pricing when the supply is inadequate and competition is insufficient. The net CONE was assumed at $8.70//kW-month in 2025 and $9.61/kW-month in 2030.

The maximum assumed natural gas supply to the region was assumed as 6.703 billion cubic feet per day (Bcf/d) in 2025 and 6.874 Bcf/d in 2030, which would be sufficient to meet LDC growth and allow for some surplus capacity to serve some generating units burning natural gas.

The assumed current pipeline capacity is 4.697 Bcf/d during the summer.

Conservation Law Foundation, “Request for 2017 Economic Study to Explore Least-Cost, Emissions-Compliant System Topologies,” (April 3, 2017), https://www.iso-ne.com/static-assets/documents/2017/04/a7_2017_economic_study_request_clf.pdf. The ISO discussed the scope of work with the PAC on May 25, 2017, but indicated that this study will have a low priority and, as such, has not finalized a study schedule. Refer to 2017 Economic Study: Scope of Work, PAC presentation (May 25, 2017), https://www.iso-ne.com/static-assets/documents/2017/05/a2_2017_economic_study_scope_of_work.pdf.

More information about the EIPC is available at http://www.eipconline.com/.

More information on the NCEP and NARUC is available at http://electricitypolicy.org/about/ and https://www.naruc.org/, respectively.

More information about NESCOE is available at www.nescoe.com.

ISO New England, “Presentations, Speeches, and Other Materials,” webpage, “External Affairs Monthly Issues Memo” document type, http://www.iso-ne.com/about/government-industry-affairs/materials.

The end-user sector in the NEPOOL stakeholder process and the ISO stakeholder committees also convey consumer interests. Additional information on the CLG is available at http://www.iso-ne.com/committees/consumer-liaison.

ISO New England and Consumer Liaison Group Coordinating Committee, 2016 Report of the Consumer Liaison Group (March 1, 2017), https://www.iso-ne.com/static-assets/documents/2017/03/2016_report_of_the_consumer_liaison_group_final.pdf.

IEEE describes the smart grid as a “next-generation” electrical power system that typically employs the increased use of communications and information technology for generating, delivering, and consuming electrical energy. See the IEEE’s Smart Grid Community webpage for a full discussion of smart grid technology: https://www.ieee.org/membership-catalog/productdetail/showProductDetailPage.html?product=CMYSG735.

PMUs use global positioning satellite technology to monitor the performance of the region’s electric power grid accurately and provide specific data, including synchrophasor power system measurements, for use in operating the grid and enhancing grid design. The IEEE defines FACTS as flexible alternating-current transmission systems that incorporate power-electronics-based controllers and other static controllers to enhance controllability and power-transfer capability. See the IEEE’s Power and Energy Society’s webpage: http://www.ieee-pes.org/nari-hingorani-facts-award.

For additional information on PSERC and EPRI, refer to http://www.pserc.wisc.edu/home/index.aspx and http://www.epri.com/.

ISO/RTO Council, “North American Wholesale Electricity Demand-Response Program Comparison, 2015 Edition” webpage and Excel spreadsheet (April 2016), http://www.isorto.org/ircreportsandfilings/2015-north-american-demand-response-characteristics-available  and  http://www.isorto.org/Documents/Report/20160425_2015NorthAmericanWholesaleElectricityDemandResponseProgramComparison.xlsx

For more information on IEEE, see http://www.ieee.org/index.html. Also refer to the Power and Energy Society at http://www.ieee-pes.org/.

The 2026 SEMA/RI Solution Study (see Section 5.5.5) used cloud computing systems to evaluate various transmission solutions in a very short period of time.

FERC,  Order No. 745, Demand Response Compensation in Organized Wholesale Energy Markets, 134 FERC ¶ 61,187 (March 15, 2011), https://www.google.com/url?sa=t&rct=j&q=&esrc=s&source=web&cd=1&ved=0ahUKEwiPuc73ndfUAhWIcT4KHUgCDwkQFgg7MAA&url=https%3A%2F%2Fwww.ferc.gov%2FEventCalendar%2FFiles%2F20110315105757-RM10-17-000.pdf&usg=AFQjCNHj8nf3O25n08Tt4ALJlua7GcmTGw&cad=rja.

State sponsorships available to renewable technologies but not available to other types of resources include state Renewable Portfolio Standards and similar renewable energy goals; state initiatives to reduce greenhouse gas emissions (e.g., global warming solutions acts) and regional carbon cap-and-trade programs, such as the Regional Greenhouse Gas Initiative; state-sponsored, long-term contracts to develop renewable resources; and federal production and investment tax credits. See the ISO’s “New England’s Capacity Markets and Renewable Energy Future,” discussion paper (June 3, 2015), https://www.iso-ne.com/static-assets/documents/2015/06/iso_ne_capacity_mkt_discussion_paper_06_03_2015.pdf.

ISO New England, “Competitive Auctions with Subsidized Policy Resources,” discussion paper (April 2017), https://www.iso-ne.com/static-assets/documents/2017/04/caspr_discussion_paper_april_14_2017.pdf. Note that “sponsored” resources more appropriately characterizes what had initially been called “subsidized” resources.

State of Connecticut, An Act Concerning Affordable and Reliable Energy, Public Act No. 15-107 (June 19, 2015), https://www.cga.ct.gov/2015/ACT/PA/2015PA-00107-R00SB-01078-PA.htm.

Massachusetts Superior Court, Suffolk County, Kain et al. v. Massachusetts Department of Environmental Protection (Kain), 474 Mass. 278 (January 8, 2016–May 17, 2016), http://masscases.com/cases/sjc/474/474mass278.html.

Massachusetts Governor Charlie Baker, ”Establishing an Integrated Climate Change Strategy for the Commonwealth,” Executive Order No. 569 (September 16, 2016),  http://www.mass.gov/governor/legislationexecorder/execorders/executive-order-no-569.html.

State of Massachusetts, Adopt new 310 CMR 7.74: Reducing CO2 Emissions from Electricity Generating Facilities, final regulation, (August 11, 2017), http://www.mass.gov/eea/docs/dep/air/climate/3dregf-electricity.pdf and http://www.mass.gov/eea/agencies/massdep/air/climate/section3d-comments.html.

State of Massachusetts, An Act To Promote Energy Diversity, Chapter 188 of the Acts of 2016 (August 2016), https://malegislature.gov/Laws/SessionLaws/Acts/2016/Chapter188.

State of Massachusetts, “Governor Charlie Baker Signs Comprehensive Energy Diversity Legislation,” press release (August 8, 2016), http://www.mass.gov/governor/press-office/press-releases/fy2017/governor-baker-signs-comprehensive-energy-diversity-law.html.

State of Massachusetts, “Energy-Storage Initiative.” webpage (2017), http://www.mass.gov/eea/energy-utilities-clean-tech/renewable-energy/energy-storage-initiative/.

State of New Hampshire, An Act Establishing a Committee to Study Transmission, Distribution, Generation, and Other Costs in the State’s Electricity System, SB125 (June 2, 2017), http://www.gencourt.state.nh.us/bill_status/bill_docket.aspx?lsr=925&sy=2017&sortoption=&txtsessionyear=2017&txtbillnumber=sb125&q=1.

State of Rhode Island, Raimondo Announces “1,000 by ‘20” Clean Energy Goal—1,000 Megawatts of Clean Energy by 2020, press release (March 1, 2017), http://www.ri.gov/press/view/29766.

State of Vermont, “Renewable Energy Standard,” webpage (2016), http://puc.vermont.gov/electric/renewable-energy-standard.