2017 Economic Study:
Exploration of Least-Cost Emissions-Compliant Scenarios

© ISO New England Inc.

october 29, 2018

ISO-NE PUBLIC

# Table of Contents

Figures	vi

Tables	vii

Nomenclature	ix

Section 1
Executive Summary	1

1.1 Purpose of the 2017 Economic Study and Metrics Analyzed	1

1.2 Scenarios	2

1.3 Methodology and Assumptions	3

1.4 Key Observations	8

1.4.1 Major Results Overall	8

1.4.2 High-Order-of-Magnitude Transmission Costs	9

1.4.3 Relative Annual Resource Costs	10

1.4.4 CO2 Emissions Compared with RGGI Targets	12

1.5 Conclusions and Next Steps	13

Section 2
Introduction	15

2.1 Economic Study Process	15

2.2 Disclaimer	15

2.3 2016 NEPOOL Scenario Analysis Process and Goals	16

2.4 Topics Addressed	16

Section 3
Description of the Scenarios	17

3.1 Scenario 3—“Renewables Plus” (also “Renew Plus”)—Generation Fleet Meets Existing RPSs,
and Additional Renewable/Clean Energy Resources Are Used Above the Existing RPS Targets	17

3.2 Scenario A—“EE + Offshore”—Change in Mix of New Renewable/Clean Energy Resources,
with Emphasis on Energy Efficiency and Offshore Wind	17

3.3 Scenario B—“Onshore Less EE/PV”—Change in Mix of New Renewable/Clean Energy Resources,
with Emphasis on Onshore Wind	17

3.4 Scenario C—“Wind Less Nuclear”—Replacement of Some of the Baseload Nuclear Generation with Renewable/Clean Energy Resources	18

3.5 Overview of Scenario Parameters	18

Section 4
Methodology and Metrics	21

4.1 Methodology	21

4.2 Metrics Analyzed	21

Section 5
Assumptions	23

5.1 Public Policies Assumed	23

5.2 Peak Demand, Annual Energy Use, and Demand Modifiers	24

5.2.1 Peak Demand and Annual Energy Use	24

5.2.2 Passive Demand and Behind-the Meter PV Resources	25

5.2.3 Plug-In Hybrid Electric Vehicles	25

5.3 Capacity Assumptions	27

5.3.1 Capacity Value Assumptions	29

5.3.2 Wind Generation	31

5.3.3 Resource Retirements	32

5.3.4 Renewable Portfolio Standards	33

5.3.5 Active Demand Resources	33

5.3.6 New England Hydroelectric Generation	34

5.3.7 Pumped Storage and Battery Storage	34

5.3.8 Transmission Interface Limits and Interchanges with Neighboring Systems	34

5.4 Fuel Prices	37

5.5 Threshold Prices	39

5.6 Environmental Emissions Allowance Assumptions	39

5.7 Annual Carrying Charges	40

5.7.1 Annual Carrying Charges for New Resources	40

5.7.2 Transmission Development Costs	41

5.7.3 High-Order-of-Magnitude Cost Estimates for Integrating Renewable Resources	47

Section 6
Results and Observations	49

6.1 Economic Results	49

6.1.1 Total Energy Production by Resource (Fuel) Type, Including Imports	49

6.1.2 Systemwide Production Costs	51

6.1.3 Annual Average LMPs by RSP Subareas	52

6.1.4 Load-Serving Entity Energy Expense and Uplift	53

6.1.5 GridView Congestion Metric by Interface	55

6.1.6 High-Order-of-Magnitude Transmission Costs	56

6.2 Operation and Planning the Transmission System for High Levels of Inverter-Based Resources	58

6.3 Relative Annual Resource Costs	59

6.4 Environmental Results	62

6.4.1 Ability of the System to Meet Renewable Portfolio Standards	63

6.4.2 Carbon Dioxide Emissions and RGGI Goals	63

6.4.3 Spilled Renewable Resource Energy	64

Section 7
Summary, Conclusions, Transitional Issues, and Next Steps	67

7.1 Key Observations	67

7.2 Transitional Issues	68

7.3 Next Steps	68

# Figures

Figure 1-1: 	Total relative annual resource costs, 2030 (constrained and unconstrained),
showing changes compared with 2030 Scenario 3 (constrained) ($ billions)	10

Figure 1-2: 	Total relative annual resource costs, 2030 (constrained and unconstrained)
 showing changes compared with 2030 Scenario 3 (constrained) (¢/kWh).	11

Figure 1-3: 	CO2 emissions, 2030 (millions of short tons, %) compared with range of RGGI limits.	13

Figure 5-1: 	Daily PHEV charging profile for the EE + Offshore and Wind Less Nuclear Scenarios
for 4.2 million vehicles, 2030 (MW).	26

Figure 5-2: 	2030 capacity value assumptions by resource type (MW).	30

Figure 5-3: 	Wind nameplate capacities assumed for the wind resources, 2030 (MW).	31

Figure 5-4: 	Pipe and bubble representations of transmission interfaces in New England
for 2030 (MW).	35

Figure 5-5: 	Reference fuel-price forecasts for New England, 2030 ($/MMBtu).	38

Figure 5-6: 	Per-unit multiplier for monthly natural gas price forecast assumptions for 2030.	38

Figure 5-7 	(A and B): The first two components of transmission upgrades potentially needed
to integrate renewable resources.	42

Figure 5-8: 	The congestion-relief system.	44

Figure 6-1: 	Total systemwide production by fuel type for each scenario, 2030 (TWh).	49

Figure 6-2: 	Production costs, 2030 ($ millions).	51

Figure 6-3: 	Annual average LMPs by RSP subarea, 2030 ($/MWh).	52

Figure 6-4: 	Load-serving entity energy expense and uplift, 2030 ($ million).	54

Figure 6-5: 	Gridview congestion metric by interface, 2030 ($ million)	55

Figure 6-6: 	Example of a daily system load in real time with and without solar power,
April 21, 2018 (MW).	58

Figure 6-7:	 Energy by source for the Renewables Plus Scenario, May 7, 2030, unconstrained (MW).	59

Figure 6-8: 	Total relative annual resource costs, 2030 (constrained and unconstrained),
showing changes compared with 2030 Scenario 3 (constrained) ($ billions).	60

Figure 6-9: 	Total relative annual resource costs, 2030 (constrained and unconstrained),
showing changes compared with 2030 Scenario 3 (constrained) (¢/kWh).	61

Figure 6-10: 	CO2 emissions, 2030 (millions of short tons, %) compared with range of RGGI limits.	63

Figure 6-11: 	Total amount of “spilled” energy produced by renewable resources, 2030
(unconstrained and constrained cases) (GWh, %).	65

# Tables

Table 1-1 	Assumed Changes in Net Demand and Resources from the Renew Plus Scenario
for the EE + Offshore, Onshore Less EE/PV, and Wind Less Nuclear Scenarios
(MW Increases and Reductions)	6

Table 1-2 	Net Demand and Resource Assumptions Used  in the Renew Plus , EE + Offshore,
Onshore Less EE/PV, and Wind Less Nuclear Scenarios (MW, millions)	7

Table 1-3 	Relative Annual Resource Costs, 2030 ($ Millions)	11

Table 1-4 	Relative Annual Resource Costs, 2030 (¢/kWh)	12

Table 4-1 	Metrics Analyzed in the 2017 Economic Study	22

Table 5-1 	Gross New England 50/50 Peak Demand and Annual Energy Use for All Scenarios	25

Table 5-2 	Capacity and Energy Assumptions for Passive Demand and BTM PV Resources 2030	25

Table 5-3 	Assumed Distribution of PHEVs by State for 2030 for the Renew Plus, EE + Offshore,
and Wind Less Nuclear Scenarios	26

Table 5-4 	PHEV Characteristics for 2030 for the Renew Plus, EE + Offshore,
and Wind Less Nuclear Scenarios	26

Table 5-5 	Summary of Capacity Assumptions Used in the Scenarios, 2030 (MW)	29

Table 5-6 	Capacity Value Assumptions for Various Resources, 2030 (MW)(a)	30

Table 5-7 	Onshore and Offshore Wind Additions and Totals for All the Scenarios, 2030 (MW)	31

Table 5-8 	Assumptions Used for Onshore and Offshore Wind Generation Nameplate Values,
2030 (MW)	32

Table 5-9 	Assumed Generating Unit Retirements by 2030 (MW)	33

Table 5-10 	Single-Value Internal Transmission-Interface Limits for Use in RSP Subarea Models
assumed for 2030 (MW)	34

Table 5-11 	Assumed Interconnections with Neighboring Systems, Import Capabilities,
and Capacity Imports for 2030 (MW)	37

Table 5-12 	Nominal Fuel Price Forecast for New England, 2030 ($/MMBtu)	39

Table 5-13 	Assumed Threshold Prices for Price-Taking Resources	39

Table 5-14 	Air Emission Allowance Prices for 2030 ($/short ton)	40

Table 5-15 	Assumed Total Overnight Generator Costs and Typical Annual Carrying Charges
for New Resources (MW, $/kW)	41

Table 5-16 	Integrator System Assumptions	43

Table 5-17 	Congestion-Relief Transmission Capacity Assumed for the Scenarios (MW)	44

Table 5-18 	Detailed Congestion-Relief System Components and Their Assumed Costs
for the Renew Plus, Onshore Less EE/PV, and Wind Less Nuclear Scenarios	46

Table 5-19 	Summary of High-Order-of-Magnitude Costs to Integrate Renewable Resources
under All Scenarios	47

Table 5-20 	Assumptions for Interconnecting Offshore Wind Resources	48

Table 6-1 	Total Systemwide Production by Fuel Type for Each Scenario, 2030 (TWh)	50

Table 6-2 	Production Costs, 2030 ($ Millions)	51

Table 6-3 	Production Costs Compared with the Renew Plus Scenario, 2030 ($ Millions)	52

Table 6-4 	LMPs in Selected Subareas, 2030 ($/MWh)	53

Table 6-5 	Load-Serving Entity Energy Expense and Uplift Costs, 2030 ($ Millions)	54

Table 6-6 	Load-Serving Entity Energy Expense and Uplift Costs, 2030 ($ Millions)
Compared with the Renew Plus Reference Scenario	55

Table 6-7 	GridView Congestion Metric by Interface, 2030 ($ Million)	56

Table 6-8 	Percentage of Hours Interface Flow Reaches or Exceeds 100% of Rating
in the Constrained and Unconstrained Cases—All Scenarios, 2030	56

Table 6-9 	Interface Flow Statistics	57

Table 6-10 	Summary of Total High-Order-of-Magnitude Transmission System Costs ($ Billions)	57

Table 6-11 	Relative Annual Resource Costs, 2030 ($ Millions)	61

Table 6-12 	Relative Annual Resource Costs, 2030 (¢/kWh)	62

Table 6-13 	CO2 Emissions Compared with RGGI Targets, 2030 (Millions of Short Tons and %)	64

Table 6-14 	Total Amount of “Spilled” Energy Produced by Renewable Resources,
2030 (Unconstrained and Constrained Cases) (GWh, %)	66

# Nomenclature

Nomenclature used in this study:

¢/kWh		cents per kilowatt-hour

$/kW-yr		dollars per kilowatt-year

$B		billion dollars

$/MMBtu	dollars per million British thermal units

$/MWh		dollars per megawatt-hours

$M/year		million dollars per year

AC		alternating current

ACC		annual carrying charge

ADR		active demand resource

AEO		Annual Energy Outlook (US Energy Information Administration)

AFUDC		allowance for funds used during construction

B		billion (dollars)

BHE		RSP subarea/area—northeastern Maine

BOSTON 	(all caps) RSP subarea covering Greater Boston, including the North Shore

BTM		behind the meter

BTU		British thermal unit

CARIS		Congestion Assessment and Resource Integration Study

CASPR		competitive auction with sponsored policy resources

CC		combined cycle

CELT		Forecast Report of Capacity, Energy, Load, and Transmission (ISO New England)

CLF		Conservation Law Foundation

CMA		Central Massachusetts area

CO2		carbon dioxide

CSC		Cross-Sound Cable

CSO		Capacity Supply Obligation

CT		RSP area—northern and eastern Connecticut

DC		direct current

DERTF		Distributed Energy Resources Task Force (NERC)

DOE		Department of Energy (US)

EE		energy efficiency

EIA 		Energy Information Administration (US DOE)

ERSWG		Essential Reliability Services Working Group (NERC)

ES		energy storage

FACTS		Flexible Alternating-Current Transmission System

FCA		Forward Capacity Auction

FCM		Forward Capacity Market

GT		gas turbine

GWh		gigawatt-hours

HG		Highgate

HQ PII		Hydro-Québec Phase II

HVDC		high-voltage direct current

hydro		hydroelectric

IC		internal combustion

IMAPP		Integrating Markets and Public Policy, ISO initiative

ISO		ISO New England

kton		kiloton

kV		kilovolt

kW		kilowatt

kWh		kilowatt-hour

kW-yr		kilowatt-year

LMP		locational marginal price

LSE 		load-serving entity

M	million (dollars)

ME		western and central Maine/Saco Valley, New Hampshire

MMBtu	million British thermal units

MW		megawatt(s)

MWe	electrical megawatts

MWh		megawatt-hour

N-1		first contingency

n.d.		no date

NEMA		Northeast Massachusetts area

NEPOOL		New England Power Pool

NERC		North American Electric Reliability Corporation

NG		natural gas

NGCC		natural gas combined cycle

NH		northern, eastern, and central New Hampshire /eastern Vermont and southwestern Maine

NICR		net Installed Capacity Requirement

NOX		nitrogen oxide

NREL		National Renewable Energy Laboratory (US DOE)

Nuc		nuclear

NYISO		New York Independent System Operator

OATT		Open Access Transmission Tariff

PAC 		Planning Advisory Committee

PHEV		plug-in hybrid electric vehicle

POI		point of interconnection

PRD		price-responsive demand

PV		photovoltaic

RARC		relative annual resource cost

REC		Renewable Energy Credit

RGGI		Regional Greenhouse Gas Initiative

RI		RSP area—Rhode Island/bordering MA

RPS		Renewable Portfolio Standard

RSP		Regional System Plan

RTEG		real-time emergency generation

SCC		seasonal claimed capability

SEMA		RSP area—Southeastern Massachusetts/Newport, Rhode Island

SEMA/RI		southeastern Massachusetts/Newport, Rhode Island, and Rhode Island bordering Massachusetts

SME		southeastern Maine

SO2		sulfur dioxide

SWCT		southwestern Connecticut

TMNSR		10-minute nonspinning reserve

TMOR		30-minute operating reserve

TMSR		10-minute spinning reserve

TO		transmission owner

TWh		terawatt-hours

VT		Vermont/southwestern New Hampshire

WMA		RSP area—Western Massachusetts

# Executive Summary

This report documents Exploration of Least-Cost Emissions-Compliant Scenarios of the 2017 ISO New England (ISO) Economic Study conducted for the ISO’s stakeholders following a request by the Conservation Law Foundation (CLF). The study examines several low-carbon-emitting resource-expansion scenarios of the regional power system and the potential effects of these different future changes on resource adequacy, operating and capital costs, and options for meeting environmental policy goals. The study presents a common framework for New England Power Pool (NEPOOL) participants, regional electricity market stakeholders, policymakers, and consumers to identify and discuss these issues and possible solutions.

Scenario analyses inform stakeholders about different future systems. These hypothetical systems should not be regarded as physically realizable plans or the ISO’s vision of realistic future development, projections, and preferences. While the scenarios do not fully capture current laws and regulations, they can assist readers by identifying key regional issues that must be addressed. For example, this report identifies several physical and economic issues associated with futures simulating the large-scale development of renewable resources. It also summarizes high-order-of-magnitude transmission system expansion costs, which provide cost information but do not identify particular facilities or include detailed plans associated with any of the scenarios.

The scope of work, assumptions, and results reflect input from the Planning Advisory Committee (PAC) during four meetings held from April 2017 through September 2018. The results are presented such that readers may make their own assumptions on costs for developing new resources and transmission. The ISO encourages interested parties to compare the results for the different scenarios and to reach their own conclusions about the possible outcomes.

## Purpose of the 2017 Economic Study and Metrics Analyzed

In 2017, in accordance with the procedures of Attachment K of the ISO’s Open-Access Transmission Tariff (OATT), CLF submitted a request for a scenario analysis that would provide information and data on the following topics:

- Potential economic effects on the ISO’s wholesale energy markets of implementing public policies aimed at greatly reducing carbon emissions in the New England states

- Relative wholesale electricity costs of supplying load and total regional emissions under the alternative scenarios

The economic study request emphasized the desire for a comparison of the relative results across scenarios. The metrics studied were as follows:

- Energy production by resource type

- Systemwide production costs

- Average locational marginal prices (LMPs)

- Average load-serving entity (LSE) energy expenses and congestion

- Generic capital costs and annual carrying charges (ACCs) for each resource type

- Transmission-expansion costs

- Generation by fuel type and the amount of “spilled” renewable resources

- Systemwide carbon dioxide (CO2) emissions

- Effects of transmission-interface constraints that may bind economic power flows

## Scenarios

The scenarios assumed considerable development of renewable and other low-carbon-emitting resources in differing amounts, types, and locations. However, none of the simulated futures considered the transitions to the scenarios for 2030, the year of study, such as the pace of resource development or the cost implications to customers.

The analysis ran simulations of production costs for three scenarios. The starting point for all three scenarios was Scenario 3 of the 2016 NEPOOL Scenario Analysis, summarized in this report as the basis of comparison. This scenario had the lowest CO2 emissions across all the scenarios of the 2016 analysis for the constrained and unconstrained cases. The simulated scenarios for the 2017 Economic Study are as follows:

- 2016 NEPOOL Scenario Analysis Scenario 3—“Renewables Plus” (also “Renew Plus”), where the generation fleet meets existing Renewable Portfolio Standards (RPSs), and the system has additional renewable/clean energy resources

- 2017 Economic Study Scenario A—“EE + Offshore” reflects a change from the Renewables Plus scenario by modifying the resource mix of new renewable/clean energy resources, with emphasis on energy efficiency (EE) and offshore wind in southern New England

- 2017 Economic Study Scenario B—“Onshore Less EE/PV” simulates a change in the mix of Renewables Plus resources with new renewable/clean energy resources, with emphasis on onshore wind in northern New England (and less on EE and solar photovoltaics [PV])

- 2017 Economic Study Scenario C—“Wind Less Nuclear” considers the replacement of some of the baseload nuclear generation in the Renewables Plus scenario with renewable/clean energy resources, especially onshore wind in northern New England

## Methodology and Assumptions

The analyses were conducted using the GridView economic dispatch program. Under differing sets of assumptions, GridView simulations perform economic dispatch that minimizes production costs for a given set of unit characteristics. New England was modeled as a constrained single area for unit commitment, and regional resources were economically dispatched in the simulations to respect the assumed “normal” transmission system transfer limits. Depending on the case, the model included approximately 900 units (new and existing) in New England.

The scenarios examined data sets for 2030, with the transmission system constrained and unconstrained and with all resource mixes meeting the net Installed Capacity Requirement (NICR). The year 2030 was selected to show longer-term indicative results.

The requested scenarios considered several public policies assumed to be in effect in the six New England states in the year of study, including Renewable Portfolio Standards; energy efficiency, solar, and net-metering programs; and the Regional Greenhouse Gas Initiative (RGGI) allowance pricing. The study does not evaluate these state polices, laws, and regulations.

The study made common and scenario-specific assumptions for a number of parameters based on the Renew Plus scenario for 2030. The following assumptions were common across all scenarios:

- Gross demand, PV, and EE forecasts summarized in the ISO’s 2016 Capacity, Energy, Load, and Transmission (CELT) Report were used to establish net load for 2025. The quantities for 2030 assumed growth continuing at the same rate for 2025 compared with 2024.

- A representative installed reserve margin of 14% was assumed to meet the net Installed Capacity Requirement to determine needed generation added to the scenarios.

- The fleet of supply and demand resources expected as of 2019/2020 using the results of the tenth Forward Capacity Auction (FCA #10) were reflected in the simulations. These cleared resources, include renewables (i.e., biofuel, landfill gas, and other fuels), central station solar photovoltaics and wind farms; coal-, oil-, and gas-fired generators; nuclear; hydroelectric and pumped-storage resources; and external capacity contracts, which will have capacity supply obligations (CSOs) from June 1, 2019, to May 31, 2020. Retired resources known as of FCA #10 were also removed from the simulation databases.

- Forward Capacity Market (FCM) and energy-only generators (i.e., those that receive revenue from the wholesale electric energy markets but do not participate in the FCM) were simulated at their summer seasonal claimed capabilities and then reduced to reflect forced outages and average daily unavailabilities of generators.

- The as-planned transmission system was used for estimating the system’s transfer limits for internal and external interfaces under constrained conditions. The 2030 internal and external transmission-interface transfer capabilities were based on the values established for 2025 for regional planning studies.

- US Energy Information Administration (EIA) fuel-price forecasts with reference projections to 2030 were used for estimating costs to produce electric energy:

- Prices for the Regional Greenhouse Gas Initiative CO2 emission allowances were specified at $24/ton for 2030 and used for estimating the costs to produce electric energy for all generating units.

- Emission allowance prices for other environmental emissions were also assumed but have much less of a significant effect on results.

The study also made several assumptions on the generic capital costs of new resources and costs for transmission development at a high order of magnitude. Annual carrying charge rates were assumed for new resources and transmission development.

Other assumptions were made for the following parameters for each scenario, as appropriate:

- Total resource mix, including retirements, additions, and general locations

- Resource capacity values

- Load profiles (load shape and daily peak), which reflect behind-the-meter resources, mainly PV and EE resources

- Wind and PV profiles, which used hourly profiles developed by the National Renewable Energy Laboratory (NREL) compatible with the hourly system loads used in the GridView simulations

- Profiles for charging plug-in hybrid electric vehicles (PHEVs) at night

- The storage and discharge of energy by pumped-storage generation and battery systems, designed to flatten the net load profile after accounting for all EE, active demand response, all PV (BTM and non-BTM), PHEVs, wind energy, hydro (excluding pumped storage), existing imports, and new imports

- Hydro generation profiles and energy delivery transfers (imports) for existing ties developed using historical diurnal profiles for 2013, 2014, and 2015, which was consistent with the 2016 Scenario Analysis assumptions

- Trigger prices for reducing imports, hydro production, wind generators, and PV outputs to decrease their production during times of oversupply (i.e., spilling) and to respect transmission system limitations

Each of the scenarios reflected differences in the assumptions made for net demand and the resource mix. Table 1-1 compares key assumptions with the Renew Plus scenario, and Table 1-2 shows the assumed values used in the simulations.

Table 1-1
Assumed Changes in Net Demand and Resources from the Renew Plus Scenario for the EE + Offshore,
Onshore Less EE/PV, and Wind Less Nuclear Scenarios (MW Increases and Reductions)

| Year 2030 | Gross Demand | Energy Efficiency | Behind-the-Meter PV (Nameplate) | Utility PV (Nameplate) | Demand Resources | Retirements | Onshore Wind (Nameplate) | Offshore Wind (Nameplate) | Battery Storage | Plug-In Hybrid Electric Vehicles (PHEV) | Add. Imports from Hydro-Québec (HQ) and New Brunswick (NB) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 2016 Scenario 3 Renew Plus (Reference) | Based on 2016 CELT Forecast 33,343 MW | 7,009 MW | 6,000 MW | 6,000 MW | FCA #10, excl. real-time emergency generation (RTEG); added 1,000 MW of active demand resources | All oldest oil/coal approx. 5,600 MW | 4,800 MW | 2,483 MW | 2,500 MW | 4.2 million | 2,000 MW |
| 2017 Scenario A EE + Offshore (Change from 2016 Scenario 3) | No change | Increased by 2,000 MW | Increased by 2,000 MW | Reduced by 2,000 MW | No change | No change | Reduced by 2,800 MW | Increased by 1,000 MW | No change | No change | Reduced by 1,000 MW |
| 2017 Scenario B Onshore Less EE/PV (Change from 2016 Scenario 3) | No change | Reduced to 2016 CELT forecast value of 4,739 MW; approx. 2,300 MW reduced | Reduced to reach target of 4,000 MW; approx. 2,000 MW reduced | Reduced to FCA #10 amounts; approx. 5,800 MW reduced | Removed additional active demand resources | No change | Increased to reach target of 7,000 MW; approx. 2,200 MW increased | No change | Removed battery storage | Removed PHEV | Reduced by 1,000 MW |
| 2017 Scenario C Wind Less Nuclear (Change from 2016 Scenario 3) | No change | No change | No change | No change | No change | Removed an additional 2,122 MW of nuclear generation | Amount determined necessary to replace 2/3 of energy production lost from additional retirements | Amount determined necessary to replace 1/3 of energy production lost from additional retirements | No change | No change | No change |

Table 1-2
Net Demand and Resource Assumptions Used  in the Renew Plus , EE + Offshore, Onshore Less EE/PV, and Wind Less Nuclear Scenarios (MW, millions)

| Year 2030 | Gross Demand 50/50 Summer Peak based on 2016 CELT | Energy Efficiency | Behind-the- Meter PV (Nameplate) | Utility PV (Nameplate) | Demand Resources | Retirements | Onshore Wind (Nameplate) | Offshore Wind (Nameplate) | Battery Storage | PHEV (# of vehicles) | Add. Imports from HQ and NB |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 2016 Scenario 3 Renew Plus (Reference) | 33,343 MW | 7,009 MW | 6,000 MW | 6,000 MW | 1,319 MW, incl. 319 MW from FCA #10 and 1,000 MW of price-responsive active demand resources | All oldest oil/coal 5,577 MW | 4,800 MW | 2,483 MW | 2,500 MW | 4.2 million | 2,000 MW |
| 2017 Scenario A EE + Offshore | 33,343 MW | 9,009 MW | 8,000 MW | 4,000 MW | 1,319 MW | 5,577 MW | 2,000 MW | 3,483 MW | 2,500 MW | 4.2 million | 1,000 MW |
| 2017 Scenario B Onshore Less EE/PV | 33,343 MW | 4,739 MW | 4,000 MW | 154 MW | 319 MW of active demand resources | 5,577 MW | 7,000 MW | 2,483 MW | 0 MW | None | 1,000 MW |
| 2017 Scenario C Wind Less Nuclear | 33,343 MW | 7,009 MW | 6,000 MW | 6,000 MW | 1,319 MW | 7,699 MW (incl. the removal of 2,122 MW of nuclear generation) | 8,906 MW | 4,085 MW | 2,500 MW | 4.2 million | 2,000 MW |

## Key Observations

All the scenarios reflect large amounts of energy efficiency and renewable wind and photovoltaic resources, but the amounts and locations of parameter assumptions affect results. The Renewables Plus scenario shows the effects of the large-scale development of renewable EE, PV, and offshore wind development in southern New England. The EE + Offshore scenario results demonstrate the effects of greater EE and offshore wind but less onshore wind and imports. The Onshore Less EE/PV cases tradeoff greater onshore wind development with less energy efficiency, PV, active demand resources, storage, PHEV, and imports. The Wind Less Nuclear simulations retire 2,122 MW of nuclear generation but add onshore wind and offshore wind.

Many of the results for Scenarios A, B, and C are similar to Scenario 3. Other results differ due to the changes in the resource mix, which reflect different types, amounts, and locations of nonemitting renewable resources. Like Scenario 3, all scenarios could present operational and transmission planning and economic issues.

### Major Results Overall

Some of the major results and observations across all scenarios are as follows:

- Although the amount of resources assumed for each scenario adequately meets the systemwide energy requirements, even when transmission constraints are modeled, the production by price-taking resources simulated as $0/MWh differ;

  - EE + Offshore (Offshore +1,000 MW; Onshore −2,800 MW) reflects the least amount of wind energy production. Onshore Less EE/PV produces more wind energy than the reference case. Wind Less Nuclear has the most energy production from wind resources, especially when the transmission system is unconstrained.

  - Production by natural-gas-fired generation fluctuates with the differences in production by price-taking resources simulated as $0/MWh and assumed retirements. The EE + Offshore scenario produces the least amount of natural-gas-fired electric energy, and the Onshore Less EE/PV scenario produces the most. Constraining the transmission system generally increases the production by gas-fired generation because limiting the Maine interfaces increases the amount of spilled onshore wind. Although the constrained Onshore Less EE/PV scenario uses the most natural-gas-fired generation, the Wind Less Nuclear scenario shows the greatest increase in natural-gas-fired production, resulting from the effects of constraining the transmission system.

- Natural gas consumption, and to a lesser extent other fossil fuels, drives production costs. EE + Offshore has the lowest systemwide production costs, while Onshore Less EE/PV has the highest. The general simulation results show the following:

  - Increased amounts of wind, PV, and EE reduce production costs.

  - Increased amounts of imports reduce production costs.

  - Transmission constraints reduce the system’s ability to utilize onshore wind and increase its reliance on natural gas.

- Retaining existing resources and locating new resources with relatively low production costs near load centers in southern New England reduces systemwide congestion and the need for transmission expansion compared with scenarios that add remote resources without transmission improvements, such as the development of renewable resources and imports in northern New England.

  - The favorable locations of nuclear plants, offshore wind interconnections, EE, and PV, which are generally close to the load centers in southern New England, tend to reduce congestion. This is shown by the EE + Offshore scenario that has the smallest difference of systemwide production costs between the constrained and the unconstrained cases.

  - For the scenarios with resource development in northern Maine, the key transmission interfaces between northern Maine and the load centers in southern New England reach their megawatt-flow limit, which causes the LMP at the sending end to be lower than at the receiving end in the constrained cases. Wind Less Nuclear shows the greatest difference in production costs between the constrained and the unconstrained cases as a result of the largest addition of onshore wind generation.

  - Scenarios with more energy production from price-taking resources result in lower average systemwide LMPs. This is shown by cases with an unconstrained transmission system. Wind Less Nuclear results in the lowest LMPs followed by EE + Offshore; Onshore Less EE/PV has the highest LMPs.

  - Transmission constraints cause the LMP at the sending end to be lower than at the receiving end, especially as additional onshore wind is added in northern Maine. The Wind Less Nuclear scenario shows the largest price separation between BHE/ME (i.e., the Regional System Plan subareas for northeastern Maine/western and central Maine and Saco Valley, New Hampshire) and the rest of the system followed by Onshore Less EE/PV. Congestion follows the same pattern of results.

The results for all the renewable scenarios are very different from today’s system and could present operational, planning, and economic issues. In these scenarios, fossil units, including natural gas combined-cycle units, have relatively low capacity factors compared with today’s system, suggesting the possibility that often, not many generating resources would be on line to provide ramping and regulation services. System operations and planning must address the technical issues associated with large-scale reductions in traditional thermal generating resources that provide inertia and other reliability services.

For example, under the study assumptions for all scenarios, in some simulated hours, the system spills renewable energy production due to surpluses and operates with very few other synchronous resources (i.e., nuclear, traditional steam, and hydro spinning generation) on the New England system. This raises issues of the system’s ability to meet operational requirements for system security, including for regulation, ramping, and reserves. Other system issues would need to be addressed also, such as system protection, power quality, voltage regulation, and stability performance. The large-scale addition of energy efficiency further increases the need to address these issues, such as high system-voltage conditions during light load. Potential solutions include the application of special control systems on inverter-based resources, additional investment in the transmission system, and the use of smart grid technologies.

### High-Order-of-Magnitude Transmission Costs

Similar to the 2016 NEPOOL Scenario Analysis, high-order-of-magnitude cost estimates for integrator and congestion-relief systems in Maine formed the basis of the transmission development costs associated with onshore wind for each individual scenario. The transmission cost estimates do not include individual plant development and interconnection costs, which are assumed as part of the capital costs of generation development. Offshore wind development assumed carefully planned points of interconnection split among Connecticut, Rhode Island, and southeastern Massachusetts that would eliminate the need for any integrator or congestion-relief systems. The points of interconnection are assumed as part of the offshore wind total overnight generator costs.

Transmission development costs increase with greater amounts of assumed onshore wind development. The EE + Offshore scenario results in the least expensive high-order-of-magnitude transmission development costs and the Wind Less Nuclear scenario resulted in the greatest costs.

### Relative Annual Resource Costs

The relative annual resource cost (RARC) metric is a means of comparing the total annual costs of all three scenarios with the constrained case for the Renewables Plus scenario. The RARC accounts for the yearly systemwide production costs, which can be thought of as operating costs, plus it captures the annual costs of capital additions by including the annualized carrying costs for new resources and high-order-of-magnitude transmission-development costs. RARC is thus a measure of the relative total costs for all scenarios  with positive values reflecting higher costs than the constrained case for the Renewables Plus scenario and negative values reflecting lower costs.  Figure 1-1 and Table 1-3 summarize the relative total operating costs and capital costs of the scenarios expressed in billions of dollars,  and Figure 1-2 and Table 1-4 summarize the RARCs shown as cents per kilowatt-hour (kWh). The white dashes in the figures compare the total annual costs of all cases with the constrained case for Renew Plus.

Figure 1-1: Total relative annual resource costs, 2030 (constrained and unconstrained), showing changes compared with 2030 Scenario 3 (constrained) ($ billions)

Notes:  Energy efficiency and solar include costs resulting from individual customer investments that do not reflect the benefits the owners would receive. Production costs reflect the price of carbon emissions at $24/ton.

Table 1-3
Relative Annual Resource Costs, 2030 ($ Millions)(a)

| Transmission | Scenario | Production Cost | 15% Transm. Cost | 15% Ties | 15% Comb. Cycle | 15% New Onshore Wind | 15% New Offshore Wind | 15% Solar | 15% Energy Efficiency | 15% Battery | Total |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Constrained | Renew Plus | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |
|  | EE + Offshore | −352 | −338 | −225 | 0 | −1,047 | 974 | 0 | 863 | 0 | −124 |
|  | Onshore Less EE/PV | 968 | 0 | −225 | 219 | 803 | 0 | −3,013 | −980 | −375 | −2,603 |
|  | Wind Less Nuclear | 396 | 338 | 0 | 0 | 1,508 | 1,560 | 0 | 0 | 0 | 3,802 |
| Unconstrained | Renew Plus | −167 | 825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 658 |
|  | EE + Offshore | −358 | −338 | −225 | 0 | −1,047 | 974 | 0 | 863 | 0 | −130 |
|  | Onshore Less EE/PV | 624 | 1,133 | −225 | 219 | 803 | 0 | −3,013 | −980 | −375 | −1,814 |
|  | Wind Less Nuclear | −152 | 1,607 | 0 | 0 | 1,508 | 1,560 | 0 | 0 | 0 | 4,524 |

- Numbers may not add due to rounding.

Figure 1-2: Total relative annual resource costs, 2030 (constrained and unconstrained), showing changes compared with 2030 Scenario 3 (constrained) (¢/kWh).

Notes:  Energy efficiency and solar include costs resulting from individual customer investments that do not reflect the benefits the owners would receive. Production costs reflect the price of carbon emissions at $19/ton.

Table 1-4
Relative Annual Resource Costs, 2030 (¢/kWh)(a)

| Transmission | Scenario | Production Cost | 15% Transm. Cost | 15% Ties | 15% Comb. Cycle | 15% New Onshore Wind | 15% New Offshore Wind | 15% Solar | 15% Energy Efficiency | 15% Battery | Total |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Constrained | Renew Plus | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 |
|  | EE + Offshore | −0.21 | −0.20 | −0.13 | 0.00 | −0.61 | 0.57 | 0.00 | 0.51 | 0.00 | −0.07 |
|  | Onshore Less EE/PV | 0.67 | 0.03 | −0.12 | 0.14 | 0.57 | 0.09 | −1.70 | −0.48 | −0.22 | −1.01 |
|  | Wind Less Nuclear | 0.23 | 0.20 | 0.00 | 0.00 | 0.89 | 0.92 | 0.00 | 0.00 | 0.00 | 2.23 |
| Unconstrained | Renew Plus | −0.10 | 0.48 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.39 |
|  | EE + Offshore | −0.21 | −0.20 | −0.13 | 0.00 | −0.61 | 0.57 | 0.00 | 0.51 | 0.00 | −0.08 |
|  | Onshore Less EE/PV | 0.45 | 0.75 | −0.12 | 0.14 | 0.57 | 0.09 | −1.70 | −0.48 | −0.22 | −0.51 |
|  | Wind Less Nuclear | −0.09 | 0.94 | 0.00 | 0.00 | 0.89 | 0.92 | 0.00 | 0.00 | 0.00 | 2.66 |

- Numbers may not add due to rounding.

Scenarios with lower RARCs show lower total operating and annual fixed costs and may be viewed as more economical relative to the other scenarios. Annual carrying costs for resource mixes drive the main differences in the total RARCs, with resource additions increasing costs and fewer new resources reducing costs. Lower scenario production costs reduce the total RARC. Although for given scenarios the results show reduced production costs for unconstrained cases compared with the constrained cases, the RARC illustrates the additional annual carrying charges of the associated high-order-of-magnitude transmission-development costs.

Figure 1-1 and Table 1-3, as well as Figure 1-2 and Table 1-4 illustrate differences among the scenarios for 2030. The Onshore Less EE/PV scenario (Scenario B) has the lowest total RARC. The production costs are higher for the Onshore Less EE/PV scenario than the other scenarios with other mixes of large penetrations of renewable resources, but it requires the lowest investment in developing new resources. The figures and tables show significantly higher total RARCs for all the other scenarios (Renew Plus, EE + Offshore, and Wind Less Nuclear scenarios) (Scenarios 3, A, and C) as a result of their higher annual carrying charges for new resources. The Wind Less Nuclear scenario results in the highest RARC due to higher resource and transmission development costs. EE + Offshore has the lowest production costs across all scenarios, but its total RARC is slightly lower than Renewables Plus after consideration of all annual operating and capital costs.

### CO2 Emissions Compared with RGGI Targets

The potential RGGI targets for total CO2 emissions in the New England states range from 13.3 million short tons (a 5.0% reduction) to 19.9 million short tons (a 2.5% reduction). Although RGGI allows for several means of complying with CO2 emission requirements, a comparison of the CO2 emissions targets with the total emissions provides a useful metric to stakeholders.

As shown in Figure 1-3, the scenarios with the large-scale development of zero-emitting resources result in lower CO2 emissions. Some key observations are as follows:

- The Renew Plus and EE + Offshore scenarios satisfy both the New England 2.5% and 5.0% reduction targets by 2030, with or without the transmission system constraints modeled.

- EE+ Offshore produces the least amount of carbon emissions across all scenarios.

- Wind Less Nuclear produces more carbon emissions compared to the Renewables Plus case. When the transmission system is unconstrained, carbon emissions of the Wind Less Nuclear scenario satisfy both the New England 2.5% and 5% reduction targets. When the transmission system is constrained, carbon emission of the Wind Less Nuclear scenario satisfies the New England 2.5% reduction target, but exceeds the New England 5.0% reduction target.

- Onshore Less EE/PV produces the most carbon emissions due to the retirement of zero-emitting nuclear generation and the addition of 1,378 MW of natural gas combined-cycle (NGCC) units. Carbon emissions for this scenario satisfy the New England 2.5% reduction target but exceeds the New England 5.0% reduction target under both constrained and unconstrained conditions of the transmission system.

Figure 1-3: CO2 emissions, 2030 (millions of short tons, %) compared with range of RGGI limits.

## Conclusions and Next Steps

Scenario analyses inform stakeholders of key regional issues and possible ways of addressing these issues. This study makes evident several issues facing the New England region and provides a common framework for future discussions on the need for physical infrastructure and improvements to the wholesale electricity markets. Key observations from the simulation results are as follows:

- Transitioning New England to a system with decreasing amounts of traditional resources (e.g., coal, oil, nuclear) and increasing amounts of renewable resources presents a number of technical and economic issues that would need to be addressed.

- The development of resources close to load centers, such as at existing generation sites, requires comparatively less transmission development than scenarios with the remote development of large amounts of renewable energy resources.

- Regional carbon-reduction obligations may require flexible compliance options (such as proposed by RGGI), additional imports from neighboring systems, and the large-scale development of energy efficiency and renewable resources.

- The study does not address transitions to the studied scenarios, which could raise several issues that need to be addressed as the region develops more energy efficiency and inverter-based resources, such as wind generation, PV, and HVDC ties. Some considerations regarding these issues are offered below:

  - Observability, controllability, and interconnection performance are key technical issues that must be addressed for distributed resources and the large-scale development of wind generation resources.

  - Advanced software will facilitate future analysis of the system, especially probabilistic simulations that consider the production of variable (i.e., intermittent) energy resources. Understanding the needs of intrahour ramping, regulation, and reserve requirements becomes increasingly important with the large penetration of variable energy resources.

  - Efficient storage technologies, such as pumped storage and distributed storage, and the ability to make rapid changes in tie schedules can provide systemwide flexibility and could facilitate the integration of variable energy resources.

# Introduction

This report presents the results of the ISO New England (ISO) 2017 Economic Study conducted in response to a request submitted by Conservation Load Foundation (CLF) and discussed with the Planning Advisory Committee (PAC). The report documents the methodologies, data and assumptions, simulation results, and observations of an economic study of the ISO New England power system that stakeholders can use to assess the implications of public policy on market design, system reliability and operability, resource costs and revenues for new generation, relative cost, and emissions.

## Economic Study Process

As a part of the regional system planning effort, the ISO may conduct economic planning studies each year, as specified in Attachment K of its Open-Access Transmission Tariff (OATT). The economic studies provide information on system performance, such as estimated production costs, load-serving entity (LSE) energy expenses, transmission congestion, and environmental emission levels. The ISO may annually perform studies in response to requests by participants that analyze various future scenarios. This information can assist stakeholders in evaluating various resource and transmission options that can affect New England’s wholesale electricity markets. The studies may also assist policymakers who formulate strategic visions of the future New England power system.

The role of the PAC in the economic study process is to discuss, identify, and otherwise assist the ISO by advising on the proposed studies. The ISO then performs up to three economic studies and subsequently reviews all results and findings with the PAC.

## Disclaimer

Scenario analyses inform stakeholders about different future systems. These hypothetical systems should not be regarded as the ISO’s vision of realistic future development, plans, projections, and preferences. The scenarios do not fully capture current laws and regulations, such as the timeframe for renewable resource development and their cost implications. They do, however, identify several key future physical and market issues the region must address, for the large-scale development of renewable resources. It also summarizes high-order-of-magnitude transmission system expansion costs, which provide cost information but do not identify particular facilities or include detailed plans associated with any of the scenarios.

## 2016 NEPOOL Scenario Analysis Process and Goals

In April 2017, CLF submitted its request to the ISO for a scenario analysis of the ISO New England system under a range of assumptions. As indicated by CLF, the goal of the study request was to explore scenarios with similar or lower total system CO2 emissions and a lower relative annual resource cost (RARC) than the 2016 Economic Study Scenario 3, set up with the generation fleet meeting the states’ existing Renewable Portfolio Standards (RPSs) and the system having additional renewable/clean energy resources. Exploring several scenarios provides New England Power Pool (NEPOOL) participants, regional electricity market stakeholders, policymakers, and consumers, with information, analyses, and observations on the potential impacts on the ISO New England markets of implementing public policies in the New England states. The study results summarize several key economic metrics and CO2 emission levels in New England for each of the scenarios.

CLF worked with the ISO to collaboratively identify the mixes of additional conventional and renewable technology resources to be included in each scenario, the respective operating profiles or drivers, operating costs, and environmental goals. In fulfillment of its tariff obligations, the ISO presented the scope of work, assumptions, and results to the PAC, who provided input on draft items of the study scope during a PAC meeting and on the draft results.

## Topics Addressed

The sections that follow describe the scenarios (Section 3), the methodology used and metrics analyzed (Section 4), the assumptions applied (Section 5), and the main results and observations (Section 6). Section 7 summarizes the key conclusions; supplemental market, operational, and transmission issues; and how policymakers and other stakeholders might be able to use this information and data.

The report includes hyperlinks throughout to presentations and other materials that contain more detailed information. These links are to PAC presentations on the background and scope of the analysis; the development of the scenarios, assumptions, methodology, and metrics used; and the draft and final results. The links also reference the 2016 NEPOOL Scenario Analysis, which provides much of the detailed background information on its Scenario 3, and the 2017 Economic Study presentations, draft report, and stakeholder comments. The links are up to date as of the publication of the report.

# Description of the Scenarios

The analysis examined three scenarios based on Scenario 3 of the 2016 NEPOOL Scenario Analysis, the Renewables Plus Scenario. While most scenario assumptions and inputs remained the same as Scenario 3, the 2017 Scenarios A, B, and C reflect changes in the resource mix, including energy efficiency (EE), behind-the meter photovoltaics (BTM PV), utility-scale PV, active demand resources, onshore wind, offshore wind, battery storage, plug-in hybrid electric vehicles (PHEVs), and imports from Canada. Section 5 discusses the assumptions in more detail, including various combinations of the assumed parameters.

## Scenario 3—“Renewables Plus” (also “Renew Plus”)—Generation Fleet Meets Existing RPSs, and Additional Renewable/Clean Energy Resources Are Used Above the Existing RPS Targets

Consistent with the 2016 NEPOOL Scenario Analysis, the basis for Scenario 3 was the mix of generation resources expected as of 2019/2020 and the gross demand and amounts of photovoltaics and energy efficiency reported in the ISO’s 2016 Report on Capacity, Energy, Load, and Transmission (2016 CELT Report). Imports on existing ties were based on historical profiles, and all physical renewable/clean energy resources as of April 1, 2016—interconnected, under construction, or with “I.3.9” approval—were used to meet the RPS requirements. Scenario 3, however, added additional renewable/clean energy resources (i.e., behind-the meter and utility-scale PV, EE, and wind, and hydroelectric imports) to replace generation retirements and provide zero-emitting energy. The renewable resource locations were consistent with the ISO’s PV forecast and the Interconnection Request Queue (the queue) as of April 1, 2016. This scenario also added two new tie lines with capacity contracts, plug-in hybrid electric vehicles, and battery energy systems. The resource mix and demand differ markedly from historic trends. The amount of resources added exceeded the assumed net Installed Capacity Requirement (NICR).

## Scenario A—“EE + Offshore”—Change in Mix of New Renewable/Clean Energy Resources, with Emphasis on Energy Efficiency and Offshore Wind

Scenario A increases the amounts of EE and offshore wind but reduces the amounts of onshore wind and new imports from Canada. The scenario trades off equal amounts of BTM PV with utility PV.

## Scenario B—“Onshore Less EE/PV”—Change in Mix of New Renewable/Clean Energy Resources, with Emphasis on Onshore Wind

Scenario B reduces the amounts of EE, BTM and utility PV, active demand resources, battery storage, PHEV, and imports from Canada. The scenario, however, adds 2,200 megawatts (MW) of onshore wind.

## Scenario C—“Wind Less Nuclear”—Replacement of Some of the Baseload Nuclear Generation with Renewable/Clean Energy Resources

Scenario C retires 2,122 MW of nuclear generation. Onshore wind is added to make up for two-thirds of the lost energy production, with additional offshore wind generators providing the remaining one-third.

## Overview of Scenario Parameters

Table 3-1 provides an overview of the main parameter changes from Scenario 3 used in the simulations for retirements, load, resource capacity, and external ties and transfer limits. Table 3-2 provides the nameplate values of the resource mix. Section 5 describes the assumptions used in greater detail.

Table 3-1
Assumed Changes in Net Demand and Resources from the Renew Plus Scenario for the
EE + Offshore, Onshore Less EE/PV, and Wind Less Nuclear Scenarios (MW increases and reductions)

| Year 2030 | Gross Demand | Energy Efficiency | Behind-the-Meter PV (Nameplate) | Utility PV (Nameplate) | Demand Resources | Retirements | Onshore Wind (Nameplate) | Offshore Wind (Nameplate) | Battery Storage | Plug-In Hybrid Electric Vehicles | Add. Imports from Hydro-Québec (HQ) and New Brunswick (NB) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 2016 Scenario 3 Renew Plus (Reference) | Based on 2016 CELT Forecast 33,343 MW | 7,009 MW | 6,000 MW | 6,000 MW | FCA #10, excl. real-time emergency generation (RTEG); added 1,000 MW of active demand resources | All oldest oil/coal approx. 5,600 MW | 4,800 MW | 2,483 MW | 2,500 MW | 4.2 million | 2,000 MW |
| 2017 Scenario A EE + Offshore (Change from 2016 Scenario 3) | No change | Increased by 2,000 MW | Increased by 2,000 MW | Reduced by 2,000 MW | No change | No change | Reduced by 2,800 MW | Increased by 1,000 MW | No change | No change | Reduced by 1,000 MW |
| 2017 Scenario B Onshore Less EE/PV (Change from 2016 Scenario 3) | No change | Reduced to 2016 CELT forecast 4,739 MW; approx. 2,300 MW reduced | Reduced to reach target of 4,000 MW; approx. 2,000 MW reduced | Reduced to FCA #10 amounts; approx. 5,800 MW reduced | Removed additional active demand resources | No change | Increased to reach target of 7,000 MW; approx. 2,200 MW increased | No change | Removed battery storage | Removed PHEV | Reduced by 1,000 MW |
| 2017 Scenario C Wind Less Nuclear (Change from 2016 Scenario 3) | No change | No change | No change | No change | No change | Removed an additional 2,122 MW of nuclear generation | Amount determined necessary to replace 2/3 of energy production lost from additional retirements | Amount determined necessary to replace 1/3 of energy production lost from additional retirements | No change | No change | No change |

Table 3-2
Net Demand and Resource Assumptions used  in the Renew Plus , EE + Offshore,
Onshore Less EE/PV, and Wind Less Nuclear Scenarios (MW, Millions)

| Year 2030 | Gross Demand 50/50 Summer Peak based on 2016 CELT | Energy Efficiency | Behind-the- Meter PV (Nameplate) | Utility PV (Nameplate) | Demand Resources | Retirements | Onshore Wind (Nameplate) | Offshore Wind (Nameplate) | Battery Storage | PHEV (# of vehicles) | Add. Imports from HQ and NB |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 2016 Scenario 3 Renew Plus (Reference) | 33,343 MW | 7,009 MW | 6,000 MW | 6,000 MW | 1,319 MW, incl. 319 MW from FCA #10 and 1,000 MW of price-responsive active demand resources | All oldest oil/coal 5,577 MW | 4,800 MW | 2,483 MW | 2,500 MW | 4.2 million | 2,000 MW |
| 2017 Scenario A EE + Offshore | 33,343 MW | 9,009 MW | 8,000 MW | 4,000 MW | 1,319 MW | 5,577 MW | 2,000 MW | 3,483 MW | 2,500 MW | 4.2 million | 1,000 MW |
| 2017 Scenario B Onshore Less EE/PV | 33,343 MW | 4,739 MW | 4,000 MW | 154 MW | 319 MW of active demand resources | 5,577 MW | 7,000 MW | 2,483 MW | 0 MW | None | 1,000 MW |
| 2017 Scenario C Wind Less Nuclear | 33,343 MW | 7,009 MW | 6,000 MW | 6,000 MW | 1,319 MW | 7,699 MW (incl. the removal of 2,122 MW of nuclear generation) | 8,906 MW | 4,085 MW | 2,500 MW | 4.2 million | 2,000 MW |

# Methodology and Metrics

This section discusses the methodology used in the 2017 Economic Study to simulate the various futures and the metrics used to study the different scenarios.

## Methodology

ABB’s GridView program, a common simulation tool vetted before stakeholders, calculates least-cost transmission-security-constrained unit commitment and economic dispatch under differing sets of assumptions and minimizes production costs for a given set of unit characteristics. The program can explicitly model a full network, but the New England study model used a “pipe and bubble” format, with “pipes” representing transmission interfaces connecting the “bubbles” representing the various planning areas.

The ISO system was modeled as a constrained single area for unit commitment, and regional resources were economically dispatched in the simulations to respect the assumed transmission system security constraints under normal and contingency conditions. Depending on the case, the model dispatched up to approximately 900 units (new and existing) in New England. For each scenario’s set of resources (with their various operating characteristics), the simulation “dispatched” power plants to meet different levels of customer demand in every hour of the year being analyzed. These simulations established a wide array of hypothetical data about how the electric power system “performed” in terms of reliability, economics, and environmental indicators and the effects of transmission system constraints.

In this analysis, all data sets were created for the year 2030. The choice of 2030 as a single study year was driven by the observation made in the 2016 NEPOOL Scenario Analysis that disparities of results among the cases appeared more evident in 2030 than for an earlier year (2025). In addition, a later year such as 2030 better captures longer-term strategic results.

## Metrics Analyzed

GridView simulated regional electricity production, the costs to produce and purchase it, energy interchange profiles with neighboring systems, and some of the potential environmental impacts, taking into account the set of assumptions applied for each scenario (as described in Section 5). Several metrics, such as production costs, are the direct result of the GridView simulation outputs, while others, including relative annual resource costs (RARCs) (see Section 6.3), combined GridView metrics with estimates that were not direct outputs of the program (e.g., annual carrying charges). The ISO developed additional metrics, including high-order-of-magnitude estimates of transmission-development costs (see Section 6.1.6). Table 4-1 summarizes the metrics generated for analyzing the scenarios.

Table 4-1
Metrics Analyzed in the 2017 Economic Study

| Economic | Resource | Transmission(a) | Environmental |
| --- | --- | --- | --- |
| Systemwide production costs, including energy production costs due to fuel, unit-commitment costs, and environmental emissions costs (million dollars/year; $M/year) | Total production in gigawatt-hours (GWh) and percentage for each resource type, including imports | Percentage of time that flows reach or exceed 100% of the interface limit for constrained and unconstrained cases | Total air emissions of carbon dioxide (CO2) compared with Regional Greenhouse Gas Initiative (RGGI) regional goal (kilotons; ktons)(b) |
| Average locational marginal prices ($/megawatt-hour; MWh) |  | Seasonal flow-duration curves for all monitored interfaces(c) | Total “bottled,” price-taking resources (i.e., PV, wind, hydro, and imports) by Regional System Plan (RSP) subarea (expressed in MWh and percentage)(d) |
| Load-serving entity energy expenses and uplift (i.e., make-whole payments) ($M/year) |  | Interface flows for all monitored interfaces in representative summer and winter peak hours(e) | Ability of renewable resource mix to physically meet regional Renewable Portfolio Standards. |
| Congestion ($M/year) |  | Preliminary high-order-of-magnitude transmission-development costs (billion dollars [$B] and $B/year) |  |
| Relative annual resource costs encompassing all annual operating costs and annual carrying charges for new resources and high-order-of-magnitude transmission-development costs ($M/year and $/kilowatt-hour; kWh) |  | Maine interface flow statistics compared with interface limits |  |

(a) 	The study does not include specific transmission planning studies but identifies approximate costs for transmission development on the basis of the interface flows and the extent of their congestion.

(b) 	The Regional Greenhouse Gas Initiative is a nine-state program in the Northeast to reduce the CO2 emissions from fossil power plants 25 MW and larger in these states. Each state is allocated a share (allowance) of an annual emissions cap on the basis of historical emissions and negotiations; one allowance equals the limited right to emit one short ton of CO2. The RGGI states are Connecticut, Delaware, Maine, Maryland, Massachusetts, New Hampshire, New York, Rhode Island, and Vermont. Additional information about RGGI is available at https://www.rggi.org/.

(c)	The study created seasonal flow duration curves for all monitored interfaces, which are not presented in this report but are available in the ISO’s PAC presentation, 2017 Economic Study (February 14, 2018), slides 66–7), https://www.iso-ne.com/static-assets/documents/2018/02/a3_2017_economic_study.pdf.

(d) “Bottled” refers to price-taking resources that cannot produce energy because of transmission system limitations that constrain production or hours when demand is insufficient to consume the full amount of potentially available production.

(e)  Interface flows for summer and winter peak hours are not presented in this report but are available at the link indicated in table note c, above, slides 61–2.

The study does not include detailed transmission analysis that would be required to fully develop plans that identify and price transmission upgrades. The results, however, provide transmission development costs that are suitable for comparing high-order-of-magnitude dollars across the scenarios.

# Assumptions

This section summarizes the major assumptions applied in the study, all of which were discussed with the PAC. The study made a set of common assumptions of the electric power system and markets and several scenario-specific assumptions. Common assumptions were made for the following parameters for the constrained and unconstrained cases, which are identical to those used in the 2016 NEPOOL Scenario Analysis for the 2030 study year:

- Annual and peak energy use, active demand resource (ADR) profiles, and capacity needs

- Fuel prices

- Generating resource capital costs and resource production characteristics (e.g., heat rates, outage rates, maintenance schedules, wind, PV, and hydro profiles, and others)

- Internal and external transmission interface transfer limits and interchanges with neighboring systems

- Transmission development capital cost methodology and dollar amounts

- Air emission regulatory targets for CO2 and emission allowance costs

The study also reflected assumptions for pumped-storage generating units, electric batteries, and plug-in hybrid electric vehicles and the energy profiles for imports from neighboring systems. The assumptions for the overall resource mix based on resource expansions and retirements, resource capacity values and locations, and external ties varied among the scenarios. The assumptions about the "base" amounts of PV and EE development also varied, although the hourly profiles for each resource type were the same.

## Public Policies Assumed

The following public policies were assumed to be in effect in various ways in the six New England states in the timeframe of the study and could affect the growth of renewable resources and their locations, reductions in net demand, and energy production costs used in the scenarios:

- The states’ Renewable Portfolio Standards’ (RPSs) and other renewable resource goals as of April 1, 2016, which set increasing targets in the six New England states for the procurement of Renewable Energy Credits (RECs) by load-serving entities

- Energy-efficiency programs, which lower the amount of physical energy that must be produced and distributed. The study assumed that EE resources help meet the NICR.

- Behind-the-meter solar and net-metering programs, which serve to decrease net load as seen by ISO New England and consequently reduce the amount of NICR needed to reliably serve loads

- Regional Greenhous Gas Initiative CO2 emissions allowance pricing, which affects production costs and regional emission levels

The study is not designed to evaluate specific public policies or advocate for any particular outcome.

## Peak Demand, Annual Energy Use, and Demand Modifiers

The study used a 2006 load shape and readily available standard models for creating a time-synchronized gross demand load profile and 2006 solar insolation patterns to represent BTM PV. The model for demand that accounted for BTM PV was determined by reducing the gross system demand by the assumptions for BTM PV production for every hour of the year. Across all scenarios, the gross peak demand for 2030 was the same as the value used for the Renew Plus scenario of the 2016 NEPOOL Scenario Analysis. The EE + Offshore, Onshore Less EE/PV, and Wind Less Nuclear scenarios reflect the megawatt amounts of BTM PV, battery storage, and PHEVs specified in the economic study request.

The scenarios also modeled several resources and behind-the-meter load modifiers as negative loads to simulate an overall reduced hourly demand that served as an input to the dispatch of generating resources. Individual technology profiles were used for energy efficiency, BTM and non-BTM PV, and wind and hydro generation. The PHEVs’ model used a profile to increase demand during off-peak hours that assumed battery use only for transportation and not discharged in support of the power system. Other battery storage systems and pumped-storage hydro charging profiles were modeled as added load, while their generation profile was modeled as negative load, which together equalized the gross load net of all other modifiers and imports.

### Peak Demand and Annual Energy Use

Table 5-1 shows the assumptions used for gross 50/50 peak demand and annual energy use for all scenarios for 2030. The values for 2030 were extrapolated from the values for 2025 contained in the 2016 CELT Report using the rate of growth for the 2025 values compared with the values for 2024, which were the last two years of the ISO’s forecast.

Table 5-1
Gross New England 50/50 Peak Demand and Annual Energy Use for All Scenarios

| Parameter | 2025 | 2030 |  |
| --- | --- | --- | --- |
| Gross New England 50/50 peak demand (MW) | 31,794 |  | 33,343(a) |
| Gross New England 50/50 annual energy use (GWh) | 152,731 |  | 158,969(b) |

(a) Gross 50/50 peak demand for 2030 = (31,794 MW) × {(31,794 ÷ 31,493)5} = 33,343 MW.

(b) Gross annual energy use for 2030 = {(152,731 GWh ÷ 151,513 GWh)5} × 152,731 GWh = 158,969 GWh.

### Passive Demand and Behind-the Meter PV Resources

The US Department of Energy (DOE) National Renewable Energy Laboratory (NREL) profiles for 2006 were used to synchronize PV production with the gross load profile. For Scenario 3, the capacity and energy assumptions for passive demand resources and BTM PV are consistent with the 2016 NEPOOL Scenario Analysis. For 2030, BTM PV nameplate installations totaling 6,000 MW were estimated to reduce gross peak loads by 25.4%. The 6,000 MW of BTM PV nameplate rating in 2030 results in 7,695 GWh of energy production.

Table 5-2 summarizes the assumptions for passive demand and BTM PV resources for all the scenarios for 2030.

Table 5-2
Capacity and Energy Assumptions for Passive Demand and BTM PV Resources 2030

| Parameter | Reference Renew Plus | Scenario A EE + Offshore | Scenario B Onshore Less EE/PV | Scenario C Wind Less Nuclear |
| --- | --- | --- | --- | --- |
| Passive demand-resource capacity (MW) | 7,009 | 9,009 | 4,739 | 7,009 |
| Passive demand-resource energy (GWh) | 53,360 | 68,590 | 25,834 | 53,360 |
| Behind-the-meter PV reductions in peak load/nameplate MW | 1,524/6,000 25.4% of nameplate | 1,536/8,000 19.2% of nameplate | 1,264/4,000 31.6% of nameplate | 1,524/6,000 25.4% of nameplate |
| Behind-the-meter PV energy production (GWh) | 7,695 | 10,260 | 5,130 | 7,695 |

### Plug-In Hybrid Electric Vehicles

Except for the EE + Offshore scenario (Scenario B), a total of 4.2 million plug-in hybrid electric vehicles were added to all scenarios. Locations were distributed by state, in accordance with the NEPOOL request, and further distributed by Regional System Plan “bubbles” (refer to Figure 5-4 below) in proportion to load. Table 5-3 shows the assumed distribution of PHEVs by state for 2030. The study assumed that the PHEVs distribute charging over the night hours and do not discharge back into the grid.

Table 5-3
Assumed Distribution of PHEVs by State for 2030 for the Renew Plus,
EE + Offshore, and Wind Less Nuclear Scenarios

| State | Percentage | 2030 No. of Vehicles |
| --- | --- | --- |
| Connecticut | 23 | 966,000 |
| Maine | 12 | 504,000 |
| Massachusetts(a) | 43 | 1,806,000 |
| New Hampshire | 11 | 462,000 |
| Rhode Island | 6 | 252,000 |
| Vermont | 5 | 210,000 |
| New England | 100 | 4,200,000 |

(a) The total for Massachusetts was reduced by 1% to eliminate a rounding issue.

Table 5-4 shows the PHEV characteristics. Figure 5-1 shows the daily PHEV charging profile.

Table 5-4
PHEV Characteristics for 2030 for the Renew Plus, EE + Offshore,
and Wind Less Nuclear Scenarios

| Characteristic | 2030 |
| --- | --- |
| Penetration (million PHEVs) | 4.2 |
| Max hourly off-peak charging (MW) | 5,825 |
| Annual charging energy (GWh) | 12,507 |

Figure 5-1: Daily PHEV charging profile for the EE + Offshore and Wind Less Nuclear Scenarios for 4.2 million vehicles, 2030 (MW).

## Capacity Assumptions

The study included assumptions regarding the needed amount of resources and reserves, resource deliverability, capacity values and summer seasonal claimed capability (SCC), nameplate values, retirements and additions, Renewable Portfolio Standards, storage amounts and operating profiles, and the overall resource mix. Resources were divided into capacity resources that meet the net Installed Capacity Requirement and energy-only resources.

Resources that received capacity supply obligations through the tenth Forward Capacity Auction (FCA #10) were considered part of the resource mix. Summer SCC values were assumed for all units having capacity supply obligations in FCA #10, but capacity values were used for wind and PV resources. Resource deliverability was assumed for all new resources; the study did not conduct detailed FCA-deliverability tests.

Additional generation without FCA #10 obligations were assumed to be, as of April 1, 2016, operating, under construction (but not cleared in an FCA), or having I.3.9 approval and still in the ISO’s Interconnection Request Queue. For all resources, operating characteristics (e.g., for heat rate, ramp rate, minimum down time, minimum up time) were used where data were available, and generic information was modeled for other generators, which was suitable for this study. Additions of natural gas combined-cycle (NGCC) units not in the queue as of April 1, 2016, but needed to meet the NICR were first added at sites of retired resources up to the size of the retired resources and, if necessary, added at the Hub.

The scenarios assumed that an installed reserve margin of 14% above the gross 50/50 peak load (minus the peak load reduction due to the BTM PV) would meet the systemwide net ICRs. This base scenario assumption is reasonable when considering the NICR summarized in recent Regional System Plans. In this calculation, energy efficiency was considered a resource that contributes toward meeting the NICR.

Operating-reserve requirements were modeled based on the first- and second-largest loss-of-source system contingencies. The system’s current operating-reserve requirements were assumed. For 10-minute reserves, the study assumed that the system needed 125% of the first-contingency (N-1) amount, divided evenly between 10-minute spinning reserve (TMSR) (50%) and 10-minute nonspinning reserve (TMNSR) (50%). Thirty-minute operating reserve (TMOR) was not modeled because it was assumed adequate and provided by hydro, pumped storage, and fast-start resources.

Table 5-5 summarizes each scenario’s capacity assumptions for 2030 for meeting or exceeding the net Installed Capacity Requirement. The sections that follow explain the assumptions in more detail, including the energy-production profiles for each type of resource.

Table 5-5
Summary of Capacity Assumptions Used in the Scenarios, 2030 (MW)

| Parameter | Reference Renew Plus | Scenario A EE + Offshore | Scenario B Offshore Less EE/PV | Scenario C Wind Less Nuclear |
| --- | --- | --- | --- | --- |
| Renewables (biofuels, landfill gas, etc.) | 976 | 976 | 976 | 976 |
| Solar(a) | 2,462 | 1,662 | 62 | 2,462 |
| Forecasted EE and active demand resources without real-time emergency generation (RTEG) | 8,328 | 10,328 | 5,058 | 8,328 |
| Nuclear | 3,347 | 3,347 | 3,347 | 1,225 |
| Hydro and pumped storage | 3,116 | 3,116 | 3,116 | 3,116 |
| Resource serving Citizen Block load (on the border served from Hydro-Québec) | 30 | 30 | 30 | 30 |
| Imports(b) | 3,006 | 2,006 | 2,006 | 3,006 |
| Wind capacity value | 1,900 | 1,472 | 2,472 | 3,448 |
| Gas after retirements (SCC) | 16,011 | 16,011 | 16,011 | 16,011 |
| Oil after retirements (SCC) | 2,114 | 2,114 | 2,114 | 2,114 |
| Coal after retirements (SCC) | 0 | 0 | 0 | 0 |
| Total capacity for existing resource after retirements | 41,290 | 41,062 | 35,192 | 40,716 |
| Battery storage (SCC) | 2,500 | 2,500 | 0 | 2,500 |
| Renewables to meet RPSs (capacity value) | 0 | 0 | 0 | 0 |
| Total capacity for existing resource plus storage and RPS renewables | 43,790 | 43,562 | 35,192 | 43,216 |
| Net Installed Capacity Requirement(c) | 36,273 | 36,260 | 36,570 | 36,273 |
| NGCC capacity added to replace retirement and to meet NICR | 0 | 0 | 1,378(d) | 0 |

(a)	Solar capacity includes FCA #10 cleared solar capacity (62 MW), plus any additional capacity from non-behind-the-meter (utility) PV resources.

(b)	Import capacity includes New York Power Authority imports under a long-term contract plus the average capacity supply obligations associated with energy flows from New Brunswick, Highgate, and Phase II occurring during 2013, 2014, and 2015. Scenarios “Renew Plus” and “Wind Less Nuclear” assume additional import capacity of 2,000 MW, Scenarios “EE + Offshore” and “Onshore Less EE/PV” assume additional import capacity of 1,000 MW, respectively.

(c)	The NICR calculation was based on assuming 114% of the net 50/50 peak load. Summer SCC values were assumed for all units having capacity supply obligations in FCA #10, but capacity values were used for wind and PV resources.

(d)	Scenario “Onshore Less EE/PV” requires an additional 1,378 MW of capacity from new NGCC units to meet the NICR.

### Capacity Value Assumptions

Consistent with Table 5-5, Figure 5-2 and Table 5-6 show the capacity value assumptions used for each resource type in each scenario for 2030.

Figure 5-2: 2030 capacity value assumptions by resource type (MW).

Note: “ES” stands for energy storage. “EE/DR” includes energy efficiency (i.e. passive demand resources), plus active demand resources, plus price-responsive demand (PRD).

Table 5-6
Capacity Value Assumptions for Various Resources, 2030 (MW)(a)

| Scenario | Wood | Onshore Wind | Offshore Wind | PV | Oil | NG | Import | Coal | EE/DR | Hydro/ES | Misc. | Nuc |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Renew Plus | 489 | 1,155 | 745 | 2,462 | 2,114 | 16,011 | 3,006 | 0 | 8,328 | 5,616 | 517 | 3,347 |
| EE + Offshore | 489 | 427 | 1,045 | 1,662 | 2,114 | 16,011 | 2,006 | 0 | 10,328 | 5,616 | 517 | 3,347 |
| Onshore Less EE/PV | 489 | 1,727 | 745 | 62 | 2,114 | 17,389 | 2,006 | 0 | 5,058 | 3,116 | 517 | 3,347 |
| Wind Less Nuclear | 489 | 2,222 | 1,226 | 2,462 | 2,114 | 16,011 | 3,006 | 0 | 8,328 | 5,616 | 517 | 1,225 |

(a) Typical capacity values are used in this study; 26% for onshore wind and 30% for offshore wind.

All scenarios assumed that the nuclear units at Millstone and Seabrook would be the first resources dispatched so that they would operate at full output and would only be reduced in the event the net loads after EE and PV could not absorb their energy. In Scenario C, the maximum amount of nuclear generation was limited to 1,225 MW because Scenario C assumed the retirement of 2,122 MW of nuclear generation, proportionally spread among existing nuclear units.

PV resources used the NREL database for photovoltaic production profiles in 2006.

### Wind Generation

Similar to photovoltaic resource production profiles, the study used NREL data to build the energy production profiles for onshore and offshore wind resources and calculate the capacity values for wind generation, which are based on reliability hours and a percentage of the nameplate assumptions. Figure 5-3 shows the wind nameplate capacities assumed in each scenario for 2030. The figure includes wind resource additions with I.3.9 approvals but not in service as of April 1, 2016. Table 5-7 shows the data for the onshore and offshore wind additions and totals.

Figure 5-3: Wind nameplate capacities assumed for the wind resources, 2030 (MW).

Note: “BHE” represents northeastern Maine; “ME,” western and central Maine/Saco Valley, New Hampshire; “VT,” Vermont/southwestern New Hampshire; “NH,” northern, eastern, and central New Hampshire/eastern Vermont, and southwestern Maine; “WMA,” western Massachusetts; “SEMA/RI,” southeastern Massachusetts/Newport, Rhode Island, and Rhode Island/bordering Massachusetts.

Table 5-7
Onshore and Offshore Wind Additions and Totals for All the Scenarios, 2030 (MW)

| Scenario | Offshore Wind In Service | SEMA/RI Offshore Wind Added | Total Offshore | Onshore Wind In Service | BHE Wind Added | ME Wind Added | NH Wind Added | VT Wind Added | WMA wind added | Onshore Additions | Maine- Only Additions | Total Onshore Wind | Total Onshore and Offshore Wind |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Renew Plus | 0 | 2,483 | 2,483 | 1,039 | 2,661 | 991 | 63 | 16 | 31 | 3,761 | 3,652 | 4,800 | 7,283 |
| EE + Offshore | 0 | 3,483 | 3,483 | 1,039 | 675 | 251 | 20 | 5 | 10 | 961 | 926 | 2,000 | 5,483 |
| Onshore Less EE/PVs | 0 | 2,483 | 2,483 | 1,039 | 4,185 | 1,558 | 125 | 31 | 63 | 5,961 | 5,743 | 7,000 | 9,483 |
| Wind Less Nuclear | 0 | 4,085 | 4,085 | 1,039 | 5,523 | 2,056 | 164 | 41 | 83 | 7,867 | 7,579 | 8,906 | 12,991 |

In all scenarios, onshore wind resources were scaled up from the amount assumed to be in service, until the scenario’s desired nameplate amount was reached. Offshore wind was added off the coast of southeastern Massachusetts and Rhode Island at the same locations as used in the 2016 NEPOOL Scenario Analysis and used production profiles supplied by NREL. Although the plants are assumed to interconnect mainly in SEMA/RI, some interconnections to Connecticut were assumed that would eliminate costs associated with the interconnector and congestion-relief systems between SEMA/RI and CT (see Section 5.7.1).  Table 5-8 summarizes the assumptions used for onshore and offshore wind generation nameplate values for the 2030 study year.

Table 5-8
Assumptions Used for Onshore and Offshore Wind Generation Nameplate Values, 2030 (MW)

| Variable(a) | Reference Renew Plus | Scenario A EE + Offshore | Scenario B Onshore Less EE/PV | Scenario C Wind Less Nuclear |
| --- | --- | --- | --- | --- |
| Existing onshore wind in service | 1,039 | 1,039 | 1,039 | 1,039 |
| SEMA/RI offshore wind added | 2,483 | 3,483 | 2,483 | 4,085 |
| BHE wind added | 2,661 | 675 | 4,185 | 5,523 |
| ME wind added | 991 | 251 | 1,558 | 2,056 |
| NH wind added | 63 | 20 | 125 | 164 |
| VT wind added | 16 | 5 | 31 | 41 |
| WMA wind added | 31 | 10 | 63 | 83 |

- Additions include wind resources with I.3.9 approval.

### Resource Retirements

For all scenarios, the retirement of existing resources is in accordance with FCA #10 results; additional retirement assumptions were made consistent with the resource assumptions for the Renew Plus scenario in the 2016 NEPOOL Scenario Analysis. Table 5-9 lists the assumed retirements of all conventional oil- and coal-fired steam units by 2030 (including dual-fuel units). In addition, Scenario C retires 2,122 MW of nuclear generation, which was removed from the simulations proportionally with the SCC values for Millstone and Seabrook.

Table 5-9
Assumed Generating Unit Retirements by 2030 (MW)

| Name | RSP Subarea(a) | Fuel Type | FCA #10 Summer Capacity (MW) | In-Service Date | Cumulative Capacity (MW) |
| --- | --- | --- | --- | --- | --- |
| Schiller 4 | NH | Coal | 48 | 1952 | 48 |
| Montville 5 | CT | Oil | 81 | 1954 | 129 |
| Schiller 6 | NH | Coal | 48 | 1957 | 176 |
| West Springfield 3 | WMA | Dual | 94 | 1957 | 271 |
| Yarmouth 1 | SME | Oil | 50 | 1957 | 321 |
| Middletown 2 | CT | Oil | 117 | 1958 | 438 |
| Yarmouth 2 | SME | Oil | 51 | 1958 | 489 |
| Merrimack 1 | NH | Coal | 108 | 1960 | 597 |
| Middletown 3 | CT | Oil | 234 | 1964 | 831 |
| Yarmouth 3 | SME | Oil | 115 | 1965 | 945 |
| Bridgeport Harbor 3 | SWCT | Coal | 383 | 1968 | 1,329 |
| Canal 1 | SEMA | Oil | 547 | 1968 | 1,876 |
| Merrimack 2 | NH | Coal | 330 | 1968 | 2,206 |
| Montville 6 | CT | Oil | 405 | 1971 | 2,611 |
| Middletown 4 | CT | Oil | 400 | 1973 | 3,011 |
| Newington 1 | NH | Oil | 400 | 1974 | 3,411 |
| Mystic 7 | BOSTON | Dual | 571 | 1975 | 3,982 |
| New Haven Harbor 1 | CT | Oil | 448 | 1975 | 4,430 |
| Canal 2 | SEMA | Oil | 545 | 1976 | 4,975 |
| Yarmouth 4 | SME | Oil | 602 | 1978 | 5,577 |
| Total |  |  |  |  | 5,577 |

(a) 	The RSP subareas above are as follows: BOSTON (all caps) covers Greater Boston, including the North Shore; CT is northern and eastern Connecticut; NH is northern, eastern, and central New Hampshire/eastern Vermont and southwestern Maine; SEMA is southeastern Massachusetts/Newport, Rhode Island; SME is southeastern Maine; SWCT is southwestern Connecticut; and WMA is western Massachusetts.

### Renewable Portfolio Standards

The 2017 Economic Study request accounted for the growth of the regional goals for renewable resources in effect at the time the assumptions were made for the 2016 NEPOOL Scenario Analysis. The 2016 study showed that the resource assumptions used for Scenario 3 exceeded the physical requirements of RPS goals for new resources. All the new scenarios of the 2017 study (Scenarios A, B, and C) reflect different mixes of renewable resources that would also physically exceed the regional RPS goals.

### Active Demand Resources

The study simulated FCA #10 active demand resources totaling 319 MW, which were dispatched to shave peak load. All scenarios modeled an additional 1,000 MW of active demand resources by 2030. For these resources, 200 MW was dispatched at $50/ MWh and 800 MW was dispatched at $500/MWh. The dispatch price determined some of the energy profiles for the active demand resources.

### New England Hydroelectric Generation

The assumption for local New England hydro generation reflected the average annual energy production. A profile for dispatching the energy was developed to shift the energy generation to the higher load hours.

### Pumped Storage and Battery Storage

Energy storage (pumped storage and batteries) tend to levelize the load. Across all scenarios, existing pumped-storage units were dispatched to equalize the daily high and low net loads after accounting for all EE, active demand response, all PV (BTM and non-BTM), PHEVs, wind energy, hydro (excluding pumped storage), existing imports, and new imports. This treatment of pumped storage, assumed to have approximately 78% efficiency, was modeled similar to its treatment in other economic studies.

Scenarios 3, A, and C add battery storage totaling 2,483 MW in 2030 with a goal of equalizing daily high and low net loads. Battery storage was assumed to have approximately 90% efficiency and was placed in the New England Hub. The recharge time varied from 1 to 4 hours, and the simulations used a discharge time of 4 hours. Scenario B did not add any battery storage.

### Transmission Interface Limits and Interchanges with Neighboring Systems

This section summarizes the assumptions covering internal and external interfaces.

#### Internal Interfaces

The system’s internal transfer limits were used to constrain economic dispatch in the GridView program. The economic dispatch simulations reflected first-contingency (N-1) limits for the summer period. Table 5-10 shows the assumptions for the internal interface transfer limits, which can constrain the flow of power between RSP bubbles. Figure 5-4 depicts the transmission interface limits (MW) assumed in the models for interfaces internal to New England, which were assumed at the same values as determined for 2025.

Table 5-10
Single-Value Internal Transmission-Interface Limits
for Use in RSP Subarea Models assumed for 2030 (MW)

| Internal Interface | MW |
| --- | --- |
| Orrington South Export | 1,325 |
| Surowiec South | 1,500 |
| Maine–New Hampshire | 1,900 |
| North–South | 2,725 |
| East–West | 3,500 |
| West–East | 2,200 |
| Boston Import (N-1) | 5,700 |
| SEMA/RI Export | 3,400 |
| SEMA/RI Import (N-1) | 1,280 |
| Southeast New England Import (N-1) | 5,700 |
| Connecticut Import (N-1) | 3,400 |
| SW Connecticut Import (N-1) | 2,800 |

Source: ISO New England, Transmission Transfer Capabilities Update, PAC presentation (June 10, 2016), https://smd.iso-ne.com/operations-services/ceii/pac/2016/06/a3_transmission_transfer_capabilities_update.pdf.

Figure 5-4: Pipe and bubble representations of transmission interfaces in New England for 2030 (MW).

Notes: The Cross-Sound Cable (CSC) capacity import capability was assumed to provide no capacity (0 MW). Similar to the Renew Plus Scenario, all the scenarios added two new ties rom Québec with equal capability and energy: one to WMA and one to the Central Massachusetts/Northeast Massachusetts (CMA/NEMA) area. See Section 5.3.8.2.

#### External Ties

The scenarios required information about the capacity imports assumed to determine the initial mix of resources. The assumptions for each scenario’s resource mix considered capacity imports with capacity supply obligations. Import capacity includes New York Power Authority imports under a long-term contract plus the average capacity supply obligations associated with New Brunswick, Highgate, and Phase II occurring during 2013, 2014, and 2015. Scenario 3 and Scenario C assume additional import capacity of 2,000 MW in 2030, and Scenario A and Scenario C assume additional import capacity of 1,000 MW.

Energy imports over the existing ties with Canada were based on diurnal profiles for 2013, 2014, and 2015. The energy profiles for imports from Québec and the Maritimes for all scenarios were developed using a methodology similar to one used in previous ISO economic studies. Because of the dispatch threshold price assumed, imports would be able to set the clearing price only when natural-gas-fired combined-cycle generation was not needed. The threshold price for imports from New Brunswick was assumed to be $10/MWh, while imports from Québec were assumed to be $5/MWh. The study also assumed no interchange would occur across the Cross-Sound Cable or New York AC interconnections as a simplifying assumption that would accentuate the results for New England resources and imports from Canada.

All scenarios modeled energy imports from two new interconnections with Québec—one interconnecting to WMA and one interconnecting to CMA/NEMA. Both new ties were assumed to have equal capacity contracts and energy-delivery assumptions. The two new interconnections totaled 2,000 MW for Scenarios 3 and C (1,000 MW in each location), and 1,000 MW for Scenarios A and B. To balance and smooth out the net load profile affected by renewables, the energy imports from external capacity resources over the new ties used a profile that imported more energy when loads net of EE and other renewable resources (PV, wind, and hydro) were higher and less when the net loads were lower.

Table 5-11 shows the import-transfer capabilities, capacity imports, and energy imports used for 2030 external interchanges with neighboring systems, including the two new ones from Québec assumed for all scenarios. Based on the historical profiles, the maximum energy import values were allowed to exceed the capacity import values, but they never exceeded the import-transfer capability of the ties.

Table 5-11
Assumed Interconnections with Neighboring Systems, Import Capabilities,
and Capacity Imports for 2030 (MW)

| Interconnection | Import Capability |  | Capacity Imports |  | Energy Delivery |
| --- | --- | --- | --- | --- | --- |
|  | Reference and Wind Less Nuclear Scenarios | EE + Offshore and Onshore Less EE/PV Scenarios | Reference and Wind Less Nuclear Scenarios | EE + Offshore and Onshore Less EE/PV Scenarios | All Scenarios |
| Highgate | 217(a) | 217(a) | 194 | 194 | Historical profile |
| HQ Phase II | 2,000(a) | 2,000(a) | 429 | 429 | Historical profile |
| HQ-WMA | 1,000 | 500 | 1,000 | 500 | Peak-shaving profile(b) |
| HQ-CMA/NEMA | 1,000 | 500 | 1,000 | 500 | Peak-shaving profile(b) |
| New Brunswick | 1,000(a) | 1,000(a) | 300 | 300 | Historical profile |
| New York AC | 1,400(a) | 1,400(a) | 83(c) | 83(c) | None |
| Cross-Sound Cable | 330(a) | 330(a) | 0 | 0 | None |

(a) 	The import capability for energy reflects the physical limitations of the ties. Although Phase II is physically designed to transfer 2,000 MW, its transfer limit is typically limited to approximately 1,500 MW under expected system conditions to respect the loss-of-source contingency limit of the New England system. Import capacity limits are typically a lower value than the import capabilities of external ties.

(b) 	Energy was imported to reduce net load peaks, which is after adjustment for EE, PHEV, PV, onshore and offshore wind, local hydro, and interchange over existing ties.

(c) 	New York Power Authority capacity imports are accounted for here.

## Fuel Prices

The assumed fuel prices for coal, oil, and natural gas were based on forecasts from the US Department of Energy (DOE), Energy Information Administration (EIA) 2016 Annual Energy Outlook (AEO) for New England. Figure 5-5 shows the 2016 AEO reference cases in 2015 $/million British thermal units (2015 $/MMBtu). The use of the forecast means that more efficient coal-fired units would be dispatched before more expensive steam and combined-cycle units burning natural gas.

Figure 5-5: Reference fuel-price forecasts for New England, 2030
($/MMBtu).

Similar to the seasonal variations used in the ISO’s three 2015 economic studies, natural gas prices were increased 10% over the nominal price in the winter and reduced 10% of the nominal price in the summer for 2030. Figure 5-6 shows the per-unit multipliers used on the forecasted monthly natural gas prices. Other fuels used the annual AEO forecast values.

Figure 5-6: Per-unit multiplier for monthly natural gas price forecast assumptions for 2030.

Table 5-12 shows the fuel price forecasts for New England for 2030 used in this analysis.

Table 5-12
Nominal Fuel Price Forecast for New England, 2030 ($/MMBtu)

| Fuel | 2030 |
| --- | --- |
| Distillate fuel oil | 22.995 |
| Residual fuel oil | 14.923 |
| Natural gas | 5.874 |
| Steam coal | 2.799 |

## Threshold Prices

Several price-taking resources were assumed to have $0/MWh production costs, including PV resources, onshore and offshore wind, local New England hydro, imports over the existing ties and imports over new ties with Canada. Threshold prices were assumed for price-taking resources to economically reduce their production during hours when total production would otherwise exceed the systemwide hourly demand (i.e., the resources would be spilled), or flows would otherwise exceed transmission interface limits in the constrained cases (i.e., the transmission limits bottled resource production). Threshold prices reduce the output of resources; they can set LMPs and are not reflected in the production costs. Table 5-13 shows the assumed threshold prices. The assumed order of threshold prices for different energy sources reflects one possible hierarchy that may not be indicative of future agreements. For example, in the future, wind may be curtailed before local New England hydro, suggesting that resources with no production costs would have different threshold prices.

Table 5-13
Assumed Threshold Prices for Price-Taking Resources

| Price-Taking Resource | Threshold Price ($/MWh) |
| --- | --- |
| Photovoltaics | 1.00 |
| Onshore and offshore wind | 4.00 |
| Local New England hydro | 4.50 |
| Imports from Québec over Highgate and Phase II ties | 5.00 |
| Imports from New Brunswick | 10.00 |
| Imports over the new ties modeled | 10.50 |

## Environmental Emissions Allowance Assumptions

The study used air emission allowance prices for nitrogen oxides, sulfur dioxide, and carbon dioxide, which affect the economic dispatch price for fossil-burning generation units. Table 5-14 shows the assumed air emission allowance prices for 2030 used in the study.

Table 5-14
Air Emission Allowance Prices for 2030 ($/short ton)

| Emission | 2030 |
| --- | --- |
| Nitrogen oxides | 6.18 |
| Sulfur dioxide | 6.18 |
| Carbon dioxide | 24.00 |

The future emission allowance prices for nitrogen oxides and sulfur dioxide were based on work by the New York ISO (NYISO). The CO2 prices were also based on a NYISO study. Although carbon prices apply to generating units greater than 25 MW (in accordance with RGGI), carbon allowance prices were assumed for all generating units consistent with discussions held with the PAC.

## Annual Carrying Charges

Annual carrying charges represent the annual revenue a facility must receive to cover its annual fixed costs and remain economically viable. This study applied annual carrying charges for new resources and transmission expansion. The values presented reflect input from the PAC.

### Annual Carrying Charges for New Resources

Although resource costs can vary significantly, generic capital costs for new resources can illustrate the differences among the scenarios. Generic overnight capital costs, also called overnight construction costs, were assumed for new resources based on US Energy Information Administration information. The costs assume construction occurring at a single point in time and reflect several details, including materials, equipment, and labor for all process facilities, fuel handling and storage, water intake structure and wastewater treatment, offices, maintenance shops, warehouses, and step-up transformer and transmission interconnection. While the estimates adjust for regional differences in costs, they do not include owners’ costs and interest expenses during construction (often referred to as “allowance for funds used during construction;” AFUDC). The total dollar costs are order-of-magnitude estimates in that the actual individual interconnection costs could vary widely from the values provided in this report.

The annual carrying charge rate of 15% was applied to the generic overnight capital costs of new resources to determine the new resources’ annual fixed costs. Table 5-15 shows the generic overnight capital costs and annual carrying charges assumed for new resources in New England.

Table 5-15
Assumed Total Overnight Generator Costs and Typical Annual Carrying Charges for New Resources (MW, $/kW)

| Technology Type | Typical Plant Size (MW) | Generic Total Overnight Plant Costs (2015 $/kW)(a) | New England-Specific Total Overnight Plant Costs (2015 $/kW)(a) | Typical Annual Carrying Charges for New-England-Specific Resources using 15% ($/kW-year) |
| --- | --- | --- | --- | --- |
| Solar photovoltaic(b) | 150 | 2,362 | 2,559 | 384 |
| Conventional combined cycle (CC) | 702 | 911 | 1,062 | 159 |
| Conventional combustion turbine (CT) | 100 | 1,026 | 1,119 | 168 |
| Offshore wind(c) | 400 | 4,605 | 6,496 | 974 |
| Onshore wind | 100 | 1,536 | 2,465 | 370 |

(a) 	The lower cost is the Overnight Plant Cost, and the higher cost is the New-England-Specific Total Overnight Cost, which includes a project Contingency Factor, a Technological Optimism Factor, and locational adjustments. The American Association of Cost Engineers defines a Contingency Factor allowance as the specific provision for unforeseeable cost elements within a defined project scope, particularly important when experience has shown the likelihood that unforeseeable events that increase costs will occur. The Technological Optimism Factor is applied to the first four units of a new, unproven design, reflecting the demonstrated tendency to underestimate actual costs for a first-of-a-kind unit. These costs represent new projects initiated in 2015.

(b) 	Net MWe AC Power.

(c)   Although the costs to develop offshore wind resources may be less than the assumed overnight generator costs used in this study, “new technology costs” were used to capture the additional costs associated with optimally interconnecting the offshore wind to Millstone, Montville, Brayton Point, Canal, and Pilgrim, which would eliminate the need for a congestion-relief system in SEMA/RI.

In addition to the resources costs shown in Table 5-15, the assumptions for the Renew Plus scenario and Scenarios A and C required the development of annual carrying charges for batteries. A 15% annual charge rate was applied to assumed battery costs of $1,000/kW, or equivalently $150/kW-year.

All scenarios considered the addition of energy-efficiency resources. The annual carrying charges for energy efficiency were $431.64/kW-year based on levelized capital costs provided by Concentric Energy Advisors.

### Transmission Development Costs

The ISO developed preliminary high-order-of-magnitude transmission-development costs to integrate renewable resources in New England based on judgement and generic costs. The cost analysis does not develop specific transmission-expansion plans but rather provides a means of comparing the transmission-development costs across scenarios.

These transmission development cost estimates include costs that would be incurred beyond individual plant-development costs, which are assumed as part of the capital costs of generation development (see Section 5.7.1). They also do not account for the costs to interconnect individual plants—also accounted for as part of the generation-development costs—or the costs associated with addressing operational issues caused by the development of large-scale inverter-based resources, especially during off-peak load periods. Transmission-development costs do not explicitly include the costs for some ancillary devices required to successfully integrate the high penetration of converter-based resources, such as special controls on the bulk power system and HVDC power electronic devices and system protection upgrades. Total transmission-development costs, however, include some costs for high inertia synchronous condensers and a margin to account for cost overruns and other unknown costs not specifically estimated.

Figure 5-7 shows the first two components of transmission upgrades needed to integrate renewable resources. Figure 5-7A shows the plant collector system, which is accounted for as part of the plant-development costs and ties individual wind turbine generators or photovoltaic generators to the collector system station. These components may include generator step-up transformers, collector strings, collector substation, collector step-up transformer, and supplemental static and dynamic reactive devices. The interconnection system is the transmission system that ties the collector system station to the point of interconnection (POI). It may include the high-voltage AC generator lead, high-voltage substation, and supplemental static and dynamic reactive devices. Explicit costs for the interconnection system were not developed because this would require detailed analysis of individual interconnections. However, some generic interconnection costs are included as part of the annual carrying charges for new resources. The transmission cost metric thus provides a metric suitable for comparing the various scenarios.

| A. The plant collector system and the interconnection system. | B. The integrator system. |
| --- | --- |

Figure 5-7 (A and B): The first two components of transmission upgrades potentially needed to integrate renewable resources.

Notes: A (on the left) shows the plant collector system and the interconnection system. Their order-of-magnitude cost estimates are included as part of the plant-development costs. B (on the right) shows the integrator system. The integrator system order-of-magnitude costs are included as part of the order-of-magnitude transmission costs summarized in this section.

Figure 5-7-B shows the integrator system that ties the POIs to the main portion of the bulk power system. It can be thought of as a means of clustering several interconnections, which can facilitate the ability of renewable resources to interconnect to the system. The integrator system may include new high-voltage AC or DC lines and converter stations and supplemental static and dynamic reactive devices. When technically possible, the benefit of having an integrator system is that, by tying the new renewable resources to the existing bulk power system, the new resources can make use of any marginal capability on the existing bulk power system. Consistent with the way resources are interconnected to the system under the New England minimum interconnection process, the sizing of the integrator is based on the nameplate amount of megawatts being “integrated.”

However, under scenarios with extremely large additions of renewable resources, an integrator system most likely would be insufficient for integrating all the additional megawatts to the bulk power system without large amounts of transmission upgrades on the existing bulk power system. In such cases, bypassing the integrator system and relying exclusively on the congestion-relief system was assumed to be the most cost-effective way to integrate extremely large additions of renewable resources. For the scenarios that considered an integrator system, the cost estimates for the system were based on engineering judgment, accounting for the general locations of wind plants.

Table 5-16 shows the assumptions for the integrator systems of onshore wind development. The integrator systems were assumed to be in service in anticipation of the assumed amounts of onshore wind resources for 2030. In the Onshore Less EE/PV and Wind Less Nuclear scenarios, the integrator system is bypassed.

Table 5-16
Integrator System Assumptions

|  | Reference Renewables Plus | Scenario A EE + Offshore | Scenario B Onshore Less EE/PV | Scenario C Wind Less Nuclear |
| --- | --- | --- | --- | --- |
| 2030 Maine nameplate wind injection (MW) | 3,652 | 926 | 5,743 | 7,579 |
| Integrator system (description) | 1 or 2 AC-parallel 345 kV paths | 1 AC or 2 AC-parallel 345 kV paths | Bypassed—assumed exclusive reliance on congestion-relief system | Bypassed—assumed exclusive reliance on congestion-relief system |
| Integrator system cost ($ billion) | 1.5 to 3.0 | 1.5 to 3.0 | — | — |
| Integrator system cost plus 50% margin ($ billion)(a) | 2.25 to 4.5 | 2.25 to 4.5 | — | — |

(a) The high-order-of-magnitude costs for an integrator system for the Renewables Plus reference scenario and the EE + Offshore scenario (A) may be similar because the necessary transmission development could be similar. More detailed transmission planning and design studies would be required to further refine these cost estimates.

Figure 5-8 shows the congestion-relief systems for wind development in Maine. The congestion-relief systems remove 100% of the transmission congestion that otherwise would prevent full energy production from the renewable resources during the summer and the winter peak hours. It also removes most of the congestion at all hours of the year. The basis for developing high-order-of-magnitude costs assumes high-voltage direct-current (HVDC) facilities tying the integrator system to Millbury, MA. This is equivalent to connecting renewable plants directly to the Hub for scenarios with extremely large additions of renewable resources.

Figure 5-8: The congestion-relief system.

In each scenario, the congestion-relief needed for wind development in Maine was first based on the difference in simultaneous interface flows between the constrained and unconstrained scenarios during the summer and winter peak hours. The ISO then examined the highest simultaneous congestion-relief need across all northern interfaces and used it to size the congestion-relief system. Finally, the congestion-relief need was compared with the highest flow on each individual interface (nonsimultaneous flow) over all hours of the year to ensure that the congestion-relief system would be adequate over most hours of the year. Table 5-17 shows the congestion-relief transmission capacity assumed for the scenarios. For the unconstrained cases, the congestion-relief systems were assumed in service by 2030 in anticipation of the assumed amounts of wind resources.

Table 5-17
Congestion-Relief Transmission Capacity Assumed for the Scenarios (MW)

|  | Reference Renewables Plus | Scenario A EE + Offshore | Scenario B Onshore Less EE/PV | Scenario C Wind Less Nuclear |
| --- | --- | --- | --- | --- |
| 2030 Maine nameplate wind injection | 3,652 | 926 | 5,743 | 7,579 |
| Needed congestion-relief capacity | 1,839 | None | 3,524 | 4,870 |

A number of high-level assumptions were made with regard to the design and cost of the congestion-relief system. The system was assumed to be composed primarily of an HVDC portion (parallel HVDC ties) and also include AC ancillary upgrades. Table 5-18 shows the detailed components of the main DC portion and AC ancillary upgrades, the assumed cost of each component, and the aggregated totals in each scenario.

Table 5-18
Detailed Congestion-Relief System Components and Their Assumed Costs for the Renew Plus, Onshore Less EE/PV, and Wind Less Nuclear Scenarios(a)

| Congestion-Relief System |  | Reference—Renewables Plus 1,839 MW (2 HVDC Ties) |  | Scenario B—Onshore Less EE/PV 3,524 MW (3 HVDC Ties) |  | Scenario C—Wind Less Nuclear 4,870 MW (4 HVDC Ties) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Equipment | $ per unit | Quantities | Total $ (billions) | Quantities | Total $ (billions) | Quantities | Total $ (billions) |
| DC portion |  |  |  |  |  |  |  |
| HVDC overhead lines | $3.5 million/mi | 2 × 200 = 400 mi. | $1.40 | (2 × 400) + ( 1 × 300) = 1,100 mi. | $3.85 | (2 × 400) + ( 2 × 300) = 1,400 mi. | $4.90 |
| Converters | $300 million/converter | 4 | $1.20 | 6 | $1.80 | 8 | $2.40 |
| Misc. DC additional equipment | $200 million/tie | 2 | $0.40 | 3 | $0.60 | 4 | $0.80 |
| Total DC portion |  |  | $3.00 |  | $6.25 |  | $8.10 |
| AC portion |  |  |  |  |  |  |  |
| Sending end—reactive devices | $0.25 million/MVAR | (included in integrator system) | -- | Approx. 1/3 × 3,600 = 1,200 MVAR | $0.30 | Approx. 1/3 × 4,800 = 1,600 MVAR | $0.40 |
| Sending end— AC terminations | $10 million/terminal expansion (assumed two terminal expansions per tie) | 2 x 2 = 4 | $0.04 | -- | -- | -- | -- |
| Sending end— New AC substations | $40 million/ AC substation | (included in integrator system) | -- | 3 (to connect POI to converter station at each tie) | $0.12 | 4 (to connect POI to converter station at each tie) | $0.16 |
| Receiving end— reactive devices | $0.25 million/MVAR | Approx. 1/3 × 1,800 = 600 MVAR | $0.15 | Approx. 1/3 × 3,600 = 1,200 MVAR | $0.30 | Approx. 1/3 × 4,800 = 1,600 MVAR | $0.40 |
| Receiving end— AC terminations | $10 million/terminal expansion (assumed two terminal expansions per tie) | 2 × 2 = 4 | $0.04 | 3 x 2 = 6 | $0.06 | 4 x 2 = 8 | $0.08 |
| Receiving end—additional upgrades on AC network | Assumed generic cost for each scenario | -- | $0.50 | -- | $1.00 | -- | $1.00 |
| Total AC portion |  |  | $0.73 |  | $1.78 |  | $2.04 |
| AC and DC portions: $B |  |  |  |  |  |  |  |
| Total—Congestion-Relief System |  |  | $3.73 |  | $8.03 |  | $10.14 |
| Total cost + 50% margin |  |  | $5.60 |  | $12.05 |  | $15.21 |

- Costs described here are preliminary high-level order-of-magnitude costs based on judgement. Also, they do not account for individual plants, collector strings, collector substations, or collector step-up transformers. The EE + Offshore Scenario (A) did not require a congestion-relief system.

### High-Order-of-Magnitude Cost Estimates for Integrating Renewable Resources

High-order-of-magnitude cost estimates for integrator and congestion-relief systems formed the basis of the transmission-development costs for each scenario. Because the costs are not based on specific transmission plans, and the cost estimates are rough, margins were then applied to account for additional costs, recognizing that actual costs would likely be considerably higher. Also, the margin represents costs of actual transmission plans that would likely require several additional transmission system improvements. Finally, an annual carrying charge rate of 15% was applied to all the high-order-of-magnitude transmission-development costs for integrating renewable resources.

Table 5-19 summarizes the high-order-of-magnitude transmission-development costs assumed for integrating renewable resources under all scenarios. The costs summarized in the table could be off by several billion dollars, but they provide a framework for stakeholder discussions. They show the relatively high transmission costs associated with the large-scale development of onshore wind resources in Maine compared with other scenarios. The low-order-of-magnitude transmission costs for the offshore wind development assumed carefully planned points of interconnection split among Connecticut, Rhode Island, and southeastern Massachusetts that would eliminate the need for any integrator or congestion-relief systems. These points of interconnection are assumed as part of the offshore wind total overnight generator costs and annual carrying charges (see Table 5-15). Table 5-20 lists the assumptions for the interconnection of offshore wind resources.

Table 5-19
Summary of High-Order-of-Magnitude Costs to Integrate Renewable Resources under All Scenarios

| Variable | Reference Renewables Plus | Scenario A EE + Offshore(a) | Scenario B Onshore Less EE/PV(b) | Scenario C Wind Less Nuclear(b) |
| --- | --- | --- | --- | --- |
| 2030 Maine nameplate wind injection (MW) | 3,652 | 926 | 5,743 | 7,579 |
| Needed congestion-relief capacity (MW) | 1,839 | --- | 3,524 | 4,870 |
| Integrator system (description) | 1 or 2 AC-parallel 345 kV paths | 1 or 2 AC-parallel 345 kV paths | — | — |
| Integrator system cost ($ billion) | $1.50 to $3.00 | $1.50 to $3.00 | — | — |
| Integrator system cost + 50% margin ($ billion) | $2.25 to $4.50 | $2.25 to $4.50 | — | — |
| Congestion-relief system (description) | Connecting Larrabee 345 kV to the Hub | (No congestion-relief system) | Connecting POIs directly to the Hub | Connecting POIs directly to the Hub |
| Congestion-relief system cost ($ billion) | $3.73 | — | $8.03 | $10.14 |
| Congestion-relief system cost + 50% margin ($ billion) | $5.60 | — | $12.05 | $15.21 |
| Total cost + 50% margin ($ billions) | $7.85 to $10.10 | $2.25 to $4.50 | $12.05 | $15.21 |

(a)  Interconnection points for the SEMA/RI offshore wind additions would avoid the need for associated congestion-relief transmission upgrades but could require the addition of long POI HVDC interconnections, the cost of which was assumed as part of the offshore wind annual carrying charges.

(b) 	Because of the absence of an integrator system for wind development in Maine for Scenarios B and C, the method used to size of the congestion-relief system may have resulted in a slightly undersized system (i.e., the method assumed the full use of the existing system transmission capability, which may not be possible without an integrator system). The resulting estimates for Scenarios B and C may be slightly low compared with those for Scenarios 3 and the Reference scenario.

Table 5-20
Assumptions for Interconnecting Offshore Wind Resources

| Suggested POI for Offshore Resources | Location | Amount of Assumed Retired Generation at the POI (MW) | Example of Possible Nameplate Interconnections (MW) |
| --- | --- | --- | --- |
| Milstone/Montville 345 kV | Connecticut | 1,127 | 1,400 |
| Kent County 345 kV | SEMA/RI | — | 800 |
| Brayton Point 345 kV | SEMA/RI | 1,525 | 1,600 |
| Pilgrim/Canal 345 kV | SEMA/RI | 1,769 | 1,600 |

# Results and Observations

This section summarizes and compares some of the key results for each scenario’s set of assumptions for 2030 constrained and unconstrained conditions. The results of the metrics studied provide information about how different public policies and subsequent mixes of resources could affect overall system and consumer costs, system reliability, generator capacity and fuel use, the environment, and transmission expansion. Detailed and summary tables and charts showing additional results and comparisons are available on the ISO’s website. The ISO encourages interested parties to compare the results for the different scenarios and reach their own conclusions about the various outcomes.

## Economic Results

This section discusses several main results from the production cost simulations, which are driven by the assumptions for resource additions and retirements, costs of fuels and emission allowance prices, the growth of net demand, and high-order-of-magnitude transmission-development costs used to integrate renewable wind resources and relieve system congestion.

### Total Energy Production by Resource (Fuel) Type, Including Imports

An examination of the metric for total systemwide energy production by resource (fuel) type explains many of the differences in the overall results. Figure 6-1 presents the results for 2030 (in terawatt-hours; TWh), showing consistency with the study’s assumptions. Table 6-1 shows the data behind these figures.

Figure 6-1: Total systemwide production by fuel type for each scenario, 2030 (TWh).

Note:  Onshore Less EE/PV has no PHEV or battery storage, therefore less total demand and less total generation.

Table 6-1
Total Systemwide Production by Fuel Type for Each Scenario, 2030 (TWh)

| Fuel Type | Renew Plus |  | EE + Offshore |  | Onshore Less EE/PV |  | Wind Less Nuclear |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Unconstrained | Constrained | Unconstrained | Constrained | Unconstrained | Constrained | Unconstrained | Constrained |
| Wind | 24.36 | 22.43 | 19.09 | 19.09 | 31.12 | 25.19 | 42.26 | 32.27 |
| PV | 16.03 | 16.03 | 15.92 | 15.92 | 5.56 | 5.56 | 16.05 | 16.04 |
| Oil | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 |
| Natural gas | 14.16 | 17.04 | 10.97 | 11.14 | 28.71 | 34.84 | 15.81 | 25.07 |
| Imports | 25.60 | 24.83 | 19.45 | 19.38 | 19.43 | 19.34 | 23.41 | 23.78 |
| Coal | 0.07 | 0.05 | 0.07 | 0.07 | 0.10 | 0.06 | 0.07 | 0.03 |
| Misc. | 2.05 | 2.26 | 1.84 | 1.82 | 2.14 | 2.52 | 1.80 | 2.45 |
| Wood | 3.70 | 3.50 | 3.45 | 3.37 | 3.66 | 3.53 | 3.27 | 3.30 |
| Nuc. | 27.24 | 27.24 | 27.20 | 27.20 | 27.26 | 27.26 | 10.16 | 10.17 |
| EE/DR | 53.98 | 54.08 | 69.16 | 69.16 | 36.12 | 36.12 | 53.92 | 54.16 |
| Hydro | 3.95 | 3.68 | 3.95 | 3.94 | 3.86 | 3.53 | 4.29 | 3.76 |
| Total(a) | 171.15 | 171.15 | 171.09 | 171.09 | 157.95 | 157.95 | 171.03 | 171.03 |

- PHEV consumes 12.52 TWh in the Renew Plus, EE + Offshore, and Wind Less Nuclear scenarios. Pumped storage plus battery storage consumes <1 TWh in every scenario.

Some observations of these results are as follows:

- The Onshore Less EE/PV scenario showed lower total systemwide energy production than the other scenarios because this scenario does not include additions of electric vehicles and battery storage, both of which consume additional energy.

- Although the amount of resources assumed for each scenario adequately meets the systemwide energy requirements, even when transmission constraints are modeled, the energy production varied by price-taking resources simulated as $0/MWh:

  - The EE + Offshore (offshore + 1,000 MW; onshore − 2,800 MW) scenario showed the least amount of wind energy production. The Onshore Less EE/PV scenario produced more wind energy than the reference case. The Wind Less Nuclear scenario resulted in the most energy production from wind resources, especially when the transmission system was unconstrained.

  - Production by natural-gas-fired generation fluctuated with the differences in production by price-taking resources simulated as $0/MWh and with the addition of assumed retirements. The EE + Offshore scenario produced the least amount of natural-gas-fired energy, and the Onshore Less EE/PV scenario produced the most. Constraining the transmission system generally increased production by gas-fired generation because imposing transmission restrictions increased the amount of spilled onshore wind as a result of flows reaching the transmission limits in the Maine interfaces. Although the constrained Onshore Less EE/PV scenario showed the most natural-gas-fired generation, the Wind Less Nuclear scenario showed the greatest increase in natural-gas-fired production, resulting from the effects of constraining the transmission system compared with the unconstrained case.

- Production by natural-gas-fired generation is high relative to other resources. Because natural-gas-unit production costs are generally higher than the production costs for other resources (with the exception of wood-fired resources), natural gas generation is mostly on the margin across all scenarios.

### Systemwide Production Costs

Production costs reflect operating costs (which account for fuel-related costs), dispatch and unit commitment, and emission allowances. Figure 6-2 shows the system production costs for the unconstrained and the constrained system for the study year. Table 6-2 shows the data behind the figures, and Table 6-3 compares the results with the Renew Plus scenario. In general, the results reflect the same trends shown by the metric for total energy production by resource type where larger amounts of renewable or imported energy with $0/MWh production costs reduce the production-cost metric. Decreased amounts of production by nuclear generators due to retirements causes increases in production costs.

Figure 6-2: Production costs, 2030 ($ millions).

Table 6-2
Production Costs, 2030 ($ Millions)

| Transmission | Renew Plus | EE + Offshore | Onshore Less EE/PV | Wind Less Nuclear |
| --- | --- | --- | --- | --- |
| Unconstrained | 1,086 | 895 | 1,877 | 1,101 |
| Constrained | 1,253 | 901 | 2,221 | 1,649 |
| Congestion(a) | 167 | 6 | 344 | 548 |

- Congestion is equal to constrained value of systemwide production costs minus the unconstrained value.

Table 6-3
Production Costs Compared with the Renew Plus Scenario, 2030 ($ Millions)

| Transmission | Renew Plus | EE + Offshore | Onshore Less EE/PV | Wind Less Nuclear |
| --- | --- | --- | --- | --- |
| Unconstrained | – | −191 | 791 | 15 |
| Constrained | – | −352 | 968 | 396 |

- Congestion is equal to constrained value of systemwide production costs minus the unconstrained value.

Natural gas consumption, and to a lesser extent other fossil fuels, drive production costs. The EE + Offshore scenario had the lowest systemwide production costs, while the Onshore Less EE/PV scenario had the highest. The general simulation results quantify reduced systemwide production costs for increased amounts of wind, PV, EE, and imports.

A comparison of the unconstrained and the constrained cases shows the benefits of retaining existing nuclear resources and locating new resources with relatively low production costs, including offshore wind, EE, PV, and new ties, near load centers in southern New England. The EE + Offshore scenario has the smallest difference of systemwide production costs between the constrained and the unconstrained cases, which is equivalent to the systemwide amount of congestion. The results for the EE + Offshore scenario illustrate the effects of reduced systemwide congestion and less of a need for transmission expansion compared with scenarios that add remote resources without transmission improvements, such as the large-scale development of renewable resources in northern New England. The Wind Less Nuclear scenario shows the greatest difference in production costs between the constrained and the unconstrained cases as a result of the largest addition of onshore wind generation. This comparison also illustrates the reductions in production costs that would be attributable to eliminating all transmission constraints.

### Annual Average LMPs by RSP Subareas

Figure 6-3 and Table 6-4 show the average LMPs in selected RSP subareas for the constrained and unconstrained cases for 2030.

Figure 6-3: Annual average LMPs by RSP subarea, 2030 ($/MWh).

Table 6-4
LMPs in Selected Subareas, 2030 ($/MWh)

| Transmission | Scenario | BHE | ME | SME | NH | BOSTON |
| --- | --- | --- | --- | --- | --- | --- |
| Unconstrained | Renew Plus | 34.19 | 34.54 | 34.55 | 35.56 | 34.07 |
|  | EE + Offshore | 31.73 | 32.05 | 32.07 | 33.00 | 31.62 |
|  | Onshore Less EE/PV | 38.58 | 37.97 | 38.21 | 38.58 | 38.37 |
|  | Wind Less Nuclear | 30.49 | 30.66 | 30.85 | 31.73 | 30.36 |
| Constrained | Renew Plus | 21.98 | 27.72 | 36.33 | 37.57 | 36.12 |
|  | EE + Offshore | 31.08 | 31.70 | 31.77 | 32.62 | 31.34 |
|  | Onshore Less EE/PV | 20.69 | 28.60 | 42.82 | 43.60 | 43.50 |
|  | Wind Less Nuclear | 13.78 | 20.11 | 37.20 | 38.71 | 37.18 |

The scenario results for the unconstrained cases show lower average systemwide LMPs because price-taking resources produce greater amounts of energy, especially when they displace less-efficient fossil fuel generating units. The cases with an unconstrained transmission system show flat LMPs across all RSP subareas. The ind Less Nuclear scenario results in the lowest LMPs, followed by the EE + Offshore and then the Renew Plus scenarios; the Onshore Less EE/PV scenario had the highest LMPs.

When transmission flows are constrained, the LMP at the receiving end is higher than at the sending end, as shown by the addition of more onshore wind resources in northern Maine. The Wind Less Nuclear scenario shows the largest price separation between BHE/ME and the rest of the system followed by the Onshore Less EE/PV scenario. Congestion follows the same pattern of results. The EE + Offshore scenario barely has any price separation as a result of low production resources being located near the load centers in southern New England.

### Load-Serving Entity Energy Expense and Uplift

Figure 6-4 shows the load-serving entity energy expenses and “uplift” costs (i.e., make-whole payments) for the constrained and unconstrained cases. Table 6-5 shows the data for this figure. Table 6-6 shows these expenses compared with the Renew Plus reference scenario. The LSE energy expense follows the same pattern as the LMPs across all scenarios. The amount of congestion is directly correlated to the amount of assumed onshore resources in Maine in each scenario. The Wind Less Nuclear scenario experiences the highest amount of congestion followed by the Onshore Less EE/PV scenario. The EE + Offshore scenario exhibits virtually no congestion because the offshore wind expansion is electrically close to the load centers in southern New England. The uplift cost is relatively small compared with the LSE energy expense for all scenarios.

Figure 6-4: Load-serving entity energy expense and uplift, 2030 ($ million).

Table 6-5
Load-Serving Entity Energy Expense and Uplift Costs, 2030 ($ Millions)

| Transmission | Type | Reference Renew Plus | Scenario A EE + Offshore | Scenario B Offshore Less EE/PV | Scenario C Wind Less Nuclear |
| --- | --- | --- | --- | --- | --- |
| Unconstrained | LSE energy expense | 5,866 | 5,447(a) | 6,064 | 5,231 |
|  | Uplift | 117 | 103 | 249 | 154 |
|  | Total | 5,983 | 5,550 | 6,313 | 5,385 |
| Constrained | LSE energy expense | 6,130 | 5,396* | 6,732 | 6,232 |
|  | Uplift | 161 | 111 | 263 | 240 |
|  | Total | 6,291 | 5,507 | 6,995 | 6,472 |

- Scenario A’s LSE energy expense for the unconstrained case exceeds the LSE energy expense for the constrained case by approximately $50 million. This relatively small amount of negative congestion results from the simulations modeling all offshore wind interconnected to the SEMA/RI area. Interconnecting some of the offshore wind into the CT area would eliminate this congestion.

Table 6-6
Load-Serving Entity Energy Expense and Uplift Costs, 2030 ($ Millions)
Compared with the Renew Plus Reference Scenario

| Transmission | Type | Renew Plus | EE + Offshore | Onshore Less EE/PV | Wind Less Nuclear |
| --- | --- | --- | --- | --- | --- |
| Unconstrained | LSE energy expense | – | −419 | 198 | −635 |
|  | Uplift | – | −14 | 132 | 38 |
|  | Total | – | −433 | 330 | −598 |
| Constrained | LSE energy expense | – | −734 | 602 | 103 |
|  | Uplift | – | −51 | 101 | 79 |
|  | Total | – | −784 | 703 | 181 |

### GridView Congestion Metric by Interface

Figure 6-5 and Table 6-7 show most of the dollar value of congestion occurs in the northern Maine interfaces. Similar to the other results discussed, the amount of congestion is driven by the large-scale expansion of onshore wind resources in northern Maine. Thus, all scenarios resulted in high amounts of congestion with the exception of the EE + Offshore scenario.

Figure 6-5: Gridview congestion metric by interface, 2030 ($ million)

Note: In this figure, congestion equals the difference of the LMPs in the RSP bubbles bordering the interface multiplied by the transfer limit of the interface.

Table 6-7
GridView Congestion Metric by Interface, 2030 ($ Million)

| Scenario | Renew Plus | EE + Offshore | Onshore Less EE/PV | Wind Less Nuclear |
| --- | --- | --- | --- | --- |
| Orrington South | 60.7 | 3.7 | 74.8 | 57.2 |
| Surowiec South | 143.8 | 0.9 | 200.5 | 283.1 |
| Maine–New Hampshire | 0.0 | 0.0 | 0.0 | 0.0 |
| North–South | 0.3 | 0.0 | 0.0 | 0.0 |
| Other | 1.5 | 2.5 | 0.0 | 0.4 |
| Total | 206.3 | 7.1 | 275.3 | 340.7 |

(a) 	In this table, congestion equals the difference of the LMPs in the RSP bubbles bordering the interface multiplied by the transfer limit of the interface.

Table 6-8 shows transmission system flows for the constrained and unconstrained scenarios. With the exception of the EE + Offshore scenario, the Orrington-South and Surowiec South interfaces reach their limits a significant amount of time in all constrained cases. The unconstrained cases show the three scenarios would also exceed the Maine-New Hampshire and North South interface limits. This is because relieving the transmission limits of the two northern interfaces results in additional transmission flows to the load centers in New England.

Table 6-8
Percentage of Hours Interface Flow Reaches or Exceeds 100% of Rating
in the Constrained and Unconstrained Cases—All Scenarios, 2030

| Transmission | Scenarios | Orrington- South | Surowiec South | Maine- New Hampshire | North- South | SEMA/RI Import(a) | SEMA/ RI Export |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Constrained | Renew Plus | 39.5 | 31.9 | 0.2 | 0.0 | 1.4 | 0.0 |
|  | EE + Offshore | 1.6 | 0.2 | 0.0 | 0.0 | 0.3 | 0.0 |
|  | Onshore Less EE/PV | 48.3 | 48.4 | 0.0 | 0.0 | 0.1 | 0.0 |
|  | Wind Less Nuclear | 44.2 | 57.3 | 0.0 | 0.0 | 0.7 | 0.2 |
| Unconstrained | Renew Plus | 48.3 | 45.1 | 14.2 | 25.0 | 17.8 | 0.0 |
|  | EE + Offshore | 2.1 | 1.1 | 0.0 | 0.0 | 5.4 | 0.0 |
|  | Onshore Less EE/PV | 64.3 | 63.5 | 37.7 | 48.9 | 5.4 | 0.0 |
|  | Wind Less Nuclear | 71.5 | 71.7 | 36.7 | 56.5 | 7.5 | 0.0 |

- Judicious interconnection points for the SEMA/RI offshore wind additions would avoid congestion attributable to unit-commitment issues and the need for associated congestion-relief transmission upgrades, but this could require the addition of long POI HVDC interconnections, the cost of which was assumed as part of the offshore wind annual carrying charges.

### High-Order-of-Magnitude Transmission Costs

Table 6-9 shows the Maine interfaces, their maximum transfer capability, the maximum megawatt flows over the interfaces for the unconstrained cases, and the percentage of time the interfaces exceed their capability for the unconstrained cases. These metrics supplement the congested interface locations as inputs to developing the congestion-relief transmission system, which is designed to relieve 100% of the congestion during the summer and winter peak hours. Table 6-10 is a summary of the total high-order-of-magnitude transmission costs.

Table 6-9
Interface Flow Statistics

| Scenario | Transfer Limit (MW) | Maximum MW Flow (Unconstr. Case) | % of Time Interface Exceeds Its Capability | Transfer Limit (MW) | Maximum MW Flow (Unconstr. Case) | % of Time Interface Exceeds Its Capability | Transfer Limit (MW) | Maximum MW Flow (Unconstr, Case) | % of Time Interface Exceeds Its Capability |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Orrington South Interface |  |  | Surowiec South Interface |  |  | Maine–New Hampshire Interface |  |  |
| Renew Plus | 1,325 | 3,366 | 48.3% | 1,500 | 4,114 | 45.1% | 1,900 | 4,695 | 14.2% |
| EE + Offshore | 1,325 | 1,596 | 2.1% | 1,500 | 1,804 | 1.1% | 1,900 | 2,559 | 0.0% |
| Onshore Less EE/PV | 1,325 | 4,735 | 64.3% | 1,500 | 5,917 | 63.5% | 1,900 | 5,799 | 37.7% |
| Wind Less Nuclear | 1,325 | 5,890 | 71.5% | 1,500 | 7,404 | 71.7% | 1,900 | 6,566 | 36.7% |

Table 6-10
Summary of Total High-Order-of-Magnitude Transmission System Costs ($ Billions)

|  | Reference Renewables Plus | Scenario A EE + Offshore | Scenario B Onshore Less EE/PV | Scenario C Wind Less Nuclear |
| --- | --- | --- | --- | --- |
| 2030 Maine nameplate wind injection (MW) | 3,652 | 926 | 5,743 | 7,579 |
| Needed congestion-relief capacity (MW) | 1,839 | — | 3,524 | 4,870 |
| Integrator system (description) | 1 or 2 AC-parallel 345 kV paths | 1 or 2 AC-parallel 345 kV paths | — | — |
| Integrator system cost ($ billion) | $1.50 to $3.00 | $1.50 to $3.00 | — | — |
| Integrator system cost + 50% margin ($ billion) | $2.25 to $4.50 | $2.25 to $4.50 | — | — |
| Congestion-relief system (description) | Connecting Larrabee 345 kV to the Hub | — | Connecting POIs directly to the Hub | Connecting POIs directly to the Hub |
| Congestion-relief system cost ($ billion) | $3.73 | — | $8.03 | $10.14 |
| Congestion-relief system cost + 50% margin ($ billion) | $5.60 | — | $12.05 | $15.21 |
| Total cost + 50% margin ($ billion) | $7.85 to $10.10 | $2.25 to $4.50 | $12.05 | $15.21 |

- Costs described here are preliminary high-level order-of-magnitude costs based on judgement. Also, they do not account for individual plants’ interconnection costs or potential costs from system operational issues.

Transmission development costs increase with greater amounts of assumed onshore wind development. The dollars are not associated with specific plans but rather form an equitable basis of comparison among the scenarios. However, the 2016 Maine Resource Integration Study helped inform the development of the cost estimates. The EE + Offshore scenario results in the least expensive high-order-of-magnitude transmission development costs, and the Wind Less Nuclear scenario resulted in the greatest costs.

## Operation and Planning the Transmission System for High Levels of Inverter-Based Resources

The large-scale development of PV can affect the net load shape. An example of the “duck curve” is shown in Figure 6-6 for the New England system that occurred on April 21, 2018. The net load decreases with daylight, and the peak occurs after dusk when PV output drops to zero. Systems with “duck curve” characteristics must address a number of technical issues, such as the ability to ramp system resources to follow the net load.

Figure 6-6: Example of a daily system load in real time with and without solar power, April 21, 2018 (MW).

Figure 6-7 shows hours in the Renew Plus scenario where the system is operating with only three nuclear units. Similar issues were evident with the three new scenarios discussed in this report. The net load shape peaks during night hours and ramps down during the morning and up during the evening hours, primarily as a result of high PV output. The fuel mix shows that storage resources supply the system during evening hours and charge during the daylight for this particular day.

Figure 6-7: Energy by source for the Renewables Plus Scenario, May 7, 2030, unconstrained (MW).

Note: GT = gas turbine; IC = internal combustion; CC = combined cycle. The net demand shown = gross demand + PHEV + storage charge – EE – PV.

The large-scale addition of asynchronous resources (PV, wind, and HVDC imports) and energy efficiency requires physical improvements to the system. Loads, net of wind, PV, EE, hydro, and nuclear, may be exceedingly low, which presents voltage and stability issues. Special control systems may be required, especially to stabilize the system and provide frequency control, ramping, and reserves. Many other technical issues must be addressed to ensure proper power quality and voltage regulation.

Protection-system issues that arise from the lack of short-circuit availability, and special equipment such as synchronous condensers and flexible alternating-current transmission systems (FACTS) needed to address other technical issues, could require major capital investment. Because of the limited scope of this part of the analysis,  the development of the high-order-of magnitude cost estimates (see Section 6.1.6) only partially reflected the costs of special equipment.

## Relative Annual Resource Costs

The relative annual resource cost (RARC) metric is a means of comparing the total annual costs of all three scenarios with the constrained case for Renewables Plus. The RARC accounts for the annual systemwide production costs, which can be thought of as yearly operating costs, plus it captures the annual costs of capital additions by including the annualized carrying costs for new resources and high-order-of-magnitude transmission-development costs. RARC is thus a measure of the relative total costs for all scenarios, expressed in billions of dollars and as cents per kilowatt-hour (kWh).

The addition of price-taking resources (simulated at $0/MWh) reduces the production cost in the simulations. For example, larger amounts of renewable resources and imports result in lower production costs (see Section 6.1.2). However, resource additions increase capital costs to the scenarios, which can be very substantial for the large-scale addition of price-taking resources. Similarly, relieving congestion by releasing bottled generation reduces production costs but adds transmission costs.

Figure 6-8 and Figure 6-9 summarize the RARCs; scenarios with positive values reflect higher costs than the constrained case for the Renewables Plus scenario, and negative values reflect lower costs. Table 6-11 and Table 6-12 show the detailed results. Figure 6-8 and Table 6-11 summarize the relative total operating costs and capital costs of the scenarios expressed in billions of dollars,  and Figure 6-9 and Table 6-12 summarize the RARCs shown as cents per kilowatt-hour (kWh). The white dashes in the figures compare the total annual costs of all cases with the constrained case for the Renew Plus scenario. Scenarios with lower RARCs show lower total operating and annual fixed costs and may be viewed as more economical relative to the other scenarios. Annual carrying costs for resource mixes drive the main differences in the total RARCs with resource additions increasing costs and fewer new resources reducing costs. Lower scenario production costs reduce the total RARC.

Figure 6-8: Total relative annual resource costs, 2030 (constrained and unconstrained), showing changes compared with 2030 Scenario 3 (constrained) ($ billions).

Notes:  Energy efficiency and solar include costs resulting from individual customer investments that do not reflect the benefits the owners would receive. Production costs reflect the price of carbon emissions at $24/ton.

Table 6-11
Relative Annual Resource Costs, 2030 ($ Millions)(a)

| Transmission | Scenario | Production Cost | 15% Transm. Cost | 15% Ties | 15% Comb. Cycle | 15% New Onshore Wind | 15% New Offshore Wind | 15% Solar | 15% Energy Efficiency | 15% Battery | Total |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Constrained | Renew Plus | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |
|  | EE + Offshore | −352 | -338 | −225 | 0 | −1,047 | 974 | 0 | 863 | 0 | −124 |
|  | Onshore Less EE/PV | 968 | 0 | −225 | 219 | 803 | 0 | −3,013 | −980 | -375 | −2,603 |
|  | Wind Less Nuclear | 396 | 338 | 0 | 0 | 1,508 | 1,560 | 0 | 0 | 0 | 3,802 |
| Unconstrained | Renew Plus | −167 | 825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 658 |
|  | EE + Offshore | −358 | -338 | −225 | 0 | −1,047 | 974 | 0 | 863 | 0 | −130 |
|  | Onshore Less EE/PV | 624 | 1,133 | −225 | 219 | 803 | 0 | −3,013 | −980 | -375 | −1,814 |
|  | Wind Less Nuclear | −152 | 1,607 | 0 | 0 | 1,508 | 1,560 | 0 | 0 | 0 | 4,524 |

- Numbers may not add due to rounding.

Figure 6-9: Total relative annual resource costs, 2030 (constrained and unconstrained), showing changes compared with 2030 Scenario 3 (constrained) (¢/kWh).

Notes:  Energy efficiency and solar include costs resulting from individual customer investments that do not reflect the benefits the owners would receive. Production costs reflect the price of carbon emissions at $19/ton.

Table 6-12
Relative Annual Resource Costs, 2030 (¢/kWh)(a)

| Transmission | Scenario | Production Cost | 15% Transm. Cost | 15% Ties | 15% Comb. Cycle | 15% New Onshore Wind | 15% New Offshore Wind | 15% Solar | 15% Energy Efficiency | 15% Battery | Total |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Constrained | Renew Plus | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 |
|  | EE + Offshore | −0.21 | −0.20 | −0.13 | 0.00 | −0.61 | 0.57 | 0.00 | 0.51 | 0.00 | −0.07 |
|  | Onshore Less EE/PV | 0.67 | 0.03 | −0.12 | 0.14 | 0.57 | 0.09 | −1.70 | −0.48 | −0.22 | −1.01 |
|  | Wind Less Nuclear | 0.23 | 0.20 | 0.00 | 0.00 | 0.89 | 0.92 | 0.00 | 0.00 | 0.00 | 2.23 |
| Unconstrained | Renew Plus | −0.10 | 0.48 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.39 |
|  | EE + Offshore | −0.21 | −0.20 | −0.13 | 0.00 | −0.61 | 0.57 | 0.00 | 0.51 | 0.00 | −0.08 |
|  | Onshore Less EE/PV | 0.45 | 0.75 | −0.12 | 0.14 | 0.57 | 0.09 | −1.70 | -−0.48 | −0.22 | −0.51 |
|  | Wind Less Nuclear | −0.09 | 0.94 | 0.00 | 0.00 | 0.89 | 0.92 | 0.00 | 0.00 | 0.00 | 2.66 |

- Numbers may not add due to rounding.

Figure 6-8 and Figure 6-9 and Table 6-11 and Table 6-12 illustrate differences among the scenarios for 2030. The Onshore Less EE/PV scenario, which requires the lowest investment in new resources development, has the lowest total RARC. Although the production costs are higher for this scenario than the other scenarios with other mixes of large penetrations of renewable resources, the figures show significantly higher total RARCs for the Renew Plus, EE +Offshore, and Wind Less Nuclear scenarios as a result of their higher annual carrying charges for new resources. The Wind Less Nuclear scenario results in the highest RARC due to higher resource and transmission development costs. Although the EE + Offshore scenario has the lowest production costs across all scenarios, its total RARC is only slightly lower than the Renew Plus scenario after consideration of all annual capital costs.

At approximately 171 TWh, the demand forecast, BTM PV, and EE result in the same net systemwide demand for the Renew Plus, EE + Offshore, and Wind Less Nuclear scenarios. As such, the cents per kilowatt-hour metric uses the same denominator for these three cases, which is directly proportional to the RARC expressed in billions of dollars. The demand in the Onshore Less EE/PV scenario was approximately 158 TWh, which increases the cents per kilowatt-hour RARC metric compared with the other cases. Although the Onshore Less EE/PV scenario resulted in the highest production costs, especially for the constrained case, it shows the lowest total RARC expressed both in billions of dollars and cents per kilowatt-hour because it has the lowest annual fixed costs across all cases.

## Environmental Results

The results for the metrics that assessed the environmental impacts associated with the different scenarios provide some insight on future emission trends. The total CO2 emissions associated with the different scenarios are directly tied to the type and amount of fossil fuels the different scenarios use to generate electricity. Assumed CO2 allowance prices based on the Regional Greenhouse Gas Initiative are key drivers of production costs, and CO2 emissions pose a potential regulatory constraint during the study years.

### Ability of the System to Meet Renewable Portfolio Standards

The 2017 Economic Study request accounted for an increase in the regional goal for renewable resources in effect at the time assumptions were made for the 2016 NEPOOL Scenario Analysis. The 2016 study showed that the resource assumptions used for the Renew Plus scenario exceeded the physical requirements of the RPS goals for new resources. The three new scenarios of the 2017 study reflect different mixes of renewable resources that would also physically exceed the regional RPS goals.

### Carbon Dioxide Emissions and RGGI Goals

At the time the study was conducted, the potential RGGI targets for total CO2 emissions  in the New England states for 2030 ranged from 13.3 million short tons (5.0% reduction) to 19.9 million short tons (2.5% reduction). RGGI currently permits the use of allowances, regardless of source or issuing state, and offsets to meet compliance obligations in any state. Allowances may be available from primary or secondary markets or neighboring states, or they may be banked and used in future compliance periods. The states also may release cost-containment reserves, which are additional CO2 allowances issued if auction prices exceed certain thresholds. RGGI excludes generators smaller than 25 MW and municipal solid waste units. Figure 6-10 compares the total CO2 emissions for the scenarios with the potential annual RGGI emission limits for the New England region. The figure shows total regional CO2 emissions for all generating units and for units subject to RGGI requirements.

Figure 6-10: CO2 emissions, 2030 (millions of short tons, %) compared with range of RGGI limits.

Table 6-13 shows more detailed CO2 emission results for 2030 and compares New England CO2 emissions with the total annual emission targets for New England and for the entire RGGI region. The scenarios with the large-scale development and production of zero-emitting resources result in lower CO2 emissions. Key observations are as follows:

- The Renew Plus and EE + Offshore scenarios satisfy both the New England 2.5% and 5.0% reduction targets by 2030, with or without the transmission system constraints modeled.

- The EE + Offshore scenario results in the lowest overall emissions.

- The Wind Less Nuclear scenario produces more carbon emissions compared with the Renewables Plus scenario. When the transmission system is unconstrained, carbon emissions of the Wind Less Nuclear scenario satisfy both the New England 2.5% and 5% reduction targets. When the transmission system is constrained, carbon emissions of the Wind Less Nuclear scenario satisfy the New England 2.5% reduction target but exceed the New England 5.0% reduction target.

- The Onshore Less EE/PV scenario produces the most carbon emissions due to the retirement of zero-emitting nuclear generation and the addition of 1,378 MW of NGCC units. Carbon emissions for this scenario satisfy the New England 2.5% reduction target but exceed the New England 5.0% reduction target, under both a constrained and unconstrained transmission system.

Table 6-13
CO2 Emissions Compared with RGGI Targets, 2030 (Millions of Short Tons and %)(a)

| Transmission | Scenario | All Sources New England (M Short Tons) | New England RGGI Sources (M Short Tons) | New England RGGI Sources’ Percentage of New England 2.5% Reduction (%) |  | New England RGGI Sources’ Percentage of New England 5.0% Reduction (%) | New England RGGI Sources’ Percentage of 9 RGGI States’ 2.5% Reduction (%)(b) | New England RGGI Sources’ Percentage of 9 RGGI States’ 5.0% Reduction (%)(b) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Unconstrained | Renew Plus | 13.1 | 10.1 |  | 51% | 76% | 17% | 26% |
|  | EE + Offshore | 11.2 | 8.4 |  | 42% | 63% | 14% | 21% |
|  | Onshore Less EE/PV | 19.7 | 16.5 |  | 83% | 124% | 28% | 42% |
|  | Wind Less Nuclear | 13.1 | 10.4 |  | 52% | 78% | 18% | 27% |
| Constrained | Renew Plus | 14.3 | 11.1 |  | 56% | 83% | 19% | 28% |
|  | EE + Offshore | 11.1 | 8.4 |  | 42% | 63% | 14% | 21% |
|  | Onshore Less EE/PV | 22.4 | 18.9 |  | 95% | 142% | 32% | 48% |
|  | Wind Less Nuclear | 17.7 | 14.3 |  | 72% | 108% | 24% | 37% |

(a) 	The proposed RGGI caps used were under consideration by the RGGI states in 2017. The RGGI states agreed to final annual caps for 2021 through 2030 in a model rule text announced on December 19, 2017. The final caps differ slightly from the proposed caps used in this analysis: the final 2030 caps total 54.7 million short tons for all nine states and 18.5 million short tons for New England (moving from a given percentage reduction to a fixed 2.275 million tons of CO2 reduction per year). By comparison, for a 2.5% reduction, the 2030 caps used in this analysis total 58.6 million short tons for all nine states and 19.9 million short tons for New England. The total and New England regional caps will likely change again with the planned additions of New Jersey and Virginia to RGGI.

(b) 	The assumed RGGI caps for all nine states total 58.6 million short tons for a 2.5% annual reduction and 39.1 million short tons for a 5% reduction.

### Spilled Renewable Resource Energy

Figure 6-11 and Table 6-14 show the total amount of spilled renewable resource energy, including photovoltaics, onshore wind, offshore wind, New England hydro, and imports on existing and new ties from Québec and the Maritimes assumed to be supplied by hydroelectric energy. The highest amount of renewable spillage occurs in the Wind Less Nuclear (transmission constrained) scenario at 16,664 GWh, or 18.01% of all production by renewables. Most of the spillage is the direct result of transmission constraints in Maine, especially north of the Surowiec South interface. Relieving the Surowiec South and Orrington South interfaces allows the delivery of electric energy produced by renewable resources to the load centers in southern New England.

Figure 6-11: Total amount of “spilled” energy produced by renewable resources, 2030 (unconstrained and constrained cases) (GWh, %).

Table 6-14
Total Amount of “Spilled” Energy Produced by Renewable Resources, 2030
(Unconstrained and Constrained Cases) (GWh, %)

| Transmission | Scenario | Renewable Energy Profile (GWh) | Total Spilled (GWh) | % of Total Renewable Spilled (%)(a) | Total Spilled Due to Transmission Constraints (GWh)(b) | Total Spilled North of Surowiec South (GWh) | Total Renewables North of Surowiec South (GWh) | % of Total Renewables Spilled North of Surowiec South (%)(c) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Unconstrained | Renew Plus | 73,237 | 3,296 | 4.50% | Unconstrained reference | 766 | 18,692 | 23.26% |
|  | EE + Offshore | 62,686 | 4,285 | 6.83% | Unconstrained reference | 916 | 10,162 | 21.37% |
|  | Onshore Less EE/PV | 63,983 | 4,011 | 6.27% | Unconstrained reference | 1,251 | 25,060 | 31.19% |
|  | Wind Less Nuclear | 92,517 | 6,516 | 7.04% | Unconstrained reference | 1,778 | 31,099 | 27.29% |
| Constrained | Renew Plus | 73,237 | 6,270 | 8.56% | 2,974 | 4,261 | 18,692 | 67.96% |
|  | EE + Offshore | 62,686 | 4,358 | 6.95% | 73 | 942 | 10,162 | 21.62% |
|  | Onshore Less EE/PV | 63,983 | 10,358 | 16.19% | 6,346 | 9,209 | 25,060 | 88.91% |
|  | Wind Less Nuclear | 92,517 | 16,664 | 18.01% | 10,148 | 14,466 | 31,099 | 86.81% |

(a) % of Total Renewable Spilled = Total Spilled (GWh)/Renewable Energy Profile (GWh).

(b) Total Spilled Due to Transmission Constraints = the difference of the total spilled between the constrained and unconstrained cases.

(c) % of Total Renewable Spilled North of Surowiec South = Total Spilled North of Surowiec South (GWh) / Total Spilled (GWh)

The results show that the large-scale development of remote resources requires transmission additions to avoid spillage. Conversely, the development of resources near load centers in southern New England avoids spillage of renewable energy and diminishes the need for transmission development to avoid congestion.

Across all scenarios, some renewables are spilled when the supply from renewables plus nuclear exceeds load consumption in the unconstrained transmission cases. Adding large amounts of asynchronous resources (PV, wind, and HVDC imports) and energy efficiency would require physical improvements to the system to avoid spilling energy produced by renewable resources, as discussed in Section 6.2. Additionally, storage may operate differently than in the current system, which predominantly stores during the off-peak evening hours and discharges during daytime early evening hours. Overall, the system would require applications of special controls.

# Summary, Conclusions, Transitional Issues, and Next Steps

This section summarizes some of the main results and conclusions of the 2017 Economic Study that assessed the effects of different renewable resource-expansion mixes on the future electric power system in New England. This section also discusses issues regarding transitioning the grid to the studied scenarios with higher amounts of renewables and provides an overview of next steps required for a successful transition.

The stakeholder process provided valuable input to the scenario analysis, including the review of the scope of work, assumptions, methodology, and draft and final results. This report, plus posted data, tables, and spreadsheets, should assist stakeholders in developing their own conclusions.

## Key Observations

The 2017 Economic Study provides many insights into system performance. Disparities of results among the cases are attributable to the differences in the resource mixes for 2030. Key observations are as follows:

- The EE + Offshore scenario shows the effects of the large-scale development of renewable EE, PV, and offshore wind development in southern New England.

- This scenario has the lowest CO2 emissions and, along with the Renew Plus scenario, meets both the 2.5% and 5% RGGI targets for both the constrained and unconstrained cases. The relative annual resource cost (RARC) for the EE + Offshore scenario is similar to the reference RARC (the Renew Plus scenario, 2016 NEPOOL Scenario Analysis 3).

- The Onshore Less EE/PV scenario demonstrates how the large-scale addition of onshore wind resources in northern New England affects the system metrics.

  - This scenario does not meet the 5% RGGI target but has the lowest RARC

- The Wind Less Nuclear scenario demonstrates how the large-scale addition of onshore wind resources in northern New England, combined with the loss of baseload nuclear generation, affects the system metrics.

  - This scenario does not meet the 5% RGGI target, and its RARC is higher than the reference RARC.

- The retirement of resources and the large-scale development of renewable resources in northern New England could trigger investment in the transmission system and special controls.

- More generally, the large-scale development of inverter-based resources throughout the system poses major technical and economic challenges that must be addressed.

- Across all scenarios, natural gas remains on the margin most of the time.

- While all scenarios meet the 2.5% RGGI target assumed in this analysis, only one of the three new 2017 Economic Study scenarios meets the 5% RGGI target assumed in this analysis for the constrained and unconstrained cases. Meeting regional RGGI targets depends on the large-scale development of renewable resources within or deliverable to New England and the compliance flexibility of the program.

- Resource development, including renewable resources and energy efficiency, near New England’s load centers in southern New England reduces the need for transmission expansion. For example, potential offshore wind resources are in electrically favorable locations, and their interconnection to strategic locations in southern New England would reduce the need for other transmission expansion.

## Transitional Issues

The study does not address transitions to the studied scenarios, which could raise several issues that would need to be addressed. As background, the North American Electric Reliability Corporation (NERC) Long-Term Reliability Assessment recommended that policymakers and regulators take these actions:

- Recognize the lead time for the development of generation, transmission, and natural gas infrastructure needed to maintain reliability as industry strives to meet policy goals and initiatives.

- Consider industry study recommendations when reviewing infrastructure requirements.

- Focus on reliability and resilience attributes to limit exposure to risk.

Additionally, as shown in the 2016 NEPOOL Scenario Analysis, scenarios incorporating higher levels of low- or zero-cost energy resources into the system, such as those studied in this analysis. may develop revenue-adequacy issues. In these instances, the general reduction in the hourly LMP may lower a typical new resource’s annual net wholesale energy market revenues to a point where it may not cover the resources’ annual carrying charges.

## Next Steps

- Similar to the 2016 NEPOOL Scenario Analysis, stakeholders can develop their own assumptions and analyze results. For example, stakeholders can develop annual carrying charges, which can be reflected in the generation cost metrics to obtain total investment costs.

The ISO will continue working with stakeholders to facilitate the implementation of technically and economically workable solutions for successfully integrating distributed and variable energy resources, especially during transitional periods. The following issues must be addressed:

- Revising the Forward Capacity Market, such as to implement competitive auctions with sponsored policy resources (CASPR), which is designed to maintain competitively based forward-capacity price signals while, over time, accommodating the entry into the FCM of new resources sponsored by public entities. The CASPR proposal was filed with FERC in January 2018 and became effective in March 2018. CASPR introduced a substitution auction that will be held annually after the primary Forward Capacity Auction. The first CASPR substitution auction will occur with the FCA #13 in February 2019.

- Planning and operating a system with the large-scale development of inverter-based resources, which presents technical challenges that would require investment in the transmission system and special controls

- Examining natural gas system deliverability issues and improving regional energy security

ISO New England , ISO New England Inc. Transmission, Markets, and Services Tariff (ISO tariff), Section II, Open Access Transmission Tariff, Attachment K, “Regional System Planning Process” (January 1, 2018), https://www.iso-ne.com/static-assets/documents/regulatory/tariff/sect_2/oatt/sect_ii.pdf and Stakeholder Process for Submitting Economic Study Requests. PAC presentation (February 22, 2017). CLF, “Request for 2017 Economic Study to Explore Least-Cost, Emissions-Compliant System Topologies” (April 4, 2017), https://www.iso-ne.com/static-assets/documents/2017/04/a7_2017_economic_study_request_clf.pdf and Study to Explore Least-Cost, Emissions-Compliant System Topologies, PAC presentation (April 12, 2017), https://www.iso-ne.com/static-assets/documents/2017/04/a7_2017_economic_study_request_clf_presentation.pdf.

Annual carrying charges represent the annual revenue a facility must receive to cover its annual fixed costs and to remain economically viable.

Spilled renewable resources are those that must reduce output to respect transmission constraints and can include imports from Canada, hydro, wind, and photovoltaics.

ISO New England, NEPOOL Scenario Analysis: Implications of Public Policies on ISO New England Market Design, System Reliability and Operability, Resource Costs and Revenues, and Emissions (November 17, 2017), https://www.iso-ne.com/static-assets/documents/2017/11/final_2016_phase1_nepool_scenario_analysis_economic_study.docx.

Normal transmission system transfer limits account for transmission system security constraints, which consider expected transmission facilities in service and first-contingency (N-1) criteria.

The net Installed Capacity Requirement is the minimum amount of resources (in megawatts) the region needs in a particular year to meet its resource adequacy planning criterion, according to the Northeast Planning Coordinating Council criteria, minus the tie-reliability benefits associated with the Hydro-Québec Phase I/II interface, called Hydro-Québec Interconnection Capability Credits.

The Regional Greenhouse Gas Initiative is a multistate program in the Northeast to reduce the CO2 emissions from fossil power plants 25 MW and larger in these states. Each state is allocated a share (allowance) of an annual emissions cap on the basis of historical emissions and negotiations; one allowance equals the limited right to emit one ton of CO2.

ISO New England, 2016 CELT Report—2016 to 2025 Forecast Report of Capacity, Energy, Loads, and Transmission
(May 2, 2016), https://www.iso-ne.com/static-assets/documents/2016/05/2016_celt_report.xls.

The ISO’s Forward Capacity Auctions are annual auctions of the Forward Capacity Market during which capacity resources compete to obtain a commitment to supply capacity in exchange for a market-priced capacity payment.

A capacity supply obligation is a requirement for a resource to provide capacity, or a portion of capacity, to satisfy a portion of the ISO's Installed Capacity Requirement acquired through a Forward Capacity Auction, a reconfiguration auction, or a CSO bilateral contract through which a market participant may transfer all or part of its CSO to another entity.

Seasonal claimed capability refers to a generator’s maximum production or output during a particular season, adjusted for physical and regulatory limitations.

Detailed transmission interface limits for 2025 used for this study are available in the ISO’s PAC presentation, Transmission Transfer Capabilities Update (June 10, 2016), slide 8, https://smd.iso-ne.com/operations-services/ceii/pac/2016/06/a3_transmission_transfer_capabilities_update.pdf.

EIA, Annual Energy Outlook, 2016: with Projections to 2040 (August 2016), https://www.eia.gov/outlooks/archive/aeo16/.

Assumptions for 2030 emission allowance prices were $6.18/ton for both nitrogen oxides (NOX) and sulfur dioxide (SO2).

A behind-the-meter resource typically is generation output by a relatively small, individual, on-site installation directly connected to a distribution facility or retail customer facility and not the regional power system, making it “invisible” to the ISO. BTM resources reduce net system demand.

The large-scale integration of inverter-based resources and transmission devices would require much greater use of special controls on central station and distributed resources, system-protection upgrades, and other system improvements not fully considered in this study. See the Electric Power Research Institute’s Grid Impacts and Challenges Arising from the Integration of Inverter-Based Variable Resources, PAC presentation (October 19, 2016), https://www.iso-ne.com/static-assets/documents/2016/10/a3_integration_and_planning_of_large_amounts_of_inverter_based_resources.pptx.

Consumer costs are determined by distribution rates, which may account for a variety of factors the RARC does not consider.

ISO New England Inc. Transmission, Markets, and Services Tariff (ISO tariff), Section II, Open Access Transmission Tariff, Attachment K, “Regional System Planning Process” (July 29, 2016), https://iso-ne.com/static-assets/documents/regulatory/tariff/sect_2/oatt/sect_ii.pdf.

Load-serving entity (LSE) energy expenses are the total electric energy revenues that resources and imports from neighboring systems would receive for supplying electric energy to the wholesale market plus the cost of congestion.

OATT, Attachment K, Section 4.1b.

CLF, “Request for 2017 Economic Study to Explore Least-Cost, Emissions-Compliant System Topologies”
(April 4, 2017), https://www.iso-ne.com/static-assets/documents/2017/04/a7_2017_economic_study_request_clf.pdf and Study to Explore Least-Cost, Emissions-Compliant System Topologies, PAC presentation (April 12, 2017), https://www.iso-ne.com/static-assets/documents/2017/04/a7_2017_economic_study_request_clf_presentation.pdf.

The general and detailed study scope of work and assumptions are available in the following ISO PAC presentation: 2017 Economic Study Scope of Work (May 11, 2017), https://www.iso-ne.com/static-assets/documents/2017/05/a2_2017_economic_study_scope_of_work.pdf. The results were discussed with the PAC and reposted to reflect comments received at the February 14, 2018, meeting; see https://www.iso-ne.com/static-assets/documents/2018/02/a3_2017_economic_study.pdf.

A behind-the-meter resource typically is generation output by a relatively small, individual, on-site installation directly connected to a distribution facility or retail customer facility and not the regional power system, making it “invisible” to the ISO. BTM resources reduce net system demand.

“I.3.9” refers to the section of the ISO tariff that includes the requirements for market participants’ and transmission owners’ (TO) submissions of new or revised plans for adding to or changing any generation or demand resource or transmission facility 69 kV or larger that could have a significant effect on the stability, reliability, or operating characteristics of a TO’s or market participant’s transmission facility or system. It also contains the ISO’s requirements for reviewing and approving these applications. These projects are included on the ISO’s Interconnection Request Queue, available at https://www.iso-ne.com/system-planning/transmission-planning/interconnection-request-queue.

ISO New England, 2017 Economic Study, Scope of Work, PAC presentation (May 25, 2017), https://www.iso-ne.com/static-assets/documents/2017/05/a2_2017_economic_study_scope_of_work.pdf.

Refer to the ISO’s “Energy Efficiency Working Group,” webpage (2017) for information and presentations on how the ISO accounts for energy-efficiency programs in its energy-efficiency forecasts; https://www.iso-ne.com/committees/planning/energy-efficiency-forecast.

This is the standard ISO model used for representing hourly demand for economic studies. Several summer heat waves and a moderate winter were experienced in 2006.

A 50/50 peak demand is a peak load with a 50% chance of being exceeded because of weather conditions, expected to occur in the summer in New England at a weighted New England-wide temperature of 90.2 °F, and in the winter, 7.0 °F.

NREL, “Solar Power Data for Integration Studies,” webpage (n.d.), https://www.nrel.gov/grid/solar-power-data.html.

Because PV does not produce energy as the sun sets, larger amounts of PV result in the net peak load (demand minus PV production) occurring later in the day during the summer. Thus, increased amounts of PV become less effective at reducing the net peak load.

In general, BTM PV GWh = (2,959 GWh ÷ 2,307 MW) × (MW nameplate BTM). Thus, (2,959 GWh ÷ 2,307 MW) × 6,000 MW = 7,695 GWh.

Seasonal claimed capability is a generator's maximum production or output during a particular season, adjusted for physical and regulatory limitations.

Regional System Plans are available at https://www.iso-ne.com/system-planning/system-plans-studies/rsp.

Operating reserve is the megawatt capability of a power system greater than system demand, which is required for providing frequency regulation, correcting load forecasting errors, and handling forced outages, and is drawn from spinning and nonspinning sources of power that may be used to recover from a contingency.

The ISO’s requirements for operating reserves are addressed in ISO New England Operating Procedure No. 8—Operating Reserve and Regulation (September 21, 2017), https://www.iso-ne.com/static-assets/documents/rules_proceds/operating/isone/op8/op8_rto_final.pdf.

A first contingency is the loss of the power system element (facility) with the largest impact on system reliability. Ten-minute spinning reserve (TMSR) is operating reserve provided by on-line operating generation that can increase output within 10 minutes in response to a contingency. Ten-minute nonspinning reserve (TMNSR) is operating reserve provided by off-line generation that can be electrically synchronized to the system and increase output within 10 minutes in response to a contingency.

Thirty-minute operating reserve (TMOR) is provided by on-line or off-line operating-reserve generation that can either increase output within 30 minutes or be electrically synchronized to the system and increase output within 30 minutes in response to a contingency. A fast-start resource can be electrically synchronized to the system and reach its maximum production or output within 10 to 30 minutes to respond to a contingency and serve demand. It also can be a demand resource that helps with recovery from a contingency and assists in serving peak demand.

The NREL database includes 8,760 hours of locational data that can be used to determine PV production for different amounts and locations of PV. A similar database exists for onshore and offshore wind.

This is similar to the wind-addition assumptions presented in the 2015 Economic Study Evaluation of Offshore Wind Deployment ISO New England, 2015 Economic Study—Evaluation of Offshore Wind Deployment (September 2, 2016), https://www.iso-ne.com/static-assets/documents/2016/09/2015_economic_study_offshore_wind_development_final.docx.

Dual-fuel capability is when a generator has the flexibility and storage capacity to use two types of fuel, typically oil and natural gas.

The transfer capabilities for external ties exceed the values simulated in the GridView simulations. For example, Phase II has a transfer capability of up to 2,000 MW, but lower values were simulated in the economic dispatch.

ISO New England, 2015 Economic Study—Evaluation of Increasing the Keene Road Export Limit (September 2, 2016),  https://www.iso-ne.com/static-assets/documents/2016/09/2015_economic_study_keene_road_increased_export_limits_fina.docx; 2015 Economic Study—Evaluation of Offshore Wind Deployment (September 2, 2016), https://www.iso-ne.com/static-assets/documents/2016/09/2015_economic_study_offshore_wind_development_final.docx; 2015 Economic Study— Strategic Transmission Analysis—Onshore Wind Integration (September 2, 2016), https://www.iso-ne.com/static-assets/documents/2016/09/2015_economic_study_onshore_wind_integration_final.docx.

The threshold price for imports was not included in the production cost metric because imports were assumed to be price takers.

EIA, 2016 Annual Energy Outlook (2016), http://www.eia.gov/forecasts/aeo/index.cfm.

New York ISO, 2015 Congestion Assessment and Resource Integration Study (CARIS), emission allowance prices (March 20, 2015).

New York ISO, “2016 CARIS 2 Input Data Summary,” Phase 2 base case fuel and emission prices spreadsheet
(July 14, 2016), http://www.nyiso.com/public/webdocs/markets_operations/services/planning/Planning_Studies/Economic_Planning_Studies_(CARIS)/CARIS_Input_Assumptions/2016%20CARIS%202%20Input%20Data%20Summary.xls.

A fixed cost is a cost that does not change with an increase or decrease in the amount of energy production. Fixed costs are expenses a company must pay, independent of any business activity. It is one of the two components of the total cost of running a business, along with variable operating costs.

Concentric Energy Advisors determined that the levelized cost of EE was $35.97/kW-month. The annual carrying charge of EE = $431.64/kW-year from $35.97/kW-month × 12. Refer to the Concentric Energy Advisors and Mott MacDonald presentation, ISO-NE CONE and ORTP Analysis (September 13, 2016), https://view.officeapps.live.com/op/view.aspx?src=https%3A%2F%2Fwww.iso-ne.com%2Fstatic-assets%2Fdocuments%2F2016%2F09%2Fa7_cone_ortp_concentric_energy_advisors.pptx.

The large-scale integration of inverter-based resources and transmission devices would require much greater use of special controls on central station and distributed resources, system-protection upgrades, and other system improvements not fully considered in this study.

The integrator system is conceptually similar to the type of upgrades considered in the ongoing 2016 Maine Resource Integration Study. See ISO New England, 2016 Maine Resource Integration Study—Status Update, PAC presentation (February 9, 2017), https://smd.iso-ne.com/operations-services/ceii/pac/2017/02/a6_maine_resource_integration_study.pdf and 2016 Maine Resource Integration Study—Steady-State Results, PAC presentation (September 21, 2016), https://smd.iso-ne.com/operations-services/ceii/pac/2016/09/a3_maine_resource_integration_study.pdf.

See the ISO’s PAC presentation containing the assumptions and results (February 14, 2018), https://www.iso-ne.com/static-assets/documents/2018/02/a3_2017_economic_study.pdf.

See the appendix of the assumptions and results in the ISO’s presentation cited above.

Subarea LMPs are calculated as the average value over the 8,760 hours of a year. Because the RSP subareas reflect different load shapes, the average LMPs are not exactly the same for every subarea in the unconstrained cases.

The study simulation results for uplift account for a generating unit’s total operating costs that energy market revenues may not be fully cover over the course of a calendar day.

Congestion here is calculated as the difference between load-serving entity energy expenses of the constrained and the unconstrained cases.

Annual interface congestion is calculated as the sum of hourly differences between LMPs in the RSP bubbles bordering the interface multiplied by the interface limit.

Information about the ISO’s 2016 Maine Resource Integration Study is available at https://www.iso-ne.com/system-planning/key-study-areas/maine.

In some systems, the shape varies even more. For example, in Hawaii the shape is called “Nessie” after the Loch Ness Monster. On April 21, 2018, the New England system experienced minimum daily net load during daylight hours for the first time.

IEEE (https://www.ieee.org/index.html) provides many references, and extensive discussions took place at the PAC on October 19, 2016; see Electric Power Research Institute, Grid Impacts & Challenges Arising from the Integration of Inverter-Based Variable Resources, PAC presentation (October 19, 2016), https://www.iso-ne.com/static-assets/documents/2016/10/a3_integration_and_planning_of_large_amounts_of_inverter_based_resources.pptx. In addition, the North American Electric Reliability Corporation (NERC) Essential Reliability Services Working Group has identified similar issues; see NERC, Essential Reliability Services Task Force Measures Framework Report (November 2015), http://www.nerc.com/comm/Other/essntlrlbltysrvcstskfrcDL/ERSTF%20Framework%20Report%20-%20Final.pdf and additional materials posted at the NERC Essential Reliability Services Working Group (ERSWG) and Distributed Energy Resources Task Force (DERTF) web page at http://www.nerc.com/comm/Other/Pages/Essential-Reliability-Services-Task-Force-(ERSTF).aspx. Also see: Nicholas Miller, “Prepared Testimony for FERC 2018 Reliability Technical Conference, Docket No. AD18-11-000 on July 31, 2018” (Hickory Ledge LLC, July 13, 2018), https://elibrary.ferc.gov/idmws/common/downloadOpen.asp?downloadfile=20180802%2D4021%2833041655%29%2Epdf&folder=2940727&fileid=14991749&trial=1.

RGGI, Inc., “Program Overview,” webpage (n.d.), http://www.rggi.org/design/overview. The RGGI CO2 budget (cap) is equal to the total number of CO2 allowances issued by RGGI states in a given year. A CO2 allowance represents a limited authorization to emit one short ton of CO2 from a regulated source, as issued by a participating state.

NERC, 2017 Long-Term Reliability Assessment (December 13, 2017), http://www.nerc.com/pa/rapa/ra/reliability%20assessments%20dl/nerc_ltra_12132017_final.pdf.

ISO New England, NEPOOL Scenario Analysis: Implications of Public Policies on ISO New England Market Design, System Reliability and Operability, Resource Costs and Revenues, and Emissions (November 17, 2017), https://www.iso-ne.com/static-assets/documents/2017/11/final_2016_phase1_nepool_scenario_analysis_economic_study.docx.

FERC, Order on Tariff Filing, Docket No. ER18-619-000, 162 FERC ¶ 61,205 (March 9, 2018), https://www.iso-ne.com/static-assets/documents/2018/03/er18-619-000_3-9-18_order_accept_caspr.pdf.