## Slide 1
Planning Advisory Committee Meeting
Net Installed Capacity Requirements (ICRs), Representative Future Net ICRs and Operable Capacity Analysis for 2019 Regional System Plan
Peter Wong
Resource studies and assessments
May 21, 2019 | westborough, ma

## Slide 2: Purpose/Background
To provide an overview of the results of the various resource adequacy related studies to be published in the 2019 Regional System Plan (RSP 19)
The scope of work for RSP19 was presented to PAC on February 13, 2019
  https://www.iso-ne.com/static-assets/documents/2019/02/a6_rsp19_scope_of_work.pptx
    In the “Upcoming PAC Discussions” slide:
      “Projections of the systemwide and locational need for capacity and operating reserves”

## Slide 3: ACRONYMS

## Slide 4: Acronyms
ARA – Annual Reconfiguration Auction
BTM PV – Behind-the-meter Photovoltaic
CCP – Capacity Commitment Period
CSO – Capacity Supply Obligation
CELT – Capacity, Energy, Loads and Transmission
CT – Connecticut
DR – Demand Resource
EE – Energy Efficiency
FCA – Forward Capacity Auction
FERC – Federal Energy Regulatory Commission
HQICCs – Hydro-Quebec Interconnection Capability Credits
ICR – Installed Capacity Requirement
ISO – ISO New England
LSR – Local Sourcing Requirement
MCL – Maximum Capacity Limit

## Slide 5: Acronyms, cont.
ME – Maine
NEMA/Boston – Northeast Massachusetts/Boston
NH – New Hampshire
NNE – Northern New England
OP-4 – Operating Procedure No. 4, Action During a Capacity Deficiency
PAC – Planning Advisory Committee
RI – Rhode Island
RSP – Regional System Plan
SA – Substitution Auction
SEMA/RI – South East Massachusetts/Rhode Island
SENE – South East New England
VT – Vermont
WCMA – West Central Massachusetts

## Slide 6: SYSTEMWIDE AND LOCAL CAPACITY RESOURCE NEEDS

## Slide 7: Actual and Representative New England Net Installed Capacity Requirements and Resulting Reserves, 2019-2020 to 2028-2029
The 2019 CELT forecast 50/50 peak loads reflect the load reductions from the BTM PV forecast.
Net ICR values for 2019-2020 to 2022-2023 are the latest values approved by FERC. These net ICR values were developed using 2018 CELT report loads. The representative future Net ICR values are calculated using the FCA 13 resources’ assumptions and 2019 CELT load forecast.
The resulting reserves percentage is calculated using the 2019 CELT Report loads. The resulting reserves percentage for 2019-2020 to 2022-2023, when calculated using their respective 2018 CELT Report loads, ranged from 16.1 % to 16.8% (These values are not shown in the above table).
The net ICR for 2023-2024 is under development and scheduled to be filed with FERC in November 2019.
Commitment Periods | 2019 CELT Forecast 50/50 Peak (MW) (a) | Actual and Representative Future Net ICR(b) (MW) | Resulting Reserves(c) (%)
2019-2020 | 28,236 | 33,390 | 18.3
2020-2021 | 28,353 | 33,520 | 18.2
2021-2022 | 28,499 | 33,550 | 17.7
2022-2023 | 28,670 | 33,750 | 17.7
2023-2024 | 28,838 | TBD(d) | TBD(d)
2024-2025 | 29,014 | 32,950 | 13.6
2025-2026 | 29,196 | 33,165 | 13.6
2026-2027 | 29,382 | 33,390 | 13.6
2027-2028 | 29,576 | 33,625 | 13.7
2028-2029 | 29,781 | 33,870 | 13.7

## Slide 8: Actual Net ICR for 2019-2020 through 2022-2023
The Net ICR values for 2019-2020 through 2022-2023 are the values calculated in 2018 and approved by FERC for FCA 13 and the ARAs that have been or will be conducted in 2019
  Background material relating to FCA 13 ICR can be downloaded at:
    https://www.iso-ne.com/static-assets/documents/2018/09/a5_icr_fca_13_and_related_values.zip
    https://www.iso-ne.com/static-assets/documents/2018/11/icr_filing_fca_13.pdf
    https://www.iso-ne.com/static-assets/documents/2018/11/updates_to_assumptions_used_in_icr.pdf
    https://www.iso-ne.com/static-assets/documents/2019/01/er19-291-000.pdf
  Background material relating to ICRs for the ARAs for 2019-2020, 2020-2021 and 2021-2022 can be downloaded at:
    https://www.iso-ne.com/static-assets/documents/2018/10/a6_icr_requirements_for_ara3_2019_2020_ara2_2020_2021_ara1_2021_2022.zip
    https://www.iso-ne.com/static-assets/documents/2018/11/icr_for_aras_2019.pdf
    https://www.iso-ne.com/static-assets/documents/2019/01/er19-447-000.pdf

## Slide 9: Actual Net ICR for 2019-2020 and Representative Net ICR for 2024-2025 through 2028-2029
Actual net ICR for 2023-2024 is under development*
  PSPC final review of all assumptions – June 20 & July 25, 2019
  PSPC review of ISO recommendation of ICR values – August 9 & August 29, 2019
  RC review/vote of ISO recommendation of ICR values – August 20 & September 25, 2019
  PC review/vote of ISO recommendation of ICR values – October 4, 2019
  File with FERC by November 5, 2019.
Representative net ICRs for 2024-2025 through 2028-2029 were developed using the methodology described in Section III. 12 of Market Rule 1.
  The assumptions relating to resources including load relief from OP-4 actions are the same as those used to develop the ICR for FCA 13. The loads are based on the 2019 CELT load forecast.
*https://www.iso-ne.com/static-assets/documents/2019/04/a6_icr_related_values_development_schedule_for_2019.pptx

## Slide 10: Summary of the FCA Obligations at the Conclusion of Each Auction (MW)(a)
  Information regarding the results of FCAs is available at https://www.iso-ne.com/static-assets/documents/2018/02/fca_obligations.xlsx.
  The net ICR equals the ICR minus the Hydro-Québec Interconnection Capability Credits.
  For FCA 13, the Capacity Supply Obligation column represents obligations acquired in both the primary auction (34,785 MW) and substitution auction (54 MW).
Capacity Commitment Period | FCA | ICR | HQICCs | Net ICR(b) | Capacity Supply Obligation(c) | Self-Supply Obligation | Import Capacity Supply Obligation
2018-2019 | 9 | 35,142 | 953 | 34,189 | 34,695 | 1,287 | 1,449
2019-2020 | 10 | 35,126 | 975 | 34,151 | 35,567 | 1,586 | 1,450
2020-2021 | 11 | 35,034 | 959 | 34,075 | 35,835 | 1,550 | 1,235
2021-2022 | 12 | 34,683 | 958 | 33,725 | 34,828 | 1,644 | 1,217
2022-2023 | 13 | 34,719 | 969 | 33,750 | 34,839 | 1,696 | 1,188

## Slide 11: Meeting Long-term Resource Adequacy Needs (MW)
The 2019 CELT forecast 50/50 peak loads reflect the load reductions from the BTM PV forecast. Details of the BTM PV forecast are available at https://www.iso-ne.com/static-assets/documents/2019/04/final-2019-pv-forecast.pdf.
b) FCA 13 known resources are based on FCA 13 auction results, which includes Mystic 8 and 9 and assumed not retired for this analysis. Details are available at https://www.iso-ne.com/static-assets/documents/2019/02/fca_13_results_filing.pdf.
c) EE cumulative forecast values are based on the 2019 EE forecast. Details are available at https://www.iso-ne.com/system-planning/system-forecasting/energy-efficiency-forecast.
d) Additional resources would be required if additional resources retire or fewer capacity imports obtain CSOs.
Commitment Period | 2019 CELT Forecast 50/50 Peak (MW) (a) | Representative Net ICR (Need) | FCA 13 (Known Resources)(b) | EE Cumulative Forecast Values (New Resource)(c) | Resource Surplus/Shortage(d)
2024-2025 | 29,014 | 32,950 | 34,839 | 581 | 2,470
2025-2026 | 29,196 | 33,165 | 34,839 | 817 | 2,491
2026-2027 | 29,382 | 33,390 | 34,839 | 1,018 | 2,467
2027-2028 | 29,576 | 33,625 | 34,839 | 1,185 | 2,399
2028-2029 | 29,781 | 33,870 | 34,839 | 1,322 | 2,291

## Slide 12: FCA 9 through FCA 13 Capacity Zones’ LSR and MCL (MW)
Source: “Summary of Historical Installed Capacity Requirements and Related Values Tables” in “Summary of the ICR and Related Values and Associated Assumptions” spreadsheet, https://www.iso-ne.com/static-assets/documents/2016/12/summary_of_historical_icr_values.xlsx. These are the latest values filed with FERC.
The SENE Capacity Zone is the aggregation of the NEMA/Boston and SEMA/RI Load Zones. The NNE capacity zone is the aggregation of the Maine, New Hampshire and Vermont Load Zones.
Capacity Commitment Period |  | LSR (MW)(a) |  |  |  | MCL (MW)(a)
 |  | CT | NEMA/ Boston | SEMA/RI | SENE(b) | NNE(b)
2018-2019 | FCA 9 | 7,020 | 3,391 | 7,479 | N/A | N/A
2019-2020 | FCA 10 | N/A | N/A | N/A | 10,083 | N/A
2020-2021 | FCA 11 | N/A | N/A | N/A | 10,182 | 8,660
2021-2022 | FCA 12 | N/A | N/A | N/A | 9,973 | 8,670
2022-2023 | FCA 13 | N/A | N/A | N/A | 10,141 | 8,545

## Slide 13: OPERABLE CAPACITY ANALYSIS

## Slide 14: Operable Capacity Analysis
The systemwide operable capacity analysis is used to estimate the net capacity that will be available under specific scenarios
The analysis identifies operable capacity margins (i.e., the amount of resources that must be operational to meet peak demand plus operating-reserve requirements) under assumed 50/50 and 90/10 peak-load conditions
The results of this analysis show either a positive or negative operating margin in meeting system operating requirements
A negative margin for a specific scenario indicates the extent of possible mitigation actions that would be required through predefined protocols, such as OP-4

## Slide 15: Operable Capacity Analysis Elements
Load net of BTM PV = the 2019 CELT forecast 50/50 and 90/10 gross peak demand minus the load reduction of BTM PV at peak
Operating reserves = the amount of reserves needed to replace the largest first contingency loss x contingency-reserve adjustment factor of 1.2 + ½ of the 2nd largest contingency loss
  1,400 MW X 1.2 + .5 x 1,250 MW = 1,680 MW + 625 MW = 2,305 MW
Total requirement = load net of BTM PV + operating reserves
Installed capacity = the net ICRs filed with FERC through 2022-2023 CCP and representative net ICRs for 2024-2025 through 2028-2029
Assumed unavailable capacity:
  Summer = 2,100 MW based on historical generator unplanned outages
  Winter = 8,600 MW based on 2014 – 2018 highest historical planned and unplanned generator outages plus the highest amount of historical assumed gas-fired generation at risk during the three week winter peak load period rounded to the nearest 100 MW
Total net capacity = installed capacity – assumed unavailable capacity
Operable capacity margin = total net capacity – total requirement

## Slide 16: Operable Capacity Analysis, cont. 2019 CELT Forecast – Summer (MW)
Note: The values for 2023-2024 are under development as part of the FCA 14 ICR development process.
Chart: Capacity Commitment Period
| 2020-2021 | 2021-2022 | 2022-2023 | 2023-2024 | 2024-2025 | 2025-2026 | 2026-2027 | 2027-2028 | 2028-2029
Total Net Capacity | 31420 | 31450 | 31650 | 0 | 30850 | 31065 | 31290 | 31525 | 31770
50/50 Peak Load Plus Operating Reserve | 30658 | 30804 | 30975 | 31144 | 31320 | 31500 | 31687 | 31881 | 32085
90/10 Peak Load Plus Operating Reserve | 32578 | 32754 | 32957 | 33156 | 33363 | 33575 | 33793 | 34018 | 34253

## Slide 17: Operable Capacity Analysis, cont. 2019 CELT Forecast – Summer (MW)
Capacity Commitment Period (Summer MW) |  | 2020-2021 | 2021-2022 | 2022-2023 | 2023-2024 | 2024-2025 | 2025-2026 | 2026-2027 | 2027-2028 | 2028-2029
50/50 forecast | Load net of BTM PV(a) | 28,353 | 28,499 | 28,670 | 28,838 | 29,014 | 29,196 | 29382 | 29,576 | 29,781
 | Operating reserves(b) | 2,305 | 2,305 | 2,305 | 2,305 | 2,305 | 2,305 | 2,305 | 2,305 | 2,305
 | Total requirement | 30,658 | 30,804 | 30,975 | 31,143 | 31,319 | 31,501 | 31,687 | 31,881 | 32,086
 | Installed capacity (net ICR)(c) | 33,520 | 33,550 | 33,750 | N/A | 32,950 | 33,165 | 33,390 | 33,625 | 33,870
 | Assumed unavailable capacity | −2,100 | −2,100 | −2,100 | −2,100 | −2,100 | −2,100 | −2,100 | −2,100 | −2,100
 | Total net capacity(d) | 31,420 | 31,450 | 31,650 | N/A | 30,850 | 31,065 | 31,290 | 31,525 | 31,770
 | Operable capacity margin(e)— 50/50 forecast | 762 | 646 | 675 | N/A | -469 | -436 | -397 | -356 | -316
90/10 forecast | Load net of BTM PV | 30,273 | 30,449 | 30,652 | 30,851 | 31,058 | 31,270 | 31,488 | 31,713 | 31,948
 | Operating reserves(b) | 2,305 | 2,305 | 2,305 | 2,305 | 2,305 | 2,305 | 2,305 | 2,305 | 2,305
 | Total requirement | 32,578 | 32,754 | 32,957 | 33,156 | 33,363 | 33,575 | 33,793 | 34,018 | 34,253
 | Installed capacity (net ICR)(c) | 33,520 | 33,550 | 33,750 | N/A | 32,950 | 33,165 | 33,390 | 33,625 | 33,870
 | Assumed unavailable capacity | −2,100 | −2,100 | −2,100 | −2,100 | −2,100 | −2,100 | −2,100 | −2,100 | −2,100
 | Total net capacity(d) | 31,420 | 31,450 | 31,650 | N/A | 30,850 | 31,065 | 31,290 | 31,525 | 31,770
 | Operable capacity margin(e)— 90/10 forecast | -1,158 | -1,304 | -1,307 | N/A | -2,513 | -2,510 | -2,503 | -2,493 | -2,483
Note: The values for 2023-2024 are under development as part of the FCA 14 ICR development process.

## Slide 18: Operable Capacity Analysis, cont.
Notes related to the “Summer Operable Capacity Analysis” table from previous slide:
These values are net of BTM PV, consistent with the other projections in this section. Because this table uses net ICR, the ISO does not subtract the EE forecast; EE is considered part of the resource mix meeting the ICR
The 2,305 MW value of operating reserves is based on the following assumptions: a first contingency of 1,400 MW plus a 20% increase in the 10-minute operating reserve to compensate for nonperformance of the reserve generating units (discussed in Section 4.4.1 of RSP 19) equal to 280 MW, and 30-minute reserves of 625 MW (one half 2nd largest contingency of 1,250 MW)
Net ICR values for 2020-2021 to 2022-2023 are the latest values accepted by FERC. These net ICR values were developed using 2018 CELT Report loads. The net ICR values for other years are consistent with the representative future net ICR values in slide 7
The net capacity values are equal to the net ICR minus the assumed unavailable capacity
“Operable capacity margin” equals “total net capacity” minus “total requirement”

## Slide 19: Mitigating Actions for a Possible Negative Summer Operable Capacity Margin (MW)
 | Possible Operable Capacity Margin (MW) |  | Load or Capacity Relief Actions of OP-4 (MW) |  |  |  | 
CCP | 50-50 Peak Load Forecast | 90-10 Peak Load Forecast | Depletion of 30-Min Reserve | Tie Benefits | 5% Voltage Reduction | Depletion of 10-Min Reserve to Minimum Level | Possible Relief Available from OP-4 Actions (MW)
2020 | 762 | -1,158 | 625 | 1,950 | 270 | 980 | 2,845
2021 | 646 | -1,304 | 625 | 2,020 | 269 | 980 | 2,914
2022 | 675 | -1,307 | 625 | 2,000 | 266 | 980 | 2,891
2023 | N/A | N/A | N/A | N/A | N/A | N/A | N/A
2024 | -469 | -2,513 | 625 | 2,000 | 257 | 980 | 2,882
2025 | -436 | -2,510 | 625 | 2,000 | 257 | 980 | 2,882
2026 | -397 | -2,503 | 625 | 2,000 | 257 | 980 | 2,882
2027 | -356 | -2,493 | 625 | 2,000 | 258 | 980 | 2,883
2028 | -316 | -2,483 | 625 | 2,000 | 259 | 980 | 2,884

## Slide 20: Operable Capacity Analysis, cont. 2019 CELT Forecast – Winter (MW)
Chart: Capacity Commitment Period
| 2020-2021 | 2021-2022 | 2022-2023 | 2023-2024 | 2024-2025 | 2025-2026 | 2026-2027 | 2027-2028 | 2028-2029
Total Net Capacity, 50/50 | 25420 | 25450 | 25650 | 0 | 24840 | 25065 | 25290 | 25525 | 25770
Total Net Capacity, 90/10 | 24920 | 24950 | 25150 | 0 | 24350 | 24565 | 24790 | 25025 | 25270
50/50 Peak Load Plus Operating Reserve | 25583 | 25725 | 25863 | 26003 | 26136 | 26269 | 26403 | 26542 | 26681
90/10 Peak Load Plus Operating Reserve | 26288 | 26443 | 26588 | 26733 | 26873 | 27012 | 27152 | 27298 | 27443
Note: The values for 2023-2024 are under development as part of the FCA 14 ICR development process.

## Slide 21: Operable Capacity Analysis, cont. 2019 CELT Forecast – Winter (MW)
Capacity Commitment Period (Winter MW) |  | 2020-2021 | 2021-2022 | 2022-2023 | 2023-2024 | 2024-2025 | 2025-2026 | 2026-2027 | 2027-2028 | 2028-2029
50/50 forecast | Load net of BTM PV(a) | 23,278 | 23,420 | 23,558 | 23698 | 23,831 | 23,964 | 24,098 | 24,237 | 24,376
 | Operating reserves(b) | 2,305 | 2,305 | 2,305 | 2,305 | 2,305 | 2,305 | 2,305 | 2,305 | 2,305
 | Total requirement | 25,583 | 25,725 | 25,863 | 26,003 | 26,136 | 26,269 | 26,403 | 26,542 | 26,681
 | Installed capacity (net ICR)(c) | 33,520 | 33,550 | 33,750 | N/A | 32,950 | 33,165 | 33,390 | 33,625 | 33,870
 | Assumed unavailable capacity(d) | -8,100 | -8,100 | -8,100 | -8,100 | -8,100 | -8,100 | -8,100 | -8,100 | -8,100
 | Total net capacity(e) | 25,420 | 25,450 | 25,650 | N/A | 24,840 | 25,065 | 25,290 | 25,525 | 25,770
 | Operable capacity margin(f)— 50/50 forecast | -163 | -275 | -213 | N/A | -1,286 | -1,204 | -1,113 | -1,017 | -911
90/10 forecast | Load net of BTM PV | 23,983 | 24,138 | 24,283 | 24428 | 24,568 | 24,707 | 24,847 | 24,993 | 25,138
 | Operating reserves(b) | 2,305 | 2,305 | 2,305 | 2,305 | 2,305 | 2,305 | 2,305 | 2,305 | 2,305
 | Total requirement | 26,288 | 26,443 | 26,588 | 26733 | 26,873 | 27,012 | 27,152 | 27,298 | 27,443
 | Installed capacity (net ICR)(c) | 33,520 | 33,550 | 33,750 | N/A | 32,950 | 33,165 | 33,390 | 33,625 | 33,870
 | Assumed unavailable capacity | -8,600 | -8,600 | -8,600 | -8,600 | -8,600 | -8,600 | -8,600 | -8,600 | -8,600
 | Total net capacity(e) | 24,920 | 24,950 | 25,150 | N/A | 24,350 | 24,565 | 24,790 | 25,025 | 25,270
 | Operable capacity margin(f)— 90/10 forecast | -1,368 | -1,493 | -1,438 | N/A | -2,523 | -2,447 | -2,362 | -2,273 | -2,173
Note: The values for 2023-2024 are under development as part of the FCA 14 ICR development process.

## Slide 22: Mitigating Actions for a Possible Negative Winter Operable Capacity Margin (MW)
 | Possible Operable Capacity Margin (MW) |  | Load or Capacity Relief Actions of OP-4 (MW) |  |  |  | 
CCP | 50-50 Peak Load Forecast | 90-10 Peak Load Forecast | Depletion of 30-Min Reserve | Tie Benefits | 5% Voltage Reduction | Depletion of 10-Min Reserve to Minimum Level | Possible Relief Available from OP-4 Actions (MW)
2020 | -163 | -1,368 | 625 | 1,950 | 207 | 980 | 3,762
2021 | -275 | -1,493 | 625 | 2,020 | 206 | 980 | 3,831
2022 | -213 | -1,438 | 625 | 2,000 | 203 | 980 | 3,808
2023 | N/A | N/A | N/A | N/A | N/A | N/A | N/A
2024 | -1,286 | -2,523 | 625 | 2,000 | 196 | 980 | 3,801
2025 | -1,204 | -2,447 | 625 | 2,000 | 195 | 980 | 3,800
2026 | -1,113 | -2,362 | 625 | 2,000 | 194 | 980 | 3,799
2027 | -1,017 | -2,273 | 625 | 2,000 | 194 | 980 | 3,799
2028 | -911 | -2,173 | 625 | 2,000 | 194 | 980 | 3,762

## Slide 23: Mitigating Actions for a Possible Negative Operable Capacity Margin (MW), cont.
The two prior tables provide high level estimates of the potential load relief available from the OP-4 Actions
Possible negative operable capacity margin values shown are based on an operable capacity analysis assuming that the system installed capacity is the net/representative ICR
5% voltage reduction values are calculated using 1.0% of the net 90/10 peak load* minus the DR capacity**
In addition to the OP-4 Actions shown on the tables, other Actions such as public appeals and voluntary load curtailment by large customers are available under OP-4
* net 90/10 peak load = gross 90/10 peak load minus BTM PV
**DR capacity = EE + Active Demand Capacity Resource + Passive Capacity Demand Resource

## Slide 24: Observations
Net ICR and “representative” net ICR* will increase from 33,390 MW for 2019 to approximately 33,870 MW by 2028
The 34,839 MW of Capacity Supply Obligations from the FCA 13 are sufficient to meet the net and “representative” net ICR values through the 2028-2029 CCP
  A comparison of the representative ICR with the FCA 13 resources plus the EE forecast shows a surplus of 2,291 MW of resources in 2029 assuming no resource retirements
*Net ICR and “representative” net ICR are annual values

## Slide 25: Observations, cont.
Under 90/10 peak load conditions, New England could be short of operable capacity during the entire study period, if there is no surplus installed capacity above the net ICR and “representative” net ICR
  Operable capacity margin ranges from approximately:
    -1,150 MW to -2,500 MW during the summer
    -1,370 MW to -2,500 MW during the winter
Under 50/50 peak load conditions, New England could be short of operable capacity margin during the winter peak demand periods for the entire study period and during the summer peak demand periods starting with the 2024-2025 Capacity Commitment Period, if there is no surplus installed capacity above the net ICR and “representative” net ICR
  Operable capacity margin ranges from approximately:
    -310 MW to -470 MW during the summer
    -160 MW to -1,200 MW during the winter

## Slide 26: Observations, cont.
Load relief from OP-4 actions will be needed to mitigate these negative operable capacity margins at the time of the peak
  Up to OP 4 action 6 would be needed to meet 50/50 loads
  Up to OP 4 action 9 would be needed to meet 90/10 loads

## Slide 27: APPENDIX I
Summary of Cleared New Capacity and Retirements for FCA 8 to FCA 13

## Slide 28: Summary of Cleared New Capacity and Retirements for FCA 8 to FCA 13 (MW)

## Slide 29: APPENDIX II
Resources in the ISO Interconnection Queue

## Slide 30: Summary of ISO Generator Interconnection Queue Projects as of April 1, 2019
Category of Projects | Projects | Total Capacity (MW)
Commercial | 142 | 17,671
Active | 177 | 19,047
Withdrawn | 297 | 65,916
Total | 616 | 102,634
Notes: All capacities are based on the projects in the ISO interconnection queue as of April 1, 2019, that would interconnect with the ISO system. Projects involving only transmission or that did not increase an existing generator’s capacity were excluded. Projects with more than one listing in the queue, representing different interconnection configurations, were counted only once.

## Slide 31: Capacity of Generation Interconnection Requests by Load Zone
All capacities are based on the projects in the ISO interconnection queue as of April 1, 2019, that would interconnect with the ISO system.
Projects involving only transmission or that did not increase an existing generator’s capacity were excluded.
Projects with more than one listing in the queue, representing different interconnection configurations, were counted only once.

## Slide 32: Active Resources in the Interconnection Queue
Characteristics of ISO-NE’s Interconnection Queue as of April 1, 2019
  177 generation projects totaling 19,047 MW
    26 wind projects ~ 11,239 MW
      14 are on-shore at 2,235 MW
      12 are off-shore at 9,004 MW
    118 solar projects ~ 3,319 MW
    8 dual fuel (gas & oil) projects ~ 1,937 MW
    5 natural gas-fired projects ~ 1,152 MW
    13 battery storage projects ~ 1,209 MW
    2 fuel cell projects ~ 78 MW
    3 hydro-electric projects ~ 74 MW
    2 biomass projects ~ 39 MW

## Slide 33: Active Resources in the ISO Generator Interconnection Queue by State and Fuel Type (MW & %)
Based on projects in the Interconnection Queue as of April 1, 2019.
The “Other Renewables” category includes 37 MW wood, 78 MW fuel cell, and 2 MW municipal solid waste. The totals for all categories reflect all queue projects that would interconnect with the system and not all projects in New England.

## Slide 34: Active Resources in the ISO Generator Interconnection Queue, by Fuel Type in each Load Zone as of April 1, 2019 (MW)
Chart: MW
| ME | NH | VT | WCMA | NEMA | SEMA | RI | CT
Natural Gas | 0 | 0 | 0 | 43 | 62 | 542 | 1109 | 1411
Wind | 2167 | 28 | 30 | 10 | 0 | 6188 | 1056 | 1760
Photovoltaic | 956 | 258 | 197 | 987 | 0 | 289 | 326 | 306
Battery Storage | 77 | 100 | 0 | 1 | 408 | 403 | 0 | 220
Other Renewables | 0 | 0 | 0 | 37 | 0 | 0 | 0 | 2
Hydro & Pumped Storage | 0 | 5 | 3 | 66 | 0 | 0 | 0 | 0