## Slide 1
Reliability Committee Meeting
August 20, 2019 | WestBorough, MA
Jonathan Black, Quan Chen, Manasa Kotha, Peter Wong and Fei Zeng
Load Forecasting and
Resource studies and assessments
Including and Excluding Mystic Units 8 & 9 Scenarios
Proposed Tie Benefits and Installed Capacity Requirement for the Fourteenth Forward Capacity Auction (FCA 14)

## Slide 2: Objective of this Presentation
Review:
The tie benefit values for the two Mystic Units 8 & 9 scenarios
The changes to the 2019 CELT Load Forecast
The ICR values for the two Mystic Units 8 & 9 scenarios
The impact of the 2019 CELT Report load forecast on ICR*
The FCA 14 ICR-Related Values** development schedule
Note: Please see Appendix III for the Acronyms used in the presentation
*Impact of assumption changes on ICR including and excluding Mystic Units 8 & 9 will be presented at September RC meetings
**The ICR, Local Sourcing Requirements, Local Resource Adequacy Requirements, Transmission Security Analysis Requirements, Maximum Capacity Limits, Marginal Reliability Impact Demand Curves and the HQICCs are collectively referred to as the ICR-Related Values.

## Slide 3: Background
The calculation of ICR-Related Values is conducted pursuant to Section III.12.9 of the Tariff
In November 2018, the ISO, joined by NEPOOL, filed with FERC proposed revisions to two assumptions used in the calculation of ICR-Related Values:
  Change the modeling of load relief assumed obtainable through the implementation of 5% voltage reduction action of OP-4 from 1.5% of the 90/10 peak to 1.0%
  Modify the unavailability of peaking generation resources in the TSA from a 20% deterministic adjustment factor to be the units’ EFORds
FERC accepted the proposed revisions in a January 8, 2019 Letter Order and these revised assumptions are used in the ICR-Related Values calculations for the FCA for the CCP 2023-2024 (FCA 14) and ARAs that will be conducted in 2020

## Slide 4: Background, cont.
Mystic Units 8 & 9 were retained for fuel security in FCA 13
  Exelon elected to continue to operate for CCP 2022-2023
For FCA 14, Mystic Units 8 and 9 are needed for fuel security*, and Exelon again has the option to unconditionally retire prior to FCA 14
  Exelon has until January 10, 2020 to decide whether to retire or continue to operate for CCP 2023-2024
The ISO is developing and will file with FERC two sets of ICR-Related Values due to the timing of Exelon’s retirement decision for Mystic Units 8 & 9
  Similar to how ICR-Related Values were developed and filed at FERC with and without Clear River Unit 1 in FCA 13
  “Including Mystic Units 8 & 9” and “Excluding Mystic Units 8 & 9” scenarios
In January 2020, it is anticipated it will be clearer which FCA 14 ICR-Related Values will be used in the FCA
  Pending Exelon’s retirement decision on January 10, 2020
  Pending FERC’s acceptance of the ICR-Related Values in mid-January 2020
*Copy of the presentation “Reevaluation of Mystic 8 & 9 for Fuel Security Reliability and FCA 14 Fuel Security Reliability Review Results for Retirement De-List Bids” can be downloaded using the following link: https://www.iso-ne.com/static-assets/documents/2019/08/a10_1_reevaluation_of_mystic_8_9_for_fuel_security_reliability_and_fca_14_fuel_security_reliability_review_results_for_retirement_delist_bids.pdf

## Slide 5: Tie Benefits Study for FCA 14
Including and Excluding Mystic Units 8 & 9 Scenarios

## Slide 6: Tie Benefits for FCA 14 ICR Calculations
This section presents the tie benefits study results for FCA 14 for the 2023-2024 CCP for two scenarios: one including, and another excluding, Mystic units 8 and 9
  Total tie benefits for New England
  Tie benefits contribution associated with individual or group of interconnection(s)
    Maritimes
    HQ Phase II
    Highgate
    New York AC ties
    Cross Sound Cable

## Slide 7: Background
Determination of Capacity Zones for FCA 14 was presented to the PSPC on May 30, 2019
  Import-constrained Capacity Zone of Southeast New England (includes the NEMA/Boston and SEMA/RI Load Zones)
  Export-constrained Capacity Zones of:
    Maine, and
    Northern New England (includes Maine, New Hampshire and Vermont Load Zones)
  Rest-of-Pool Capacity Zone
Transmission transfer capability limits associated with Capacity Zones are relaxed in the tie benefits study
Detailed study assumptions and results were presented to the PSPC on May 30, 2019 and July 25, 2019, respectively
  https://www.iso-ne.com/static-assets/documents/2019/05/a62_fca14_tie_benefits_assumpts_05302019_rev1.pdf
  https://www.iso-ne.com/static-assets/documents/2019/07/pspc_a05_tiebenefitswithandwithoutmystic89.pptx
Detailed study methodology, assumptions and results are included in the Appendix II

## Slide 8: Summary of Tie Benefits Study Results for FCA 14 Including and Excluding Mystic Units 8 & 9
 | Including Mystic Units 8 & 9 (MW) | Excluding Mystic Units 8 & 9 (MW)
Total Tie Benefits | 1,940 | 1,910
Maritimes | 501 | 493
HQ Phase II | 941 | 943
Highgate | 136 | 134
New York AC ties | 362 | 340
CSC | 0 | 0

## Slide 9: Comparison of Tie Benefits Results for FCA 14 and FCA 13
 | 2023-2024 (FCA 14) Including Mystic Units 8 & 9 (MW) | 2023-2024 (FCA 14) Excluding Mystic Units 8 & 9 (MW) | 2022-2023 (FCA 13) (MW)
Total Tie Benefits | 1,940 | 1,910 | 2,000
Maritimes | 501 | 493 | 516
HQ Phase II | 941 | 943 | 969
Highgate | 136 | 134 | 149
New York AC ties | 362 | 340 | 366
CSC | 0 | 0 | 0

## Slide 10: Results of a Sensitivity Simulation
To identify the impact of the change to the load relief assumed obtainable from implementing the 5% voltage reduction
 | Total Tie Benefits (MW)
Including Mystic Units 8 & 9 (Base Case) | 1,940
Assume Load Relief from Voltage Reduction to be 1.5% of 90/10 Peak | 1,965

## Slide 11: Observations
For FCA 14, including or excluding Mystic Units 8 & 9 in the New England resource mix, will change the total tie benefits to New England by 30 MWs
  The two Mystic Units 8 & 9 scenarios produced different tie benefits associated with the individual or group of ties
Tie benefits for FCA 14 are lower than tie benefits for FCA 13 by 60 MW to 90 MW, depending on the Mystic Units 8 & 9 scenario
Results of a sensitivity simulation show that:
  If load relief from implementing the 5% voltage reduction were assumed to be 1.5% of the 90/10 peak demand, total tie benefits would have been 1,965 MW as compared with 1,940 MW of tie benefits for the “Including Mystic Units 8 & 9” scenario. The increasing in tie benefits is consistent with a similar trend observed about the impacts of the ICR assumption changes previously discussed at the August 1, 2018 RC meeting

## Slide 12: Conclusions
FCA 14 tie benefits assumptions for the calculation of the ICR-Related Values will be 1,940 MW for the “Including Mystic Units 8 & 9” scenario and 1,910 MW for the “Excluding Mystic Units 8 & 9” scenario
Hydro Quebec Interconnection Capability Credits for FCA 14 for the “Including Mystic Units 8 & 9” scenario will be 941 MW while for the “Excluding Mystic Units 8 & 9” scenario will be 943 MW

## Slide 13: Changes to the 2019 CELT Load Forecast

## Slide 14: 2019 CELT Load Forecast Changes
The 2019 CELT load forecast* was reviewed in detail at the July 25, 2019 PSPC meeting. The 2019 CELT load forecast has incorporated the following component changes to the load forecast methodology in addition to the standard update to the underlying macro economic assumption and model estimation period:
  Forecast Cycle Change (Standard Update)
    This would be the normal forecast change as done in the past
    Underlying input macro economic assumptions seen in 2019 vs 2018
    Model estimation period – daily peak load and weather for the historical period covering 2004-2018 (2003-2017 used last year)
  2019 Changes to the methodology of the load forecast model
    Added a Second Weather Variable (Modeling Specification)
      Incorporated a second weather variable, cooling degree days (CDD), in addition to weighted temperature-humidity index (WTHI)
    Separated July and August Peak Modeling (Monthly Peak Demand Modeling)
      Developed separate July and August monthly models rather than a combined July/August summer seasonal peak model
    Shortened Weather History (Weather History Change)
      Historical weather period used to generate probabilistic forecast shortened from 40 years to 25 years
      New 25-year period covers 1991-2015 (1975-2014 used last year)
  *For details of the 2019 load forecast, please see Review of the 2019 Long-Term Load Forecast presentation at: https://www.iso-ne.com/static-assets/documents/2019/07/20190725_a03_2019_longterm_forecasts_icr.pptx
  For details on the load forecast methodologies and assumptions, please see: https://www.iso-ne.com/committees/reliability/load-forecast/

## Slide 15: Summer Seasonal Peak Load Distribution* in Per Unit of the 50/50 Peak for CCP 2023-2024
*Seasonal peak load forecast distribution (Forecast is Gross with reduction for BTM PV) is based on section 1.6 of the CELT Reports.
For copy of CELT reports, please visit: https://www.iso-ne.com/system-planning/system-plans-studies/celt
CELT Forecast Distribution from 2015 – 2019 CELT Reports
 |  | Peak Load Forecast at Milder Than Expected Weather |  |  |  | Gross Forecast at Expected Weather | Peak Load Forecast at More Extreme Than Expected Weather |  |  |  | 
Year of CELT Report | Probability of Forecast Being Exceeded | 10/90 | 20/80 | 30/70 | 40/60 | 50/50 | 60/40 | 70/30 | 80/20 | 90/10 | 95/5
2015 | Summer MW | 29,901 | 30,181 | 30,231 | 30,656 | 31,131 | 31,631 | 32,146 | 32,886 | 33,746 | 34,491
 | Per Unit of 50/50 Peak | 0.96 | 0.97 | 0.97 | 0.98 | 1.00 | 1.02 | 1.03 | 1.06 | 1.08 | 1.11
2016 | Summer MW | 28,870 | 29,146 | 29,520 | 29,943 | 30,415 | 30,915 | 31,427 | 32,159 | 33,002 | 33,739
 | Per Unit of 50/50 Peak | 0.95 | 0.96 | 0.97 | 0.98 | 1.00 | 1.02 | 1.03 | 1.06 | 1.09 | 1.11
2017 | Summer MW | 28,406 | 28,692 | 29,062 | 29,496 | 29,960 | 30,469 | 30,986 | 31,714 | 32,562 | 33,311
 | Per Unit of 50/50 Peak | 0.95 | 0.96 | 0.97 | 0.98 | 1.00 | 1.02 | 1.03 | 1.06 | 1.09 | 1.11
2018 | Summer MW | 27,790 | 28,068 | 28,427 | 28,849 | 29,300 | 29,794 | 30,297 | 31,004 | 31,828 | 32,556
 | Per Unit of 50/50 Peak | 0.95 | 0.96 | 0.97 | 0.98 | 1.00 | 1.02 | 1.03 | 1.06 | 1.09 | 1.11
2019 | Summer MW | 27,354 | 27,762 | 28,127 | 28,435 | 28,838 | 29,398 | 29,734 | 30,102 | 30,851 | 31,327
 | Per Unit of 50/50 Peak | 0.95 | 0.96 | 0.98 | 0.99 | 1.00 | 1.02 | 1.03 | 1.04 | 1.07 | 1.09

## Slide 16: Summer Seasonal Peak Load Distribution* in Per Unit of the 50/50 Peak for CCP 2023-2024
*Seasonal peak load forecast distribution (Forecast is Gross with reduction for BTM PV) is based on section 1.6 of the CELT Reports.
Chart: 
| 10/90 | 20/80 | 30/70 | 40/60 | 50/50 | 60/40 | 70/30 | 80/20 | 90/10 | 95/5
 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2015 | 0.96049 | 0.96948 | 0.97109 | 0.98474 | 1 | 1.0161 | 1.0326 | 1.0564 | 1.084 | 1.1079
2016 | 0.9492 | 0.95828 | 0.97057 | 0.98448 | 1 | 1.0164 | 1.0333 | 1.0573 | 1.0851 | 1.1093
2017 | 0.94813 | 0.95768 | 0.97003 | 0.98451 | 1 | 1.017 | 1.0342 | 1.0585 | 1.0869 | 1.1119
2018 | 0.94847 | 0.95794 | 0.97021 | 0.9846 | 1 | 1.0169 | 1.034 | 1.0581 | 1.0863 | 1.1111
2019 | 0.94852 | 0.96266 | 0.97532 | 0.98601 | 1 | 1.0194 | 1.0311 | 1.0438 | 1.0698 | 1.0863
CELT Forecast Distribution from 2015 – 2019 CELT Reports

## Slide 17
2018 CELT and 2019 CELT Gross Load Forecast Comparison Peak Load Distribution* for CCP 2023-2024
Chart: Load (MW)
50/50 PK - 2019CELT | 0 | 120
50/50 PK - 2018CELT | 0 | 120
90/10 PK - 2018CELT | 0 | 120
90/10 PK - 2019CELT | 0 | 120
* Gross peak load distribution (without reduction for BTM PV).

## Slide 18
2018 CELT and 2019 CELT Gross Load Forecast Comparison
Tail Peak Load Distribution* Relative to 50/50 Peak
Chart: Load Level Relative to 50/50 Peak (MW)
peak | 0 | 120
* Gross peak load distribution (without reduction for BTM PV).

## Slide 19
2018 CELT and 2019 CELT Gross Load Forecast Comparison
Tail Peak Load Distribution* Relative to 90/10 Peak
Chart: Load Level Relative to 90/10 Peak (MW)
Peak | 0 | 120
* Gross peak load distribution (without reduction for BTM PV).

## Slide 20: Observations
The annual peaks of 2019 gross load forecast are lower than the annual peaks of the 2018 gross load forecast for the CCP 2023-2024
  ~500 MW decrease in 50/50 peak
  ~1,000 MW decrease in 90/10 peak
The seasonal peak load distribution of the 2019 CELT forecast shows lower high loads in per unit of the 50/50 peak load as compared with the prior four CELT forecasts
The 2019 CELT forecast probability distribution of peak loads, used for ICR calculation, is also lower when compared with the distribution of the 2018 CELT forecast
  The number of expected days of occurrence for the same load level are lower in the 2019 forecast
  The 2019 CELT forecast curve of the peak load probability distribution relative to its 50/50 peak load has shifted downward when compared with the 2018 Forecast curve
    Implying that the impact on the ICR will be greater than the delta of the 50/50 peak loads between the two forecasts
  The 2019 CELT forecast curve of the peak load probability distribution relative to its 90/10 peak load is similar to the 2018 CELT forecast curve
    Implying that the impact on the ICR will be similar to the delta of the 90/10 peak loads between the two forecasts

## Slide 21: ICR for FCA 14
Including and Excluding Mystic Units 8 & 9 Scenarios

## Slide 22: ICR Values for FCA 14
This section presents the results of the calculation of the ICR for the two Mystic Units 8 and 9 scenarios
The rest of the ICR-Related Values for the two Mystic scenarios including the “Effect of Updated Assumptions on ICR” will be presented to the RC in the September 10 and 25 meetings

## Slide 23: ICR Calculation Details Including Mystic Units 8 & 9
Notes:
All values in the table are in MW except the reserve margin shown in percent
ALCC is the “additional load carrying capability” used to bring the system to the target reliability criterion
APk is the forecast gross 50/50 peak load
Total Capacity Breakdown | 2023-2024 FCA ICR (MW)
Generating Capacity Resources | 30,695
Demand Resources | 3,859
Import Capacity Resources | 83
Tie Benefits | 1,940
OP-4 Actions 6 & 8 (Voltage Reduction) | 270
Minimum System Reserve | (700)
Total Capacity | 36,147
Installed Capacity Requirement Calculation Details | 2023-2024 FCA ICR (MW)
Annual Peak | 28,838
Total Capacity | 36,147
Tie Benefits | 1,940
HQICCs | 941
OP-4 Actions 6 & 8 (Voltage Reduction) | 270
Minimum System Reserve | (700)
ALCC | 1,906
Installed Capacity Requirement | 33,431
Net ICR | 32,490
Reserve Margin with HQICCs | 15.9%
Reserve Margin without HQICCs | 12.7%

## Slide 24: ICR Calculation Details Excluding Mystic Units 8 & 9
Notes:
All values in the table are in MW except the reserve margin shown in percent
ALCC is the “additional load carrying capability” used to bring the system to the target reliability criterion
APk is the forecast gross 50/50 peak load
Total Capacity Breakdown | 2023-2024 FCA ICR (MW)
Generating Capacity Resources | 29,282
Demand Resources | 3,859
Import Capacity Resources | 83
Tie Benefits | 1,910
OP-4 Actions 6 & 8 (Voltage Reduction) | 270
Minimum System Reserve | (700)
Total Capacity | 34,704
Installed Capacity Requirement Calculation Details | 2023-2024 FCA ICR (MW)
Annual Peak | 28,838
Total Capacity | 34,704
Tie Benefits | 1,910
HQICCs | 943
OP-4 Actions 6 & 8 (Voltage Reduction) | 270
Minimum System Reserve | (700)
ALCC | 647
Installed Capacity Requirement | 33,438
Net ICR | 32,495
Reserve Margin with HQICCs | 16.0%
Reserve Margin without HQICCs | 12.7%

## Slide 25: Comparison of ICR Values (MW) CCP 2023-2024 (FCA 14) Vs. CCP 2022-2023 (FCA 13)
Notes:
The Existing Capacity Resources category consists of existing resources that have Qualified Capacity for FCA 14 at the time of the ICR calculation and reflects applicable retirements and terminations
For details on the FCA 13 (2022-2023) ICR-Related Values calculation see: https://www.iso-ne.com/static-assets/documents/2018/09/a5_icr_fca_13_and_related_values.zip
50/50 and 90/10 peak loads are shown for informational purposes
 | FCA 14 |  | FCA 13
 | Including Mystic Units 8 & 9 | Excluding Mystic Units 8 & 9 | 
Gross Load Forecast - 50/50 Peak (Net of BTM PV) | 28,838 | 28,838 | 29,093
Gross Load Forecast - 90/10 Peak (Net of BTM PV) | 30,851 | 30,851 | 31,592
Existing Capacity Resources | 34,637 | 33,194 | 33,867
Tie Benefits | 1,940 | 1,910 | 2,000
HQICCs | 941 | 943 | 969
Load Relief from implementing 5% voltage reduction | 270 | 270 | 422
Installed Capacity Requirement | 33,431 | 33,438 | 34,719
Net ICR (ICR minus HQICCs) | 32,490 | 32,495 | 33,750

## Slide 26: Effect of Updated Assumptions on ICR* Including Mystic Units 8 & 9
Assumption |  |  |  |  | Effect on ICR (MW)
 | 2023-2024 FCA 14 |  | 2022-2023 FCA 13 |  | 
Tie Benefits | 362 MW New York |  | 366 MW New York |  | TBD
 | 501 MW Maritimes |  | 516 MW Maritimes |  | 
 | 941 MW Quebec (HQICCs) |  | 969 MW Quebec (HQICCs) |  | 
 | 136 MW Quebec via Highgate |  | 149 MW Quebec via Highgate |  | 
Total | 1,940 MW |  | 2,000 MW |  | 
 | MW | Weighted Forced Outage (%) | MW | Weighted Forced Outage | 
Generation & IPR** | 30,695 | 5.7% | 30,781 | 7.0% | TBD
Demand Resources | 3,859 | 1.0% | 3,490 | 1.2% | 
Imports | 83 | 0.5% | 80 | 0.0% | 
 | MW |  | MW |  | 
90/10 Gross Load Forecast*** | 30,851 |  | 31,592 |  | TBD
 | MW | % | MW | % | 
Implement 5% VR (OP-4) | 270 | 1.00% | 422 | 1.50% | TBD
 | MW |  | MW |  | 
ICR | 33,431 |  | 34,719 |  | -1,288
Net ICR | 32,490 |  | 33,750 |  | -1,260
*Methodology: using the model for the 2022-2023 FCA 13 ICR calculation, change one assumption at a time and note the change in ICR
**Generation forced outage assumption is a weighted average of individual generator’s 5-year average EFORd and Intermittent Power Resources assumed 100% available
***The 90/10 peak value (net of the published value of BTM PV) is shown for reference; the MARS model uses hourly profiles of forecasted load and BTM PV

## Slide 27: FCA 14 ICR Results Summary and Observations
Due to the size of the Mystic Units 8 & 9 and their availability relative to the availability of the system resources mix, including Mystic Units 8 & 9 would increase the system ICR
However, tie benefits including Mystic Units 8 & 9 is 30 MW higher than excluding them, resulting in an overall decrease of system ICR
The difference in ICR and net ICR between the two Mystic Units 8 & 9 scenarios are 7 MW and 5 MW, respectively
  Higher ICR and net ICR when Mystic Units 8 & 9 are excluded from the system
Net ICR for FCA 14 would be 1,255 MW to 1,260 MW lower than the net ICR for FCA 13, depending on the Mystic units’ participation in the 2023-2024 CCP
 | ICR (MW) | HQICCs (MW) | Net ICR (MW) | Total Tie Benefits (MW)
Including Mystics Units 8 & 9 | 33,431 | 941 | 32,490 | 1,940
Excluding Mystics Units 8 & 9 | 33,438 | 943 | 32,495 | 1,910

## Slide 28: IMPACT OF Changes to the Load Forecast Methodology on ICR for FCA 14

## Slide 29: Analysis to Identify Impact on ICR associated with the Changes in Load Forecast Methodology
The following simulations were conducted using a common set of resource assumptions developed for FCA 14 ICR calculations for the scenario that includes Mystic Units 8 & 9 to identify the impact of each methodology change to the gross load forecast model for the CCP 2023-2024:
  2018 Case
    Calculate the ICR using the 2018 CELT gross load forecast for the CCP 2023-2024
  Forecast Cycle Case
    Calculate the ICR with the same load forecast modeling methodology as used to develop the 2018 CELT gross load forecast
      Updated underlying input assumptions associated with the 2019 CELT forecast
      Revised daily peak load and weather model estimation period
        Used 2004-2018 instead of the 2003-2017 period used in the 2018 CELT load forecast

## Slide 30: Analysis to Identify Impact on ICR associated with the Changes in Load Forecast Methodology, cont.
  Second Weather Variable Case
    Using the Forecast Cycle Case input assumptions modify the gross load forecast based on incorporating a second weather variable, cooling degree days (CDD), in addition to the weighted temperature-humidity index (WTHI)
  Separate July and August Peak Load Model Case
    Using the Forecast Cycle Case input assumptions modify the gross load forecast developed by using separate July and August monthly peak models rather than a combined July/August summer seasonal peak model
  Shorter History Weather Period Case
    Using the Forecast Cycle Case input assumptions modify the gross load forecast developed based on a shorter historical weather period, from 40 years to 25 years, to generate the probabilistic forecast. The new 25-year period covers 1991 through 2015 instead of the 40-year (1975 through 2014) period used in the 2018 CELT load forecast

## Slide 31: Analysis to Identify Impact on ICR associated with the Changes in Load Forecast Methodology, cont.
Methodology to Obtain Impact of Individual Changes
The impact of the forecast cycle change is obtained by comparing the ICR of the 2018 Case with the ICR of the Forecast Cycle Case
The impact of each component change to the load forecast methodology is obtained by comparing the ICR of the cases with and without the change

## Slide 32: Estimated Impacts on ICR due to 2019 Gross Load Forecast Changes
 |  | Estimated Impacts on net ICR (MW)
Changes to Gross Load Forecast for CCP 2023-2024 | Forecast Cycle Case | -300
 | Second Weather Variable Case | -855
 | Separate July and August Peak Load Model Case | +45
 | Shorter History Weather Period Case | -140
 | All Changes Together | -1,250

## Slide 33: Observations Impact of Load Forecast Methodology on ICR
If the forecast methodology were not changed and a new load forecast is developed for the 2023-2024 CCP with the underlying forecast assumptions updated, the net ICR would have been 300 MW lower as compared with the net ICR simulated using the 2018 CELT gross loads for 2023-2024
The change in load forecast methodology that most impacted the net ICR is the addition of a second weather variable to the methodology
  It decreased the net ICR by 855 MW
A shorter historical period lowered the net ICR by 140 MW
A separate monthly peak load model for July and August increased the net ICR by 45 MW as compared with using a combined July/August peak period model
The decrease in Net ICR corresponds to the decrease in the 90/10 gross peak load forecast of ~ 1,000 MW between the 2018 CELT and 2019 CELT forecasts
  Consistent with the outcome that high peak loads have more impact on system Loss of Load Expectation

## Slide 34: FCA 14 ICR-Related values development schedule

## Slide 35: FCA 14 ICR-Related Values Development Schedule
Date | Topic
April 24 | RC reviewed the 2019 PSPC development schedule for the ICR-Related Values for the FCM auctions to be conducted in 2020
May 30/June 20 | PSPC reviewed FCA 14 ICR-Related Values calculation assumptions
July 25 | PSPC reviewed tie benefits study results including and excluding Mystic Units 8 & 9
August 9 | PSPC reviewed proposed ICR including and excluding Mystic Units 8 & 9
August 20 | RC review of proposed tie benefits and ICRs including and excluding Mystic Units 8 & 9
August 29 | PSPC review of proposed LSRs, TSAs, LRAs, MCLs and the MRI system and Capacity Zone Demand Curves including Mystic Units 8 & 9
September 9 | PSPC review of proposed LSRs, TSAs, LRAs, MCLs and the MRI system and Capacity Zone Demand Curves excluding Mystic Units 8 & 9
September 10 | RC review of proposed LSRs, TSAs, LRAs, MCLs and the MRI system and Capacity Zone Demand Curves including Mystic Units 8 & 9
September 25 | RC review of proposed tie benefits and review/vote of proposed ICR-Related Values both including and excluding Mystic Units 8 & 9
October 4 | PC review/vote of proposed ICR-Related Values both including and excluding Mystic Units 8 & 9
By November 5 | File with FERC ICR-Related Values both including and excluding Mystic Units 8 & 9

## Slide 37: Appendix I
Assumptions for the FCA14 ICR-Related Values Calculations

## Slide 38: Modeling the New England Control Area for FCA 14
The General Electric Multi-Area Reliability Simulation model (GE MARS) is used to calculate several of the ICR-Related Values
Internal transmission constraints are not modeled in the ICR calculation. All loads and resources are assumed to be connected to a single electric bus
  Internal transmission constraints are addressed through the LSR and MCLs
A LSR will be calculated for the import-constrained Southeast New England (SENE) Capacity Zone, consisting of the NEMA/Boston, SEMA and RI Load Zones
MCLs will be calculated for two export-constrained Capacity Zones. The Maine Capacity Zone and the Northern New England (NNE) Capacity Zone, consisting of the combined Load Zones of Maine, New Hampshire and Vermont
  The Maine Capacity Zone will be nested in the NNE Capacity Zone
The MRI based method for calculating demand curves will be used to develop System and Capacity Zone Demand Curves

## Slide 39: Cost of New Entry (CONE) - for the MRI Demand Curve
CONE for the cap of the MRI system Demand Curve for FCA 14 has been calculated as:
  Gross CONE: $11.472/kW-month
  Net CONE : $8.187/kW-month
  FCA Starting Price : $13.099/kW-month
See link to FCM parameters by CCP: https://www.iso-ne.com/static-assets/documents/2015/09/FCA_Parameters_Final_Table.xlsx

## Slide 40: Assumptions for the ICR-Related Values Calculations
Load forecast
  Net of behind-the-meter (BTM) photovoltaic (PV) forecast
  Load forecast distribution
Resource data will be based on qualified existing capacity values for FCA 14
  Generating Capacity Resources
  Intermittent Power Resources (IPR)
  Import Capacity Resources
  Demand Resources (DR)
These qualified capacity values reflect
  The significant decrease of existing qualified resources
  The resource retirements and terminations
    The unconditional Permanent and Retirement De-List Bids and
    Permanent De-List Bids that are at or above the FCA 14 Starting Price

## Slide 41: Assumptions for the ICR-Related Values Calculations, cont.
Resource availability
  Generating Capacity Resources’ availability
  IPR availability
  DR availability
Load or capacity relief assumed obtainable from implementing the following actions of the Operating Procedure No. 4, Action during a Capacity Deficiency (OP-4)
  Request emergency assistance from neighboring Control Areas (Tie reliability benefits)
    Quebec (includes Hydro-Quebec Interconnection Capability Credits (HQICCs))
    Maritimes
    New York
  Initiate 5% voltage reduction

## Slide 42: Load Forecast Data
Load forecast assumption from the 2019 Forecast Report of Capacity, Energy, Loads and Transmission (CELT) load forecast*
The load forecast weather-related uncertainty is represented by specifying a series of multipliers on the peak load and the associated probabilities of each load level occurring
  The multipliers used to describe the load forecast uncertainty are derived from the 52 weekly peak load distributions described by the expected value (mean), the standard deviation and the skewness
*The 2019 CELT load forecast is available at https://www.iso-ne.com/system-planning/system-forecasting/load-forecast/

## Slide 43: Load Forecast Data, cont. Modeling of BTM PV
FCA 14 ICR calculations will use an hourly profile of BTM PV corresponding to the load shape for the year 2002, used by the Northeast Power Coordinating Council (NPCC) for reliability studies. For more information on the development of the hourly profile see: https://www.iso-ne.com/static-assets/documents/2017/06/pspc_6_22_2017_2002_PV_profile.pdf
  Used for all probabilistic ICR-Related Values calculations
  Modeled in GE MARS by Regional System Plan (RSP) 13-subarea representation
  Includes an 8% transmission and distribution gross-up
  Peak load reduction uncertainty is modeled (randomly selected by MARS from a seven day window distribution)
The values of BTM PV published in the 2019 CELT Report are the values of BTM PV subtracted from the gross load forecast to determine the net load forecast
The published 90/10 net load forecast for the SENE sub-areas is used in the TSA
Notes:
For more info on the PV forecast, see https://www.iso-ne.com/static-assets/documents/2019/04/final-2019-pv-forecast.pdf

## Slide 44: Load Forecast Data, cont. New England System Load Forecast
Probability Distribution of Seasonal Peak Load (MW)
Monthly Peak Load (MW) - Net of BTM PV
There is a distribution associated with each monthly peak. The distribution associated with the seasonal peak load forecast is shown below:
Corresponds to the reference forecast labeled “ISO-NE Control Area & New England States Monthly Peak Load Forecast“ from worksheet “4 Mnth Peak” of the 2019 Forecast Data
  https://www.iso-ne.com/static-assets/documents/2019/04/forecast_data_2019.xlsx
From Table 1.6 - Seasonal Peak Load Forecast Distributions (forecast is reference with reduction for BTM PV) of the 2019 CELT
  https://www.iso-ne.com/static-assets/documents/2019/04/2019_celt_report.xls
CCP | JUN | JUL | AUG | SEP | OCT | NOV | DEC | JAN | FEB | MAR | APR | MAY
2023-2024 | 25,339 | 27,650 | 28,838 | 23,779 | 18,467 | 20,250 | 23,698 | 23,183 | 22,725 | 20,336 | 18,359 | 21,757
 | 10/90 | 20/80 | 30/70 | 40/60 | 50/50 | 60/40 | 70/30 | 80/20 | 90/10 | 95/5
Summer 2023 | 27,354 | 27,762 | 28,127 | 28,435 | 28,838 | 29,398 | 29,734 | 30,102 | 30,851 | 31,327
Winter 2023-2024 | 23,373 | 23,476 | 23,558 | 23,659 | 23,698 | 23,800 | 24,003 | 24,178 | 24,428 | 24,514

## Slide 45
Resource Data – Generating Capacity Resources (MW) Including Mystic Units 8 and 9
Qualified Existing Generating Capacity Resources for FCA 14 Reflect
  Significant decreases
  The resource retirements and terminations
      The unconditional Permanent and Retirement De-List Bids and
      Permanent De-List Bids that are at or above the FCA 14 Starting Price
  Mystic 8 & 9 included in the values for NEMA/Boston and the system total. The simulation without these two units would reflect 1,413 MW lower in non-intermittent Generating Capacity Resources
  Intermittent Power Resources (IPR) have both summer and winter values modeled; non-intermittent Generating Capacity Resources winter values provided for informational purpose
Load Zone | Non-Intermittent Generating Resource |  | Intermittent Power Resource |  | Total | 
 | Summer | Winter | Summer | Winter | Summer | Winter
CONNECTICUT | 9,825.078 | 10,286.142 | 104.931 | 105.983 | 9,930.009 | 10,392.125
MAINE | 2,874.064 | 3,068.435 | 260.541 | 331.584 | 3,134.605 | 3,400.019
NORTH EAST MASSACHUSETTS & BOSTON | 2,702.047 | 3,105.979 | 48.991 | 43.266 | 2,751.038 | 3,149.245
NEW HAMPSHIRE | 4105.26 | 4,274.734 | 112.334 | 190.476 | 4,217.594 | 4,465.21
RHODE ISLAND | 1,826.126 | 2,025.848 | 42.3 | 40.602 | 1,868.426 | 2,066.45
SOUTH EAST MASSACHUSETTS | 4,445.137 | 4,806.408 | 162.667 | 160.885 | 4,607.804 | 4,967.293
VERMONT | 198.016 | 246.303 | 71.574 | 115.722 | 269.59 | 362.025
WEST CENTRAL MASSACHUSETTS | 3,812.334 | 4,063.863 | 103.869 | 97.337 | 3,916.203 | 4,161.2
Total New England | 29,788.062 | 31,877.712 | 907.207 | 1,085.855 | 30,695.269 | 32,963.567

## Slide 46
Resource Data – Import Capacity Resources (MW)
Qualified Existing Import Capacity Resources for FCA 14
The NYPA supplied Import Capacity Resources’ performance (availability) will be modeled with the performance assumptions associated with the New York AC ties
Import Capacity Resource | Qualified Summer MW | Modeled MW | External Interface
NYPA - CMR | 68.800 | 68.800 | New York AC Ties
NYPA - VT | 14.000 | 14.000 | New York AC Ties
Total MW | 82.800 | 82.800 | 

## Slide 47
Resource Data – Demand Resources (MW)
Qualified Existing Demand Resources for FCA 14
Includes the 8% transmission and distribution loss adjustment (gross-up)
 | On-Peak Demand Resource |  | Seasonal Peak Demand Resource |  | Active Demand Capacity Resource (ADCR) |  | Total | 
Load Zone | Summer | Winter | Summer | Winter | Summer | Winter | Summer | Winter
CONNECTICUT | 148.266 | 85.416 | 575.582 | 644.829 | 189.261 | 188.555 | 913.109 | 918.8
MAINE | 192.035 | 171.347 | - | - | 139.535 | 157.431 | 331.57 | 328.778
NORTH EAST MASSACHUSETTS & BOSTON | 764.388 | 748.865 | - | - | 95.715 | 94.421 | 860.103 | 843.286
NEW HAMPSHIRE | 130.434 | 127.452 | - | - | 46.32 | 45.6 | 176.754 | 173.052
RHODE ISLAND | 284.335 | 292.368 | - | - | 47.581 | 44.082 | 331.916 | 336.45
SOUTH EAST MASSACHUSETTS | 436.75 | 434.351 | - | - | 51.202 | 49.326 | 487.952 | 483.677
VERMONT | 116.852 | 115.544 | - | - | 52.664 | 58.27 | 169.516 | 173.814
WEST CENTRAL MASSACHUSETTS | 456.121 | 466.709 | 26.618 | 8.387 | 105.641 | 101.986 | 588.38 | 577.082
Grand Total | 2,529.181 | 2,442.052 | 602.2 | 653.216 | 727.919 | 739.671 | 3,859.3 | 3,834.939

## Slide 48: Capacity Zone Resource and 50/50 Peak Load Forecast Assumptions Used in LRA and MCL Calculations (MW) Including Mystic Units 8 and 9
An LRA requirement will be calculated for the SENE Capacity Zone; MCLs will be calculated for the Maine and NNE Capacity Zones
Zonal requirements will be determined using the load forecast and resource assumptions for the appropriate RSP sub-areas as the transmission transfer capability analysis will be performed using the RSP 14-bubbles for the import and export constrained interfaces
The 50/50 load forecast values for the Capacity Zones will be the sum of the appropriate RSP sub-areas and are shown for informational purposes
Note that the values are presented based on RSP subarea
Resource Type | SENE | Maine | NNE | New England
Non-Intermittent Generating Resource | 8973.310 | 2874.064 | 7177.34 | 29788.062
Intermittent Resource | 253.958 | 260.541 | 436.349 | 907.207
Import Resource | - | - | - | 82.8
On-Peak Demand Resource | 1,501.125 | 186.250 | 423.634 | 2,529.181
Seasonal-Peak Demand Resource | 0.688 | - | - | 602.2
Active Demand Capacity Resource | 198.599 | 135.331 | 232.228 | 727.919
Total | 10927.680 | 3456.186 | 8269.552 | 34637.369
 | SENE | Maine | NNE | New England
50/50 Load Forecast Net BTM PV | 12,540 | 2,117 | 5,430 | 28,839

## Slide 49: LRA, TSA & MCL Internal Transmission Transfer Capability Assumptions
    Maine - New Hampshire Export
      N-1 Limit: 1,900 MW
    Northern New England Export (North-South interface)
        N-1 Limit: 2,725 MW
    Southeast New England Import
        N-1 Limit: 5,700 MW
        N-1-1 Limit: 4,600 MW
*Based on transmission transfer capability limits presented at the March 20, 2019 RC meeting. The presentation is available at: https://www.iso-ne.com/static-assets/documents/2019/03/a7_fca_14_transmission_transfer_capabilities_and_capacity_zone_development.pdf

## Slide 50: Availability Assumptions - Generating Capacity Resources
Forced outages assumption
  Each generating unit’s Equivalent Forced Outage Rate on Demand (non-weighted EFORd) will be modeled
  Based on a 5-year average (January 2014 – December 2018) of Generation Availability Data System (GADS) data submitted by generators
  NERC GADS class average data will be used for immature/non-commercial units
Scheduled outage assumption
  Each generating unit’s weeks of maintenance modeled
  Based on a 5-year average (January 2014 – December 2018) of each generator’s actual historical average of planned and maintenance outages scheduled at least 14 days in advance
  NERC GADS class average data will be used for immature/non-commercial units

## Slide 51: Availability Assumptions - Generating Capacity Resources including Mystic Units 8 and 9
Assumed summer MW weighted EFORd and maintenance weeks are shown by resource category for informational purposes. In the LOLE simulations used for determining ICR-Related Values, individual unit assumptions will be modeled.
Resource Category | Summer MW | Assumed Average EFORd (%) Weighted by Summer Ratings | Assumed Average Maintenance Weeks Weighted by Summer Ratings
Combined Cycle | 14,653 | 3.7 | 5.2
Fossil | 5,108 | 14.4 | 5.2
Combustion Turbine | 3,477 | 10.6 | 2.7
Nuclear | 3,333 | 1.2 | 3.8
Hydros (includes pumped Storage) | 3,069 | 2.0 | 5.6
Diesel | 121 | 7.9 | 2.0
Miscellaneous | 27 | 11.6 | 4.4
Total | 29,788 | 5.9 | 4.8

## Slide 52: Availability Assumptions - IPR
Modeled as 100% available since their outages have been incorporated in their 5-year historical output used in calculating their Existing Qualified Capacity

## Slide 53: Availability Assumptions – Demand Resources
DR average performance percentages are applied to FCA 14 qualified Existing DR
Average of 2014 – 2018 historical summer and winter DR performance
Modeled as a forced outage rate of 1-performance in blocks by DR type and Load Zone
Historical DR performance assumed in ICR calculations
  FCA 11 total New England DR modeled was 2,926 MW at 98%
  FCA 12 was 3,211 MW at 98%
  FCA 13 was 3,502 MW at 99%
 | On Peak Demand Resource |  | Seasonal Peak Resource |  | Active Demand Capacity Resource |  | Total | 
Load Zone | Summer (MW) | Perform- ance (%) | Summer (MW) | Perform- ance (%) | Summer (MW) | Perform- ance (%) | Summer (MW) | Perform- ance (%)
CONNECTICUT | 148.266 | 100 | 575.58 | 100 | 189.261 | 95 | 913.109 | 99
MAINE | 192.035 | 100 | - | - | 139.535 | 100 | 331.570 | 100
NORTH EAST MASSACHUSETTS & BOSTON | 764.388 | 100 | - | - | 95.715 | 89 | 860.103 | 99
NEW HAMPSHIRE | 130.434 | 100 | - | - | 46.320 | 96 | 176.754 | 99
RHODE ISLAND | 284.335 | 100 | - | - | 47.581 | 85 | 331.916 | 98
SOUTH EAST MASSACHUSETTS | 436.750 | 100 | - | - | 51.202 | 97 | 487.952 | 100
VERMONT | 116.852 | 100 | - | - | 52.664 | 98 | 169.516 | 99
WEST CENTRAL MASSACHUSETTS | 456.121 | 100 | 26.62 | 100 | 105.641 | 91 | 588.380 | 98
Total New England | 2,529.181 | 100 | 602.200 | 100 | 727.919 | 95 | 3,859.300 | 99

## Slide 54: Availability Assumptions – Import Capacity Resources
System Import Capacity Resources
  The forced and planned outage assumptions will be based on the availability assumptions associated with the transmission line used to import the capacity resource. The following table shows the availability assumptions updated for the external ties based on the new proposed methodology for developing external tie lines’ forced and scheduled outage rates:
Unit/plant Import Capacity Resources
  The forced and planned outage assumptions will be based on the assumptions associated with the unit/plant supplying the import capacity

## Slide 55: Availability Assumptions – Tie Benefits
The tie benefits availability assumptions will be based on the availability assumptions associated with the external transmission line recently updated using the newly proposed methodology
  These are the same values used to model the performance of the Import Capacity Resources that are system based
  They are repeated in this slide for clarity
*Based on recently updated values using the newly proposed methodology presented at the March 30, 2019 PSPC meeting. The presentation is available at: https://www.iso-ne.com/static-assets/documents/2019/05/a5_tie_line_availability_05302019.pdf
External Ties | Forced Outage Rate (%) | Maintenance (Weeks)
HQ Phase II | 0.9 | 3.2
Highgate | 0.1 | 1.2
New Brunswick Ties | 0 | 3.2
New York AC Ties | 0.5 | 5.3
Cross Sound Cable | 0 | 6.0

## Slide 56: OP-4 Assumptions Action 6 & 8 - 5% Voltage Reduction (MW)
Uses the 90-10 Peak load forecast minus BTM PV and all passive DR and ADCR
Multiplied by the 1.0% estimating relief obtainable from OP-4 voltage reduction
 | 90-10 Peak Load (Net of BTM PV) | Passive Demand Capacity Resources | Active Demand Capacity Resources | Action 6 & 8 5% Voltage Reduction
June 2023-Sept 2023 | 30,851 | 3,131 | 728 | 270
October 2023-May 2024 | 24,428 | 3,095 | 740 | 206

## Slide 57: OP-4 Assumptions, cont. Tie Benefits (MW)
Tie benefits are based on the results of the 2023-2024 tie benefits study. The assumptions and results of the study are discussed in a separate presentation that can be accessed using the following link: https://www.iso-ne.com/static-assets/documents/2019/07/pspc_a05_tiebenefitswithandwithoutmystic89.pptx

## Slide 58: OP4 Assumptions, cont. - Minimum System Reserve Assumption (MW)
Minimum system reserve is the minimum reserves held for transmission system security
Modeled at 700 MW

## Slide 59: Summary of all MW Modeled in the ICR Calculations Including Mystic Units 8 and 9
Notes:
TBD = To be determined
The tie benefits assumptions are updated based on the study
IPRs have both the summer and winter capacity values modeled
OP-4 voltage reduction includes both Action 6 and Action 8 MW assumptions.
Minimum System Reserve is the minimum reserves held for transmission security
Excluding the Mystic Units 8 & 9 would lower the total MW modeled by 1,443 MW and tie benefits would be 1,910 MW
Resource Type/OP-4 | FCA 14
Non-Intermittent Generating Capacity Resource | 29,788.062
Intermittent Power Resources | 907.207
Import Capacity Resources | 82.8
Demand Resources | 3859.3
Voltage reduction | 270
Minimum System Reserve | -700.00
Tie benefits | 1940
Total MW modeled in ICR | 36,147.369

## Slide 60: Appendix II
Tie Benefits Study for FCA 14 – Scope, Methodology, Assumptions and Results

## Slide 61: Scope of Study
To calculate tie benefits from neighboring Control Areas to New England for the 2023-2024 CCP by using a probabilistic analysis, according to the methodology described in Section III.12.9 of Market Rule 1.
The calculations include:
  Total tie benefits from all neighboring Control Areas (i.e., Quebec, Maritimes (New Brunswick) and New York)
  Tie benefits associated with each neighboring Control Area
  Tie benefits associated with an individual interconnection or a group of interconnections of interest

## Slide 62: Simulation Model
The General Electric (GE) Multi-Area Reliability Simulation (MARS) model* is used to simulate New England and its directly interconnected neighboring Control Areas (i.e., Quebec, Maritimes (New Brunswick) and New York)
An equivalent model is used to reflect the impacts of the known capacity imports/exports between New England’s directly interconnected neighboring Control Areas and their respective neighboring Control Areas (i.e., PJM and Ontario)
* MARS is a “pipe-and-bubble” transportation model

## Slide 63: Appendix II A
Tie Benefits Study for FCA 14 – Methodology

## Slide 64: Study Methodology - Summary Calculation Process
Process 1.0
  Calculate the tie benefits values for all possible interconnection states using isolated New England system as the reference
Process 2.0
  Calculate initial total tie benefits for New England from all neighboring Control Areas
Process 3.0
  Calculate initial tie benefits for each individual neighboring Control Area
  Pro-rate tie benefits values of individual Control Areas based on the total tie benefits, if necessary
Process 4.0
  Calculate initial tie benefits for individual interconnection or group of interconnections
  Pro-rate tie benefits values of individual interconnection or group of interconnections based on the individual Control Area tie benefits, if necessary
Process 5.0
  Adjust tie benefits of individual interconnection or group of interconnections to account for capacity imports
Process 6.0
  Calculate the final tie benefits for each individual neighboring Control Area
Process 7.0
  Calculate the final total tie benefits for New England

## Slide 65: Study Methodology Calculation Process 1.0
Calculation of tie benefits values for all possible interconnection states
  Bring all interconnected areas to LOLE of 0.1 days/year simultaneously
  Calculate New England’s LOLE for all the possible interconnection states, e.g.
    with no interconnections (isolated state)
    With any single interconnection only
    With any of two interconnections
    With any of three interconnections
    …
  Calculate the equivalent tie benefits values for each interconnection state using the isolated state as reference
    As the equivalent MW to bridge the LOLE delta between these two states

## Slide 66: Study Methodology Calculation Process 2.0
Calculation of total tie benefits for New England
  Compare the following two interconnection states
    New England system with all interconnections to neighboring Control Areas connected
    New England System with all interconnections with neighboring Control Areas disconnected
  Total tie benefits for New England is the equivalent MW value to bridge the LOLE delta between these two states
  This initial total tie benefits value is subject to adjustment to account for capacity imports in a later process

## Slide 67: Study Methodology Calculation Process 3.0
Calculation of initial tie benefits for each individual neighboring Control Area
  all interconnections connected to a given neighboring Control Area are grouped together to represent the state of interconnection between New England and that neighboring Control Area
  For each target neighboring Control Area, identify all the related interconnection states and calculate the equivalent tie benefits values for each of these states
    With a total of three neighboring control areas, there are four interconnection states for each neighboring area
    Use the simple average of values for all the interconnection states to represent the tie benefits of the target neighboring Control Area
  If the sum of the individual control area tie benefits calculated above is different than the total tie benefits calculated in Process 2.0, each Control Area’s tie benefits shall be adjusted based on the ratio of the individual Control Area tie benefits to the total tie benefits
  These initial individual Control Area tie benefits are subject to further adjustment to account for capacity imports in a later process.

## Slide 68: Study Methodology Calculation Process 5.0
Adjustment to the initial tie benefits for individual interconnection or group of interconnections
  Deduct capacity imports from the import capability of each individual interconnection or group of interconnections to determine the remaining available import capability to support tie benefits
    Capacity imports are the Qualified Existing Import Capacity for FCA 2022-2023
  Compare the tie benefits value of an individual interconnection or group of interconnections as determined in Process 4.0 to its remaining transmission import capability
    If the tie benefits value is greater than the remaining transmission import capability, the tie benefit value of the individual interconnection or group of interconnections is capped to the remaining transmission import capability
    Otherwise, no adjustments are made

## Slide 69: Study Methodology Calculation Process 6.0
Determination of tie benefits for individual neighboring Control Areas
  Final tie benefits for each neighboring Control Area are the sum of the tie benefits from the individual interconnections or groups of interconnections with that Control Area, after accounting for any adjustment for capacity imports as determined in Process 5.0

## Slide 70: Study Methodology Calculation Process 7.0
Determination of total tie benefits for New England
  Final total tie benefits from all neighboring control areas are the sum of the Control Area tie benefits after accounting for any adjustment for capacity imports as determined in Process 6.0

## Slide 71: Appendix II B
Tie Benefits Study for FCA 14 – Assumptions

## Slide 72: Resource Assumptions
New England
Modeled all FCA 14 Existing Capacity Resources
  Ratings, EFORd, maintenance weeks consistent with assumptions for the FCA 14 ICR calculations
Neighboring Control Areas
Modeled resources based on
  2018 NPCC Long Range Adequacy Overview & 2019 NPCC Summer Assessment
    Quebec
    Maritimes
    New York
      2019 New York Gold Book
    Ontario & PJM (for the purpose of modeling the impacts of capacity imports/exports with Quebec and New York)

## Slide 73: Load Assumptions
New England
Load Forecast
  Based on the 2019 Forecast Report of Capacity, Energy, Loads and Transmission Report load data
    Behind-the-meter photovoltaic (BTM PV) forecast is modeled with an hourly profile
    The performance uncertainty of BTM PV is modeled using a 7-day uncertainty window
Load Shape
  2002 hourly shape; consistent with current NPCC studies
Neighboring Control Areas
  Load Forecast
  Based on their latest load models used in NPCC studies for the year 2023
  2002 hourly shape; consistent with current NPCC studies

## Slide 74: Control Area Modeling
    Quebec, Maritimes, New England, and New York are simulated using a subarea transportation model
    An equivalent model is used to reflect the impacts of the known capacity import/export between New England’s directly interconnected neighboring Control Areas and their respective neighboring Control Areas (i.e., PJM and Ontario)

## Slide 75: FCA 14 Transmission Interfaces and Transfer Capabilities
New England
    Regional System Plan (RSP) subarea representation
    Transfer capabilities consistent with FCA 14 transmission transfer capabilities* reviewed at the Planning Advisory Committee (PAC)
    Interfaces associated with FCA 14 Capacity Zones are not modeled
        Maine – export-constrained
        Northern New England (NNE) – export-constrained
        Southeast New England (SENE) – import-constrained
      Neighboring Control Areas
    Consistent with their latest model used in NPCC studies
*Based on transmission transfer capability limits presented at the March 20, 2019 RC meeting. The presentation is available at: https://www.iso-ne.com/static-assets/documents/2019/03/a7_fca_14_transmission_transfer_capabilities_and_capacity_zone_development.pd

## Slide 76: FCA 14 Internal Interface Transfer Capability
Notes are discussed in the following presentation:

## Slide 77: FCA 14 Internal Interface Transfer Capability (Notes)
a) Limits are for the summer period, except where noted to be winter
  The limits may not include possible simultaneous impacts, and should not be considered as “firm”
  For the years within the FCM horizon (CCP 2023-2024 and sooner), only accepted certified transmission projects are included when identifying transfer limits
  For the years beyond the FCM horizon (CCP 2024-2025 and later), transmission upgrades with an approved proposed plan are included according to their expected in-service dates

## Slide 78: FCA 14 Internal Interface Transfer Capability (Notes) (cont.)
b) Increase associated with the Greater Boston upgrades, without the Wakefield – Woburn 345 kV line (CCPs 2019-2020 and 2020-2021)
c) Increase associated with the Greater Boston upgrades, with the Wakefield – Woburn 345 kV line in service (CCP 2021-2022 and later)
d) Increase associated with the Greater Hartford/Central Connecticut upgrades
e) Increase associated with the Southwest Connecticut upgrades
f) Increase associated with the SEMA/RI Reliability project upgrades

## Slide 79: FCA 14 External Interface Import Capability
Notes are discussed in the following presentation:

## Slide 80: FCA 14 External Interface Import Capability (Notes)
Limits are for the summer period
  The limits may not include possible simultaneous impacts, and should not be considered as “firm” (the bases for these limits are subject to more detailed review in the future)
The electrical limit of the New Brunswick-New England (NB-NE) tie is 1,000 MW
  When adjusted for the ability to deliver capacity to the greater New England Control area, the NB-NE transfer capability is 700 MW
    This is because of downstream constraints; in particular Orrington South
The capability for the Highgate facility is listed at the New England AC side of the Highgate terminal

## Slide 81: FCA 14 External Interface Import Capability (Notes) (cont.)
The Hydro-Quebec Phase II interconnection is a DC tie with equipment ratings of 2,000 MW. Due to the need to protect for the loss of this line at full import level in the PJM and NY Control Areas’ systems, ISO-NE has assumed its transfer capability for capacity and reliability calculation purposes to be 1,400 MW
  This assumption is based on the results of loss-of-source analyses conducted by PJM and NY
Import capability on the Cross Sound Cable is dependent on the level of local generation
New York interface limits
  These are without CSC and with the Northport Norwalk Cable at 0 MW flow
  Simultaneously importing into NE and SWCT or CT can lower the NY-NE capability (very rough decrease = 200 MW)

## Slide 82: FCA 14 Transmission Interfaces Availability Assumptions
      New England
Internal transmission interfaces are modeled 100 % available because the power can be delivered using multiple paths
External availability assumptions are based on results of a study conducted in 2019
      Please note that the MARS program only allows modeling the forced outage rate. It is assumed that maintenance needs will have minimum reliability impact because they are scheduled during periods when the system is reliable
      Neighboring Control Areas
    Consistent with their latest model used in NPCC studies
*Based on transmission transfer capability limits presented at the March 20, 2019 RC meeting. The presentation is available at: https://www.iso-ne.com/static-assets/documents/2019/03/a7_fca_14_transmission_transfer_capabilities_and_capacity_zone_development.pd

## Slide 83: Other Assumptions Operating Reserves and Relief from Voltage Reduction
  New England
    Assume 2,305 MW of system-wide operating reserves
      Allowed to deplete to a minimum of 700 MW as OP-4 actions progress prior to firm load shedding
      Local reserve requirements are based on the latest Forward Reserve Market auction requirements
        CT: 0 MW (summer); 0 MW (winter)
        SWCT: 0 MW (summer); 0 MW (winter)
        BOSTON: 0 MW (summer); 326 MW (winter)
    Voltage reductions
      Consistent with the ICR calculation, and the amount for subareas calculated as
        (90/10 subarea net peak load* MW minus all Active Demand Capacity Resources and Passive Demand Resources) x 1.0%
  Neighboring Control Areas
    Consistent with their latest model in NPCC studies
  *Net peak load is the gross load minus the load reduction associated with BTM PV

## Slide 84: Appendix II C
Tie Benefits Study for FCA14 - System Diagrams for Information Purposes

## Slide 85: Interconnected System Representation for 2023 (MW)
A
C
D
F
G
J
K
900 S
1,000 W
575 S
575 W
200
1,400
550
700
0
1,000
1,500
800
600
800
800
Total NY-NE
(Excludes CSC)
414
315
150
660
0
1,200 S
0 W
NOR
CT
W-MA
BHE
CMA
330
VT
0
Equivalent for PJM-NY boundary
300
600
New
York
Maritimes
Quebec
New
England
Mtl
100
200
300
1,400
1,400
660
9999
2,000
J3
J3
J4
K2
0
200
0
NB
0
NM
NS
PEI
300
300
9,999
350
150
ND
Que
Cent.
JB
MAN
Chur.
22,290
5,200
12,900
15,050
2,250
2,138
1
190 S
198 W
425
1,000
0
815
315
660
0
660
0
1,045
100
199
660
Cedars
RECO
0
315
140
385

## Slide 86: New York System Representation for 2023 (MW)
F
G
H
I
J
K
2,300
5,650
1,600
2,650
1,999
2,770 -
3,100*
1,600
3,475
1,999
1,999
5,750
8,450
1,999
4,400
235- 505 *
342
1,293
To VT
To WMA
To NOR
1,000
414
800
800
0
1,500
A
B
C
E
D
9,999
1,500
1,600
1,999
To Quebec
140
1,000
To CT
330
CE Group
4,510-5,000*
3,400
235
1,999
800
600
0
900
0
Total East
9,999
9,999
UPNY-SENY
1,999
5,500
1,528
29 –282 *
LI Sum
500
0
2,275
AG
9,999
PJM to G&J
9,999
2,000
99,999
18
LI West
J3
VFT
HTP
315
815
RECO
CPVVEC
0
1,999
5,600
DSY49Y50
1,000
425
Equivalent for PJM-NY boundary
CSC
To Cedars
2,750
9,999
2,275
1000
1,000
0
600
9999
500
K2
660
K1
* Rating a function of unit availabilities and/or area loads.
0
660
0
0
315
315
9999
150
0
J2
385
0
PJM to G
1045 9999
To CT
0
330
330
660
660

## Slide 87: New England System Representation for 2023 (MW)
East – West
3,500/3.000
Orrington South
Surowiec South
ME - NH
North – South
2,725 (relaxed)
Boston Import
5,700
SEMA/RI Export/Import
3,400/1,800
Southwest CT Import
2,800
Connecticut
(Excludes CSC) 3,400
Norwalk - Stamford
9,999 In
NB - NE
Highgate
Phase II
To D
To F
To G
To K
To NB
To Quebec
To Quebec
RI
ME
BHE
SEMA
CMA/
NEMA
Boston
NH
SME
SWCT
CT
WMA
NOR
VT
200
1,200 S
0 W
1,400
700
550
0
800
800
800
1,325
1,500
1,900
To K
330 (CSC)
0
600
0
100
Total NY-NE
(Excludes CSC)
1,400
1,400
414
* Rating a function of unit availabilities and/or area loads.
0
Southeast Import
5,700 (relaxed)
(relaxed)

## Slide 88: Abbreviations of Subareas in Diagram
Maritimes
NB 'NEW BRUNSWICK'
NS 'NOVA SCOTIA'
PEI 'PRINCE EDWARD ISLAND'
NM 'NORTHERN MAINE ISA'
Quebec
JB 'JAMES BAY'
Chur 'CHURCHILL'
MAN 'NORTH COAST/MANIC'
Que Cent. 'CENTRE (Que.)'
Mtl 'SOUTHWEST/MTL'
ND 'NICOLET-DESCANTONS'
CEDARS ' for cedar sale'
New York
A 'AREA_A, West'
B 'AREA_B, Genesee'
C 'AREA_C, Central'
D 'AREA_D, North'
E 'AREA_E, Mohawk Valley '
F 'AREA_F, Capital'
G 'AREA_G, Hudson Valley'
CPVVEC 'AREA FOR CPV VEC'
H 'AREA_H, Millwood '
I 'AREA_I, Downwoode '
J 'AREA_J, New York City '
J3 ‘Staten Island’
HTP (J4) 'HTP CABLE'
VFT (J5 ) 'LINDEN VFT CABLE-'
K 'AREA_K, Long Island'
RECO 'RECO PJM'
K1 ‘CSC cable”
K2 ‘Contracts over Neptune cable”

## Slide 89: Abbreviations of Subareas in Diagram, cont.
New England
BHE ‘Northeastern Maine’
ME ‘Western and central Maine and Saco Valley, New Hampshire’
SME ‘Southeastern Maine’
NH ‘Northern, eastern, and central New Hampshire; eastern Vermont; and southwestern Maine’
VT ‘Vermont and southwestern New Hampshire’
Boston ‘Greater Boston, including the North Shore’
CMA/NEMA ‘Central Massachusetts and northeastern Massachusetts’
WMA ‘Western Massachusetts’
SEMA ‘Southeastern Massachusetts and Newport, Rhode Island’
RI ‘Part of Rhode Island bordering Massachusetts’
CT ‘Northern and eastern Connecticut’
SWCT ‘Southwestern Connecticut’
NOR ‘Norwalk and Stamford, Connecticut’

## Slide 90: Appendix ii - D FCA 14 Tie Benefits study Results including Mystic Units 8 and 9

## Slide 91: Process 1.0 Calculation of Tie Benefits for All Interconnection States (Including Mystic Units 8 & 9)
X – disconnected √ - connected
Interconnection State | Description | Interconnection Status |  |  |  |  | LOLE | Equivalent TB (MW)
 |  | Maritimes | HQ Phase II | Highgate | NY AC ties | CSC |  | 
1 | Cut All | x | x | x | x | x | 0.55233 | 0
2 | Cut None | √ | √ | √ | √ | √ | 0.09932 | 1940
3 | Cut MT | x | √ | √ | √ | √ | 0.13652 | 1490
4 | Cut HQ Phase II | √ | x | √ | √ | √ | 0.18353 | 1110
5 | Cut Highgate | √ | √ | x | √ | √ | 0.10865 | 1815
6 | Cut NY AC ties | √ | √ | √ | x | √ | 0.11169 | 1770
7 | Cut CSC | √ | √ | √ | √ | x | 0.09932 | 1940
8 | Cut MT & HQ Phase II | x | x | √ | √ | √ | 0.25853 | 740
9 | Cut MT & Highgate | x | √ | x | √ | √ | 0.14713 | 1385
10 | Cut MT & NY AC ties | x | √ | √ | x | √ | 0.16152 | 1265
11 | Cut MT & CSC | x | √ | √ | √ | x | 0.13652 | 1490
12 | Cut HQ Phase II & Highgate | √ | x | x | √ | √ | 0.20220 | 1005
13 | Cut HQ Phase II & NY AC ties | √ | x | √ | x | √ | 0.24663 | 785
14 | Cut HQ Phase II & CSC | √ | x | √ | √ | x | 0.18353 | 1110
15 | Cut Highgate & NY AC ties | √ | √ | x | x | √ | 0.12410 | 1625
16 | Cut Highgate & CSC | √ | √ | x | √ | x | 0.10865 | 1815
17 | Cut NY AC ties & CSC | √ | √ | √ | x | x | 0.11169 | 1770
18 | Cut MT, HQ Phase II & Highgate | x | x | x | √ | √ | 0.28445 | 640
19 | Cut MT, HQ Phase II & NY AC ties | x | x | √ | x | √ | 0.44632 | 200
20 | Cut MT, HQ Phase II & CSC | x | x | √ | √ | x | 0.25853 | 740
21 | Cut MT, Highgate & NY AC ties | x | √ | x | x | √ | 0.17863 | 1145
22 | Cut MT, Highgate & CSC | x | √ | x | √ | x | 0.14713 | 1385
23 | Cut MT, NY AC ties & CSC | x | √ | √ | x | x | 0.16152 | 1265
24 | Cut HQ Phase II, Highgate & NY AC ties | √ | x | x | x | √ | 0.28722 | 630
25 | Cut HQ Phase II, Highgate & CSC | √ | x | x | √ | x | 0.20220 | 1005
26 | Cut HQ Phase II, NY AC ties & CSC | √ | x | √ | x | x | 0.24663 | 785
27 | Cut Highgate, NY AC ties & CSC | √ | √ | x | x | x | 0.12410 | 1625
28 | Cut MT, HQ Phase II, Highgate & NY AC ties | x | x | x | x | √ | 0.55233 | 0
29 | Cut MT, HQ Phase II, Highgate & CSC | x | x | x | √ | x | 0.28445 | 640
30 | Cut MT, HQ Phase II, NY AC ties & CSC | x | x | √ | x | x | 0.44632 | 200
31 | Cut MT, Highgate, NY AC ties & CSC | x | √ | x | x | x | 0.17863 | 1145
32 | Cut HQ Phase II, Highgate, NY AC ties & CSC | √ | x | x | x | x | 0.28722 | 630

## Slide 92: Process 2.0 Calculation of Initial Total Tie Benefits
Compare state 1 (without any ties) and state 2 (with all the ties)
  Total tie benefits = 1,940 MW
  This value is subject to the adjustment later to account for imports

## Slide 93: Process 3.0 Calculation of Tie Benefits for Neighboring Control Areas
All interconnections connected to a given neighboring Control Area are grouped together to represent the state of interconnection between New England and that neighboring Control Area. The simple average of values for all the interconnection states represents the tie benefits of the target neighboring Control Area (four states for each area)
Tie benefits from Maritimes
  1 vs. 32 = 630 2 vs. 3 = 450 12 vs. 18 = 365 17 vs. 23 = 505
  Average = 487.5 MW
Tie benefits from Quebec
  1 vs. 23 = 1,265 2 vs. 12 = 935 3 vs. 18 = 850 17 vs. 32 = 1,140
  Average = 1,047.5 MW
Tie benefits from New York
  1 vs. 18 = 640 2 vs. 17 = 170 3 vs. 23 = 225 12 vs. 32 = 375
  Average = 352.5 MW
Tie benefits after proration (since 487.5 + 1,047.5 + 352.5 = 1,887.5 ≠ 1,940)
  Maritimes initial tie benefits = 1,940 * 487.5 / (487.5 + 1,047.5 + 352.5) = 1,940 * 0.2583 = 501 MW
  Hydro Quebec initial tie benefits = 1,940 * 1,047.5 / (487.5 + 1,047.5 + 352.5) = 1,940 * 0.5550 = 1,077 MW
  NY initial tie benefits = 1,940 * 352.5 / (487.5 + 1,047.5 + 352.5) = 1,940 * 0.1868 = 362 MW

## Slide 94: Process 4.0 Calculation of Tie Benefits for Individual or Group of Interconnections
Each individual interconnection or group of interconnections subject to the individual tie benefits contribution calculation is treated independently. The simple average of values for all the interconnection states represents tie benefits of the target interconnection or group of interconnections
Interconnections with Maritimes
  No individual interconnections subject to the calculation
Interconnections with Quebec
  HQ Phase II and Highgate are subject to the calculation
  HQ Phase II
    1 vs. 31 = 1,145 2 vs. 4 = 830 3 vs. 8 = 750 5 vs. 12 = 810
    9 vs. 18 = 745 17 vs. 26 = 985 23 vs. 30 = 1,065 27 vs. 32 = 995
    Average = 916 MW
  Highgate
    1 vs. 30 = 200 2 vs. 5 = 125 3 vs. 9 = 105 4 vs. 12 = 105
    8 vs. 18 = 100 17 vs. 27 = 145 23 vs. 31 = 120 26 vs. 32 = 155
    Average = 132 MW
  Tie benefits after proration (since 916 + 132 = 1,048 ≠ 1,077)
    TB_Ph-II_initial = 1,077 * 916 / (916 + 132) = 1,077 * 0.8740 = 941 MW
    TB_HG_initial = 1,077 * 132 / (916 + 132) = 1,077 * 0.1260 = 136 MW

## Slide 95: Process 4.0 (cont.)
Interconnections with New York
  NY AC ties and Cross Sound Cable (CSC) are subject to the calculation
  NY AC ties
    1 vs. 29 = 640 2 vs. 6 = 170 3 vs. 10 = 225 7 vs. 17 = 170
    11 vs. 23 = 225 12 vs. 24 = 375 18 vs. 28 = 640 25 vs. 32 = 375
    Average = 353 MW
  CSC
    1 vs. 28 = 0 2 vs. 7 = 0 3 vs. 11 = 0 6 vs. 17 = 0
    10 vs. 23 = 0 12 vs. 25 = 0 18 vs. 29 = 0 24 vs. 32 = 0
    Average = 0 MW
  Tie benefits after proration (since 353 + 0 = 353 ≠ 362)
    NY AC initial tie benefits = 362 * 353 / (353 + 0) = 362 * 1.0 = 362 MW
    CSC initial tie benefits = 362 * 0 / (353 + 0) = 362 * 0 = 0 MW

## Slide 96: Process 5.0 Adjustment to Initial Tie Benefits Values
Tie benefits determined in Process 4.0 for individual interconnection or group of interconnections are adjusted to account for capacity imports
Interconnections with Maritimes
  No adjustments required as no existing capacity imports
Interconnections with Quebec
  HQ Phase II
    No adjustments required as no existing capacity imports
  Highgate
    No adjustments required as no existing capacity imports
Interconnections with New York
  NY AC Ties
    Existing import = 82.8 MW
    Assumed total import capability = 1,400 MW
    Remaining import capability after import = 1,400 – 82.8 = 1,317.2 MW
    Tie benefits value calculated in Process 4.0 = 362 MW
    Since 362 < 1,317.2 MW, no adjustment is required
    NY ACT tie benefits = 362 MW
  CSC
    No adjustments required since there are no tie benefits
    CSC tie benefits = 0 MW

## Slide 97: Process 6.0 Determination of Tie Benefits for Individual Neighboring Control Area
Final tie benefits for each neighboring Control Area are the sum of the tie benefits from the individual interconnections or groups of interconnections with that Control Area, after accounting for the adjustments for capacity imports as determined in Process 5.0
  Maritimes = 501 MW
  Quebec = 941 + 136 = 1,077 MW
  New York = 362 + 0 = 362 MW

## Slide 98: Process 7.0 Determination of Total Tie Benefits for New England
Final tie benefits for each neighboring Control Area are the sum of the tie benefits from the individual interconnections or groups of interconnections with that Control Area after accounting for the adjustments for capacity imports as determined in Process 5.0
  Total tie benefits = 501 + 1,077 + 362 = 1,940 MW

## Slide 99: Summary of Tie Benefits Study Results Including Mystic Units 8 & 9
Total tie benefits = 1,940 MW, with the following contributions:
  Maritimes ties = 501 MW
  HQ Phase II = 941 MW
  Highgate = 136 MW
  NY AC ties = 362 MW
  Cross Sound Cable = 0 MW

## Slide 100: Appendix II - e FCA 14 Tie Benefits Study Results excluding Mystic Units 8 and 9

## Slide 101: Process 1.0 Calculation of Tie Benefits for All Interconnection States (Excluding Mystic Units 8 & 9)
X – disconnected √ - connected
Interconnection State | Description | Interconnection Status |  |  |  |  | LOLE | Equivalent TB (MW)
 |  | Maritimes | HQ Phase II | Highgate | NY AC ties | CSC |  | 
1 | Cut All | x | x | x | x | x | 0.52974 | 0
2 | Cut None | √ | √ | √ | √ | √ | 0.09999 | 1910
3 | Cut MT | x | √ | √ | √ | √ | 0.13458 | 1485
4 | Cut HQ Phase II | √ | x | √ | √ | √ | 0.18116 | 1090
5 | Cut Highgate | √ | √ | x | √ | √ | 0.10828 | 1790
6 | Cut NY AC ties | √ | √ | √ | x | √ | 0.11110 | 1750
7 | Cut CSC | √ | √ | √ | √ | x | 0.09999 | 1910
8 | Cut MT & HQ Phase II | x | x | √ | √ | √ | 0.26696 | 670
9 | Cut MT & Highgate | x | √ | x | √ | √ | 0.14543 | 1370
10 | Cut MT & NY AC ties | x | √ | √ | x | √ | 0.15766 | 1265
11 | Cut MT & CSC | x | √ | √ | √ | x | 0.13458 | 1485
12 | Cut HQ Phase II & Highgate | √ | x | x | √ | √ | 0.19845 | 985
13 | Cut HQ Phase II & NY AC ties | √ | x | √ | x | √ | 0.23881 | 785
14 | Cut HQ Phase II & CSC | √ | x | √ | √ | x | 0.18116 | 1090
15 | Cut Highgate & NY AC ties | √ | √ | x | x | √ | 0.12219 | 1610
16 | Cut Highgate & CSC | √ | √ | x | √ | x | 0.10828 | 1790
17 | Cut NY AC ties & CSC | √ | √ | √ | x | x | 0.11110 | 1750
18 | Cut MT, HQ Phase II & Highgate | x | x | x | √ | √ | 0.28773 | 590
19 | Cut MT, HQ Phase II & NY AC ties | x | x | √ | x | √ | 0.42690 | 195
20 | Cut MT, HQ Phase II & CSC | x | x | √ | √ | x | 0.26696 | 670
21 | Cut MT, Highgate & NY AC ties | x | √ | x | x | √ | 0.17442 | 1135
22 | Cut MT, Highgate & CSC | x | √ | x | √ | x | 0.14543 | 1370
23 | Cut MT, NY AC ties & CSC | x | √ | √ | x | x | 0.15766 | 1265
24 | Cut HQ Phase II, Highgate & NY AC ties | √ | x | x | x | √ | 0.27866 | 625
25 | Cut HQ Phase II, Highgate & CSC | √ | x | x | √ | x | 0.19845 | 985
26 | Cut HQ Phase II, NY AC ties & CSC | √ | x | √ | x | x | 0.23881 | 785
27 | Cut Highgate, NY AC ties & CSC | √ | √ | x | x | x | 0.12219 | 1610
28 | Cut MT, HQ Phase II, Highgate & NY AC ties | x | x | x | x | √ | 0.52974 | 0
29 | Cut MT, HQ Phase II, Highgate & CSC | x | x | x | √ | x | 0.28773 | 590
30 | Cut MT, HQ Phase II, NY AC ties & CSC | x | x | √ | x | x | 0.42690 | 195
31 | Cut MT, Highgate, NY AC ties & CSC | x | √ | x | x | x | 0.17442 | 1135
32 | Cut HQ Phase II, Highgate, NY AC ties & CSC | √ | x | x | x | x | 0.27866 | 625

## Slide 102: Process 2.0 Calculation of Initial Total Tie Benefits
Compare state 1 (without any ties) and state 2 (with all the ties)
  Total tie benefits = 1,910 MW
  This value is subject to the adjustment later to account for imports

## Slide 103: Process 3.0 Calculation of Tie Benefits for Neighboring Control Areas
All interconnections connected to a given neighboring Control Area are grouped together to represent the state of interconnection between New England and that neighboring Control Area. The simple average of values for all the interconnection states represents the tie benefits of the target neighboring Control Area (four states for each area)
Tie benefits from Maritimes
  1 vs. 32 = 625 2 vs. 3 = 425 12 vs. 18 = 395 17 vs. 23 = 485
  Average = 482.5 MW
Tie benefits from Quebec
  1 vs. 23 = 1,265 2 vs. 12 = 925 3 vs. 18 = 895 17 vs. 32 = 1,125
  Average = 1,052.5 MW
Tie benefits from New York
  1 vs. 18 = 590 2 vs. 17 = 160 3 vs. 23 = 220 12 vs. 32 = 360
  Average = 332.5 MW
Tie benefits after proration (since 482.5 + 1,052.5 + 332.5 = 1,868 ≠ 1,910)
  Maritimes initial tie benefits = 1,910 * 482.5 / (482.5 + 1,052.5 + 332.5) = 1,910 * 0.2584 = 493 MW
  Hydro Quebec initial tie benefits = 1,910 * 1,052.5 / (482.5 + 1,052.5 + 332.5) = 1,910 * 0.5636 = 1,077 MW
  NY initial tie benefits = 1,910 * 332.5 / (482.5 + 1,052.5 + 332.5) = 1,910 * 0.1780 = 340 MW

## Slide 104: Process 4.0 Calculation of Tie Benefits for Individual or Group of Interconnections
Each individual interconnection or group of interconnections subject to the individual tie benefits contribution calculation is treated independently. The simple average of values for all the interconnection states represents tie benefits of the target interconnection or group of interconnections
Interconnections with Maritimes
  No individual interconnections subject to the calculation
Interconnections with Quebec
  HQ Phase II and Highgate are subject to the calculation
  HQ Phase II
    1 vs. 31 = 1,135 2 vs. 4 = 820 3 vs. 8 = 815 5 vs. 12 = 805
    9 vs. 18 = 780 17 vs. 26 = 965 23 vs. 30 = 1,070 27 vs. 32 = 985
    Average = 922 MW
  Highgate
    1 vs. 30 = 195 2 vs. 5 = 120 3 vs. 9 = 115 4 vs. 12 = 105
    8 vs. 18 = 80 17 vs. 27 = 140 23 vs. 31 = 130 26 vs. 32 = 160
    Average = 131 MW
  Tie benefits after proration (since 922 + 131 = 1,053 ≠ 1,077)
    HQ Phase II initial tie benefits = 1,077 * 922 / (922 + 131) = 1,077 * 0.8756 = 943 MW
    Highgate initial tie benefits = 1,077 * 131 / (922 + 131) = 1,077 * 0.1244 = 134 MW

## Slide 105: Process 4.0 (cont.)
Interconnections with New York
  NY AC ties and Cross Sound Cable (CSC) are subject to the calculation
  NY AC ties
    1 vs. 29 = 590 2 vs. 6 = 160 3 vs. 10 = 220 7 vs. 17 = 160
    11 vs. 23 = 220 12 vs. 24 = 360 18 vs. 28 = 590 25 vs. 32 = 360
    Average = 332.5 MW
  CSC
    1 vs. 28 = 0 2 vs. 7 = 0 3 vs. 11 = 0 6 vs. 17 = 0
    10 vs. 23 = 0 12 vs. 25 = 0 18 vs. 29 = 0 24 vs. 32 = 0
    Average = 0 MW
  Tie benefits after proration (since 332.5 + 0 = 332.5 ≠ 340)
    NY AC initial tie benefits = 340 * 332.5 / (332.5 + 0) = 340 * 1.0 = 340 MW
    CSC initial tie benefits = 340 * 0 / (332.5 + 0) = 340 * 0 = 0 MW

## Slide 106: Process 5.0 Adjustment to Initial Tie Benefits Values
Tie benefits determined in Process 4.0 for individual interconnection or group of interconnections are adjusted to account for capacity imports
Interconnections with Maritimes
  No adjustments required as no existing capacity imports
Interconnections with Quebec
  HQ Phase II
    No adjustments required as no existing capacity imports
  Highgate
    No adjustments required as no existing capacity imports
Interconnections with New York
  NY AC Ties
    Existing import = 82.8 MW
    Assumed total import capability = 1,400 MW
    Remaining import capability after import = 1,400 – 82.8 = 1,317.2 MW
    Tie benefits value calculated in Process 4.0 = 340 MW
    Since 340 < 1,317.2 MW, no adjustment is required
    NY ACT tie benefits = 340 MW
  CSC
    No adjustments required since there are no tie benefits
    CSC tie benefits = 0 MW

## Slide 107: Process 6.0 Determination of Tie Benefits for Individual Neighboring Control Area
Final tie benefits for each neighboring Control Area are the sum of the tie benefits from the individual interconnections or groups of interconnections with that Control Area, after accounting for the adjustments for capacity imports as determined in Process 5.0
  Maritimes = 493 MW
  Quebec = 943 + 134 = 1,077 MW
  New York = 340 + 0 = 340 MW

## Slide 108: Process 7.0 Determination of Total Tie Benefits for New England
Final tie benefits for each neighboring Control Area are the sum of the tie benefits from the individual interconnections or groups of interconnections with that Control Area after accounting for the adjustments for capacity imports as determined in Process 5.0
  Total tie benefits = 493 + 1,077 + 340 = 1,910 MW

## Slide 109: Summary of Tie Benefits Study Results Excluding Mystic Units 8 & 9
Total tie benefits = 1,910 MW, with the following contributions:
  Maritimes ties = 493 MW
  HQ Phase II = 943 MW
  Highgate = 134 MW
  NY AC ties = 340 MW
  Cross Sound Cable = 0 MW

## Slide 110: Appendix III
Acronyms

## Slide 111: Acronyms
ALCC – Additional Load Carrying Capability
ARA – Annual Reconfiguration Auction
BTM PV – Behind-the-meter Photovoltaic
CCP – Capacity Commitment Period
CDD – Cooling Degree Days
CELT – Capacity, Energy, Loads and Transmission
CSC – Cross Sound Cable
CSO – Capacity Supply Obligation
CT – Connecticut
DR – Demand Resource
EE – Energy Efficiency
EFORd – Equivalent Forced Outage Rate on Demand
FCA – Forward Capacity Auction
FCM – Forward Capacity Market

## Slide 112: Acronyms, cont.
FERC – Federal Energy Regulatory Commission
HQICCs – Hydro-Quebec Interconnection Capability Credits
ICR – Installed Capacity Requirement
ISO – ISO New England
LRA – Local Resource Adequacy
LSR – Local Sourcing Requirement
MARS -Multi-Area Reliability Simulation
MCL – Maximum Capacity Limit
MRI – Marginal Reliability Impact
NEPOOL – New England Power Pool
Net ICR – ICR minus HQICCs
NNE – Northern New England
NPCC – Northeast Power Coordinating Council

## Slide 113: Acronyms, cont.
OP-4 – Operating Procedure No. 4, Action During a Capacity Deficiency
PAC – Planning Advisory Committee
PC – Participants Committee
PK - Peak
PSPC – Power Supply Planning Committee
RC – Reliability Committee
RI – Rhode Island
SEMA – Southeastern Massachusetts
SENE – Southern New England
SWCT – Southwest Connecticut
TSA – Transmission Security Analysis
VR – Voltage Reduction
WTHI – Weighted Temperature-Humidity Index