## Cover Sheet
Request for Proposal
Modeling Data Workbook
Boston 2028 RFP
December 20, 2019
© ISO New England Inc.
ISO-NE Public

## PSSE - Bus
Tab Set-up: The requested information copies the format used to build a model in PSEE.
Tab Purpose: Identify all buses that are part of the respondent's Phase One Proposal Submittal.
Tab Instruction: The yellow colored columns must be filled out. The white colored columns are not required to be filled out. The grey colored columns are automatically filled in by PSSE and shall not be filled in by the QTPS Respondent. Additional instructions are provided at the bottom of this spreadsheet.
New (N) or Existing (E) Bus | If Bus is to be removed, Input "R" | Bus Number | Bus Name | Base kV | Area Number | Area Name | Zone Number | Zone Name | Owner Number | Owner Name | Code | Voltage (pu) | Angle (deg) | Normal Vmax (pu) | Normal Vmin (pu) | Emergency Vmax (pu) | Emergency Vmin (pu) | Comments
Additional Instructions
If additional rows are needed to input data, insert each new row beneath the last row with a data entry.
For entries in the "Bus Number" column, the specified bus numbers shall be in the range of 900000 to 910000.
For entries in the "Area Number" column, one of the following area numbers are to be used based on the location of the modeled bus: 101: New England 102: New York 104: Quebec 105: New Brunswick 99: Other

## PSSE - Plant
Tab Set-up: The requested information copies the format used to build a model in PSEE.
Tab Purpose: Identify all plants that are part of the respondent's Phase One Proposal Submittal.
Tab Instruction: The yellow colored columns must be filled out. The white colored columns are not required to be filled out. The grey colored columns are automatically filled in by PSSE and shall not be filled in by the QTPS Respondent. Additional instructions are provided at the bottom of this spreadsheet.
New (N) or Existing (E) Plant | Remove (R), or Modify (M) | Bus Number | Bus Name | Area Number | Area Name | Code | Pgen (MW) | Qgen (Mvar) | Qmax (MW) | Qmin (Mvar) | Vsched (pu) | Remote Bus | Remote Bus Name | Voltage (pu) | RMPCT | Comments
Additional Instructions
If additional rows are needed to input data, insert each new row beneath the last row with a data entry.

## PSSE - Machine
Tab Set-up: The requested information copies the format used to build a model in PSEE.
Tab Purpose: Identify all machines that are part of the respondent's Phase One Proposal Submittal.
Tab Instruction: The yellow colored columns must be filled out. The white colored columns are not required to be filled out. The grey colored columns are automatically filled in by PSSE and shall not be filled in by the QTPS Respondent. The black colored columns shall not be used. Additional instructions are provided at the bottom of this spreadsheet.
New (N) or Existing (E) Machine | Remove (R), or Modify (M) | Bus Number | Bus Name | Id | Area Number | Area Name | Zone Number | Zone Name | Code | V Sched (pu) | Remote Bus | In Service Yes (Y), or No (N) | Pgen (MW) | Pmax (MW) | Pmin (MW) | Qgen (Mvar) | Qmax (Mvar) | Qmin (Mvar) | Mbase (MVA) | R Source (pu) | X Source (pu) | Rtran (pu) | Xtran (pu) | Gentap (pu) | Owner 1 | Fraction 1 | Owner 2 | Fraction 2 | Owner 3 | Fraction 3 | Owner 4 | Fraction 4 | RG-Pos (pu) | XG-Pos (pu) | RG-Neg (pu) | XG-Neg (pu) | RG-Zero (pu) | XG-Zero (pu) | Wind Machine Code | Wind Machine Power Factor | Comments
Additional Instructions
If additional rows are needed to input data, insert each new row beneath the last row with a data entry.

## PSSE - Load
Tab Set-up: The requested information copies the format used to build a model in PSEE.
Tab Purpose: Identify all loads that are part of the respondent's Phase One Proposal Submittal.
Tab Instruction: The yellow colored columns must be filled out. The white colored columns are not required to be filled out. The grey colored columns are automatically filled in by PSSE and shall not be filled in by the QTPS Respondent. The black colored columns shall not be used. Additional instructions are provided at the bottom of this spreadsheet.
New (N) or Existing (E) Load | Remove (R), or Modify (M) | Bus Number | Bus Name | ID | Code | Area Number | Area Name | Zone Number | Zone Name | Owner Number | Owner Name | In service Yes (Y), or No (N) | Scalable (Y) or (N) | Interruptible (Y) or (N) | Pload (MW | Qload (MVAR) | Ipload (MW) | Iqload (MVAR) | Ypload (MW) | Yqload (MVAR) | Grounded (Y) or (N) | Comments
Additional Instructions
If additional rows are needed to input data, insert each new row beneath the last row with a data entry.

## PSSE - Fixed Shunt
Tab Set-up: The requested information copies the format used to build a model in PSEE.
Tab Purpose: Identify all fixed shunt devices that are part of the respondent's Phase One Proposal Submittal.
Tab Instruction: The yellow colored columns must be filled out. The white colored columns are not required to be filled out. The grey colored columns are automatically filled in by PSSE and shall not be filled in by the QTPS Respondent. Additional instructions are provided at the bottom of this spreadsheet.
New (N) or Existing (E) Fixed Shunt | Remove (R), or Modify (M) | Bus Number | Bus Name | Id | Area Number | Area Name | Zone Number | Zone Name | Code | In service Yes (Y), or No (N) | G-Shunt (MW) | B-Shunt (Mvar) | Comments
Additional Instructions
If additional rows are needed to input data, insert each new row beneath the last row with a data entry.
This tab is used to model fixed shunts that are not able to be remotely or automatically switched within 30 minutes.

## PSSE - Switched Shunt
Tab Set-up: The requested information copies the format used to build a model in PSEE.
Tab Purpose: Identify all switched shunts that are part of the respondent's Phase One Proposal Submittal.
Tab Instruction: The yellow colored columns must be filled out. The white colored columns are not required to be filled out. The grey colored columns are automatically filled in by PSSE and shall not be filled in by the QTPS Respondent. The black colored columns shall not be used. Additional instructions are provided at the bottom of this spreadsheet.
New (N) or Existing (E) Switched Shunt | Remove (R), or Modify (M) | Bus Number | Bus Name | Area Number | Area Name | Zone Number | Zone Name | Code | In Service Yes (Y), or No (N) | Control Mode | Adjustment Method | Vhi (pu) | Vlo (pu) | Remote Bus Number | Remote Bus Name | RMPCT (%) | Device Name | Binit (Mvar) | Blk 1 Steps | Block 1 Bstep (Mvar) | Block 2 Steps | Block 2 Bstep (Mvar) | Block 3 Steps | Block 3 Bstep (Mvar) | Block 4 Steps | Block 4 Bstep (Mvar) | Block 5 Steps | Block 5 Bstep (Mvar) | Block 6 Steps | Block 6 Bstep (Mvar) | Block 7 Steps | Block 7 Bstep (Mvar) | Block 8 Steps | Block 8 Bstep (Mvar) | BLK 1 Bzero (Mvar) | BLK 2 Bzero (Mvar) | BLK 3 Bzero (Mvar) | BLK 4 Bzero (Mvar) | BLK 5 Bzero (Mvar) | BLK 6 Bzero (Mvar) | BLK 7 Bzero (Mvar) | BLK 8 Bzero (Mvar) | Comments
Additional Instructions
If additional rows are needed to input data, insert each new row beneath the last row with a data entry.
This tab is used to model fixed shunts that are able to be remotely or automatically switched within 30 minutes.
For the "Control Mode" column, one of the following control modes must be specified: -Locked -Discrete, control voltage -Continuous, control voltage -Control plant MVAR -Control VSC converter MVAR -Control another switched shunt MVAR -Control FACTS shunt element MVAR
For the "Adjustment Method" column, one of the following adjustment methods must be specified: -Sequential input order -Nearest combination

## PSSE - Branch (incl. zero seq)
Tab Set-up: The requested information copies the format used to build a model in PSEE.
Tab Purpose: Identify all branches that are part of the respondent's Phase One Proposal Submittal.
Tab Instruction: The yellow colored columns must be filled out. The white colored columns are not required to be filled out. The grey colored columns are automatically filled in by PSSE and shall not be filled in by the QTPS Respondent. The black colored columns shall not be used. Additional instructions are provided at the bottom of this spreadsheet.
New (N) or Existing (E) Branch | Remove (R), or Modify (M) | From Bus Number | From Bus Name | To Bus Number | To Bus Name | Id | Line R (pu) | Line X (pu) | Charging B (pu) | In Service Yes (Y), or No (N) | Metered (From), or (To) Bus | Rate A (MVA) | Rate B (MVA) | Rate C (MVA) | Line G From (pu) | Line B From (pu) | Line G To (pu) | Line B To (pu) | Length | Owner 1 | Fraction 1 | Owner 2 | Fraction 2 | Owner 3 | Fraction 3 | Owner 4 | Fraction 4 | R-Zero (pu) | X-Zero (pu) | B-Zero (pu) | Zero Seq G From (pu) | Zero Seq B From (pu) | Zero Seq G To (pu) | Zero Seq B To (pu) | Protection Mode | MOV Rated Current (kA) | Comments
Additional Instructions
If additional rows are needed to input data, insert each new row beneath the last row with a data entry.
Zero sequence branch data for short circuit analysis shall be included in this worksheet.

## PSSE - 2 Winding
Tab Set-up: The requested information copies the format used to build a model in PSEE.
Tab Purpose: Identify all 2-winding transformers that are part of the respondent's Phase One Proposal Submittal.
Tab Instruction: The yellow colored columns must be filled out. The white colored columns are not required to be filled out. The grey colored columns are automatically filled in by PSSE and shall not be filled in by the QTPS Respondent (unless otherwise indicated). The black colored columns shall not be used. Additional instructions are provided at the bottom of this spreadsheet.
New (N) or Existing (E) 2 winding transformer | Remove (R), or Modify (M) | From Bus Number | From Bus Name | To Bus Number | To Bus Name | Id | Name | In Service Yes (Y), or No (N) | Metered (From), or (To) Bus | Winding 1 Side - (From) or (To) Bus | Controlled Bus | Controlled Side - (Tapped) or (Not Tapped) *Need to specify if Controlled Bus is not a terminal of the Tx | Tap Positions | Control Mode | Auto Adjust - (Yes) or (No) | Winding I/O Code | Impedance I/O Code | Admittance I/O Code | Specified R (pu or watts) | Specified X (pu) | Rate A (MVA) | Rate B (MVA) | Rate C (MVA) | Magnetizing G (pu or watts) | Magnetizing B (pu) | Owner 1 | Fraction 1 | Owner 2 | Fraction 2 | Owner 3 | Fraction 3 | Owner 4 | Fraction 4 | Winding MVA Base | Wnd 1 Ratio (pu or kV) | Wnd 1 Nominal kV | Wnd 1 Angle (degrees) | Wnd 2 Ratio (pu or kV) | Wnd 2 Nominal kV | Rmax (ratio or angle) | Rmin (ratio or angle) | Vmax (pu, kV MW, or Mvar) | Vmin (pu, kV MW, or Mvar) | Wnd Connect Angle | Load Drop Comp R(pu) | Load Drop Comp X(pu) | Impedance Table | R (table corrected pu or watts) | X (table corrected pu) | Vector Group | Edit Vector Group | Connection Code | Edit Connection | Leakage Impedance I/O Code | Grounding Impedance I/O Code | RG1 | XG1 | R01 (pu) | X01 (pu) | RG2 | XG2 | R02 (pu) | X02 (pu) | RNutrl | XNutrl | Comments
Additional Instructions
If additional rows are needed to input data, insert each new row beneath the last row with a data entry.
For the "Control Mode" column, one of the following must be specified: -None -Voltage -MVAR -MW symmetrical PAR -DC Line -MW asymmetrical PAR
For the "Controlled Side" column, data must be specified in this column if a corresponding entry in the "Controlled Bus" is a bus location other than a terminal of the transformer being modeled: -Tapped -Not Tapped
For the "Winding I/O Code" column, one of the following must be specified: -Turns ratio (pu on bus base kV) -Winding voltage (kV) -Turns ratio (pu on nom winding kV)
For the "Impedance I/O Code" column, one of the following must be specified: -Zpu (system base) -Zpu (winding kV base) -Load loss & ¦Z¦
For the "Admittance I/O Code" column, one of the following must be specified: -Y pu (system base) -No load loss & exc. I

## PSSE - 3 Winding - Transformer
Tab Set-up: The requested information copies the format used to build a model in PSEE.
Tab Purpose: Identify all 3 winding transformers that are part of the respondent's Phase One Proposal Submittal.
Tab Instruction: The yellow colored columns must be filled out. The white colored columns are not required to be filled out. The grey colored columns are automatically filled in by PSSE and shall not be filled in by the QTPS Respondent. The black colored columns shall not be used. Additional instructions are provided at the bottom of this spreadsheet.
New (N) or Existing (E) 3 winding transformer | Remove (R), or Modify (M) | From Bus Number | From Bus Name | To Bus Number | To Bus Name | Last Bus Number | Last Bus Name | Id | Name | In Service | Non-metered End | Winding Data I/O Code | Impedance Data I/O Code | Admittance Data I/O Code | W1-2 R (pu or watts) | W1-2 X (pu) | W2-3 R (pu or watts) | W2-3 X (pu) | W3-1 R (pu or watts) | W3-1 X (pu) | Magnetizing G (pu or watts) | Magnetizing B (pu) | Winding 1-2 MVA Base | Winding 2-3 MVA Base | Winding 3-1 MVA Base | Star Point Bus Voltage | Star Point Bus Angle | Owner 1 | Fraction 1 | Owner 2 | Fraction 2 | Owner 3 | Fraction 3 | Owner 4 | Fraction 4 | Actual R1-2 (pu or watts) | Actual R1-2 (pu) | Actual R2-3 (pu or watts) | Actual R2-3 (pu) | Actual R3-1 (pu or watts) | Actual R3-1 (pu) | Vector Group | Edit Vector Group | Connection Code | Edit Connection | User Code | Leakage Impedance I/O Code | Grounding Impedance I/O Code | RG1 | XG1 | R01 (pu) | X01 (pu) | RG2 | XG2 | R02 (pu) | X02 (pu) | RG3 | XG3 | R03 (pu) | X01 (pu) | RNutrl | XNutrl | Comments
Additional Instructions
If additional rows are needed to input data, insert each new row beneath the last row with a data entry.
For each entry in this spreadsheet, there should be three entries in the "PSSE - 3 Winding - Transformer" spreadsheet.
For the "In Service" column, one of the following must be specified: -All out-of-service -All in-service -Winding 2 out-of-service -Winding 3 out-of-service -Winding 1 out-of-service
For the "Non-Metered End" column, one of the following must be specified: -From Bus -To Bus -Last Bus
For the "Winding I/O Code" column, one of the following must be specified: -Turns ratio (pu on bus base kV) -Winding voltage (kV) -Turns ratio (pu on nom winding kV)
For the "Impedance I/O Code" column, one of the following must be specified: -Zpu (system base) -Zpu (winding kV base) -Load loss & ¦Z¦
For the "Admittance I/O Code" column, one of the following must be specified: -Y pu (system base) -No load loss & exc. I

## PSSE - 3 Winding - Winding
Tab Set-up: The requested information copies the format used to build a model in PSEE.
Tab Purpose: Identify all 3-winding windings that are part of the respondent's Phase One Proposal Submittal.
Tab Instruction: The yellow colored columns must be filled out. The white colored columns are not required to be filled out. The grey colored columns are automatically filled in by PSSE and shall not be filled in by the QTPS Respondent. Additional instructions are provided at the bottom of this spreadsheet.
New (N) or Existing (E) 3-winding winding | Remove (R), or Modify (M) | Id (From PSSE-3 Winding-Transformer Tab | Bus Number | Bus Name | Winding | Rate A | Rate B | Rate C | Ratio (pu or kV) | Nominal (kV) | Angle (deg) | Control Mode | Auto Adjust Yes (Y), or No (N_ | Rmax (ratio or angle) | Rmin (ratio or angle) | Vmax (pu, kV MW, or Mvar) | Vmin (pu, kV MW, or Mvar) | Wnd Connect Angle | Controlled Bus | Controlled Bus Name | Controlled Side Yes (Y), or No (N) *Need to specify if Controlled Bus is not a terminal of the Tx | Tap Positions | Load Drop Comp R (pu) | Load Drop Comp X (pu) | Impedance table | Nominal R (pu system base) | Nominal X (pu system base) | R (table corrected pu) | X (table corrected pu) | Comments
Additional Instructions
If additional rows are needed to input data, insert each new row beneath the last row with a data entry.
For each entry in the "PSSE - 3 Winding - Transformer" spreadsheet, there should be three entries in this spreadsheet.
For the "Control Mode" column, one of the following must be specified: -None -Voltage -MVAR -MW symmetrical PAR -DC Line -MW asymmetrical PAR
For the "Controlled Side" column, data must be specified in this column if a corresponding entry in the "Controlled Bus" is a bus location other than a terminal of the transformer being modeled.

## PSSE - FACTS
Tab Set-up: The requested information copies the format used to build a model in PSEE.
Tab Purpose: Identify all FACTS devices that are part of the respondent's Phase One Proposal Submittal.
Tab Instruction: The yellow colored columns must be filled out. The white colored columns are not required to be filled out. The grey colored columns are automatically filled in by PSSE and shall not be filled in by the QTPS Respondent. Additional instructions are provided at the bottom of this spreadsheet.
New (N) or Existing (E) FACTS | Remove (R), or Modify (M) | Device Name | Sending Bus Number/Name | Terminal Bus Number/Name (default = 0 to represent STATCON) | Control Mode | P Setpoint (MW) (default = 0.0) | Q Setpoint (Mvar) (default = 0.0) | V send setpoint (pu) | Shunt Max (MVA) | RMPCT (%) | Bridge Max (MW) | V term max (pu) | V term min (pu) | V series max (pu) | I Series Max (MVA) (default = 0.0) | Dummy Series X (pu) (default = 0.05) | Constant Series Imp. R (default = 0.0005) *Use if Control Mode = Constant series Z | Constant Series Imp. X (default = 0.0) *Use if Control Mode = Constant series Z | Constant Series V Mag (default = 0.0) *Use if Control Mode = Constant series V | Constant Series V Ang (default = 0.0) *Use if Control Mode = Constant series V | IPFC Constant Series Vd (default = 0.0) *Use if Control Mode involves Vd & Vq | IPFC Constant Series Vq (default = 0.0) *Use if Control Mode involves Vd & Vq | V Series Reference (Sending end voltage) or (Series current) *Use if Control Mode = Constant series Z, Constant series V, or involves Vd & Vq | Owner Name | Remote Bus Number (Default = 0) | Remote Bus Name | Comments
Additional Instructions
If additional rows are needed to input data, insert each new row beneath the last row with a data entry.
For the "Control Mode" column, one of the following must be specified: -Block -Normal -Series bypassed -Constant series Z -Constant series V -IPFC master, P & Q -IPFC slave, P -IPFC master, Vd & Vq -IPFC slave, Vd & Vq Note that only the first two control modes listed (Block and Normal) are to be used when no bus has been specified in the "Terminal Bus Number/Name" column (i.e. a "0" has been entered in this column).

## PSSE - 2 Term DC - Lines
Tab Set-up: The requested information copies the format used to build a model in PSEE.
Tab Purpose: Identify all 2-terminal DC lines that are part of the respondent's Phase One Proposal Submittal.
Tab Instruction: The yellow colored columns must be filled out. The white colored columns are not required to be filled out. Additional instructions are provided at the bottom of this spreadsheet.
New (N) or Existing (E) 2 terminal DC line | Remove (R), or Modify (M) | Line Name | Rectifier | Inverter | Control Mode | Rdc-Ohm (ohms) | Rcmp-Ohm (ohms) | Delti (pu) | Setval (amps or MW) | Vschedule (kV) | Dcvmin (kV) | Vcmode (kV) *Must be specified if "Control Mode" = Power | Metered (R for Rectifier) or (I for Inverter) | CCC Itmax | CCC Accel | Comments
Additional Instructions
If additional rows are needed to input data, insert each new row beneath the last row with a data entry.
Each DC line entry in this worksheet must have two corresponding entries in the "PSSE - 2 Term DC - Converter" worksheet (one for the rectifier and one for the inverter)
Entries in the "Line Name" column must be entered as non-blank alphanumeric identifiers (up to 12 characters). Do not use blanks or special characters. The "Line Name" entered on this spreadsheet must be identical to the "Line Name" for the corresponding entries in the "PSSE - 2 Term DC - Converter" spreadsheet.
For the "Control Mode" column, one of the following must be specified: -Blocked -Power -Current

## PSSE - 2 Term DC - Converter
Tab Set-up: The requested information copies the format used to build a model in PSEE.
Tab Purpose: Identify all 2-terminal DC converter stations that are part of the respondent's Phase One Proposal Submittal.
Tab Instruction: The yellow colored columns must be filled out. The white colored columns are not required to be filled out. Additional instructions are provided at the bottom of this spreadsheet.
Line Name | Type | Bus Number | Bus Name | Max Firing Angle (deg) | Min Firing Angle (deg) | Bridges in Series | Primary Base Voltage (kV) | Commutating Resistance (ohms) | Commutating Reactance (ohms) | Measuring Bus (default = 0) | Trans Ratio (pu) (default = 1.0) | Tap Setting (pu) (default = 1.0) | Max Tap Setting (pu) (default = 1.5) | Min Tap Setting (pu) (default = 0.51) | Tap Step (pu) (default = 0.00625) | Reactance of CCC (ohms) (default = 0.0) | From Bus AC Tx Number (default = 0) | To Bus AC Tx Number (default = 0) | Id (default = 1)
Rectifier
Inverter
Rectifier
Inverter
Rectifier
Inverter
Rectifier
Inverter
Rectifier
Inverter
Rectifier
Inverter
Rectifier
Inverter
Rectifier
Inverter
Additional Instructions
If additional rows are needed to input data, insert each new row beneath the last row with a data entry.
Each DC line entry in the "PSSE - 2 Term DC - Lines" tab must have two corresponding entries on this worksheet: One for the rectifier terminal and one for the inverter terminal (rectifier and inverter entries are differentiated in the "Type" column). The "Line Name" entry for the Inverter and Rectifier terminals on this worksheet must match the "Line Name" entry in the PSSE - 2 Term DC - Lines" worksheet for the corresponding DC line.

## PSSE - VSC DC - Lines
Tab Set-up: The requested information copies the format used to build a model in PSEE.
Tab Purpose: Identify all 2-terminal Voltage Source DC lines that are part of the respondent's Phase One Proposal Submittal.
Tab Instruction: The yellow colored columns must be filled out. The white colored columns are not required to be filled out. Additional instructions are provided at the bottom of this spreadsheet.
New (N) or Existing (E) 2 terminal DC line | Remove (R), or Modify (M) | Line Name | Converter 1 | Converter 2 | Control Mode | Rdc-Ohm (ohms) | Owner 1 (default = 0) | Fraction 1 (default = 1.0) | Owner 2 (default = 0) | Fraction 2 (default = 1.0) | Owner 3 (default = 0) | Fraction 3 (default = 1.0) | Owner 4 (default = 0) | Fraction 4 (default = 1.0)
Additional Instructions
If additional rows are needed to input data, insert each new row beneath the last row with a data entry.
Each DC line entry in this worksheet must have two corresponding entries in the "PSSE -VSC DC - Converter" worksheet (one for Converter 1 and one for Converter 2)
Entries in the "Line Name" column must be entered as non-blank alphanumeric identifiers (up to 12 characters). Do not use blanks or special characters. The "Line Name" entered on this spreadsheet must be identical to the "Line Name" for the corresponding entries in the "PSSE - VSC DC - Converter" spreadsheet.
For the "Control Mode" column, one of the following must be specified: -Blocked -In-service

## PSSE - VSC DC - Converters
Tab Set-up: The requested information copies the format used to build a model in PSEE.
Tab Purpose: Identify all 2-terminal Voltage Source DC converter stations that are part of the respondent's Phase One Proposal Submittal.
Tab Instruction: The yellow colored columns must be filled out. The white colored columns are not required to be filled out. Additional instructions are provided at the bottom of this spreadsheet.
Line Name | Type | Bus Number | Bus Name | DC Control Type | DC Setpoint (kV or MW) | AC Control Mode | AC Setpoint (pu or pf) | A Loss (kW) (default = 0.0) | B Loss (kW / AMP) (default = 0.0) | Min Conv. Loss (kW) (default = 0.0) | MVA/%Rating (default = 0.0) | AC Current Rating (amp) (default = 0) | PWR Weighting Fraction (default = 1.0) | Max Reactive Power (Mvar) | Min Reactive Power (Mvar) | RMPCT (%) (default = 100.0) | Remote Bus Number (default = 0)
| Converters 1 | [5 empty] | 1.022
| Converters 2 | [5 empty] | 1.014
Converters 1
Converters 2
Converters 1
Converters 2
Converters 1
Converters 2
Converters 1
Converters 2
Converters 1
Converters 2
Converters 1
Converters 2
Converters 1
Converters 2
Additional Instructions
If additional rows are needed to input data, insert each new row beneath the last row with a data entry.
Each DC line entry in the "PSSE -VSC DC - Lines" tab must have two corresponding entries on this worksheet: One for the "Converter 1" terminal and one for the "Converter 2" terminal. The "Line Name" entry for the Converter 1 and Converter 2 terminals on this worksheet must match the "Line Name" entry in the PSSE - VSC DC - Lines" worksheet for the corresponding DC line.
For the "DC Control Type" column, one of the following must be specified: -Out-of-service -kV -MW
For the "AC Control Mode" column, one of the following must be specified: -Voltage -P.F.

## Short Circuit - Breakers
Tab Set-up: The requested information is consistent with the data required to build short circuit models in ASPEN.
Tab Purpose: Provide short circuit modeling information for all new and modified circuit breakers that are part of the respondent's Phase One Proposal Submittal.
Tab Instruction: The yellow colored columns must be filled out. The white colored columns are not required to be filled out. Additional instructions are provided at the bottom of this spreadsheet.
Name (Designation Nomenclature) | Rated Short Circuit Amps | Max Design kV | Operating kV | Rating Method | Rated Momentary Amps | Interrupting Time in Cycles | Contact Parting Time
Additional Instructions
If additional rows are needed to input data, insert each new row beneath the last row with a data entry.
For the "Rating Method" column, please specify one of the following: -IEEE - Symmetrical Current: for breakers that are rated on a symmetrical-current basis using ANSI/IEEE standards. Most breakers made in the US after 1964 are rated this way. Only Rated Short Circuit Amps is needed. -IEEE - Total Current: for breakers that are rated on a total-current basis using ANSI/IEEE standards. Breakers made in the US before 1965 are rated this way. Both Rated Short Circuit MVA and Rated Momentary Amps are needed. -IEC: for breakers rated using IEC standards. Breakers made by European manufacturers are rated this way. Both Rated Breaking Amps and Rated AC Making Amps are needed. When in doubt, you can identify the breaker type by examining the nameplate. The rating for an IEEE total-current rated breaker is in MVA, whereas the rating for an IEEE symmetrical-current rated breaker is in amperes. The nameplate for an IEC breaker usually shows both rated breaking current and rated making current in amperes.

## Short Circuit - Mutual Line Imp
Tab Set-up: The requested information is consistent with the data required to build short circuit models in ASPEN.
Tab Purpose: Provide short circuit modeling information on mutual line impedances for all new and modified branches that are part of the respondent's Phase One Proposal Submittal.
Tab Instruction: The yellow colored columns must be filled out. The white colored columns are not required to be filled out. Additional instructions are provided at the bottom of this spreadsheet.
This Line | [5 empty] | Coupled Line
Terminal 1 (bus number) | Terminal 1 (Name) | Terminal 2 (bus number) | Terminal 2 (Name) | From (%) | To (%) | Terminal 1 (bus number) | Terminal 1 (Name) | Terminal 2 (bus number) | Terminal 2 (Name) | From (%) | To (%) | R (pu on 100 MVA) | X (pu on 100 MVA)
Additional Instructions
If additional rows are needed to input data, insert each new row beneath the last row with a data entry.
When transmission lines of different circuits are parallel for long distances it is necessary to calculate the mutual line impedances.
Positive and zero sequence data for all branches shall be provided in the "PSSE - Branch (incl. zero seq)" worksheet.

## Short Circuit - 2 Winding
Tab Set-up: The requested information is consistent with the data required to build short circuit models in ASPEN.
Tab Purpose: Provide short circuit modeling information for all new and modified two winding transformers that are part of the respondent's Phase One Proposal Submittal.
Tab Instruction: The yellow colored columns must be filled out. The white colored columns are not required to be filled out. Additional instructions are provided at the bottom of this spreadsheet.
Terminal 1 (bus number) | Terminal 2 (bus number) | Nameplate Rated kVA (Self Cooled OA) | Nameplate Aux Cooling #1 kVA Rating (FA) | Nameplate Aux Cooling #2 kVA Rating (FOA) | H Winding Voltage (V) | X Winding Voltage (V) | Nameplate H-X Winding Impedance (%) | Actual Tap Position (V) | Impedance at Tap Setting (%) | Test Report Positive Sequence Winding Resistance (%) | Test Report Zero Sequence Winding Impedance (%) | Test Report Zero Sequence Winding Resistance (%) | Test Report Load Loss (W)
Additional Instructions
If additional rows are needed to input data, insert each new row beneath the last row with a data entry.

## Short Circuit - 3 Winding
Tab Set-up: The requested information is consistent with the data required to build short circuit models in ASPEN.
Tab Purpose: Provide short circuit modeling information for all new and modified three winding transformers that are part of the respondent's Phase One Proposal Submittal.
Tab Instruction: The yellow colored columns must be filled out. The white colored columns are not required to be filled out. Additional instructions are provided at the bottom of this spreadsheet.
Terminal 1 (bus number) | Terminal 2 (bus number) | Terminal 3 (bus number) | Nameplate Rated kVA (Self Cooled OA) | Nameplate Aux Cooling #1 kVA Rating (FA) | Nameplate Aux Cooling #2 kVA Rating (FOA) | H Winding Voltage (V) | X Winding Voltage (V) | Y Winding Voltage (V) | Nameplate H-X Winding Impedance Average per-Phase (%) | Nameplate H-X Winding Impedance Base (kVA) | Nameplate H-Y Winding Impedance Average per-Phase (%) | Nameplate H-Y Winding Impedance Base (kVA) | Nameplate X-Y Winding Impedance Average per-Phase (%) | Nameplate X-Y Winding Impedance Base (kVA) | Actual Tap Position (V) | H-X Impedance at Tap Setting (%) | H-X Impedance at Tap Setting Base (kVA) | H-Y Impedance at Tap Setting (%) | H-Y Impedance at Tap Setting Base (kVA) | X-Y Impedance at Tap Setting (%) | X-Y Impedance at Tap Setting Base (kVA) | Test Report H-X Positive Sequence Winding Resistance (%) | Test Report H-Y Positive Sequence Winding Resistance (%) | Test Report X-Y Positive Sequence Winding Resistance (%) | Test Report H-X Zero Sequence Winding Impedance (%) | Test Report H-X Zero Sequence Winding Base (kVA) | Test Report H-X Zero Sequence Winding Resistance (%) | Test Report H-Y Zero Sequence Winding Impedance (%) | Test Report H-Y Zero Sequence Winding Base (kVA) | Test Report H-Y Zero Sequence Winding Resistance (%) | Test Report X-Y Zero Sequence Winding Impedance (%) | Test Report X-Y Zero Sequence Winding Base (kVA) | Test Report X-Y Zero Sequence Winding Resistance (%) | Test Report Zero Sequence Winding Resistance (%) | Test Report H-X Load Loss (W) | Test Report H-Y Load Loss (W) | Test Report X-Y Load Loss (W)
Additional Instructions
If additional rows are needed to input data, insert each new row beneath the last row with a data entry.
For the "Test Report H-X Positive Sequence Winding Resistance", "Test Report H-Y Positive Sequence Winding Resistance", "Test Report X-Y Positive Sequence Winding Resistance", "Test Report H-X Zero Sequence Winding Resistance", "Test Report H-Y Zero Sequence Winding Resistance", and "Test Report X-Y Zero Sequence Winding Resistance" columns, if Winding to Winding Resistance is not listed on Transformer Manufacturer Test Report then use Copper Load Losses to estimate: -Resistance=load losses (kW)/ Rated kVA)
For the "Test Report H-X Zero Sequence Winding Resistance", "Test Report H-X Zero Sequence Winding Impedance", "Test Report H-Y Zero Sequence Winding Resistance", "Test Report H-Y Zero Sequence Winding Impedance", "Test Report X-Y Zero Sequence Winding Resistance", and "Test Report X-Y Zero Sequence Winding Impedance" columns, if zero sequence values are not listed in Manufacturer's Test Report then use positive sequence values. Shell type transformer zero sequence impedance is equal to the positive sequence impedance. Core type transformer zero sequence impedance is 85 to 100% of the positive sequence impedance. This is caused by the core-type transformer lower exciting impedance.

## Short Circuit - Generator
Tab Set-up: The requested information is consistent with the data required to build short circuit models in ASPEN.
Tab Purpose: Provide short circuit modeling information for all new and modified transmission related machines (e.g. synchronous condensers) that are part of the respondent's Phase One Proposal Submittal.
Tab Instruction: The yellow colored columns must be filled out. The white colored columns are not required to be filled out. Additional instructions are provided at the bottom of this spreadsheet.
Location (bus number) | Generator kVA (kVA) | Generator Voltage (V) | Generator Step-Up Transformer Low Side Voltage (V) | Direct axis Saturated Transient Reactance Xd” (pu, on generator MVA base) | Saturated Negative Sequence Reactance X2 (pu, on generator MVA base) | Saturated Zero Sequence Reactance X0 (pu, on generator MVA base) | Armature Winding Positive Sequence Resistance (R1) (pu, on generator MVA base) | Armature Winding Negative Sequence Resistance (R2) (pu, on generator MVA base) | Armature Winding Zero Sequence Resistance (R0) (pu, on generator MVA base) | Neutral Grounding Impedance (ohm)
Additional Instructions
If additional rows are needed to input data, insert each new row beneath the last row with a data entry.