## Slide 1: Eversource 115-kV Structure Replacement Projects Connecticut and Massachusetts (2018 - 2019) TCA Submittal Presentation
NEPOOL Reliability Committee Meeting
February 19, 2020

## Slide 2: Agenda
1
Project Scope Summary
Geographic Locations
Structure Inspections
Cost Summary

## Slide 3: Project Scope Summary
2
Eversource Manages ~4,000 Circuit Miles of Transmission Voltage OH lines, including ~3400 structure miles
  Nearly 40% of all transmission in New England
  Eversource maintains over 20,000 115-kV structures
Wood poles are showing significant signs of age-related degradation and a program is underway to address those structures on our transmission system
This presentation provides an overview of the TCAs covering the 2018-2019 replacement program for Eversource 115-kV wood transmission poles requiring replacement due to degradation.
Projects with additional scope (replacement of conductor, lattice tower lines, etc.) are generally presented individually

## Slide 4: CT 115-kV Geographic Locations
115-kV Line (OH) 115-kV Line (UG)
115-kV Line In Scope (OH)
3

## Slide 5: WMA 115-kV Geographic Locations
115-kV Line (OH)
115-kV Line (UG)
115-kV Line In Scope (OH)
4

## Slide 6: EMA 115-kV Geographic Locations
115-kV Line (OH) 115-kV Line (UG)
115-kV Line In Scope (OH)
5

## Slide 7: Structure Inspections
□ Foot Patrol - Line crews walk/drive line to observe general condition of structures (ground level up) and general condition of ROW (access, vegetation, encroachments)
□ Structure Ground Line – Specialized crews excavate at each structure (~18”) to determine subsurface integrity of pole and apply treatment as necessary
□ High Resolution Aerial – Entire system flown, and with detail hover review at most structures, accompanied by high-resolution photos
□ Thermography - Infra-red camera (typically on helicopter) observes line for hot-spots
□ Comprehensive Drone - Started in 2017 - Combines foot and High Res Aerial. Plan to inspect whole system in 3 years
□ Items Reviewed - Wood Structures
Significant Woodpecker Damage
Severe Checking/Splits/Cracking
Insect Damage
Structure with Rot or Decay
Severe Fracturing, Buckling, Leaning
Compression Breaks
Fire Damage
Damage / Vandalism
Hardware / Insulator damage
Structures are Graded in Accordance with EPRI Guidelines
  A: Nominal Defect - No action required.
  B: Minimal Defect - Monitor degradation
  C: Moderate Defect - Repair or replace under next maintenance.
  D: Severe Defect - Repair, reinforce, or replace immediately
Replace C and D structures in one mobilization
  Other structures (A/B) may be replaced during scope in order to minimize costs and impacts to environment.
  For example, where significant effort associated with access road construction is required for C/D structures, other adjacent structures of similar age may be replaced during the same construction effort
Engineering provides training to inspectors on appropriate grading criteria - Field Inspectors provide structure grade while in field, and observe entire structure. Results reviewed by team
New Structures are typically Light-Duty Steel (wood pole equivalent std) /Direct Embed poles, and comply with most recent strength and clearance requirements

## Slide 8: Pole Damage – Woodpeckers/Pole Top/Structural
MA - 1768 Line
CT - 1726 Line
MA - 65-508 Line
CT - 1448 Line
CT - 1769 Line
MA - 65-508 Line
(Brace failure)

## Slide 9: 115 kV Lines Summary - Costs
Connecticut |  |  | 
Line # | TCA # | Description | TCA Submitted Cost ($000)
1050 | ES-19-TCA-18 | Middletown substation - Dooley substation | $7,230
1256 | ES-19-TCA-50 | Canton substation - NE Simsbury substation | $9,959
1261 | ES-19-TCA-48 | Haddam substation - Bokum substation | $20,352
1310 | ES-19-TCA-19 | Manchester substation - S. Windsor substation | $8,299
1448 | ES-19-TCA-20 | Manchester substation - Rood Avenue substation | $6,928
1465 | ES-19-TCA-89 | Shunock substation - Mystic substation | $7,743
1470 | ES-19-TCA-73 | Peaceable substation - Wilton substation | $11,111
1565 | ES-19-TCA-29 | Plumtree substation - Peaceable substation | $9,095
1620 | ES-19-TCA-21 | Middletown substation - Haddam substation | $9,993
1635 | ES-19-TCA-22 | S. Windsor substation - Barbour Hill substation | $5,608
1726 | ES-19-TCA-23 | Farmington substation - North Bloomfield substation | $16,272
1759 | ES-19-TCA-44 | Portland substation - Hopewell substation | $6,076
1765 | ES-19-TCA-96 | West Side substation - Berlin substation | $13,122
1766 | ES-19-TCA-81 | Westside substation - Dooley substation | $5,426
1767 | ES-19-TCA-45 | Hopewell substation - Manchester substation | $5,250
1768 (CT/MA) | ES-19-TCA-47 | North Bloomfield, CT - Southwick MA | $7,586
1769 | ES-19-TCA-24 | Berlin substation - East New Britain substation | $8,247
1772 | ES-19-TCA-46 | Pratt and Whitney substation - Haddam substation | $10,328
1783 | ES-19-TCA-25 | East New Britain substation - Newington substation - Farmington substation | $8,113
1785 | ES-19-TCA-26 | Berlin substation - Newington substation | $8,968
1910 | ES-19-TCA-51 | Todd substation - Southington substation | $5,780
1770 (1268/1485) | ES-19-TCA-52 | Brookfield Jct. - Shepaug substation | $8,811
TOTAL |  |  | $200,297
Massachusetts |  |  | 
Line # | TCA # | Description | TCA Submitted Cost ($000)
65-508 | ES-19-TCA-93 | Station #447, West Walpole substation - Station #65, Medway substation | $14,043
1428 | ES-19-TCA-54 | Fairmont substation - Mt. Tom substation | $7,487
F132 | ES-19-TCA-77 | Doreen substation - Partridge substation - Adams substation | $14,772
TOTAL |  |  | $36,302

## Slide 10: Conclusion
Inspections have indicated significant degradation and decreased load carrying capacity of wood 115-kV structures. Replacing the structures resolves multiple structural/hardware issues and supports safe and reliable operation.
Replace wood 115-kV structures with steel pole structures based on identified deficiencies found during inspections.
Hardware, insulators, and guys to be replaced with structures.
All new structures designed to meet current design criteria.
The total estimated TCA cost for the 115-kV structure replacements is at $236.6M
Note: The ISO-NE PAC presentation was October 17, 2018

## Slide 11: Questions