## Slide 1
Power System and Market Studies at ISO New England
Current Capabilities
Xiaochuan Luo
BUSINESS architecture and Technology
MAY 27, 2020 | Joint MC/RC TELECONFERNCE
Revision 1

## Slide 2: Overview of ISO-NE’s Modeling Capabilities
To aid stakeholders in the decision on what models and tools to employ in their future grid study, the ISO has compiled information on its key modeling capabilities for reliability, economic, and market assessments
The ISO’s existing studies can be categorized by four time horizons:
  Long-term (3 - 10 years)
  Mid-term (21 days - 3 years)
  Short-term (1 day – 21 days)
  Real-time (5 min – 24 hours)
The ISO offers information on its processes and tools for reference and discussion, with emphasis on its long-term modeling

## Slide 3: Long-Term Strategic ANALYSES and Modeling Processes

## Slide 4: Long-term Modeling Capabilities
ISO carries out a variety of studies focusing on assessing changes in the bulk transmission system, the generation resource mix, and market conditions in 3-10 years
  Reliability studies, economic studies, and market simulations
Modeling capabilities include:
  Forecasting regional demand of electricity
  Evaluating transmission system adequacy and resource interconnections
  Evaluating long-term resource adequacy
  Analyzing energy policies and their impact on planning, operations, and markets
  Evaluating new market designs

## Slide 5: Long-Term Strategic Analysis Process
Scenarios
Scenarios
Scenarios
Models
Regional System Plan
Market, Transmission & Environmental Impact
Strategy
Reliability
Load Forecast
Economic
Outlook
Regulatory Policies
Other
Network
Dynamic
Market
Economic
Markets
Market Designs
Assessments

## Slide 6: Key Processes for Reliability Studies
Resource
Adequacy
Transmission Adequacy
Proposed Plan Applications (PPA)
Performing Reliability Assessments
Capacity requirements and margin
Transmission needs and solutions
Impact on reliability or operating characteristics of the system
Regional System
Plan
Analyzing Reliability Outcomes
Load Forecast
Generation forced outage rate
Steady-state power flow
Dynamic
Short-Circuit
Electromagnetic Transients
(EMT)
Building Network
Models

## Slide 7: Key Processes for Economic Studies
Simulate economic operation of
power system chronologically, in hourly intervals (ranging from one day to many years)
Resource Mix
Fuel Price Forecast
Allowance for Environmental Emissions
Load Forecast
Transmission Network
Constructing Test System
Performing Production Cost Simulations
Energy production by fuel type
Production cost, LMP, transmission congestion
Carbon emission, Renewable spillage, etc.
Market, Transmission, Environment Impact
Analyzing Economic Study Outcomes

## Slide 8: Key Processes for Market Simulation
Unit Commitment
Economic Dispatch
Simultaneous Feasibility Test
Resource Mix
Market Offer Data
Load Forecast
Transmission Network
Constructing Test System
Running Market Simulations
Pricing and Settlement Calculation
Statistical Analysis
Bidding Behavior / Market Impact Analysis
Market Design Assessment
Analyzing Market Outcomes
Test Data Set

## Slide 9: Forecasting Regional Electricity Demand
Demand forecasting is a fundamental task in providing one of the key inputs to reliability studies, economic studies and market simulations
ISO develops up to 10-year projections of electric energy usage and seasonal peak demand, based on
  Economic outlook
  Weather and load patterns
  Pending or proposed legislation, regulation, and standards
It also includes forecasting of
  Energy Efficiency (EE)
  Behind the Meter (BTM) PV
  Electrification

## Slide 10: Evaluating Transmission System Adequacy and Resource Interconnections
An essential capability for evaluating system reliability
  Identify transmission overloads, voltage violations and system dynamic behavior under different system conditions
Widely used in planning studies:
  Regional planning needs assessment and solution development
  Annual NERC TPL Standards compliance assessment
  Annual assessment of transmission transfer capability
  Proposed Plan Application (I.3.9) study
    New generators
    Changes to existing generators
    Transmission upgrades
    Elective transmission upgrades

## Slide 11: Evaluating Long-term Resource Adequacy
Estimate representative net Installed Capacity Requirements (ICR) beyond Capacity Commitment Period (up to 10 yrs), based on
  Latest Capacity, Energy, Loads, and Transmission (CELT) load forecast
  Latest Forward Capacity Auction (FCA) resource assumptions
System-wide Operable Capacity Analysis (up to 10 yrs) to estimate operable capacity margin
  50/50 and 90/10 peak load, plus operating reserve requirements
  Representative net ICR, plus assumed unavailable capacity
  Load or capacity relief actions of Operating Procedure 4 (OP-4)

## Slide 12: Long-Term Reliability Studies
Studies | Purposes of the Study | Type of analysis (models)
Long-term load forecasting | 10-year projections of electric energy usage and seasonal peak demand, based on economic outlook, weather and load patterns, etc. Includes forecasting of EE, BTM PV and electrification | Descriptive statistics Probabilistic and AI-based predictive forecast modeling, etc.
Regional planning needs assessment and solution development | Evaluate transmission system adequacy over a 10-year planning horizon and identify reliability-based transmission needs Development of transmission solutions to address identified needs using either the Solution Study process or the Competitive Solution process | Steady-state power flow Transient stability Short circuit

## Slide 13: Long-Term Reliability Studies, cont.
Studies | Purposes of the Study | Type of analysis (models)
Proposed Plan Application (I.3.9) study | Determine whether the proposed changes have any significant adverse effect on the stability, reliability or operating characteristics of the bulk power system Include new generators, changes to existing generators, transmission upgrades, and elective transmission upgrades | Steady-state power flow Transient stability Short circuit Electromagnetic transient
NERC TPL compliance study | Annual compliance assessment of New England Bulk Electric System (BES) with NERC TPL planning criteria | Steady-state power flow Transient stability Short circuit Geomagnetic disturbance (GMD)

## Slide 14: Analyzing Energy Policies and Their Impact on Planning, Operations, and Market
New England Wind Integration Study (NEWIS)
  Determined the operational, planning and market impact of integrating substantial wind resources
  ISO-NE, GE, EnerNex, AWS Truepower
Economic Studies
  Analyze impacts on energy market, transmission system, or environment, based on different scenarios of future resource mix and transmission expansion options
System operational analysis and renewable energy integration study (SOARES)
  Focused on system imbalance and operating reserves needs under different scenarios

## Slide 15: Evaluating New Market Designs
ISO evaluates new market designs through a variety of production cost simulation and market simulation tools
  Impact analysis studies of new market design alternatives using market simulation tools developed in-house with Unit Commitment, Economic Dispatch, and Pricing capabilities
  Analysis of various alternative pricing schemes for different market products using production and in-house developed market clearing software
  Retrospective market studies using Day-Ahead study system

## Slide 16: Limitations of in-use Economic and Market Simulation Tools
Current production (GE) or in-house developed market simulation tool lack long-term simulation capability
Production cost simulation tools don’t capture real-time operational impact; require significant efforts of benchmarking upon change of market structure
Electric Power Enterprise Control System (EPECS) simulation tool
  Performance
    Input/output data, simulation process control and speed
  Modeling capability
    Storage modeling, transmission constraints, etc.
  Modeling accuracy
    Reflection of ISO-NE market clearing, LMP, settlement, etc.

## Slide 17: Long-Term Economic Studies and Market Simulations
Studies | Purposes of the Study | Type of analysis (models)
Economic Study | Analyze impacts on energy market, or transmission system, or environment, based on different scenarios of future resource mix and transmission expansion options | Production cost simulation
Wind Integration Study | Determine the operational, planning and market impact of integrating substantial wind resources in NE | Mesoscale wind Statistical analysis Production cost simulation
System operational analysis and renewable energy integration study | Investigate the effect of varying generation mix on system imbalance and operating reserves | Market Simulation

## Slide 18: Long-Term Economic Studies and Market Simulations, cont.
Studies | Purposes of the Study | Type of analysis (models)
Fast-start pricing assessment | Assess the market impact of fast-start pricing on both DAM and real-time market; The study implemented fast-start pricing prototype in the real-time market, and performed settlement calculations. | LMP calculation
ESI market mitigation rule design | Design the market mitigation rules for ESI based on simulating different offering strategies for energy options and assessing the corresponding impact on the market | GAMS-based market simulator

## Slide 19: Modeling Challenges for Long-Term Studies
Increasing number of inverter-based resources
  Accuracy of dynamic models, esp. off-shore wind
  Weak grid interconnection (control interaction resonance, protection, etc.)
  Impact of reduced system inertia
Strong and rapid growth of distributed energy resources
  Tripping of DERs for a transmission fault adds to source loss
  Accurate dynamic models and parameters
  Mix of legacy and smart inverters
  Under frequency and under voltage load shedding

## Slide 20: Modeling Challenges for Long-Term Studies, cont.
Transmission and distribution coordination
  Unbalanced transmission faults
  1-ph and 3-ph inverters in distribution system
  May need T&D co-simulation
Multi-timescale market simulation
  Simulation of the market operation process
  Coupling of different markets
  Consistent data set
  Consideration of uncertain parameters
  Computational performance

## Slide 21: New Requirements for Network Models
Bus-branch model
  Eastern Interconnection representation
  All transmission planning studies and operations planning technical studies
  DERs are explicitly modeled at the specific substation, either as negative loads (1-5 MW) or generators (>5MW)
Node-breaker model
  EMS representation (NE, NY, and NB)
  DA and RT network analysis and market clearing, outage coordination, FTR
  Gradually expand the EMS model with sub-transmission network, potentially to model future DER integration

## Slide 22: Shorter-Term ANALYSES and Modeling Processes

## Slide 23: Mid-term Modeling Capabilities
ISO operates mid-term markets and conducts planning studies to address both transmission and resource adequacy in a 3-year time frame
Modeling capabilities include:
  Assessing resource adequacy and reliability impacts of FCM resources
  Evaluating reliability and economic impacts of transmission and generation outages
  Establishing transmission operating limits and guides
See Appendix for additional detail*

## Slide 24: Short-term Modeling Capabilities
ISO prepares for the real-time system and market operation through a variety of planning processes up to 21 days before the operating day
Modeling capabilities include:
  Short-term load forecasting
  Evaluating short-term transmission and generation outages
  Establishing current operating plan (COP)
See Appendix for additional detail*

## Slide 25: Real-time Modeling Capabilities
ISO maintains system balance using various power system monitoring and controls, as well as decision- making tools during real-time system operation
Modeling capabilities include
  Assessing real-time security
  Economically dispatching systems while maintaining system security
See Appendix for additional detail*

## Slide 26: Linking analysis with tools

## Slide 27: List of Analysis Types and Tools
Analysis Types | Tools
Long- term load forecasting | ISO developed tools based on statistics, ANN, etc.
Short-term load forecasting | Simday, ANN, MetrixND
Market Clearing | FCA MCE FTR (FTRO/SFT) DAM (RSC/SPD/SFT) RTM (SPD/SFT) LMPC (LMP Calculator)
Market simulation | Day-ahead Study System (DASS) EPECS Simulator (Dartmouth) GAMS-based market simulator

## Slide 28: List of Analysis Types and Tools, cont.
Analysis Types | Tools
Steady-state power flow analysis | PSS/E, TARA, PowerWorld, PSAT/VSAT EMS PWRFLOW, RTCA, ILC, etc.
Voltage and transient stability | PSS/E, VSAT/TSAT
Small signal analysis | SSAT
Short circuit | ASPEN
On-line cascading failure analysis | POM, TSAT
Electromagnetic transient (EMT) | PSCAD
Production cost simulation | GridView, PROBE
Resource adequacy assessment | GE MARS
AGC simulation | KERMIT

## Slide 29: conclusion

## Slide 30: Current and Future Modeling Needs
Discussion covers the ISO’s current capabilities for modeling and tools addressing various time horizons
If the Future Grid studies would benefit from these capabilities, the ISO offers them to assist in that effort
If there is a gap between the ISO’s modeling processes and tools and those deemed necessary for the Future Grid studies, the ISO will work with stakeholders on the best way to address such gaps

## Slide 32: Appendix

## Slide 33: MID-TERM Modeling and Studies

## Slide 34: Assessing Resource Adequacy and Reliability Impacts of FCM Resources
Determining Tie Benefits and ICR
Determining FCA and ARA parameters
Interconnection analysis during FCM new resource qualification
Reliability reviews of
  permanent or retirement delist bids
  dynamic de-list bids between FCA rounds
  monthly CSO bi-laterals and reconfiguration auction

## Slide 35: Evaluating Reliability and Economic Impacts of Transmission and Generation Outages
Evaluating the reliability impact of long-term (21 days – 2 years) transmission and generation outage request
Evaluating the economic impact of long-term (>90 days) transmission outage request

## Slide 36: Establishing Transmission Operating Limits and Guides
Transmission operations technical studies to identify thermal, voltage and stability limits
  Transmission Operating Guides (TOGs)
System restoration studies to develop and validate restoration plan
Operational studies to determine Load Power Factor (LPF) limits, voltage schedules and limits for generators and key transmission substations, etc.

## Slide 37: Mid-term Reliability Studies
Studies | Purposes of the Study | Type of analysis (models)
Resource Adequacy | Determine Tie Benefits Determine FCA and ARA parameters | Sequential Monte-Carlo simulation
Interconnection analysis during FCM new resource qualification | Ensure that the new generating resource does not cause overloads that cannot be fixed in time for the CCP Assess capacity deliverability within the load zone | Steady-state power flow
FCA dynamic de-list bids reliability review | Reliability study to determine acceptance or rejection of dynamic delist bids between rounds of the FCA | Steady-state power flow
Monthly FCM reliability analysis | Reliability reviews of bi-lateral and Reconfiguration Auction in support of the Monthly FCM process | Steady-state power flow

## Slide 38: Mid-term Reliability Studies, cont.
Studies | Purposes of the Study | Type of analysis (models)
Long-term transmission and generation outage reliability analysis | Evaluates the reliability impact of long-term outage request (> 21 days) per OP-19. | Steady-state power flow Transient stability
Transmission operations technical studies | Identify thermal, voltage and stability limits Transmission Operating Guides (TOGs) | Steady-state power flow Transient stability Short circuit Electromagnetic transient

## Slide 39: Mid-term Reliability Studies, cont.
Studies | Purposes of the Study | Type of analysis (models)
System restoration study | Develop and verify restoration plans after a partial or total shutdown of the New England BES | Steady-state power flow Dynamic stability Electromagnetic transient
System voltage and reactive study | Establish load power factor limits for study areas as defined in OP-17 Develop voltage schedules and limits for generators and key transmission substations | Steady-state power flow Dynamic stability

## Slide 40: Mid-term Economic Studies and Market
Studies | Purposes of the Study | Type of analysis (models)
Forward Capacity Auction | Determine capacity market clearing; Annual/monthly/CASPR | Market clearing
Long-term transmission outage economic analysis | Evaluate economic impact of long-term transmission outages (> 90 days) Reposition transmission outages that exceed an incremental production cost of at least $200,000 per week | Production cost simulation
FTR Auction | Determine FTRs awards and market clearing prices; Annual/ Monthly and BOPP | FTR Market clearing

## Slide 41: SHORT-TERM Modeling and studies

## Slide 42: Short-term Load Forecasting
Forecast hourly system-wide demand for today and the next two days
Forecast capacity deficiency seven days in advance, based on forecasted weather, generating capacity, and peak demand

## Slide 43: Evaluating Short-Term Transmission and Generation Outage
Evaluate the reliability impact of short-term transmission and generation outage request (< 21 days)
Estimate economic impact of short-term transmission outages (1 to 5 days in advance)
21-day energy security assessment forecast per OP-21

## Slide 44: Establishing Current Operating Plan (COP)
Calculate day-ahead 2nd contingency interface limits, which are enforced in Day-Ahead Market
Day-Ahead Market clearing and analysis
Reserve Adequacy Analysis (RAA) to assess system reliability for the operating day

## Slide 45: Short-term Reliability Studies
Studies | Purposes of the Study | Type of analysis (models)
Short-term transmission and generation outage reliability analysis | Evaluates the reliability impact of short-term transmission and generation outage request (< 21 days) per OP-19. | Steady-state power flow Transient stability
Day-Ahead 2nd contingency interface limits | Calculate limits and load shed values for 2nd contingency interfaces. Calculate proxy limits which are enforced in the DAM | Steady-state power flow (TTC Calculator)

## Slide 46: Short-term Reliability Studies, cont.
Studies | Purposes of the Study | Type of analysis (models)
21-day energy security assessment forecast | Forecast 21-day energy security based on current system conditions, forecasted weather, load, generators’ reports of stored-fuel inventories and emissions limitations, and status of fuel delivery systems. | Production cost simulation
Short term load forecasting | Forecast hourly system wide demand for today and the next two days Forecast capacity deficiency seven days in advance | ANN Similar day METRIX

## Slide 47: Short-term Economic Studies and Market
Studies | Purposes of the Study | Type of analysis (models)
Short-term outage economic analysis | Evaluate economic impact of short-term transmission outages (1 to 5 days in advance) | Production cost simulation
Price Analysis | Satisfy FERC’s data inquiry Compute the constraint sensitivities used in LMP calculation | DA Study System
Day-ahead Market clearing | Clear DAM | SCUC SCED CA
Reserve Adequacy Analysis | Assess system reliability for the operating day | SCUC

## Slide 48: REAL-TIME Modeling and studies

## Slide 49: Assessing Real-time Security
Evaluating system conditions using real-time data to assess existing (pre-Contingency) and potential (post-Contingency) operating conditions
  State Estimation, real-time contingency analysis, interface limits, etc.
On-line voltage stability assessment
On-line transient stability assessment
On-line cascading analysis
Resilience – look ahead power grid risk monitoring for extreme events (prototype)

## Slide 50: Economically Dispatching Systems While Maintaining System Security
Intra-day SCRA study to assess system security and needs for intraday unit commitment
Real time unit commitment and economic dispatch
Automatic generation control
Compute real-time LMP and fast-start lost opportunity cost
Analyzing real-time pricing

## Slide 51: Real Time Reliability
Studies | Purposes of the Study | Type of analysis (models)
Real time analysis and assessment | Evaluate system conditions using real-time data to assess existing (pre-Contingency) and potential (post-Contingency) operating conditions | State Estimation RTCA ILC
On-line voltage stability assessment | Compute interface limits based on voltage violation and voltage instability | Steady state power flow P-V analysis
On-line transient stability assessment | Compute interface limits based on angle stability, transient voltage dip, and oscillation damping | Transient stability

## Slide 52: Real Time Reliability, cont.
Studies | Purposes of the Study | Type of analysis (models)
On-line Cascading Analysis | Evaluate system exposure to instability, cascading failure, and uncontrolled separation for more severe than (n-1) conditions | Steady-state power flow Transient stability
Resilience – look ahead power grid risk monitoring for extreme events (Prototype) | Estimate equipment outage probabilities taking into account real-time weather forecast, network equipment loading conditions, network equipment fragility characteristics, and available historical data | Weather model Statistics Facility fragility models

## Slide 53: Real-Time Market
Studies | Purposes of the Study | Type of analysis (models)
Intra-day SCRA | Assess system security and needs for intraday unit commitment | SCED
Real-time unit commitment and dispatch | Determine the commitment of fast-start units; runs every 15 minutes Dispatch resources to satisfy system demand Determine the dispatch points for variable resources (DNE) | SCUC SCED
CTS process | Determine schedules for transactions with NYISO; every 15 min | SCED

## Slide 54: Real-Time Market, cont.
Studies | Purposes of the Study | Type of analysis (models)
RT pricing | Compute real-time LMP and fast-start lost opportunity cost | LMP calculation
LMPC Monitoring and Analysis | Analyze real-time prices | Dispatch and LMP analysis