2019 Economic Study:

Offshore Wind Integration

© ISO New England Inc.

JUNE 30, 2020

ISO-NE PUBLIC

# Table of Contents

Figures	iv

Tables	v

Section 1
Executive Summary	1

Section 2
Background	2

Section 3
Purpose of the 2019 NESCOE Economic Study and Metrics Analyzed	4

Section 4
Scenarios	5

Section 5
Methodology and Assumptions	8

5.1 Modeling Tools and Methodology	8

5.2 Assumptions	8

5.2.1 Parameters for Unconstrained and Constrained Transmission Simulations	9

5.2.2 Interchanges	10

5.2.3 Weather Assumptions	10

5.2.4 Load Assumptions	10

5.2.5 Regulation, Ramping, and Reserve Capability	11

5.2.6 Fuel-Price Assumptions	11

5.2.7 Air Emission Allowance Prices	11

5.2.8 Threshold Prices	12

Section 6
Key Observations	13

6.1.1 Oversupply (Spillage)	13

6.1.2 Systemwide Production Costs	16

6.1.3 Annual Average Locational Marginal Prices	18

6.1.4 Load-Serving Entity Energy Expense and Uplift Costs	19

6.1.5 Congestion by Interface	20

6.1.6 Native New England Resource CO2 Emissions	21

6.1.7 Ancillary Services	22

6.1.8 Marginal Emissions	25

6.1.9 Transmission Interconnection	26

Section 7
Summary	37

# Figures

Figure 4-1: 	US Bureau of Ocean Energy Management lease areas showing the location
of offshore wind sites and interconnection points used for the preliminary results.	7

Figure 5-1: 	Assumed New England system representation for the 2030 study year.	9

Figure 6-1: 	Total amount of spilled resource energy (terawatt-hours; TWh) by scenario studied.	14

Figure 6-2: 	Monthly spilled resource energy (TWh) for the 8000_1 constrained scenario.	15

Figure 6-3: 	Energy production during two low-spill days (MW).	15

Figure 6-4: 	Energy resource production of the two highest spill days.	16

Figure 6-5: 	Energy resource spillage of the two highest spill days.	16

Figure 6-6: 	Systemwide production costs ($ million).	17

Figure 6-7: 	Annual average LMPs by RSP subarea ($/MWh).	19

Figure 6-8: 	Congestion by interface ($ million).	20

Figure 6-9: 	Native New England resource CO2 emissions (millions of short tons).	21

Figure 6-10: 	Native New England resource CO2 emissions (millions of short tons)
by month for the 8000_1 scenarios.	21

Figure 6-11: 	Comparison of select 2016 Economic Study Phase II scenarios
with NESCOE 8,000 MW scenarios.	23

Figure 6-12: 	CO2 emission rates for the two marginal emissions analyses.	26

Figure 6-13: 	Anticipated injection capabilities without major transmission reinforcements.	27

Figure 6-14: 	Likely significant reinforcements for additional injections.	28

Figure 6-15: 	Potential transmission solution for the Cape Cod area.	29

Figure 6-16: 	Potential transmission solution for the Brayton Point area.	30

Figure 6-17: 	Montville area overloads.	31

Figure 6-18: 	Kent County area overloads.	32

Figure 6-19: 	Alternative 345 kV upgrades.	32

Figure 6-20: 	HVDC alternatives into the Mystic and K Street substations.	33

Figure 6-21: 	Conceptual application of offshore cable technology using AC and DC submarine cables.	34

# Tables

Table 4-1 	Offshore Wind Integration Scenarios for the NESCOE 2019 Economic Study	5

Table 4-2 	Interconnection Sensitivities to the 8,000 MW Offshore Wind Additions Scenario (MW)	7

Table 5-1 	Interchange with Neighboring Systems (MW)	10

Table 5-2 	Threshold Prices for the 2019 NESCOE Economic Study ($/MWh)	12

Table 6-1 	Total Systemwide Production by Fuel Type (TWh) for the 8,000 MW Scenarios
Constrained (Cstr.) and Unconstrained (Uncstr.) Transmission	18

Table 6-2 	Load-Serving Entity Energy Expenses and Uplift Costs ($ Million)	19

Table 6-3 	Load-Serving Entity Energy Expenses and Uplift Costs for the Sensitivity Scenarios
($ Million)	20

Table 6-4 	Summary of Ancillary Services Analysis Observations	25

Table 6-5 	Summary of Megawatt Injection Levels (MW) for Offshore Wind by Interconnection Point
and Associated Transmission Infrastructure	35

# Executive Summary

This report documents the Offshore Wind Integration scenarios of the 2019 ISO New England (the ISO or ISO-NE) Economic Study conducted for the ISO’s stakeholders following a request by the New England States Committee on Electricity (NESCOE). The NESCOE 2019 Economic Study examined transmission system and wholesale market impacts associated with the increasing penetration of incremental offshore wind (OSW) resources. The study included offshore wind projects under development at the time of the NESCOE request, including Vineyard Wind (800 megawatts [MW]) and Revolution Wind (200 MW), and considered an additional 7,000 MW of offshore wind strategically placed in southern New England. This study also provided alternatives for transmission system expansion for specific offshore wind interconnection points, but it does not include detailed plans associated with any of the scenarios examined.

Results of the production cost analyses indicate that, for judiciously chosen interconnection points and configurations, high levels of offshore wind in southern New England do not cause significant transmission-interface congestion. When 6,000 MW or less of offshore wind is added to southern New England, less than 2% of renewable energy is spilled. The curtailment of offshore wind resources attributed to oversupply (i.e., spillage) occurs when loads are lower, not from transmission congestion. Offshore wind depresses the use of traditional generating resources and imports, and emissions decrease for the New England control area. In the 8,000 MW scenarios, the system uses as much as 86.1% of available offshore wind energy, and carbon dioxide (CO2) emission rates fall approximately 50%.

Results of the transmission analyses indicate that with the specific interconnection configurations identified in this study and the proximity to major load centers, approximately 5,800 MW of offshore wind can be interconnected to points along the southern shores of Massachusetts, Rhode Island, and Connecticut without significant upgrades to the onshore transmission network. The study identified alternatives that could be considered to bring the interconnected total (above the assumed base of 1,000 MW) to the full additional 7,000 MW requested by NESCOE. Once all the 5,800 MW of “low-hanging-fruit” interconnection capability on the southern shore was used, two alternative approaches to additional offshore wind interconnection were compared. One approach continued to interconnect megawatts to the southern shore points. Significant upgrades to the existing onshore transmission system were required for these injections. The alternative approach considered using high-voltage direct-current (HVDC) submarine cables to travel further distances in the ocean to connect offshore collection stations directly to load centers such as Boston. This approach involved more expensive offshore transmission infrastructure but avoided significant upgrades to the existing onshore grid.

The overall levels of investment in these alternatives appear comparable, and both alternatives should be considered for injections of offshore wind beyond the 5,800 MW of interconnection capability identified on the southern shore. Under each approach, estimates of the overall transmission component could be $1 billion or more for each 1,200 MW addition. However, actual costs are highly dependent on the specific circumstances of each project, especially for the onshore AC expansion, which will be location specific.

# Background

The 2019 NESCOE Economic Study was one of three economic studies submitted to the ISO in 2019. The other two economic study requests were from RENEW and Anbaric, and separate reports will be issued accordingly.

As a part of the regional system planning effort and as specified in Attachment K of its Open-Access Transmission Tariff (OATT), the ISO may conduct economic planning studies each year. The economic studies provide information on system performance, such as estimated production costs, load-serving entity (LSE) energy expenses, transmission congestion, and environmental emission levels. Scenario analyses also inform stakeholders about different future systems. These hypothetical systems should not be regarded as physically realizable interconnection plans or the ISO’s vision of realistic future development, projections, and preferences.

The role of the Planning Advisory Committee (PAC) in the economic study process is to discuss, identify, and otherwise assist the ISO by advising on the proposed studies. For this study, the scope of work and assumptions were driven by stakeholders and the study proponent, NESCOE. Results were discussed during PAC meetings held from April 2019 through June 2020 and summarized in this report. The ISO encourages interested parties to compare the assumptions and results for the different scenarios and to reach their own conclusions about the possible outcomes.

The ISO’s production cost study results for the NESCOE Economic Study for scenarios up to 6,000 MW of offshore wind interconnections were presented to the PAC on December 19, 2019, with a follow-up on January 23, 2020. Production cost results for 8,000 MW of offshore wind interconnections were presented to the PAC on February 20, 2020, with follow-up on April 23, 2020. Both ancillary services and marginal emissions analyses (MEAs) were presented on May 20, 2020. A detailed discussion of transmission interconnection issues for the NESCOE Economic Study was provided to PAC members on April 23, 2020, May 20, 2020, and June 17, 2020.

The report includes hyperlinks throughout to PAC presentations and other materials that contain more detailed information. Some of these links are for materials containing Critical Energy Infrastructure Information (CEII). These links are up to date as of the publication of the report.

# Purpose of the 2019 NESCOE Economic Study
and Metrics Analyzed

In April 2019, NESCOE submitted a request for a scenario analysis on offshore wind integration that would provide information and data on the following topics:

- Scenario analysis

  - Increasing levels of incremental offshore wind resources

- Transmission analysis

  - High-level conceptual transmission overlays

  - Transmission upgrade concepts, alternatives, and trade-offs

  - Various points of  interconnection

- Additional Analysis

  - Ancillary services analysis

  - Emissions effects

The NESCOE 2019 Economic Study requested the ISO to consider the interconnection of as much as 8,000 MW (nameplate) of new offshore wind resources by 2030. The transmission analysis request sought to provide interested stakeholders with information on several transmission configurations available to integrate various levels of additional offshore wind resources, at different points of interconnection into southern New England, and to estimate transmission upgrade costs associated with these conceptual configurations. In addition, NESCOE requested that the study consider wholesale market impacts and power sector air emissions for each scenario studied.

NESCOE sought to provide New England state officials, regulators, stakeholders, and offshore wind developers a range of potential transmission designs to consider, as well as associated market needs. NESCOE considered information in this regard to be informative for developing or implementing state policies aimed at maximizing ratepayer benefits as the New England power grid continues to evolve to incorporate offshore wind.

# Scenarios

The scenarios assumed considerable development of offshore wind resources in varying increments between 1,000 MW to 8,000 MW (nameplate) interconnecting to southern New England. In addition to the 1,000 MW offshore wind projects under contract (Reference Case), the six scenarios were studied and included up to an additional 7,000 MW of offshore wind (nameplate) interconnected by 2030. Table 4-1 summarizes the simulated scenarios for the 2019 NESCOE Economic Study.

Table 4-1
Offshore Wind Integration Scenarios for the NESCOE 2019 Economic Study

| NESCOE Year 2030 Scenarios(a) | Offshore Wind Additions (Nameplate) | RFP-Committed Generation | Retirements | Demand from Heat Pumps | Demand from Electric Vehicles | Battery Storage Additions |
| --- | --- | --- | --- | --- | --- | --- |
| Reference Case | 0 MW | NECEC (1,090 MW of firm import)(b) 1,000 MW of off-shore wind (nameplate)(c) | FCA 13 and Mystic 8 and 9(d) | None | None | None |
| NESCOE_2000 | 1,000 MW |  |  |  |  |  |
| NESCOE_3000 | 2,000 MW |  |  |  |  |  |
| NESCOE_3000 | 3,000 MW |  |  |  |  |  |
| NESCOE_5000 | 4,000 MW |  |  |  |  |  |
| NESCOE_6000 | 5,000 MW |  |  |  |  |  |
| NESCOE_8000 | 7,000 MW |  |  | 2,050 MW | 550,000 vehicles | 2,000 MW |

(a) For all scenarios, the ISO’s 2019 Forecast Report of Capacity, Energy, Loads, and Transmission (CELT Report) (https://www.iso-ne.com/static-assets/documents/2019/04/2019_celt_report.xls) was the source for data on gross demand, energy efficiency (EE), and behind-the-meter photovoltaics (BTM PV) (April 30, 2019), https://www.iso-ne.com/static-assets/documents/2019/04/2019_celt_report.xls. Supply-side resource capacity (for new and existing generation and demand) was based on the results of the thirteenth Forward Capacity Auction (FCA 13) for Capacity Commitment Period 2022-2023; see ISO New England Inc., Docket No. ER19-___-000, FERC filing (February 28, 2019), https://www.iso-ne.com/static-assets/documents/2019/02/fca_13_results_filing.pdf.

(b) NECEC refers to New England Clean Energy Connect.

(c) RFP-commitment offshore wind projects include Vineyard Wind (800 MW) and Revolution Wind (200 MW).

(d) Included in the 2030 resource mix are 452 MW of coal and 5,298 MW of oil-fired resources.

The transmission interconnection assessment considered a total of 8,000 MW of offshore wind, which corresponds to the base 1,000 MW and the incremental 7,000 MW requested by NESCOE. The primary locations of new offshore wind resources were in US Bureau of Ocean Energy Management (BOEM) lease areas, off the shores of Massachusetts and Rhode Island, and in Wind Energy Areas (WEAs) on the Outer Continental Shelf (see Figure 4-1). The ISO contemplated onshore interconnection points for offshore wind based on the results of several interconnection studies conducted for projects in the ISO Interconnection Request Queue. The ISO identified the approximate megawatt quantities that could interconnect without major transmission upgrades. Proposed locations are anticipated to use AC cable connections from the wind farm lease areas to coastal 345 kV substations. Interconnection points include the following locations:

- Cape Cod (Bourne/Barnstable) (MA): 2,400 MW

- Brayton Point (MA): 1,600 MW

- Montville (CT): 800 MW

- Kent County/Davisville (RI): 1,000 MW

In addition, the ISO identified an initial scenario to use HVDC submarine transmission to connect from an offshore collection substation directly to Boston, Massachusetts, specifically, the Mystic substation at 1,200 MW. This scenario assumed the retirement of Mystic 8 and 9 resources.

Figure 4-1: US Bureau of Ocean Energy Management lease areas showing the location of offshore wind sites and interconnection points used for the preliminary results.

For production cost scenarios with 8,000 MW of offshore wind additions, four sensitivities were performed varying the amount of offshore wind additions to the five aforementioned interconnection points, as described in Table 4-2.

Table 4-2
Interconnection Sensitivities to the 8,000 MW Offshore Wind Additions Scenario (MW)

| Sensitivity | Interconnection Points (MW) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | Montville (CT) | Kent County (RI) | Brayton Point (SEMA)(a) | Barnstable (SEMA)(a) | Mystic (Boston) | Total |
| 8000_1 | 800 | 1,000 | 1,600 | 2,400 | 2,200 | 8,000 |
| 8000_2 | 800 | 1,000 | 1,600 | 3,400 | 1,200 | 8,000 |
| 8000_3 | 800 | 1,000 | 2,600 | 2,400 | 1,200 | 8,000 |
| 8000_4 | 1,300 | 1,500 | 1,600 | 2,400 | 1,200 | 8,000 |

(a) SEMA refers to Southeastern Massachusetts.

# Methodology and Assumptions

Study results are driven by assumptions, and some assumptions have a greater impact on the study results than others (i.e., threshold prices for various resource types). To gain efficiencies, the assumptions for all three economic studies submitted in 2019 were determined in concert. At the May 21, 2019, and August 8, 2019, PAC meetings, the ISO reviewed in detail the assumptions associated with the 2019 NESCOE Economic Study. A status update was given on November 20, 2019. This section highlights the importance of certain assumptions and how modeling was performed for the 2019 NESCOE Economic Study.

## Modeling Tools and Methodology

The analyses were conducted using ABB’s GridView economic-dispatch program. The program is a complex simulation tool that calculates least-cost transmission-security-constrained unit commitment and economic dispatch under differing sets of assumptions and minimizes production costs for a given set of unit characteristics. The program explicitly models a full network, and New England was modeled as a constrained single area for unit commitment.

The as-planned transmission system was used for estimating the system’s transfer limits for internal and external interfaces. The 2030 transfer capabilities for internal and external transmission interfaces were based on the values established for 2025 for Forward Capacity Market (FCM) and regional planning studies. Regional resources were economically dispatched in the simulations to respect the assumed “normal” transmission system transfer limits.

## Assumptions

This section summarizes the assumptions made for the following parameters:

- Unconstrained and constrained transmission

- Interchanges with neighboring systems

- Weather

- Load levels

- Regulation, ramping, and reserve capability

- Fuel prices

- Air-emission allowances

- Resource threshold prices ($/MWh)

### Parameters for Unconstrained and Constrained Transmission Simulations

Production costs were simulated under unconstrained and constrained conditions. Under unconstrained transmission, the New England transmission system was modeled as a single-bus system. Under constrained transmission scenarios, the system was modeled using the “pipe” and Regional System Plan (RSP) “bubble” configuration, with “pipes” representing transmission interfaces that connect the “bubbles,” which represent the various planning areas. See Figure 5-1.

Figure 5-1: Assumed New England system representation for the 2030 study year.(a)

Notes: BHE = Northeastern Maine; CMA/NEMA = Central Massachusetts/Northeast Massachusetts; CSC = Cross-Sound Cable; CT = Connecticut; NB = New Brunswick, Canada; NE = New England; NH = New Hampshire; NOR = Norwalk; NY = New York; SEMA/RI = Southeast Massachusetts/Rhode Island; SME = Southern Maine; Southeast Massachusetts; SWCT = Southwest Massachusetts; OSW = offshore wind; VT = Vermont; WMA = Western Massachusetts. Refer to the System Planning Subareas map at this ISO link: https://www.iso-ne.com/about/key-stats/maps-and-diagrams/. (a) Ratings are a function of unit availabilities, area loads, or both. (b) The Surowiec-South Interface limit is 2,500 MW per NESCOE’s request.

### Interchanges

Table 5-1 shows the assumed 2030 external interchanges with neighboring systems, including the new tie from Québec (i.e., the New England Clean Energy Exchange; NECEC). The same interface capabilities were assumed for all scenarios. Based on the historical profiles, the maximum energy-import values reflected FCM capacity imports and other energy imports, but they never exceeded the import-transfer capability of the ties.

Table 5-1
Interchange with Neighboring Systems (MW)

| Interconnection | Import Capability (MW) | Interchange Modeling |
| --- | --- | --- |
| HIghgate | 217(a) | Historical diurnal profile averaged over 2016 through 2018 |
| Hydro-Québec (HQ) Phase II | 2,000(a) | Historical diurnal profile averaged over 2016 through 2018 |
| HQ-NECEC | 1,200 | Assumed firm energy delivery of 1,090 MW across all hours |
| New Brunswick | 1,000(a) | Historical diurnal profile averaged over 2016 through 2018 |
| New York AC | 1,400(a) | Assume no interchange(b) |
| CSC | 330(a) | Assume no interchange(b) |

(a) These values represent import capability for energy

(b) Assuming no interchange allows a straight comparison of the regional production cost across all scenarios.

### Weather Assumptions

The Reference Case and production cost scenarios (up to 6,000 MW), reported in the December 19, 2019, PAC presentation, used 2006 weather to align wind, solar, and load profiles (scaled to 2030). These profiles were similar to those used in the 2016 Economic Studies. In the January 2020 timeframe, new profiles were available. Therefore, for the 8,000 MW scenarios, 2015 wind, solar, and load profiles (scaled to 2030) were used. The use of different weather-year profiles can result in different magnitudes for the study metrics, but broad results would be similar.

### Load Assumptions

Energy storage (i.e., pumped storage and batteries) are used to levelize the load net of dispatchable resources. Across all scenarios, existing pumped-storage units were dispatched to equalize the daily high and low net loads after accounting for all energy efficiency, active demand resources, all photovoltaic (behind-the-meter [BTM] and non-BTM), plug-in hybrid electric vehicles (PHEVs), wind energy, hydro (excluding pumped storage), existing imports, and new imports. This treatment of pumped storage was assumed to have approximately 74% efficiency. Battery storage was assumed to have approximately 90% efficiency and was spread nearly equally around each RSP bubble. The batteries were assumed to have enough storage to discharge at full output for four hours.

### Regulation, Ramping, and Reserve Capability

To address market challenges, including load following, regulation, operating reserves, and operation during low-load periods for the 2019 NESCOE Economic Study, the ISO used the same study approach as the 2016 Economic Study Phase II Study, Dartmouth College’s Electric Power Enterprise Control System (EPECS) simulation tool. EPECS augments the GridView model, which uses one-hour time-step increments, by using a one-minute time increment to provide an integrated platform for assessing simulated operating reserves, interface and tie-line performance, and regulation performance. Leveraging the results of Phase II of the 2016 Economic Study, the ISO was able to analyze the use of regulation, ramping, and reserves capability needed to maintain the supply/demand balance of the New England bulk electric power system.

### Fuel-Price Assumptions

The assumed fuel prices for coal, oil, and natural gas were based on forecasts from the US Department of Energy (DOE), Energy Information Administration (EIA) 2019 Annual Energy Outlook (AEO) for New England.

### Air Emission Allowance Prices

The study used the following allowance-price assumptions for 2030 for nitrogen oxide (NOX), sulfur dioxide (SO2), and carbon dioxide (CO2) air emissions, which affect the economic dispatch price for fossil-burning generation units:

- Nitrogen oxides: $6.18/short ton

- Sulfur dioxide: $6.18/short ton

- Carbon dioxide: $24.00/short ton

These prices are consistent with those used for the 2017 Economic Study. To check compliance with the Massachusetts Global Warming Solutions Act (GWSA), CO2 emissions from affected fossil fuel generators located in Massachusetts were compared to allowable limits.

### Threshold Prices

Threshold prices were assigned to certain resource types in this study, including photovoltaics (PV), onshore wind, and offshore wind, to facilitate the analysis of load levels where the amount of $0/megawatt-hour (MWh) resources exceeded the system load, which leads to oversupply. The threshold prices govern which type of resources to back down first to balance supply and demand and inform the model about which resources’ output to reduce—or spill. Threshold prices are not indicative of “true” cost, expected bidding behavior, or the preference for one type of resource over another. The 2019 NESCOE Economic Study used similar threshold prices as in prior economic studies (2016 and 2017), with two adjustments:

- The behind-the-meter PV and utility-scale PV (FCM and energy only) were differentiated.

- A preferential threshold price was applied to energy from the newly proposed NECEC tie because of publicly available contract terms.

The use of different threshold prices other than indicated in Table 5-2 may produce different outcomes.

Table 5-2
Threshold Prices for the 2019 NESCOE Economic Study ($/MWh)

| Price-Taking Resource | Threshold Price ($/MWh) |
| --- | --- |
| Behind-the-meter PV | 1 |
| NECEC (1,090 MW) | 2 |
| Utility-scale PV | 3 |
| Onshore/offshore wind | 4 |
| New England hydro | 4.5 |
| Imports from HQ (Highgate and Phase II) | 5 |
| Imports from NB | 10 |

# Key Observations

The study considered existing offshore wind projects under development, including Vineyard Wind (800 MW) and Revolution Wind (200 MW), and an additional 7,000 MW of offshore wind strategically placed in southern New England. A Reference Case with no new offshore wind additions was added to facilitate meaningful comparisons between the other scenarios and today’s system.

The most relevant production cost, ancillary services, marginal emissions, and transmission interconnection results are included in this report. All offshore integration scenarios produced similar results, directionally, regardless of how much offshore wind was interconnected. Together, the results of the study included several scenarios and four sensitives that provide useful information, as follows, when considered as a whole:

- The degree of resource development capable of achieving carbon-reduction goals;

- The significant potential for spilling offshore wind energy

- Directionally relevant cost estimates and revenue impacts

This report highlights the results of the 8,000 MW scenario and four sensitivities because these are the most insightful.

### Oversupply (Spillage)

“Spilled” energy occurs when resource production exceeds the system’s ability to use the power, whether to protect transmission security or due to the lack of demand for the power when produced. The large-scale development of remote resources, such as offshore wind or onshore wind in northern Maine, may require transmission additions to avoid transmission-related spillage. Conversely, the development of resources near load centers in southern New England generally avoids transmission-related spillage of renewable energy and diminishes the need for transmission development to avoid congestion. The 2019 NESCOE Economic Study confirmed that well-placed offshore wind, interconnecting to certain substations in southern New England, resulted in minimal transmission-related spillage.

The spillage of renewable resources, such as offshore wind, has economic impacts and can undermine state initiatives to reduce the carbon footprint of New England. Spilled energy reduces a resource’s energy market revenues and correspondingly increases the amount a resource must recover through other wholesale electricity markets and state-jurisdictional mechanisms.

The NESCOE 2019 Economic Study results revealed that spillage is similar, regardless of the interconnection points in southern New England, due to the lack of congestion. The rate of spillage increases as offshore wind buildout increases. Most spillage is attributed to oversupply when loads are lower, not to transmission congestion. Generally, the spillage results across the 0 MW (Reference Case) to the 6,000 MW of offshore wind scenarios can be considered insignificant (less than 2.16% of renewable energy), and in the 8,000 MW cases, offshore wind replaces existing resources and imports. Figure 6-1 highlights the spillage for all scenarios studied.

Figure 6-1: Total amount of spilled resource energy (terawatt-hours; TWh) by scenario studied.

In the 8000_1 constrained scenario, 15.17 TWh of spillage (of imports, hydro, wind, and solar) occurs annually, which is similar to the other 8,000 MW offshore wind scenarios. However, spillage varies significantly by month from 0.15 to 2.69 TWh, as depicted in Figure 6-2, due to the interaction of wind, solar, and load profiles.

Figure 6-2: Monthly spilled resource energy (TWh) for the 8000_1 constrained scenario.

The least amount of spillage in the 8000_1 constrained scenario occurred in the summer months of July and August when demand is generally high. Examining these months more closely and analyzing the two lowest spill days of July 27 and July 28 shows essentially no spillage because energy production from all resources is needed to meet demand. See Figure 6-3.

Figure 6-3: Energy production during two low-spill days (MW).

The most spillage in the 8000_1 constrained scenario occurred in April. Looking more closely at the April results and the two high-spill days shows that wind production was sizable, supporting the premise that spillage is due to oversupply at times of lower loads. See Figure 6-4 and Figure 6-5.

Figure 6-4: Energy resource production of the two highest spill days.

Figure 6-5: Energy resource spillage of the two highest spill days.

### Systemwide Production Costs

Production costs reflect operating costs (which account for fuel-related costs), dispatch and unit commitment, and emission allowances. Natural gas consumption, and to a lesser extent other fossil fuels, drive production costs. The amount of resources assumed for each scenario is adequate to meet the systemwide energy requirements without significant transmission upgrades.

In general, as offshore wind energy increases across the scenarios, natural-gas-fired generation decreases and production costs decrease, as shown in Figure 6-6. In the 8,000 MW scenarios, offshore wind displaces other zero-cost resources instead of thermal-emitting resources, resulting in lower incremental savings. Oil-fired generation is not committed in these scenarios; however, a very small amount coal-fired generation (i.e., approximately 0.07 TWh in the 8000_1 constrained scenario) is committed (primarily in the winter months of December, January, and February) in all scenarios. Production costs are slightly lower in unconstrained cases because they use more zero-cost energy north of the Maine-New Hampshire interface.

Figure 6-6: Systemwide production costs ($ million).

Focusing on the 8,000 MW scenarios, Table 6-1 shows the system production costs by fuel type for the unconstrained and the constrained system for the 2030 study year. The small production cost differences among the scenarios can be attributed to wind capacity factors of various portions of the BOEM lease area.

Table 6-1
Total Systemwide Production by Fuel Type (TWh) for the 8,000 MW Scenarios
Constrained (Cstr.) and Unconstrained (Uncstr.) Transmission

| Scenario | 8000_1 |  | 8000_2 |  | 8000_3 |  | 8000_4 |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Fuel Type | Cstr. | Uncstr. | Cstr. | Uncstr. | Cstr. | Uncstr. | Cstr. | Uncstr. |
| Offshore wind | 27.60 | 27.61 | 27.55 | 27.56 | 27.26 | 27.27 | 27.61 | 27.62 |
| Onshore wind | 3.79 | 3.79 | 3.77 | 3.77 | 3.78 | 3.77 | 3.78 | 3.78 |
| Natural gas | 16.63 | 16.64 | 16.67 | 16.67 | 16.77 | 16.77 | 16.55 | 16.54 |
| Oil | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 |
| Imports | 19.39 | 19.40 | 19.41 | 19.41 | 19.54 | 19.55 | 19.43 | 19.45 |
| Coal | 0.07 | 0.03 | 0.05 | 0.04 | 0.05 | 0.03 | 0.06 | 0.04 |
| Landfill gas/ municipal solid waste | 2.69 | 2.69 | 2.69 | 2.69 | 2.70 | 2.70 | 2.69 | 2.69 |
| Photovoltaics | 9.47 | 9.47 | 9.47 | 9.47 | 9.47 | 9.47 | 9.47 | 9.47 |
| Wood | 4.70 | 4.70 | 4.70 | 4.70 | 4.70 | 4.70 | 4.70 | 4.69 |
| Nuclear | 29.85 | 29.85 | 29.85 | 29.85 | 29.85 | 29.85 | 29.85 | 29.85 |
| Energy efficiency/ demand response | 36.09 | 36.09 | 36.09 | 36.09 | 36.09 | 36.09 | 36.09 | 36.09 |
| Hydro | 6.26 | 6.27 | 6.27 | 6.28 | 6.33 | 6.33 | 6.29 | 6.30 |

### Annual Average Locational Marginal Prices

The impact of additional offshore wind was observed in the NESCOE 2019 Economic Study through evaluating average locational marginal prices (LMPs) for selected RSP subareas, under constrained and unconstrained scenarios of the 2030 study year. The scenarios analyzed for the unconstrained cases show lower average systemwide LMPs because price-taking resources produce greater amounts of energy, especially when they displace less-efficient fossil fuel generating resources. When transmission flows are constrained, the LMP at the receiving end is higher than at the sending end. Price separation at the Maine-New Hampshire interface decreases as offshore wind production supplants the demand for onshore wind resources in Maine. For example, price separation across the Maine-New Hampshire interface was caused by periodic oversupply of wind energy in Maine. Then, as installed offshore wind production levels increased, periodic oversupply of offshore wind equalized the threshold-based prices on either side of the interface more often. This resulted in a lower annual value for the price-separation metric. As illustrated in Figure 6-7, the reference scenario has the largest price separation between BHE/ME/SME and the rest of the system. The separation decreases as offshore wind is added, which lowers the LMPs outside Maine.

Figure 6-7: Annual average LMPs by RSP subarea ($/MWh).

### Load-Serving Entity Energy Expense and Uplift Costs

Load-serving entities (LSEs) represent organizations that directly serve retail electricity customers. Risk management is particularity important to LSEs because they are sensitive to and may not be able to hedge against sudden or unexpected price variations, which could affect their customers. Table 6-2 shows load-serving entity energy expenses (LSEEE) and “uplift” costs (i.e., make-whole payments) for all constrained and unconstrained cases.

Table 6-2
Load-Serving Entity Energy Expenses and Uplift Costs ($ Million)

| Transmission | Type | Scenario |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | 0000 | 1000 | 2000 | 3000 | 5000 | 6000 | 8000_1 | 8000_2 | 8000_3 | 8000_4 |
| Constrained | LSE energy expense | 5,972 | 5,654 | 5,178 | 4,715 | 3,848 | 3,762 | 3,147 | 3,160 | 3,188 | 3,152 |
|  | Uplift | 189 | 201 | 225 | 252 | 302 | 311 | 351 | 348 | 346 | 347 |
|  | Total | 6,161 | 5,855 | 5,403 | 4,967 | 4,150 | 4,073 | 3,498 | 3,508 | 3,534 | 3,499 |
| Unconstrained | LSE energy expense | 6,016 | 5,672 | 5,185 | 4,727 | 3,858 | 3,766 | 3,156 | 3,162 | 3,197 | 3,159 |
|  | Uplift | 173 | 193 | 220 | 248 | 298 | 307 | 347 | 346 | 342 | 343 |
|  | Total | 6,189 | 5,865 | 5,405 | 4,975 | 4,157 | 4,073 | 3,504 | 3,507 | 3,538 | 3,502 |

While uplift costs increase somewhat across the scenarios, the net of LSEEE and uplift costs decreases by more than 50% between the 0 MW and 8,000 MW offshore wind scenarios. Table 6-3 highlights the LSE energy expenses and uplift costs for the four sensitivities of the 8,000 MW scenario because these scenarios have the least LSEEE and greatest uplift costs and illustrate again that varying the amount of offshore wind additions among the five aforementioned interconnection points in southern New England has little effect on costs.

Table 6-3
Load-Serving Entity Energy Expenses and Uplift Costs for the Sensitivity Scenarios ($ Million)

| Transmission | Type | Scenarios |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  |  | 8000_1 | 8000_2 | 8000_3 | 8000_4 |
| Constrained | LSE energy expense | 3,147 | 3,160 | 3,188 | 3,152 |
|  | Uplift | 351 | 348 | 346 | 347 |
|  | Total | 3,498 | 3,508 | 3,534 | 3,499 |
| Unconstrained | LSE energy expense | 3,156 | 3,162 | 3,197 | 3,159 |
|  | Uplift | 347 | 346 | 342 | 343 |
|  | Total | 3,504 | 3,507 | 3,538 | 3,502 |

### Congestion by Interface

Locating new resources with relatively low production costs (i.e., offshore wind) near load centers in southern New England reduces systemwide congestion and the need for transmission expansion compared with scenarios that add remote resources without transmission improvements, such as the development of renewable resources and imports in northern New England. All offshore wind interconnections for the 2019 NESCOE Economic Study were in southern New England and did not cause significant interface congestion when evaluated with the pipe and bubble methodology (refer to Section 5.2.1). Though minimal, congestion varies as the amount of offshore wind production increases and the demand for constrained resources declines. As illustrated in Figure 6-8, congestion in the 8,000 MW scenarios is vastly less than in the 0 MW offshore wind scenarios, and the ME-NH interface becomes the binding interface once the Surowiec-South transfer limit is increased to 2,500 MW.

Figure 6-8: Congestion by interface ($ million).

### Native New England Resource CO2 Emissions

The results for the metrics that assessed the environmental impacts associated with the different scenarios provide some insight on future emission trends. The total CO2 emissions associated with the different scenarios are directly associated with the type and amount of fossil fuels the different scenarios use to generate electricity. For the NESCOE 2019 Economic Study, carbon emissions are similar across the 8,000 MW offshore wind scenarios but are reduced by approximately one-third from the 0 MW (Reference Case) scenario for native New England resources in the 2030 study year, as shown in Figure 6-9.

Figure 6-9: Native New England resource CO2 emissions (millions of short tons).

Looking closely at the 8000_1 scenario in Figure 6-10, CO2 emissions are highest when loads are high and wind and solar production is low. Results are similar for the other 8,000 MW offshore wind scenarios.

Figure 6-10: Native New England resource CO2 emissions (millions of short tons) by month for the 8000_1 scenarios.

### Ancillary Services

Without sufficient ancillary services, the electrical grid can be become unstable and potentially experience extreme consequences, such as brownouts and blackouts. Ancillary services primarily focus on the ability of the electrical grid to maintain the constant balance between equally sized supply and demand for electricity needed for grid stability. As part of its 2019 economic-study request, NESCOE asked the ISO to identify possible new grid opportunities as market needs change to address challenges, including the ancillary services of load following, regulation, operating reserves, and operation during low-load periods. This ancillary services analysis deals with the many physical qualities of the grid that must be kept in balance for the grid to remain stable.

The ISO used the Dartmouth Electric Power Enterprise Control System (EPECS) simulation tool to explore NESCOE’s request. Leveraging the results of the 2016 Economic Study Phase II Study (see Section 5.2), the ISO was able to analyze the use of regulation, ramping, and reserves capability needed to maintain the supply/demand balance of the New England bulk electric power system. While the ISO sought to simulate the NESCOE scenarios in more detail, timeframe limitations precluded this analysis.

#### Reserve Requirements

The ISO currently maintains the supply/demand balance through reserve requirements. These requirements specify that at least a certain amount of additional supply resources must be either on line (10-minute spinning reserve; TMSR) or ready to synchronize within 30 minutes (30-minute operating reserve; TMOR) to compensate for the unexpected loss of other supply resources.

With an increased amount of variable resources, like offshore wind, an increase in reserve requirements could be required to maintain system stability in the 2030 system. This analysis finds that the ISO’s current TMSR requirement, which is equal to the size of the system’s largest on-line resource (typically a nuclear resource), is insufficient for the System Operational Analysis and Renewable Energy Integration Study (SOARES) 2030-3 scenario (see Section 5.2.5), which had a high amount of renewables. Although of different renewable types, the overall quantity of renewables in the SOARES 2030-3 scenario is equivalent to those in the NESCOE 8,000 MW scenarios, as seen in Figure 6-11.

Figure 6-11: Comparison of select 2016 Economic Study Phase II scenarios with NESCOE 8,000 MW scenarios.

However, the EPECS analysis also finds that increasing the resource requirement has a nonlinear relationship with decreasing the amount of time that the system supply and demand are not in balance. Therefore, increasing TMSR requirements under the ISO’s current operations structure will not necessarily improve system performance or increase reliability. More analysis is needed to determine the relationship between increased system operational requirements and increased reliability.

#### Ramping, Load-Following, and Regulation Reserve

This study also finds that ramping reserves and load-following reserves (LFRs) have a more significant impact on lowering system imbalances than TMSR. Ramping reserve is a physical quantity that measures the ability of current on-line supply resources to ramp their output up or down from current levels in response to anticipated system needs (in addition to whatever increase or decrease the resource may be scheduled for). Load-following reserve is the amount of upward or downward change in output that a resource could move to from its current output. Ramping reserve and load-following reserves are not ISO requirements but physical quantities that EPECS can track and quantify. In other words, ramping reserve is how quickly system resources can move their output up or down in a given period, generally 10 minutes, while load-following reserve is the total amount units can move up or down.

In historical system operations, load following and ramping reserves are a byproduct of system commitment and dispatch to meet system demand and TMSR requirements. However, with high renewables, the previously direct relationship between a resource’s ability to supply megawatts to meet demand and its ability to fluctuate its output as demanded for system stability becomes less direct. This is because renewable resources are generally not controllable like thermal resources, and they are dispatched at maximum output at all times.

Therefore, in a high-renewable system, monitoring load following and ramping reserves becomes of interest. This analysis finds that the SOARES 2030-3 scenario has insufficient load following “up” and ramping reserves in both directions, the directions referring to whether the resource fleet must move from its current output point up or down to its maximum or minimum output levels.

The EPECS model uses instantaneous and infinite curtailment (i.e., spillage) of renewables, hydro, and imports to balance the system during times of oversupply. This severe restriction of resources acts as a type of load following “down” reserve—instead of thermal supply resources needing to ramp down to compensate for renewable variability, the EPECS dispatch lessens or removes variability. If public policy or system operations finds that this level of spillage is not feasible, load following “down” reserves may also be insufficient.

This analysis also finds that forecast error in “day-ahead” commitment and other dispatch steps that occur before real time have an increasing impact as the amount of renewables increases. In short, given a fixed value of forecast error (e.g., 7%), if total wind resources increase from 1,000 MW to 10,000 MW, the resulting magnitude (in megawatts) from the error significantly increases. If the forecast error of solar, wind, and load move in opposite directions, the resultant imbalance can be significant. This variation can be mitigated somewhat through the commitment of fast-start units that can come on line within 30 minutes. In the high-renewables scenarios, three additional fast-start units committed at approximately 45 MW were committed every hour throughout the year compared with the scenarios with limited renewables.

With the constant potential for imbalances, real-time resources increase their ability to fluctuate their output in response to variability in the second-to-second timeframe, which is called regulation reserves. Specific thermal generators committed for this purpose, batteries, flywheels, or other technologies can supply regulation reserves. This analysis has +/- 122 MW of regulation reserves. In the SOARES 2030-3 scenario, the 122 MW of regulation reserve was completely exhausted by system requirements in 33% of the 2030 study year.

#### Summary of Ancillary Services

In sum, the ancillary services analysis indicated that additional amounts of reserves are needed to support approximately 8,000 MW of additional renewable resources as modeled in the 2030-3 scenario. While the 2030-3 scenario shows the need for regulation, ramping, LFR, and TMSR reserves, the 2030-6 scenario only shows the need for more regulation and TMSR reserves. This implies some of the lesser NESCOE offshore wind megawatt scenarios will not need significant increases in reserves.

Notably, the current EPECS model and ISO system operations rely primarily on thermal resources to provide most reserves (the exception being LFR down, which is provided via curtailment). If instead renewables are able to provide reserves via inverter control and flexible curtailment, the results of this analysis would change.

Further study is needed to identify the exact megawatt amount of reserves. Given that the current relationship between increased TMSR and decreased imbalances in nonlinear, specifying a required megawatt amount is not possible. Rather, further study will evaluate alternate reserve products that have a monotonic (i.e., linear) relationship between the reserve product and system imbalances. Ramping reserves and load-following reserves have a monotonic relationship with imbalances, and further study could explore acquiring reserves to meet these reserve requirements instead of just tracking them as physical quantities. Table 6-4 summarizes the results of this study.

Table 6-4
Summary of Ancillary Services Analysis Observations

| Type of Ancillary Service | Description | Current Market Product | Results |
| --- | --- | --- | --- |
| Regulation | The capability of specially equipped generators to increase or decrease their generation output every four seconds in response to signals they receive from the ISO to balance supply levels with the second-to-second variations in demand | Automatic generator control (AGC)/ Regulation Market | Regulation reserves with a 244 MW range (up 122 MW to down 122 MW) are exhausted 33% of the time. Regulation usage increases significantly in high-renewable scenarios. Further study can iterate different regulation amounts to find needed amounts and system dispatch to relieve regulation. |
| Load-following reserves | The quantity of load-following reserves is equal to the capacity of the aggregate generation fleet to move up or down (i.e., economic surplus). | No current product | A shortage of upward LFR occurred 24% of the year, reflecting constrained upward dispatch. These occur primarily during low net-load conditions in the spring and autumn. Downward LFR reserves were sufficient in all 2016 Phase II scenarios. The curtailment of semidispatchable (profiled) resources functions as a kind of downward LFR. |
| Ramping reserves | The rate of capacity change available (as a function of unit commitment and dispatch) to correct the anticipated imbalance in the next real-time market time step | No current product | Upward ramping reserves are insufficient up to 15% of the year in the 2030-3 scenario; downward ramping reserves are only insufficient 2% of the year. |
| Operating reserves | Unloaded capacity of generating resources—either on line or off line—that can deliver electric energy within 10 or 30 minutes to respond to contingencies, such as those caused by unexpected outages (i.e., a large generator goes off line). Ten-minute reserves must be synchronized with the grid; 30-minute resources must be able to energize and synchronize with the grid within 30 minutes. | 10-minute spinning and 30-minute operating reserves | TMSR shows significant exhaustion in the 2030-3 and 2030-6 scenarios. TMOR does not show exhaustion in the high-renewable scenarios. While TMOR can serve other needs, being available within 30 minutes does not assist with the moment-to-moment variation in variable-resource output. The relationship of TMSR and TMOR to imbalances are nonlinear because the requirement is an inequality (i.e., greater than or equal to a given value must be acquired). |

### Marginal Emissions

During the December 2019 discussions of the preliminary results of the NESCOE 2019 Economic Study, the ISO presented information on marginal emissions. Although not part of the original scope of work, the ISO performed marginal emissions analyses to determine the percentage of time various resource types would be marginal and how their distribution might change under scenarios with high renewables. Information about physical location (i.e., load zones) of marginal units and the period when units are marginal could not be determined with this analysis.

The ISO developed two complementary analyses using outputs from the GridView model. These analyses vary from the annual marginal emissions analyses (MEAs) the ISO develops in how they determine the marginal resource; however, using the GridView model allowed future scenarios not available via the MEA method to be analyzed. The two approaches were as follows:

- Approach 1 compared the results of two scenarios with different amounts of wind and calculated the change in the annual emissions per additional megawatt-hour of offshore wind.

- Approach 2 inferred the marginal native New England generation in GridView simulations.

The results from both approaches, as shown on Figure 6-12, are that marginal CO2 emission rates decrease approximately 50% as the system dispatches fewer carbon-emitting resources.

Figure 6-12: CO2 emission rates for the two marginal emissions analyses.

Note: * Estimates of this metric cannot be calculated from the annual simulations due to increased amounts of heat pumps and offshore wind energy.

### Transmission Interconnection

For the NESCOE 2019 Economic Study, the ISO developed future interconnection scenarios for offshore wind. The ISO focused on the interconnection points identified by offshore wind interconnection customers with interconnection requests in the ISO queue. Using the results and observations from several of the interconnection studies associated with these requests, the ISO identified the approximate megawatt quantities of inverter-based resources (e.g., offshore wind) that could interconnect without major transmission upgrades beyond these local points. The ISO then sought to identify the upgrades that would be needed to continue to increase the interconnection levels beyond the initial “base scenario” amounts of the following:

- Cape Cod (Bourne/Canal/Pilgrim) (MA): 2,400 MW

- Brayton Point (MA): 1,600 MW

- Montville (CT): 800 MW

- Kent County/Davisville (RI): 1,000 MW

- Mystic (MA): 1,200 MW

In a significant finding, the ISO determined that with the expected transmission topology for the 2030 study year, approximately 7,000 MW of new offshore wind (5,800 MW connected to the southern shore substations and 1,200 MW connected to Mystic) has the potential to be interconnected without major additional 345 kV reinforcements, as illustrated in Figure 6-13.

Figure 6-13: Anticipated injection capabilities without major transmission reinforcements.

Note: Assumes FCA 13 retirements have occurred, including the retirement of Mystic 8 and 9.

The ISO studied each of the five coastal injection locations to determine potential transmission reinforcements. Some 345 kV reinforcement or expansion may still be needed for this interconnection configuration, and the ISO does not anticipate that all offshore wind projects will be able to run simultaneously at nameplate levels at all times on the system. Additional offshore wind megawatt injections, at the interconnection points on the southern shore above the levels shown in Figure 6-13, would require significant transmission reinforcements, as represented conceptually in Figure 6-14.

Figure 6-14: Likely significant reinforcements for additional injections.

Exploring each of the four southern coastal injection locations further to determine whether additional megawatts of offshore wind could be added above the base scenario amounts revealed that significant upgrades to the onshore New England transmission system would be needed for these additional injections. The transmission reinforcements needed to interconnect the additional megawatts above the base scenario may be difficult to site and expensive to build.

#### Cape Cod Area

Screening analysis of the addition of 3,200 MW (i.e., 800 MW more than the 2,400 MW indicated in the base scenario) to the Cape Cod area identified the following limitations with the existing transmission system:

- Thermal limitations, particularly the Stoughton K Street 345 kV cables

- Significant exposure to problematic loss-of-right-of-way extreme contingencies

- Expected manifestation of very low short-circuit ratios (relatively low system strength), indicating weak grid conditions, as unstable behavior of the wind farms

- Stability issues, such as undamped oscillations and degraded bulk power system behavior, as defined by Northeast Power Coordinating Council (NPCC) criteria

The nature of the limitations found in the 3,200 MW case indicate that 2,400 MW of injection appears to represent a “hard ceiling” of the amount that can readily be interconnected to the Cape Cod area. Not only would new transmission be needed to address both the weak grid issues and the thermal issues on the Stoughton to K Street 345 kV lines, it would need to be in its own right of way to avoid an unacceptable exposure to the loss of supply (i.e., the loss of up to 3,200 MW of connected offshore wind) for the loss of the right of way. See Figure 6-15.

Figure 6-15: Potential transmission solution for the Cape Cod area.

#### Brayton Point Area

Screening analysis of the addition of 2,400 MW (i.e., 800 MW more than the 1,600 MW indicated in the base scenario) to the Brayton Point area identified the following limitations with the existing transmission system:

- Numerous N-1 and N-1-1 thermal violations in the areas surrounding Brayton Point and Grand Army substations

- Introduction of significant exposure to problematic loss-of-right-of-way extreme contingencies

- Expected manifestation of very low short-circuit ratios (relatively low system strength), indicating weak grid conditions, as unstable behavior of the wind farms

The nature of the limitations found in the 2,400 MW case indicated several problems that proved very difficult to address effectively with new transmission upgrades. New 345 kV connections from Brayton Point to Millbury, West Medway, or West Walpole substations introduced or exacerbated thermal overloads along these 345 kV sections and on the Stoughton to K Street 345 kV lines. High density of existing circuits makes it more difficult to find separate rights of way. A potential solution that the ISO considered would be a new 345 kV circuit from Brayton Point to K Street or Mystic substation (if already adding injection at the K Street substation). See Figure 6-16.

Figure 6-16: Potential transmission solution for the Brayton Point area.

#### Montville Area

Screening analysis of the addition of 1,600 MW (i.e., 800 MW more than the 800 MW indicated in the base scenario) to the Montville area identified the following limitations with the existing transmission system:

- Numerous N-1 and N-1-1 thermal violations in the areas surrounding the Montville substation

- Expected manifestation of very low short-circuit ratios (relatively low system strength), indicating weak grid conditions, as unstable behavior of the wind farms

The ISO evaluated the addition of a new 345 kV line between Kent County and Montville substations. System performance was poor with the new line and several overloads occurred on existing facilities after adding more offshore wind at Montville. See Figure 6-17.

Figure 6-17: Montville area overloads.

#### Kent County/Davisville Area

Screening analysis of the addition of 1,800 MW (i.e., 800 MW more than the 1,000 MW indicated in the base scenario) to the Kent County area identified the following limitations with the existing transmission system:

- Numerous N-1 and N-1-1 thermal violations in the areas surrounding the Kent County substation

- Introduction of significant exposure to problematic loss-of-right-of-way extreme contingencies

- Expected manifestation of very low short-circuit ratios (relatively low system strength), indicating weak grid conditions, as unstable behavior of the wind farms

To resolve the overloads in the Kent County area, transmission improvements would need to be completed in concert with transmission upgrades in the Montville area as described above. Even with the addition of the new hypothetical 345 kV line between Kent County and Montville substations, system performance remained poor and overloads of existing facilities occurred after adding more offshore wind at Kent County, as well. See Figure 6-18.

Figure 6-18: Kent County area overloads.

An alternative transmission solution was also considered to the aforementioned Montville-Kent County 345 kV transmission line—specifically, a new 345 kV circuit, in separate right of way, from Kent County to the Sherman Road substation and a new 345 kV transmission line from Montville substation to the Southwest Connecticut area. See Figure 6-19. Note that significant congestion would be anticipated with this Kent County offshore wind injection due to the existing combined-cycle facilities in this area. For the Montville 345 kV interconnection, an alternative transmission solution was identified using a new 345 KV circuit connecting Montville to Southwest Connecticut.

Figure 6-19: Alternative 345 kV upgrades.

#### Mystic Area

The ISO considered alternatives using AC, DC, or both types of submarine cable for interconnecting offshore wind to the Mystic and K Street substations in Boston. Many offshore wind developers initially prefer to use AC cable connections from the proposed wind farm lease areas to coastal 345 kV substations. However, the ISO determined that additional offshore wind could be connected using HVDC connections from the offshore wind farms to load center substations, avoiding significant onshore transmission upgrades. For the 2019 NESCOE Economic Study, the ISO considered Mystic and K Street substations as examples of candidate sites for the HVDC connections, as illustrated in Figure 6-20. Other load-center substations, such as Southwest Connecticut, could be considered as well.

Figure 6-20: HVDC alternatives into the Mystic and K Street substations.

Submarine DC cable can also be used to connect from an offshore collector substation to the interconnection point at the onshore substation. Submarine DC technology can be used for very long distances (hundreds of miles). Converter stations are needed at both ends (one at the offshore collector substation and one at the onshore interconnection point) to convert from DC back to AC and add significantly to the overall cost. A single HVDC cable can be used to connect up to 1,200 MW of generation.

Submarine AC cable from an offshore collector substation to the interconnection point at the onshore substation can be used for distances of up to approximately 40 to 60 miles. Typical applications are operated at 225 to 275 kV and are rated to carry approximately 400 MW for each (three-phase) cable. Very commonly, developers have proposed projects that use two AC cables for an 800 MW project.

Again, considering the 8000_1 scenario, a conceptual application of offshore cable technology was examined. Figure 6-21 illustrates a potential configuration, comprising both AC and DC submarine cable technology, to deliver offshore wind to load pockets in New England with minimal additional transmission reinforcements.

Figure 6-21: Conceptual application of offshore cable technology using AC and DC submarine cables.

#### Infrastructure Summary

As summarized in Table 6-4, approximately 5,800 MW of offshore wind can be interconnected using AC cable connections to interconnection points along the southern New England coast without needing significant upgrades to the onshore transmission network. Note that some local 345 kV reinforcement/expansion is still likely to be needed for this scenario. Additional interconnections above 5,800 MW to the southern New England coast would drive the need for significant onshore network upgrades. Alternatively, HVDC connections could be used to continue to travel further distances and connect additional offshore wind directly to the load centers. The connection of 2,200 MW using offshore HVDC was identified as not requiring major onshore transmission upgrades. In addition to the 5,800 MW connected using AC cables to the southern New England coast, the 2,200 MW using offshore HVDC would provide 8,000 MW of connected offshore wind.

Table 6-5
Summary of Megawatt Injection Levels (MW) for Offshore Wind by Interconnection Point
and Associated Transmission Infrastructure

| Total Offshore Wind Injection Scenario (MW) | Southern Shore Connection Points and Amounts (MW) Using AC Cables |  |  |  | Onshore Connection Points and Amounts (MW) Using HVDC Cables |  | Offshore Infrastructure (Number of Cables) |  | Major Additional Onshore Transmission Infrastructure Identified to Accommodate Interconnection Scenario(c) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | #1 Bourne/ Barnstable | #2 Brayton Point | #3 Kent Co/ Davisville | #4 Montville | #A Mystic | #B K Street | Offshore AC Cables(a) | Offshore HVDC Cables(b) |  |
| 2,000 | 800 | 500 | 700 | - | - | - | 5 | - | None |
| 3,000 | 1,500 | 800 | 700 | - | - | - | 8 | - | None |
| 5,000 | 2,400 | 800 | 1,000 | 800 | - | - | 13 | - | None |
| 5,800 | 2,400 | 1,600 | 1,000 | 800 | - | - | 15 | - | None |
| 7,000 | 2,400 | 1,600 | 1,000 | 800 | 1,200 | - | 15 | 1 | None |
| 8,000_1 | 2,400 | 1,600 | 1,000 | 800 | 1,200 | 1,000 | 15 | 2 | None |
| 8,000_2 | 3,400 | 1,600 | 1,000 | 800 | 1,200 | - | 17 | 1 | New approximately 60-mile 345 kV line in separate right-of-way from Barnstable, MA, to K Street substation |
| 8,000_3 | 2,400 | 2,600 | 1,000 | 800 | 1,200 | - | 17 | 1 | New approximately 50-mile 345 kV line in separate right-of-way from Brayton Point to K Street substation (or Mystic, if injection is already added at K Street) |
| 8,000_4 | 2,400 | 1,600 | 2,000 | 800 | 1,200 | - | 17 | 1 | New approximately 30-mile 345 kV line in separate right-of-way from Kent Co, RI, to Sherman Road substation(d) |
| 8,000_5 | 2,400 | 1,600 | 1,000 | 1,800 | 1,200 | - | 17 | 1 | New approximately 60-mile 345 kV line from Montville CT, to Southwest CT |

(a) Each offshore three-phase AC cable is assumed to be approximately 40–60 miles long and rated for approximately 400 MW, operating at 230–280 kV.

(b) Each offshore HVDC cable is assumed to be approximately 150–200 miles long and rated for up to 1,200 MW.

(c) Some local 345 kV reinforcement/expansion is still likely to be needed for all interconnection scenarios.

(d) Significant congestion would be observed with this offshore wind injection and upgrade when the existing combined-cycle facilities in this part of the system are running.

Injection Level Color Code

[Grab your reader’s attention with a great quote from the document or use this space to emphasize a key point. To place this text box anywhere on the page, just drag it.]

Injection level is below the level where major infrastructure beyond the local interconnection area would be needed.

[Grab your reader’s attention with a great quote from the document or use this space to emphasize a key point. To place this text box anywhere on the page, just drag it.]

Injection level is at the limit above which major infrastructure beyond the local interconnection area would be needed for additional injections

[Grab your reader’s attention with a great quote from the document or use this space to emphasize a key point. To place this text box anywhere on the page, just drag it.]

Injection level is above the level where major infrastructure beyond the local interconnection area would be needed.

#### Alternatives in the Marketplace

The offshore wind sector is in a very dynamic phase of evolution and limited component cost data are available. Recent procurement announcements have signaled continued reductions in overall project costs. The ISO has no reliable data on current projects on the scale of what is modeled in this study.

This study explored two alternative approaches for continued interconnection beyond the initial 5,800 MW:

- Additional offshore AC connections with significant onshore transmission upgrades

- Offshore HVDC connections that bypass onshore grid constraints

The overall cost of each approach could be comparable. Under each approach, estimates of the overall transmission component could be $1 billion or more for each 1,200 MW addition. But actual costs are highly dependent on the specific circumstances of each project, especially for the onshore AC expansion, which will be location-specific.

Considering both alternatives for any prospective project is appropriate because of the project-specific costs and the continued rapid evolution of offshore wind development costs.

# Summary

This section summarizes the results of the NESCOE 2019 Economic Study that assessed the effects of different offshore wind-expansion scenarios on the future electric power system in New England. The results for several scenarios and four sensitives provide useful information when considered as a whole. The most relevant observations of the NESCOE 2019 Economic Study are as follows:

- The significant potential for spilling offshore wind energy

- The degree of resource development capable of achieving carbon-reduction goals

- Transmission interconnection alternatives for as much as 8,000 MW of offshore wind

The results revealed that spillage is very similar, regardless of the interconnection points in southern New England, with the rate of spillage increasing as offshore wind buildout increases. Most spillage is attributed to oversupply when loads are lower, not transmission congestion. Spillage varies significantly by month, from 0.15 to 2.69 TWh, due to the interaction of wind, solar, and load profiles. The least amount of spillage in the 8,000 MW scenario occurred in the summer months of July and August when demand is generally high. The study did not consider measures to address spillage of offshore wind energy. However, when New England has oversupply, using energy storage or selling energy to neighboring control areas may be an alternative to reduce spillage.

The study of environmental impacts associated with different levels of offshore wind additions provide insight on future emission trends. The total CO2 emissions associated with the different scenarios analyzed in this study are directly tied to the type and amount of fossil fuels modeled. Carbon dioxide emissions were reduced by approximately one-third in the 8,000 MW offshore wind scenarios compared with the Reference Case of 0 MW of offshore wind. Additionally, the results indicated that CO2 emissions are highest in July and August when wind and solar production are lowest and loads are at their highest.

Another important finding of this study was that, based on the expected transmission topology for the 2030 study year, approximately 5,800 MW of new offshore wind has the potential to be interconnected in southern New England without needing major additional 345 kV reinforcements. Adding additional offshore wind (above the base scenario of 5,800 MW) would require significant transmission reinforcements that may be difficult to site and expensive to build. However, the study also explored options to interconnect offshore wind to the Mystic and K Street substations in Boston. The ISO determined that the use of HVDC connections into Boston could avoid significant onshore transmission upgrades, and an additional 2,200 MW could be interconnected to key areas in the region.

Because the offshore wind sector is evolving, and component cost data are not readily available, the ISO had no reliable data to estimate interconnection costs as NESCOE requested. However, the ISO believes the overall cost of each interconnection approach is comparable and may cost $1 billion or more for each 1,200 MW addition above 5,800 MW of installed offshore wind capacity. But actual costs are highly dependent on the specific circumstances of each project, especially for the onshore AC expansion, which will be location-specific.

Offshore wind additions are beneficial to reduce the New England carbon footprint but are less flexible and weather dependent. Renewables are anticipated to replace fossil-fuel resources as they retire. Understanding the feasibility and market impacts of offshore wind expansion in New England is essential. The 2019 NESCOE Economic Study illustrates that as much as 8,000 MW of offshore wind can be interconnected without the need for significant transmission reinforcements and would result in minimal spillage during the summer months when demand is high.

This 5,800 MW includes the base 1,000 MW identified at the time of the NESCOE request.

The RENEW Economic Study requested the ISO to study the economic impact of conceptual increases in hourly operating limits on the Orrington-South interface from conceptual transmission upgrades. The Anbaric Economic Study requested the ISO to study the impacts on the energy market prices and air emissions when the system experiences large penetrations of offshore wind resources (up to 12,000 MW). RENEW Northeast, Proposal for Economic Study of Orrington-South Interface, PAC presentation (April 25, 2019), https://www.iso-ne.com/static-assets/documents/2019/04/a2_renew_2019_economic_study_request_presentation.pdf, and Theodore Paradise (Sr. Vice President, Transmission Strategy and Counsel, Anbaric Development Partners, LLC), “2019 ISO New England Economic Study Request for Offshore Wind Impacts,” letter to Peter Bernard (chair, ISO New England Inc. Planning Advisory Committee) (April 1, 2019), https://www.iso-ne.com/static-assets/documents/2019/04/anbaric_2019_economic_study_request.pdf.

ISO New England , ISO New England Inc. Transmission, Markets, and Services Tariff (ISO tariff), Section II, Open Access Transmission Tariff, Attachment K, “Regional System Planning Process” (January 22, 2020), https://www.iso-ne.com/static-assets/documents/regulatory/tariff/sect_2/oatt/sect_ii.pdf.

Load-serving entity (LSE) energy expenses are the total electric energy revenues that resources and imports from neighboring systems would receive for supplying electric energy to the wholesale market plus the cost of congestion.

OATT, Attachment K, Section 4.1b.

ISO-NE, PAC presentations, 2019 Economic Study—Preliminary NESCOE Results (December 19, 2019), https://www.iso-ne.com/static-assets/documents/2019/12/a3_2019_economic_study_preliminary_nescoe_results.pdf; 2019 Economic Study—Follow-Up to the December 2019 Meeting (January 23, 2020), https://www.iso-ne.com/static-assets/documents/2020/01/a4_jan_2020_economic_study_qa_final-67f4425e.pdf.

ISO-NE, PAC presentations, NESCOE 2019 Economic Study—8,000 MW Offshore Wind Results (February 20, 2020), https://www.iso-ne.com/static-assets/documents/2020/02/a6_nescoe_2019_Econ_8000.pdf; 2019 NESCOE Economic Study—Follow-Up to the February 2020 Meeting (April 23, 2020), https://www.iso-ne.com/static-assets/documents/2020/04/a5-nescoe-2019-econ-study-follow-to-the-feb-2019.pdf.

ISO-NE, PAC presentations (May 20, 2020), NESCOE 2019 Economic Study—Ancillary Services Analysis, https://www.iso-ne.com/static-assets/documents/2020/05/a4_nescoe_2019_economic_study_ancillary_services_analysis.pdf, and NESCOE 2019 Economic Study—Additional Information Regarding Marginal Unit Emissions, https://www.iso-ne.com/static-assets/documents/2020/05/a5_nescoe_2019_economic_study_additional_information_on_marginal_unit_emissions.pdf.

ISO-NE, PAC presentations, 2019 Economic Study Offshore Wind Transmission Interconnection Analysis (dated March 18, 2020), https://smd.iso-ne.com/operations-services/ceii/pac/2020/03/a7_osw_economic_study-trans_interconnection_analysis.pdf; 2019 Economic Study Offshore Wind Transmission Interconnection Analysis (May 20, 2020), https://smd.iso-ne.com/operations-services/ceii/pac/2020/05/a3_2019_economic_study_offshore_wind_transmission_interconnection_analysis_ceii.pdf; Regional System Plan Transmission Projects and Asset Condition June 2020 Update (June 17, 2020), https://www.iso-ne.com/event-details?eventId=140525.

Information on how to access Critical Energy Infrastructure Information (CEII) materials is available at the ISO’s “Request Data and Information,” webpage (2020), https://www.iso-ne.com/participate/support/request-information.

NESCOE, 2019 Economic Study Request: Offshore Wind Integration, PAC presentation (April 25, 2019), https://www.iso-ne.com/static-assets/documents/2019/04/a2_nescoe_2019_economic_study_request_presentation.pptx.

NESCOE’s original request sought to examine increasing levels of offshore wind penetration in 2030 and 2035, which was later amended to examine 2030 only.

The ISO determined interconnection points early in the study process, which it presented to stakeholders at the May 21, 2019, PAC meeting; see 2019 Economic Studies, https://www.iso-ne.com/static-assets/documents/2019/05/a2_2019_economic_study_draft_scope_of_work_and_high_level_assumptions.pptx. Optimal interconnection points were based on the anticipated 2030 transmission system, where offshore wind additions (of approximately 7,000 MW) have the potential to avoid major additional 345 kilovolt (kV) reinforcements. The study assumed that this scenario would need a combination of 345 kV reinforcements and expansion and that not all the 8,000 MW of offshore wind would be able to operate simultaneously at nameplate levels.

The 29 MW Block Island offshore wind resource was considered an existing resource for this study.

The ISO New England Interconnection Request Queue lists the status of requests for the interconnection of new or uprated (increased capacity) generating facilities in New England, including elective transmission upgrades (ETUs) and transmission service requests; see https://www.iso-ne.com/system-planning/transmission-planning/interconnection-request-queue/ and https://irtt.iso-ne.com/reports/external.

The interconnection process is described in Schedule 22, Large Generator Interconnection Procedures (LGIP) (https://www.iso-ne.com/static-assets/documents/regulatory/tariff/sect_2/sch22/sch_22_lgip.pdf), Schedule 23, Small Generator Interconnection Procedures (SGIP) (https://www.iso-ne.com/static-assets/documents/regulatory/tariff/sect_2/sch23/sch_23_sgip.pdf), and Schedule 25, Elective Transmission Upgrade Interconnection Procedures (ETU) (https://www.iso-ne.com/static-assets/documents/2015/02/sch_25.pdf).

ISO-NE, PAC presentations, 2019 Economic Studies—Draft Scope of Work and High-Level Assumptions (May 21, 2019), https://www.iso-ne.com/static-assets/documents/2019/05/a2_2019_economic_study_draft_scope_of_work_and_high_level_assumptions.pptx; 2019 Economic Studies—Detailed Assumptions (August 8, 2019), https://www.iso-ne.com/static-assets/documents/2019/08/a8_2019_economic_studies_detailed_assumptions.pptx.

ISO-NE, 2019 Economic Study Requests Status Update, PAC presentation (November 20, 2019), https://www.iso-ne.com/static-assets/documents/2019/11/a6_2019_economic_study_request_status_update.pdf.

Detailed transmission interface limits for 2025 used for this study are available in the ISO’s PAC presentation, Forward Capacity Auction 14 Transmission Transfer Capabilities & Capacity Zone Development (March 21, 2019), slide 25, https://www.iso-ne.com/static-assets/documents/2019/03/a8_fca14_transmission_transfer_capabilities_and_capacity_zone_development.pdf.

Normal transmission system transfer limits account for transmission system security constraints, which consider expected transmission facilities in service and first-contingency (N-1) criteria. A first contingency is the loss of the power system element (facility) with the largest impact on system reliability. A second contingency (N-1-1) (discussed in Section 6.1.9) occurs after a first contingency when the facility that, at that time, has the largest impact on the system is lost. N-1-1 also can refer to a constraint met by maintaining an operating reserve that can increase output when the first contingency occurs.

For more information on RSP areas, refer to the “System Planning Subareas” map at this ISO website link: https://www.iso-ne.com/about/key-stats/maps-and-diagrams/#system-planning-subareas. Also refer to the ISO’s “Regional System Plan” webpage at: https://www.iso-ne.com/system-planning/system-plans-studies/rsp/.

Refer to footnote 6.

ISO-NE,  2016 Economic Study: NEPOOL Scenario Analysis, Phase I, final report (November 17, 2017), https://www.iso-ne.com/static-assets/documents/2017/11/final_2016_phase1_nepool_scenario_analysis_economic_study.docx; Amro M. Farid (Dartmouth College), 2016 Economic Study Phase II—Regulation, Ramping and Reserves, PAC presentations (December 20, 2017, and April 24, 2018), https://www.iso-ne.com/static-assets/documents/2020/05/2-2018-04-13-pac-presentation.pdf, and ISO-NE, 2016 Economic Phase II Study, PAC presentation (December 20, 2017), https://www.iso-ne.com/static-assets/documents/2017/12/a2_2016_economic_study_phase_2_regulation_ramping_reserves_introduction.pdf. The 2016 Economic Study Phase II Study is also known as the System Operational Analysis and Renewable Energy Integration Study (SOARES).

This simulation methodology is consistent with the methodology used in the 2016 Economic Studies. Refer to footnote 22.

The EPECS simulator consists of four simulation layers: (1) day-ahead resource scheduling as a security-constrained unit commitment (SCUC); (2) real-time resource scheduling as a real-time unit commitment (RTUC); (3) real-time balancing as a security-constrained economic dispatch (SCED); and (4) real-time physical power flow with integrated regulation service.

Timeframe limitations precluded EPECS simulations on the specific 2019 Economic Study scenarios. However, several cases from the 2016 Economic Study resemble the renewable and clean-energy assumptions from the 8,000 MW scenarios in the 2019 Economic Study and provide directional guidance discussed further below; see Section 6.1.7.

EIA, 2019 Annual Energy Outlook (2019), https://www.eia.gov/outlooks/archive/aeo19/.

State of Massachusetts, An Act Establishing the Global Warming Solutions Act, 2008 acts, Chapter 298 (August 7, 2008), https://malegislature.gov/Laws/SessionLaws/Acts/2008/Chapter298.

Although offshore wind resources were modeled as price-taking resources in this study due to their threshold price of $0/MWh, these resources do exhibit some flexibility if they are “held-back” for reserves or operated under do-not-exceed dispatch (DNE) provisions. The DNE methodology sets an upper limit of how much generation the system can accommodate from an intermittent power resource. The resource may operate freely between 0 MW and this limit but must not exceed it. This helps maximize the amount of intermittent generation on the system by accommodating the variable nature of these resources’ fuel.

Petition of Massachusetts Electric Company and Nantucket Electric Company, each d/b/a National Grid for approval by the [Massachusetts] Department of Public Utilities (DPU) of a long-term contract for procurement of Clean Energy Generation, pursuant to Section 83D of An Act Relative to Green Communities, St. 2008, c. 169, as amended by St. 2016, c. 188, § 12, DPU 18-64; DPU 18-65; with three Power Purchase Agreements for firm qualified clean energy from hydroelectric generation and between the following parties and H.Q. Energy Services (US) Inc. as of June 13, 2018: (1) NSTAR Electric Co. d/b/a Eversource Energy (US) Inc., Exhibit JU-3-A Page 1 of 87, revised October 17, 2018 (https://fileservice.eea.comacloud.net/FileService.Api/file/FileRoom/9946888); (2) Massachusetts Electric Company and Nantucket Electric Company d/b/a National Grid, redacted DPU 18-64/18-65/18-66, October 17, 2018, Exhibit JU-3-B, Page 1 of 97 (https://fileservice.eea.comacloud.net/FileService.Api/file/FileRoom/9946889); and (3) Fitchburg Gas and Electric Light Co. d/b/a Unitil DPU 18-64/18-65/18-66, revised October 17, 2018, Exhibit JU-3-C, Page 1 of 85 (https://fileservice.eea.comacloud.net/FileService.Api/file/FileRoom/9946890). Docket (accessed June 22, 2020): https://eeaonline.eea.state.ma.us/DPU/Fileroom/dockets/bynumber/18-65.

Additional results are included in PAC presentations: December 19, 2019 and January 23, 2020 (footnote 6); February 20, 2020, and April 23, 2020 (footnote 7); and May 20, 2020 (footnote 8). Transmission interconnection results are summarized in the April 23, 2020, and May 20, 2020, PAC presentations.

As discussed in Section 5.2.8, threshold prices drive the curtailment of specific resources, and the order of the spilled resources; the prices do not reflect actual expectations of market outcomes. The NESCOE 2019 Economic Study used both 2006 and 2015 weather years to shape the 2030 wind, solar, and load profiles (see Section 4.2.3). If a different weather year were used, the results would differ.

The differences in spillage of the 8,000 MW scenarios is due to varying capacity factors among the different scaled interconnection values rather than one certain interconnection configuration being more valuable than another.

As a general trend, offshore wind patterns vary when wind production is highest in the shoulder months and lower during the peak months.

During the aforementioned low-spill days, the New Brunswick import spillage was minimal.

Oil resources operate based on economic commitment and usually when natural gas prices rise due to high demand. The assumed fuel prices for this 2019 NESCOE Economic Study do not feature this oil-price inversion because this type of operational condition (where oil-fired resources are economical) never occurs in the study. Given the large amount of renewable and clean resources in the scenarios studied, whether the oil-price inversion would occur is unknown. This study also does not assess fuel-security concerns that sometime drive the operation of oil-fired generators. ISO-NE, NESCOE 2019 Economic Study—8,000 MW Offshore Wind Results, PAC presentation (February 20, 2020), slides 10 and 27, https://www.iso-ne.com/static-assets/documents/2020/02/a6_nescoe_2019_Econ_8000.pdf.

Recall that the 8,000 MW scenarios include heat pumps and plug-in hybrid electric vehicles. Annually, heat pumps and PHEVs make up only 4% of net load. However, during winter evening peaks, they are approximately 10% of net load. Storage or energy that would otherwise be spilled often serve this load addition.

While overall interfaces are not congested, transmission analysis revealed specific interface line overloads that would require upgrades.

In this study, the Surowiec-South interface limit was increased to 2,500 MW (from 1,500 MW).

NESCOE, Request for 2019 Economic Study to Analyze Offshore Wind Integration, memorandum (April 1, 2019), page 2, https://www.iso-ne.com/static-assets/documents/2019/04/nescoe_2019_economic_study_request.pdf.

The two methods are not directly comparable with the Marginal Emissions Analyses report. Thus, the ISO provided a 0 MW offshore wind scenario as a baseline and assessed only unconstrained scenarios. For information on the ISO’s marginal emissions analyses, see: ISO-NE, 2018 ISO New England Electric Generator Air Emissions Report (May 2020), https://www.iso-ne.com/static-assets/documents/2020/05/2018_air_emissions_report.pdf.

Scenarios without heat pumps were compared with one another (i.e., 0 MW to 5,000 MW of offshore wind additions). Similarly, scenarios with heat pumps were compared with one another (i.e., 6,000 MW to 8,000 MW, including the four sensitivities to the 8,000 scenario, of offshore wind additions).

The two RFP-commitment offshore wind projects, Vineyard Wind (800 MW) and Revolution Wind (200 MW), are not included in the 7,000 MW. Also note that some local 345 kV reinforcements and expansion may still be needed and that a system impact study could identify a more prescriptive list of transmission upgrades. Because southern New England is heavily populated, and available land is at a premium, local transmission upgrades may be costly and require extensive siting.

More information on NPCC standards is available at https://www.npcc.org/Standards/default.aspx.