## Slide 1
June 16, 2020 | webex
Doug Smith
(413) 535-4176 | dlsmith@iso-ne.com
Metering Requirements for DC Coupled Assets
Proposed Revisions to OP-18

## Slide 2
Metering Requirements for DC-Coupled Assets
Proposed Effective Date: August 6, 2020
Several participants are installing electric storage and intermittent generation behind the same point of interconnection and some of these “co-located” facilities are DC coupled, meaning that both the storage and intermittent components share one or more inverters
The purpose of today’s session is to review and request an advisory vote the proposed redline of OP-18 drafted to address the metering of DC coupled Assets
This OP-18 redline (Rev. 20) also includes ministerial changes unrelated to the DC metering issue

## Slide 3: Summary of Prior RC Presentations
On April 27th, we described the DC metering issue along with an overview of the proposed solution
  Material from that meeting is included as Appendix 2 and 3
On May 19th
  We went through the OP-18 redlines for DC Metering, and also discussed the changes to OP-18 Appendices C and D related to DC Metering
  We described the ministerial changes to OP-18 unrelated to DC metering
  We discussed feedback received from Participants
  Material from that meeting is included as Appendix 1

## Slide 4: The Impact of These Changes
Once adopted along with corresponding changes to Manuals M-28 and M-RPA, DC coupled facilities will be able to participate in the ISO administered markets as separate assets
Metering and telemetering requirements for DC coupled facilities will be equivalent to requirements for other facilities

## Slide 5: A Incremental Change Since the May RC Meeting in the new OP-18 Section IV.9 is Proposed
9. DC coupled Assets participating in one or more of the Markets separately must meet the following requirements:
a) DC Wh metering must be installed for each Asset.
b) AC Wh metering compliant with this OP must be installed at or compensated to the Interconnection Point.
c) Reported interval MWh per hour values for each DC coupled Asset must sum to the reported measured AC MWh per hour compensated to the Interconnection Point in each interval.
d) Both unadjusted DC MWh per hour values and reported interval MWh per hour values for each DC coupled Asset shall be made available to all Lead Market Participants for the Assets prior to reporting to ISO-NE.

## Slide 6: Stakeholder Schedule
Stakeholder Committee and Date | Scheduled Project Milestone
Reliability Committee April 22, 2020 | Discussion of issue and proposed solution
Reliability Committee May 19, 2020 | Discussion of revisions to OP-18
Reliability Committee June 16, 2020 | Vote on revisions to OP-18
Participants Committee August 6, 2020 | Vote

## Slide 8: Appendix 1
Presentation from May Meeting

## Slide 9: Proposed OP-18 Changes Related to DC Metering

## Slide 10: OP-18 Section IV.9 (new)
9. DC coupled Assets participating in one or more of the Markets separately must meet the following requirements:
a) DC Wh metering must be installed for each Asset.
b) AC Wh metering compliant with this OP must be installed at or compensated to the Interconnection Point.
c) Reported interval MWh per hour values for each DC coupled Asset must sum to the reported AC MWh per hour compensated to the Interconnection Point in each interval.
d) Both unadjusted DC MWh per hour values and reported interval MWh per hour values for each DC coupled Asset shall be made available to all Lead Market Participants for the Assets prior to reporting to ISO-NE.

## Slide 11: OP-18 Section V.A.1.i (new)
i. DC coupled Assets participating in one or more of the Markets separately shall adhere to the following:
i. If the maximum output of the combined facility is under 5 MW and it is registered as a Settlement Only Resource, the Assets are not required to provide telemetry data pursuant to this section V.
ii. DC telemetry for each Asset shall be adjusted to the AC Interconnection Point.
iii. No MVAr values are required for low side DC components

## Slide 12: OP-18 Section VII
VII.A - Note ANSI Standards apply to AC metering
VII.B.7 (new section)
  DC metering associated with DC coupled Assets participating separately in any Market shall be of equivalent accuracy and precision to AC meters meeting the ANSI C12 standard. Specifications for such devices shall be provided to the ISO and/or Host Participant upon request.

## Slide 13: OP-18 Section IX
IX.D.2 add ‘HV’ before ‘DC’ to indicate this section is specific to HVDC meters
Add new section IX.D.3 with language parallel to D.2 specific to non-HVDC DC meter testing requirements:
3. DC Wh metering for DC coupled assets participating separately in any Market shall conform to the following requirements:
  a. DC test voltage source equipment for generating current and voltage inputs to the meter shall be traceable to NIST for accuracy.
  b. Voltmeters used for monitoring the input voltages to the dc meter during the test shall be traceable to NIST for accuracy.
  c. Meter nominal test voltage shall be the meter input voltage corresponding to the DC voltage rating of the inverter.
  d. Meter “full load test amperes” shall be the meter input voltage corresponding to the DC ampere rating of the inverter.

## Slide 14: OP-18 Section IX (continued)
  e. The test points for the meter shall be as follows:
    Full load test amperes and nominal test voltage
    Full load test amperes and 50% of nominal test voltage
    50% of full load test amperes and nominal test voltage
    50% of full load test amperes and 50% of nominal test voltage
  f. Where meter pulse outputs are compared to calculated target values, and pulses from a standard, to determine meter accuracy, worksheets detailing the test conditions and target pulse counts will be made available prior to testing the meter.

## Slide 15: OP-18 Appendix C: Minimum Accuracy Standards
Add row for DC metering systems, 1% minimum accuracy
Add note indicating DC standard applies to DC coupled Assets that must be allocated AC metering data

## Slide 16: OP-18 Appendix D: Metering and Telemetering Diagrams
New Figure 7 for DC coupled asset metering distribution concept
  Include allocation formulas for losses and loads between AC and DC meters

## Slide 17: Input Received from Stakeholders to Date
Developers as well as Host Utilities have been generally supportive of ISO’s proposal
Both requested specific language for allocating losses and loads between the AC and DC metering points to each asset
  In response, we propose specific language in IV.9 requiring that the reported data sum to the AC meter data
  We also propose formulas for the allocation in Figure 7 of Appendix D that will work for allocations of any two-asset facility
  However, given that 1) we have language for loss compensation in IV.B.7 that does not specify allocations for other multiple Asset facilities, and 2) we anticipate that dc coupled facilities may have many different physical configurations, we do not believe more specificity is appropriate
  We do support a general principle that the use of the inverter is a reasonable way to allocate these loads, and have detailed that approach in Appendix 2
One developer asked about a multi-inverter system and if we can have an associated diagram
  We believe that if each component is summed prior to the allocation, the formula in Appendix D figure 7 can still be applied

## Slide 18: Proposed OP-18 Changes UnRelated to DC Metering

## Slide 19: Proposed OP-18 Revision 20 Changes Unrelated to DC Metering
General clean up – should/must to shall, capitalization, document references
Language that allows for potentially different telemetry requirements for ‘Ld-node Generators’ where the asset is located in the distribution system
  Reference OP-12 presentation
  Telemetry of kV, MW and MVAR is required at a minimum
Tie line and frequency data scan rate clarification
Explicit HVDC description/clarifications (100 kV and above)
Telemetry component test timeframes (from 4 to 6 years)
Appendix C table consolidation

## Slide 20: Conclusion
ISO-NE proposes changes to OP-18 to enable DC coupled facilities to participate in ISO markets as separate Assets
  The proposed redline changes leverage existing processes to the extent possible and ensure that metering and telemetry for DC-Coupled facilities meets the same standards that apply to other generating facilities
  Manual M-RPA and M-28 changes are also needed
  The proposed solution will ensure that metering and telemetry for these facilities meets the same standards that apply to other generating facilities
Other ministerial changes are included in this redline
ISO-NE is targeting a Q3 2020 effective date because some DC coupled facilities are likely to be commercial by then

## Slide 21: Appendix 2
Proposed Solution Conceptual Framework (From April 2020 RC Meeting)

## Slide 22: Why is DC Metering Needed?
ISO-NE published specific guidance on market participation options for all co-located facilities via a PDF and an associated recording on April 7
  Allowable configurations include both registering the entire facility as a single asset and registering the two components as separate assets
Participants will register the components of their co-located facility as separate energy market Assets when, for example:
  The two components qualified and cleared separately in the FCM
  The two components have separate Lead Market Participants
If the facility is DC-coupled and intends to participate as separate Assets, DC metering must be used to distinguish their individual power flows

## Slide 23: DC-Coupled Facility Registered as Two Assets
Point of Interconnection (POI)
Note power flow at POI and A2 may be positive or negative.

## Slide 24: DC Metering Challenges Addressed
Define accuracy and testing requirements for DC metering systems within OP-18 to be functionally equivalent to the requirements for other assets
Establish a process for Assigned Meter Readers to allocate the AC RQM to each asset using DC metering data
  To the extent that telemetry is required for either or both assets, a similar process will be established
Define a means of allocating any loads and losses that occur between the DC meters and AC point of interconnection to each asset for all possible power flow scenarios
  The Appendix to this presentation gets into details of how this issue can be resolved

## Slide 25: Proposed Solution Leverages Existing Process
Host Participant is generally the Assigned Meter Reader
  They install, read, and report AC Revenue Quality Metering (RQM) daily to the ISO for energy market settlement
  Any discrepancies are resolved between the parties prior to resettlement
In cases where the Assigned Meter Reader is not the Host Participant
  The Assigned Meter Reader reports the data to the Host Participant
  The Host Participant must agree with the data before it can be reported to the ISO by the Assigned Meter Reader
  Timelines are spelled out in Manual M-28
  Any discrepancies that are not resolved in time for initial settlement will be resolved during resettlement
Developer and/or their Designated Entity installs and reports any required real-time telemetry

## Slide 26: Overview of Proposed Solution
Host Participant installs AC RQM at or compensated to the Point of Interconnection (POI) of the facility
  This is what is currently done for non DC-coupled facilities
Lead Participant(s) install DC meters for each component that meet new requirements to be specified in OP-18 (equivalent to RQM standards for AC meters)
Lead Participant(s) designate a single Assigned Meter Reader (not required to be the Host Participant) for all assets
Assigned Meter Readers are responsible for allocating the AC RQM to each asset based on the DC meter data and reporting it for energy market settlement
If real-time telemetry is required, it is provided by the Designated Entity such that it represents the Asset’s impact on the POI power flow

## Slide 27: Proposed Solution Details

## Slide 28: AC Energy Metering and Telemetry
AC RQM and any required telemetering is installed at or compensated to the POI
  The Local Distribution Company typically installs the AC RQM as part of its interconnection work
  The Lead Market Participant and/or its Designated Entity is responsible for any required telemetering of real time MW/MVAr
AC metering and telemetry is needed to measure the entire facility’s energy and power, which must be allocated to each Asset

## Slide 29: DC Energy Metering
Project Owner/Developer installs DC metering for each component
  Separate DC meters for intermittent generator and battery
  In the case of multiple shared inverters, this would require at least two metering points for each inverter
  Meter requirements to be integrated into OP-18:
    RQM equivalent accuracy and precision
    Clocks synchronized to NIST
    MWh consumption/generation data (5 minute or hourly intervals)
      Daily reporting schedule per Manual M-28
    Single Assigned Meter Reader

## Slide 30: Real-Time Telemetry
Real-time telemetry is required for all assets (including DC-coupled assets) other than those at facilities that are capable of < 5 MW that elect Settlement Only treatment
  5 MW threshold is for maximum capability at the POI for all assets
  4 second updates of instantaneous power for AGC (regulation), 10 second otherwise
Any required Asset telemetry values must be allocated from the AC telemetry (located at or compensated to the POI) using each asset’s DC telemetry as the allocator
  MW, MVAr, AC Voltage, AVR status
Lead Participant and their Designated Entity are responsible for all required telemetry

## Slide 31: DC Metering and Telemetry Requirements
ANSI standards for RQM are not applicable to DC equipment
  DC metering will be required to meet the same (or higher) accuracy and precision as ANSI C12
  Documentation of this will be required
Telemetry component tests for devices at voltages below 69 kV are 4.5% of the largest fiducial kW value and +/- 3% for voltages is acceptable to ISO Operations
Equivalent accuracy ratings for sensors and meters as OP-18 Appendix C
  Overall system accuracy of 1% of Fiducial Value
All communications equipment must comply with OP-18 Section VIII

## Slide 32: DC Meter Testing Requirements
Equivalent to similar AC testing requirements (See OP-18 Section IX)
Testing devices traceable to NIST
The test points for the meter shall be as follows:
  Full load test amperes, nominal voltage
  Full load test amperes, 50% nominal voltage
  50% of full load test amperes, full load voltage
  50% of full load test amperes, 50% nominal voltage
Current requirements for calibration of digital telemetry are changing from 4 to 6 years, which would also apply to DC metering

## Slide 33: Energy Market Settlement Process
Assigned Meter Reader designated by Lead Market Participant
  Assigned Meter Reader will need to be the same for all DC-Coupled assets at a facility
  Potential Daily Process:
    Assigned Meter Reader accesses AC RQM interval data as well as DC interval data for each Asset
    Assigned Meter Reader allocates AC RQM data to each asset based on DC meter data
    Assigned Meter Reader shares allocations with Host Participant by 0800 on first business day after Operating Day (or mutually agreed to time) [M-28 5.3(b)]
    Assigned Meter Reader must ensure that the Host Participant is in agreement prior to reporting the data to ISO-NE [M-28 5.3(c)]
    Assigned Meter Reader reports interval data for each Asset to ISO-NE by 1300 on second business day after the Operating Day [M-28 5.3(d)]
    Any corrections must follow the data reconciliation process (M-28 6.1)

## Slide 34: Appendix 3
Examples of allocation of losses and loads between AC and DC metering points

## Slide 35: Allocation Examples
These examples show how any load and/or losses between the AC POI metering and the DC metering points can be allocated to each asset
For these examples:
  We assume one PV asset and one Continuous Storage Facility, see one line diagram on next slide
  We assume there is no separately metered station service load
  The Continuous Storage Facility will be discussed as a single asset for simplicity
Arrows indicate the direction of positive power flow
Allocation formulas are for illustrative purposes
  Other allocation methodologies may be appropriate depending on the specific facility

## Slide 36: DC-Coupled Facility Registered as Two Assets
AC ‘revenue quality’ interval metering (NetPOI)
Any required real-time telemetry (Neths) must represent each asset at the POI
Point of Interconnection (POI)
Note power flow at POI and A2 may be positive or negative.

## Slide 37: Example 1 – Mid-day
A1 = 8 MW; A2 = -5 MW; Netpoi = 2.7 MW = Neths
Solar outputting 8 MW dc, Battery charging 5 MW dc and facility outputting 2.7 MW at POI
A1reported = 7.7 MW
A2reported = -5 MW
Only the PV is using the inverter, so losses are allocated to it

## Slide 38: Example 2 – Both Generating
A1 = 1 MW; A2 = 4 MW; Netpoi = 4.7 MW = Neths
Solar outputting 1 MW dc, Battery outputting 4 MW dc and facility outputting 4.7 MW at POI
A1reported = 0.94 MW
A2reported = 3.76 MW
Losses allocated proportionally

## Slide 39: Example 3 – Battery Only
A1 = 0 MW; A2 = 3 MW; Netpoi = 2.8 MW = Neths
Solar outputting 0 MW dc, Battery outputting 3 MW dc and facility outputting 2.8 MW at POI
A1 = 0 MW
A2 = 2.8 MW
PV cannot report negative generation, so losses are all allocated to the battery
  This is logical in that only the battery is using the inverter

## Slide 40: Example 4 – PV Only
A1 = 3 MW; A2 = 0 MW; Netpoi = 2.8 MW = Neths
Solar outputting 3 MW dc, Battery 0 MW dc and facility outputting 2.8 MW at POI
A1 = 2.8 MW
A2 = 0 MW
PV is allocated all losses – battery is not using the inverter

## Slide 41: Example 5 – Charging from PV and Grid
A1 = 1 MW; A2 = -4 MW; Netpoi = -3.2 MW = Neths
Solar outputting 1 MW dc, Battery charging 4 MW dc and facility load is 3.2 MW at POI
A1 = 1 MW
A2 = -4.2 MW
Losses are all allocated to the battery
  Only the battery is using the inverter

## Slide 42: Example 6 – 100% of PV charging the Battery
A1 = 4 MW; A2 = -4 MW; Netpoi = -.1 MW = Neths
Solar outputting 4 MW dc, Battery charging 4 MW dc and facility load is 0.1 MW at POI
A1 = 4 MW
A2 = -4.1MW
We expect the case of A1 exactly equal to -A2 is very rare, but in this case losses are allocated to the battery
Note: Netpoi must be ≤ zero when A1 = -A2

## Slide 43: Allocation – Reference Equations
Other allocation methodologies may be appropriate depending on the specific facility
Any allocation methodology must be acceptable to both market participants and be applied consistently to a given facility
 |  | Interval data for Settlement: | MW/MVAR Telemetry (if required):
Asset 1 | If Netpoi > 0 | Max{(Netpoi-A2),A1-[(A1+A2-Netpoi)*(A1/A1+A2)]} | Max{(Neths-A2),A1-[(A1+A2-Neths)*(A1/A1+A2)]}
 | If Netpoi ≤ 0 | A1 | A1
Asset 2 (CSF) | Netpoi-Asset 1 | Netpoi-Asset 1 | Neths-Asset 1

## Slide 44: Allocation of Losses - Summary
PV | Battery | Inverter | Losses
0 | Outputting | Outputting | Battery
0 | Inputting | Inputting | Battery
Outputting | Outputting | Outputting | Split proportionally
Outputting | Inputting | Outputting | PV
Outputting | Inputting | Inputting | Battery
Outputting | 0 | Outputting | PV