## Slide 1
ISO-NE CONE and ORTP Analysis
July 14, 2020
Danielle Powers, Meredith Stone
Emma Nicholson, Keith Paul, Joe Farrell

## Slide 2: Overview & Purpose: Agenda
  Review of detailed capital and operating costs for CONE and ORTP units
  Review of energy and ancillary services offsets
    Proposed methodology
    Scarcity adjustment to E&AS revenues
    Level of excess supply adjustment to E&AS prices
    Preliminary results

## Slide 3
Capital and Operating Costs – CONE Technologies

## Slide 4
Proposed Costs for CONE Calculations: Key Assumptions from June MC Meeting
Key Assumptions | 
Location | New London County, CT
Electric Interconnection | 2-mile electrical interconnection (to 345 kV system) plus network upgrades
Gas Interconnection | 2-mile gas lateral plus metering station
Dual Fuel | No. 2 oil for backup
Environmental Controls | Selective Catalytic Reduction CO catalyst – only Combined Cycle facility
Cooling | Dry Cooling for the frame units and aeroderivative

## Slide 5
COST COMPONENT | 2019$ | $/kW
TOTAL CIVIL/ STRUCTURAL/ARCHITECTURAL | $18,868,656 | 
TOTAL MECHANICAL COSTS | $137,734,984 | 
TOTAL ELECTRICAL/ INSTRUMENTATION AND CONTROLS COST | $27,852,487 | 
TOTAL CONSTRUCTION MANAGEMENT | $7,590,308 | 
TOTAL OTHER PROJECT COSTS | $12,450,000 | 
PROJECT CONTINGENCY | $14,314,750 | 
EPC CONTRACTOR FEE | $15,316,783 | 
TOTAL EPC COSTS | $234,127,969 | $623
Electrical Interconnection | $7,000,000 | 
Electrical System Upgrade Costs/Substation Upgrades | $13,500,898 | 
Gas Interconnection | $2,000,000 | 
Fuel Inventories | $4,500,000 | 
Financing Fees | $9,365,119 | 
Working Capital | $2,341,280 | 
TOTAL NON-EPC COSTS | $38,707,296 | $103
TOTAL OVERNIGHT CAPITAL COSTS | $272,835,265 | $726
Proposed Costs for CONE Calculations: Simple Cycle GE7HA.02 – Proposed Capital Costs
Source: Data is based on Mott MacDonald confidential estimating database

## Slide 6
COST COMPONENT | Current CONE Recalculation 2019$ | 2016 CONE Recalculation 2016$ | % Change
TOTAL CIVIL/ STRUCTURAL/ARCHITECTURAL | $18,868,656 | $16,899,000 | 
TOTAL MECHANICAL COSTS | $137,734,984 | $ 137,251,000 | 
TOTAL ELECTRICAL/ INSTRUMENTATION AND CONTROLS COST | $27,852,487 | $27,482,000 | 
TOTAL CONSTRUCTION MANAGEMENT | $7,590,308 | $3,866,000 | 
TOTAL OTHER PROJECT COSTS | $12,450,000 | $10,930,000 | 
PROJECT CONTINGENCY | $14,314,750 | $17,253,000 | 
EPC CONTRACTOR FEE | $15,316,783 | $14,198,000 | 
TOTAL EPC COSTS | $234,127,969 | $227,879,000 | 3%
Electrical Interconnection | $7,000,000 | $7,000,000 | 
Electrical System Upgrade Costs/Substation Upgrades | $13,500,898 | $20,000,000 | 
Gas Interconnection | $2,000,000 | $2,000,000 | 
Fuel Inventories | $4,500,000 | $4,200,000 | 
Financing Fees | $9,365,119 | $--1 | 
Working Capital | $2,341,280 | $2,320,000 | 
TOTAL NON-EPC COSTS | $38,707,296 | $35,520,000 | 9%
TOTAL OVERNIGHT CAPITAL COSTS | $272,835,265 | $263,399,000 | 4%
Proposed Costs for CONE Calculations: Simple Cycle GE7HA.02 – Capital Cost Comparison
1 Financing Fee included in 2019 to reflect current financing structure

## Slide 7
Fixed O&M | Proposed Values | 2025$/ kW-mo
O&M (LTSA plus ongoing O&M) | $46.26/kW-yr | $3.86
Site Leasing | $25,000/acre/yr | $0.04
Property Taxes | 2.9% | $0.37
Insurance | 0.6% of installed costs | $0.39
Proposed Costs for CONE Calculations: Simple Cycle GE7HA.02 – Proposed O&M Costs

## Slide 8
Fixed O&M | Current CONE Recalculation (2025$/ kW-mo) | 2016 CONE Recalculation (2021$/ kW-mo) | % Change
O&M (LTSA plus ongoing O&M) | $3.86 | $3.21 | 20%
Site Leasing | $0.04 | $0.05 | -20%
Property Taxes | $0.37 | $0.75 | -51%
Insurance | $0.39 | $0.45 | -13%
Proposed Costs for CONE Calculations: Simple Cycle GE7HA.02 – O&M Cost Comparison

## Slide 9
Source: Data is based on Mott MacDonald confidential estimating database
Proposed Costs for CONE Calculations: Simple Cycle Aeroderivative LM6000 – Proposed Capital Costs
COST COMPONENT | 2019$ | $/kW
TOTAL CIVIL/ STRUCTURAL/ARCHITECTURAL | $13,966,356 | 
TOTAL MECHANICAL COSTS | $73,833,022 | 
TOTAL ELECTRICAL/ INSTRUMENTATION AND CONTROLS COST | $19,461,006 | 
TOTAL CONSTRUCTION MANAGEMENT | $5,051,272 | 
TOTAL OTHER PROJECT COSTS | $8,125,000 | 
PROJECT CONTINGENCY | $8,430,566 | 
EPC CONTRACTOR FEE | $9,020,706 | 
TOTAL EPC COSTS | $137,887,927 | $1,407
Electrical Interconnection | $7,000,000 | 
Electrical System Upgrade Costs/Substation Upgrades | - | 
Gas Interconnection | $2,000,000 | 
Fuel Inventories | $4,450,000 | 
Financing Fees | $5,515,517 | 
Working Capital | $1,378,879 | 
TOTAL NON-EPC COSTS | $20,344,396 | $208
TOTAL OVERNIGHT CAPITAL COSTS | $158,232,324 | $1,615

## Slide 10
COST COMPONENT | Current CONE Recalculation 2019$ | 2016 CONE Recalculation 2016$ | % Change
TOTAL CIVIL/ STRUCTURAL/ARCHITECTURAL | $13,966,356 | $11,696,000 | 
TOTAL MECHANICAL COSTS | $73,833,022 | $78,377,000 | 
TOTAL ELECTRICAL/ INSTRUMENTATION AND CONTROLS COST | $19,461,006 | $19,132,000 | 
TOTAL CONSTRUCTION MANAGEMENT | $5,051,272 | $3,392,000 | 
TOTAL OTHER PROJECT COSTS | $8,125,000 | $8,230,000 | 
PROJECT CONTINGENCY | $8,430,566 | $11,719,000 | 
EPC CONTRACTOR FEE | $9,020,706 | $8,807,000 | 
TOTAL EPC COSTS | $137,887,927 | $141,353,000 | -2%
Electrical Interconnection | $7,000,000 | $7,000,000 | 
Electrical System Upgrade Costs/Substation Upgrades | - | $20,000,000 | 
Gas Interconnection | $2,000,000 | $2,000,000 | 
Fuel Inventories | $4,450,000 | $900,000 | 
Financing Fees | $5,515,517 | $--1 | 
Working Capital | $1,378,879 | $1,400,000 | 
TOTAL NON-EPC COSTS | $20,344,396 | $31,300,000 | -35%
TOTAL OVERNIGHT CAPITAL COSTS | $158,232,324 | $172,653,000 | -8%
Proposed Costs for CONE Calculations: Simple Cycle Aeroderivative LM6000 – Capital Cost Comparison
1 Financing Fee included in 2019 to reflect current financing structure

## Slide 11
Proposed Costs for CONE Calculations: Simple Cycle Aeroderivative LM6000 – Proposed O&M Costs
Fixed O&M | Proposed Values | 2025$/ kW-mo
O&M (LTSA plus ongoing O&M) | $97.89/kW-yr | $8.16
Site Leasing | $25,000/acre/yr | $0.10
Property Taxes | 2.9% | $0.81
Insurance | 0.6% of installed costs | $0.85

## Slide 12
Proposed Costs for CONE Calculations: Simple Cycle Aeroderivative LM6000 – O&M Cost Comparison
Fixed O&M | Current CONE Recalculation 2025$/ kW-mo | 2016 CONE Recalculation 2021$/ kW-mo | % Change
O&M (LTSA plus ongoing O&M) | $8.16 | $7.04 | 16%
Site Leasing | $0.10 | $0.18 | -44%
Property Taxes | $0.81 | $2.70 | -70%
Insurance | $0.85 | $1.62 | -48%

## Slide 13
Source: Data is based on Mott MacDonald confidential estimating database
Proposed Costs for CONE Calculations: Combined Cycle GE7HA.02 – Proposed Capital Costs
COST COMPONENT | 2019$ | $/kW
TOTAL CIVIL/ STRUCTURAL/ARCHITECTURAL | $49,040,012 | 
TOTAL MECHANICAL COSTS | $267,032,120 | 
TOTAL ELECTRICAL/ INSTRUMENTATION AND CONTROLS COST | $54,036,722 | 
TOTAL CONSTRUCTION MANAGEMENT | $11,414,582 | 
TOTAL OTHER PROJECT COSTS | $29,015,000 | 
PROJECT CONTINGENCY | $28,737,690 | 
EPC CONTRACTOR FEE | $30,749,329 | 
TOTAL EPC COSTS | $470,025,455 | $879
Electrical Interconnection | $7,000,000 | 
Electrical System Upgrade Costs/Substation Upgrades | $20,000,000 | 
Gas Interconnection | $2,000,000 | 
Fuel Inventories | $4,500,000 | 
Financing Fees | $18,801,018 | 
Working Capital | $4,700,255 | 
TOTAL NON-EPC COSTS | $57,001,273 | $107
TOTAL OVERNIGHT CAPITAL COSTS | $527,026,728 | $986

## Slide 14
Proposed Costs for CONE Calculations: Combined Cycle GE7HA.02 – Capital Cost Comparison
COST COMPONENT | Current CONE Recalculation 2019$ | 2016 CONE Recalculation 2016$ | % Change
TOTAL CIVIL/ STRUCTURAL/ARCHITECTURAL | $49,040,012 | $49,885,000 | 
TOTAL MECHANICAL COSTS | $267,032,120 | $268,998,000 | 
TOTAL ELECTRICAL/ INSTRUMENTATION AND CONTROLS COST | $54,036,722 | $58,309,000 | 
TOTAL CONSTRUCTION MANAGEMENT | $11,414,582 | $12,531,000 | 
TOTAL OTHER PROJECT COSTS | $29,015,000 | $26,507,000 | 
PROJECT CONTINGENCY | $28,737,690 | $38,531,000 | 
EPC CONTRACTOR FEE | $30,749,329 | $29,751,000 | 
TOTAL EPC COSTS | $470,025,455 | $484,512,000 | -3%
Electrical Interconnection | $7,000,000 | $7,000,000 | 
Electrical System Upgrade Costs/Substation Upgrades | $20,000,000 | $20,000,000 | 
Gas Interconnection | $2,000,000 | $ 2,000,000 | 
Fuel Inventories | $4,500,000 | $4,200,000 | 
Financing Fees | $18,801,018 | $--1 | 
Working Capital | $4,700,255 | $7,000,000 | 
TOTAL NON-EPC COSTS | $57,001,273 | $40,200,000 | 42%
TOTAL OVERNIGHT CAPITAL COSTS | $527,026,728 | $524,712,000 | 0.4%
1 Financing Fee included in 2019 to reflect current financing structure

## Slide 15
Proposed Costs for CONE Calculations: Combined Cycle GE7HA.02 – Proposed O&M Costs
Fixed O&M | Proposed Values | 2025$/ kW-mo
O&M (LTSA plus ongoing O&M) | $70.72/kW-yr | $5.89
Site Leasing | $25,000/acre/yr | $0.06
Property Taxes | 2.9% | $0.66
Insurance | 0.6% of installed costs | $0.51

## Slide 16
Proposed Costs for CONE Calculations: Combined Cycle GE7HA.02 – O&M Cost Comparison
Fixed O&M | Current CONE Recalculation 2025$/ kW-mo | 2016 CONE Recalculation 2021$/ kW-mo | % Change
O&M(LTSA plus ongoing O&M) | $5.89 | $3.12 | 89%
Site Leasing | $0.06 | $0.06 | 0%
Property Taxes | $0.66 | $1.26 | -48%
Insurance | $0.51 | $0.56 | -9%

## Slide 17
Questions

## Slide 18
Capital and Operating Costs – ORTP Technologies

## Slide 19
  Recommended size
    82.5 MW onshore wind facility with Vestas V150-5.6MW wind turbines
  Recommended location
    Central New Hampshire
  Capacity factor
    Utilized two publicly available data sources for wind speed information at the selected location for the wind facility
      National Renewable Energy Laboratory (NREL) wind speed map
      Reanalysis data provides a predominant wind direction of West / Northwest for the selected location
    Based on a review of this windspeed information and climate data from nearby Mount Washington, the predicted gross yield is 380 GWh with a gross capacity factor of 51.6%
    Mott MacDonald estimated a total efficiency factor of 0.834 based on 15 wind turbine generator locations, an average speed of 19.1 mph, and project specific assumptions for efficiency estimates including assumed indicative wake efficiency, electrical efficiency, availability, scheduled maintenance, possible curtailment (i.e., congestion on the transmission system), power curve performance, suboptimal operation, performance degradation due to icing, blade degradation, and hysteresis
    The net yield is estimated to be 317GWh with a net capacity factor of 43.1%
    Recommended capacity factor = 43.1%
Proposed Costs for ORTP Calculations: On-Shore Wind - Assumptions

## Slide 20
Source: Data is based on Mott MacDonald confidential estimating database
Proposed Costs for ORTP Calculations: On-Shore Wind – Proposed Capital Costs
COST COMPONENT | 2019$ | $/kW (Nameplate)
TOTAL CIVIL/ STRUCTURAL/ARCHITECTURAL | $84,075,000 | 
TOTAL MECHANICAL COSTS | $4,300,000 | 
TOTAL ELECTRICAL/ INSTRUMENTATION AND CONTROLS COST | $11,328,780 | 
TOTAL CONSTRUCTION MANAGEMENT | $2,400,000 | 
Medium Voltage Collection System | $5,730,000 | 
Project Substation and O&M Building | $5,350,000 | 
Meteorological Towers | $421,000 | 
PROJECT CONTINGENCY | $7,952,335 | 
OWNERS DEVELOPMENT COSTS | $320,000 | 
TOTAL EPC COSTS | $121,877,115 | $1,477
Owner’s Contingency | $16,000 | 
Electrical Interconnection | $7,000,000 | 
Electrical System Upgrade Costs/Substation Upgrades | $38,000,000 | 
Financing Fees | $4,875,085 | 
Working Capital | $1,218,771 | 
TOTAL NON-EPC COSTS | $51,109,856 | $620
TOTAL OVERNIGHT CAPITAL COSTS | $172,986,970 | $2,097

## Slide 21
Proposed Costs for ORTP Calculations: On-Shore Wind – Capital Cost Comparison
COST COMPONENT | Current CONE Re-calculation 2019$ (82.5 MW Nameplate) | Current CONE Recalculation 2019$/ kW-mo | 2016 CONE Recalculation 2016$ (52 MW Nameplate) | 2016 CONE Recalculation 2016$/ kW-mo | % Change
TOTAL EPC COSTS | $121,877,115 | $1,477 | $110,000,000 | $2,115 | -30%
TOTAL NON-EPC COSTS | $51,109,856 | $619 | $24,980,000 | $480 | 29%
TOTAL OVERNIGHT CAPITAL COSTS | $172,986,970 | $2097 | $134,980,000 | $2,596 | -19%

## Slide 22
Proposed Costs for ORTP Calculations: On-Shore Wind – Proposed O&M Costs
Fixed O&M | Proposed Values | 2025$/kW-mo (Nameplate)
O&M (LTSA plus ongoing O&M) | $34.91/kW-yr | $2.91
Site Leasing | $175/acre/yr | $0.83
Property Taxes | 1.0% | $0.10
Insurance | 0.3% of installed costs | $0.55

## Slide 23
Proposed Costs for ORTP Calculations: On-Shore Wind – O&M Cost Comparison
Fixed O&M | Current CONE Recalculation 2025$/kW-mo (Nameplate) | 2016 CONE Recalculation 2021$/kW-mo (Nameplate) | % Change
O&M (LTSA plus ongoing O&M | $2.91 | $3.00 | -3%
Site Leasing | $0.83 | $1.39 | -40%
Property Taxes | $0.10 | $0.21 | -52%
Insurance | $0.55 | $0.70 | -21%

## Slide 24
  Recommended size
    800 MW offshore wind facility
  Recommended location
    Massachusetts Offshore Wind Lease area interconnected at Brayton Point Station
  Capacity factor
    Initially calculated based on regional wind data for the Massachusetts Lease Areas.
    ISO-NE provided specific buoy data for the Massachusetts Lease areas which was utilized along with turbine data to calculate capacity factor.
    Wind speed was estimated at 10.25 m/s at hub height of 110 meters.
    Recommended capacity factor = 47%
Proposed Costs for ORTP Calculations: Off-Shore Wind - Assumptions

## Slide 25
Source: Data is based on Mott MacDonald confidential estimating database
Proposed Costs for ORTP Calculations: Off-Shore Wind – Proposed Capital Costs
COST COMPONENT | 2019$ | 2019$/kW (Nameplate)
Offshore Substation Platform | $465,000,000 | 
Install Submarine Export Cabling | $583,000,000 | 
Construct Landfall Transition Box | $134,000,000 | 
Interarray Cabling | $288,000,000 | 
Major Equipment | $2,333,000,000 | 
PROJECT CONTINGENCY | $380,300,000 | 
TOTAL EPC COSTS | $4,183,300,000 | $5,229
Owner’s Development Costs | $217,000,000 | 
Owner’s Contingency | $21,700,000 | 
Electrical Interconnection | $70,000,000 | 
Financing Fees | $167,332,000 | 
Working Capital | $41,833,000 | 
TOTAL NON-EPC COSTS | $517,865,000 | $647
TOTAL OVERNIGHT CAPITAL COSTS | $4,701,165,000 | $5,876

## Slide 26
Proposed Costs for ORTP Calculations: Off-Shore Wind – Proposed O&M Costs
Fixed O&M | Proposed Values | 2025$/kW-mo (Nameplate)
O&M (LTSA plus ongoing O&M) | $93.47/kW-yr | $7.79
Site Leasing | $665/MW | $0.06
Property Taxes | 1.0% | $0.28
Insurance | 0.3% of installed costs | $1.55

## Slide 27
  Recommended size
    20MW fixed mount based on recent new entry in New England
  Recommended location
    Windham County, CT
  Capacity factor
    Based on historical generation data from existing solar facilities in ISO-NE that were used to estimate an hourly generation profile
    The hourly generation profile is based on a daily average hourly capacity factor (i.e., one 24-hour generation profile for each month) of solar facilities in Massachusetts and Connecticut in each month during the last three year for all facilities with a commercial online date of June 2016 or later
    Recommended capacity factor = 17.2%
Proposed Costs for ORTP Calculations: Solar- Assumptions

## Slide 28
Proposed Costs for ORTP Calculations: Solar – Proposed Capital Costs
COST COMPONENT | 2019 $ | 2019$/kW (Nameplate)
TOTAL CIVIL/ STRUCTURAL/ARCHITECTURAL | $1,291,792 | 
TOTAL ELECTRICAL/ INSTRUMENTATION AND CONTROLS COST | $1,578,384 | 
TOTAL CONSTRUCTION MANAGEMENT | $804,250 | 
Major Equipment | $15,130,734 | 
Solar SCADA & Monitoring | $245,333 | 
Solar Testing & Energization | $143,130 | 
Other Indirect Costs | $2,476,527 | 
PROJECT CONTINGENCY | $1,123,225 | 
OWNERS DEVELOPMENT COSTS | $743,014 | 
TOTAL EPC COSTS | $23,536,389 | $1,177
Owner’s Contingency | $74,301 | 
Electrical Interconnection | $2,000,000 | 
Financing Fees | $941,456 | 
Working Capital | $235,364 | 
TOTAL NON-EPC COSTS | $3,251,121 | $162
TOTAL OVERNIGHT CAPITAL COSTS | $26,787,510 | $1,339
Source: Data is based on Mott MacDonald confidential estimating database

## Slide 29
Proposed Costs for ORTP Calculations: Solar – Proposed O&M Costs
Fixed O&M | Proposed Values | 2025$/kW-mo (Nameplate)
O&M (LTSA plus ongoing O&M) | $15.77/kW-yr | $1.31
Site Leasing | $10,000/MW | $0.83
Property Taxes | 1.0% | $0.34
Insurance | 0.3% of installed costs | $0.55

## Slide 30
  Recommended size
    150MW/300MWh
    Lithium ion facility
  Recommended location
    Kent County, Rhode Island
Proposed Costs for ORTP Calculations: Battery Storage - Assumptions
Reference: Mott MacDonald

## Slide 31
Source: Data is based on Mott MacDonald confidential estimating database
Proposed Costs for ORTP Calculations: Battery Storage – Proposed Capital Costs
COST COMPONENT | 2019 $ | 2019$/kW (Nameplate)
GRAND TOTAL CIVIL/ STRUCTURAL/ARCHITECTURAL | $423,748 | 
GRAND TOTAL ELECTRICAL/ INSTRUMENTATION AND CONTROLS COST | $1,293,969 | 
GRAND TOTAL CONSTRUCTION MANAGEMENT | $1,467,930 | 
Project Substation and O&M Building | $6,828,905 | 
Major Equipment | $101,550,688 | 
Solar Testing & Energization | $291,726 | 
Other Indirect Costs | $10,171,811 | 
PROJECT CONTINGENCY | $5,834,217 | 
Owners development costs | $964,834 | 
TOTAL EPC COSTS | $128,827,827 | $859
Owner’s Contingency | $48,242 | 
Electrical interconnection | $1,000,000 | 
Financing Fees | $5,153,113 | 
Working Capital | $1,288,278 | 
TOTAL NON-EPC COSTS | $7,489,633 | $50
TOTAL OVERNIGHT CAPITAL COSTS | $136,317,460 | $909

## Slide 32
Proposed Costs for ORTP Calculations: Battery Storage – Proposed O&M Costs
Fixed O&M | Proposed Values | 2025$/kW-mo (Nameplate)
O&M (LTSA plus ongoing O&M) | $25.90/kW-yr | $2.16
Site Leasing | $10,000/MW | $0.83
Property Taxes | 1.0% | $0.06
Insurance | 0.3% of installed costs | $0.24

## Slide 33
  Recommended size
  5 MW PV array and 5 MW, 10 MWh battery
  Recommended location
    Bristol County, Massachusetts
  PV capacity factor same as standalone solar facility (17.2%)
Proposed Costs for ORTP Calculations: Solar + Battery Storage - Assumptions

## Slide 34
Source: Data is based on Mott MacDonald confidential estimating database
Proposed Costs for ORTP Calculations: Solar + Battery Storage – Proposed Capital Costs
COST COMPONENT | 2019$ | 2019$/kW (Nameplate)
GRAND TOTAL CIVIL/ STRUCTURAL/ARCHITECTURAL | $613,488 | 
GRAND TOTAL ELECTRICAL/ INSTRUMENTATION AND CONTROLS COST | $531,828 | 
GRAND TOTAL CONSTRUCTION MANAGEMENT | $818,924 | 
Major Equipment | $7,233,944 | 
Solar SCADA & Monitoring | $219,684 | 
Solar Testing & Energization | $77,624 | 
Other Indirect Costs | $1,719,841 | 
PROJECT CONTINGENCY | $1,020,709 | 
Owners development costs | $650,651 | 
TOTAL EPC COSTS | $12,886,692 | $1,289
Owner’s Contingency | $65,065 | 
Electrical interconnection | $114,540 | 
Financing Fees | $515,468 | 
Working Capital | $128,867 | 
TOTAL NON-EPC COSTS | $823,839 | $82
TOTAL OVERNIGHT CAPITAL COSTS | $13, 710,631 | $1,371

## Slide 35
Proposed Costs for CONE Calculations: Solar + Battery Storage – Proposed O&M Costs
Fixed O&M | Proposed Values | 2025$/kW-mo (Nameplate)
O&M (LTSA plus ongoing O&M) | $46.17/kW-yr | $3.85
Site Leasing | $2,850/acre/yr | $0.83
Property Taxes | 1.0% | $0.07
Insurance | 0.3% of installed costs | $0.36

## Slide 36
Questions

## Slide 37
Proposed Energy and Ancillary Services Offsets - Overview

## Slide 38: Proposed E&AS Offset: E&AS Offset Methodology Overview
Simplified hourly dispatch (“dispatch model”) of the candidate unit’s energy and ancillary services awards, if applicable, in Day-Ahead (“DA”) and Real-Time (“RT”) to estimate E&AS revenues
Dispatched using adjusted historical DA and RT Locational Marginal Prices (“LMPs”)
Additional revenue adjustments made outside of the dispatch model:
  Add energy/reserve scarcity hour revenues to reflect expected scarcity conditions in 2025 (ORTP models), and scarcity conditions “at-criteria” (Net CONE models)
  Add expected PFP performance payments
  Expected ESI revenues presented separately
  FRM revenues presented separately to account for possible FRM Sunset

## Slide 39: Proposed E&AS Offset: E&AS Offset Methodology Overview (cont’d)
Used adjusted historical LMPs and real-time ancillary services prices as the basis of a simplified economic dispatch
  Hourly zonal DA and RT prices consistent with the location of each candidate unit
  CONE Dispatch model prices - historical DA and RT LMPs adjusted to:
    Remove the effects of recent long supply conditions with a Level of Excess (“LOE”) adjustment
    Remove the impact of energy/reserve revenue from scarcity hours in the historical DA LMPs and RT LMPs and RT reserves prices
  ORTP Dispatch model prices - historical DA and RT LMPs adjusted to:
    Remove the impact of energy/reserve revenue from scarcity hours in the historical DA LMPs and RT LMPs and reserves prices
    Does not include the LOE adjustment
Simplified Dispatch Model
  Excel-based dispatch with unit modeled as a price taker
  Used adjusted hourly DA and RT (hourly average of 5-minute) prices
  Construct an hourly offer for resource based on its economics (e.g., fuel * heat rate, variable O&M, emissions, and startup, etc.) and applies the FRM requirements if applicable
Calculating offset with and without the FRM
  Upon consideration, Concentric finds it appropriate to use historical FRM prices
  FRM market is generally large enough to absorb a unit of up to 375 MW
  Simple cycle, Aeroderivative, and Battery assumed to participate in the FRM based on their economics

## Slide 40: Proposed E&AS Offset: E&AS Offset ISO-NE Market Price Adjustment Overview
CONE | ORTP
Dispatch model uses ISO-NE energy and ancillary services prices from calendar years 2017 through 2019 adjusted for: Energy/reserve revenue scarcity hours adjustment LOE adjustment Historical FRM prices Other Adjustments Energy/reserve scarcity hours revenue is added back using H=15.3 PFP adjustment using expected H=15.3 at criterion for CONE units | Dispatch model uses ISO-NE energy and ancillary services prices from calendar years 2017 through 2019 adjusted for: Energy/reserve revenue scarcity hours adjustment Historical FRM prices Other Adjustments Energy/reserve scarcity hours revenue is added back using H=8.4 PFP adjustment using expected H=8.4 for ORTP units REC revenues

## Slide 41: Proposed E&AS Offset: Renewable Energy Credits
Average MA Class I REC Price for 2017, 2018, 2019 Indices
  Average of all trade dates through vintage year-end
  Adjusted to 2025$
Assume no in-state sale constraints; all renewable resources eligible for MA Class 1 REC Price
 | 2017 | 2018 | 2019
Average traded price through vintage year (2019 $) | $22.52 | $13.81 | $21.72
Average traded price through vintage year (nominal $) | $17.18 | $12.49 | $22.96
2017-2019 Average (2019 $) | $19.35 |  | 
2025$ | $ 21.79 |  | 

## Slide 42: Proposed E&AS Offset: Energy/Reserve Revenue Scarcity Hours Adjustment
The expected impact of energy and reserve shortage hours in the future are incorporated in a standalone energy/reserve scarcity hour adjustment outside of the E&AS dispatch model
Within the E&AS dispatch model, Concentric removed the price impacts of administrative shortage prices set by the Reserve Constraint Penalty Factor (RCPF) from the energy and real-time reserve prices
  Energy/reserve scarcity effects that reflected expected future conditions were added back outside of the E&AS dispatch model
  Separate energy/reserve scarcity hour revenue adjustments were used for CONE (at criterion) and ORTP (at excess supply conditions) units
Total RCPF dollars in the real-time LMP in the 2017-2019 period is $4,374.99 per MW
  In an efficient market, the day-ahead and real-time prices converge in expectation
  Convergence would include the expected amount of RCPF pricing that would impact the real-time LMPs
  Using a “perfect-expectation” assumption, $4,374.99 per MW would also be removed from the day-ahead prices
  Assuming the expectation of real-time scarcity is realized equally across all on-peak hours; the day-ahead scarcity adjustment downward is $4374.99/12,224 hours = $0.36/MWh

## Slide 43: Proposed E&AS Offset: Energy/Reserve Revenue Scarcity Hours Adjustment (cont.)
Day-ahead LMP |  |  |  |  | DA RCPF Adjustment |  |  |  | RCPF adjusted DA LMP |  | 
Year | Super Peak | Peak | Off-Peak |  | Super Peak | Peak | Off-Peak |  | Super Peak | Peak | Off-Peak
2017 | $43.88 | $36.36 | $29.36 |  | ($0.36) | ($0.36) | $0.00 |  | $43.52 | $36.00 | $29.36
2018 | $56.23 | $47.95 | $38.61 |  | ($0.36) | ($0.36) | $0.00 |  | $55.88 | $47.59 | $38.61
2019 | $38.08 | $33.54 | $27.53 |  | ($0.36) | ($0.36) | $0.00 |  | $37.72 | $33.18 | $27.53
Real-time LMP |  |  |  |  | RT RCPF Adjustment |  |  |  | RCPF adjusted RT LMP |  | 
Year | Super Peak | On | Off |  | Super Peak | Peak | Off-Peak |  | Super Peak | Peak | Off-Peak
2017 | $44.85 | $36.40 | $30.28 |  | ($0.76) | $0.00 | $0.00 |  | $44.08 | $36.40 | $30.28
2018 | $58.08 | $46.28 | $38.59 |  | ($4.94) | $0.00 | $0.00 |  | $53.13 | $46.28 | $38.59
2019 | $35.57 | $33.05 | $27.42 |  | $0.00 | $0.00 | $0.00 |  | $35.57 | $33.05 | $27.42
Super Peak hours are weekdays in HE 18-19 in all months and weekdays in HE 14-19 in June through September, excluding NERC holidays. Peak hours are non-Super Peak hours, Monday through Saturday in HE 8-23, excluding NERC holidays. Off-peak hours are all other hours.
Summary of impact of energy/reserve revenue scarcity hours adjustment
on day-ahead and real-time LMPs.

## Slide 44: Proposed E&AS Offset: Energy/Reserve Revenue Scarcity Hours Adjustment (cont.)
The energy/reserve revenue scarcity hours adjustment made to market prices in the dispatch model is added back separately in the financial model, based on the expected energy/reserve market revenues each resource would receive during scarcity hours
  For example, the unit with availability A, expected scarcity hours of H, and the $1,000 scarcity RCPF would have the following energy/reserve revenue scarcity hours adjustment : A*H*$1,000/MWh
Summary of Preliminary Energy/Reserve Revenue Scarcity Hours Adjustment 2025$/kW-mo (Nameplate) | 
Combined cycle CONE | $1.17
Simple cycle CONE | $1.25
Aeroderivative CONE | $1.17
Combined cycle ORTP | $0.64
Simple cycle ORTP | $0.64
Onshore wind ORTP | $0.64
Offshore wind ORTP | $0.64
Solar ORTP | $0.64
Battery ORTP | $0.64
Co-located Resource – ORTP | $0.64
  CONE unit H = 15.3
  because system is
  modeled at criterion
  ORTP unit H = 8.4
  because system is
  modeled at current conditions

## Slide 45: Proposed E&AS Offset: Level of Excess Adjustment
The LOE adjustment is designed to reflect a system at criterion
  See presentation of Deborah Cooke for discussion
For CONE units, the LOE adjustment is made to day-ahead and real-time energy prices and real-time reserve prices (TMSR, TMNSR, and TMOR) given the co-optimization of real-time energy and reserves
Hour Category | Jan 17 | Feb 17 | Mar 17 | Apr 17 | May 17 | Jun 17 | Jul 17 | Aug 17 | Sep 17 | Oct 17 | Nov 17 | Dec 17
High On-Peak | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 1.00 | 1.00 | 1.00 | 1.00 | 1.00 | 1.00 | 1.00
On-Peak | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 1.00 | 1.00 | 1.00 | 1.00 | 1.00 | 1.00 | 1.00
Off Peak | 0.98 | 0.99 | 0.99 | 0.99 | 1.00 | 1.00 | 1.00 | 1.00 | 1.00 | 1.00 | 1.00 | 0.99
Hour Category | Jan 18 | Feb 18 | Mar 18 | Apr 18 | May 18 | Jun 18 | Jul 18 | Aug 18 | Sep 18 | Oct 18 | Nov 18 | Dec 18
High On-Peak | 0.98 | 1.00 | 1.00 | 1.00 | 1.00 | 0.94 | 0.87 | 0.82 | 0.88 | 0.94 | 0.93 | 0.92
On-Peak | 0.98 | 1.00 | 1.00 | 1.00 | 1.00 | 0.95 | 0.90 | 0.88 | 0.95 | 0.96 | 0.95 | 0.95
Off Peak | 0.98 | 1.00 | 1.00 | 1.00 | 1.00 | 0.98 | 0.97 | 0.97 | 0.99 | 0.99 | 0.96 | 0.97
Hour Category | Jan 18 | Feb 18 | Mar 18 | Apr 18 | May 18 | Jun 18 | Jul 18 | Aug 18 | Sep 18 | Oct 18 | Nov 18 | Dec 18
High On-Peak | 0.98 | 1.00 | 1.00 | 1.00 | 1.00 | 0.94 | 0.87 | 0.82 | 0.88 | 0.94 | 0.93 | 0.92
On-Peak | 0.98 | 1.00 | 1.00 | 1.00 | 1.00 | 0.95 | 0.90 | 0.88 | 0.95 | 0.96 | 0.95 | 0.95
Off Peak | 0.98 | 1.00 | 1.00 | 1.00 | 1.00 | 0.98 | 0.97 | 0.97 | 0.99 | 0.99 | 0.96 | 0.97
Source: ISO-NE Presentation, July 2020

## Slide 46: Proposed E&AS Offset: Preliminary Pay-for-Performance Adjustment
Preliminary adjustment for Pay-for-Performance (PFP)
  H=15.3 for CONE units
  H=8.4 for ORTP units
  PPR = $5,455 (current rate being used as a placeholder)
 | Availability “A” value | Preliminary PFP Offsets 2025$/kW-mo (Nameplate)
Combined cycle CONE | 0.92 | $0.48
Simple cycle CONE | 0.98 | $0.84
Aeroderivative CONE | 0.92 | $0.48
Combined cycle ORTP | 0.92 | $0.39
Simple cycle ORTP | 0.92 | $0.39
Onshore wind ORTP | 0.92 | $0.39
Offshore Wind O | 0.92 | $0.39
Solar ORTP | 0.92 | $0.39
Battery ORTP | 0.92 | $0.39
Co-located Resource ORTP | 0.92 | $0.39

## Slide 47
Preliminary CONE Energy and Ancillary Services Offsets

## Slide 48: Preliminary CONE E&AS Offsets: Dispatch Methodology Overview for the Simple Cycle and Aero Units
Cost Assumptions
Next-day gas price at Algonquin City Gates RGGI prices SO2 prices
Unit Characteristics
Size, heat rate, VOM, emissions, and startup cost Physical characteristics: 1-hour minimum run time, quick start capability FRM award assumes 30% of unit can provide TMNSR FRM award assumes 70% of unit can provide TMOR
Economic Offer Price
Single offer block based on economic costs If offline, dispatch considers amortized startup cost and energy costs over one hour If online, dispatch only considers incremental production costs
Market Offer Price
Offer price is the same in day-ahead and real-time markets Dispatch/commitment of fast-start units is determined in the real-time market Day-ahead award is a financial position
FRM Hour
Offer Price = Max {economic offer, Daily Threshold Price}
Non-FRM Hour
Offer Price=economic offer

## Slide 49: Preliminary CONE E&AS Offsets: Dispatch methodology Overview for the Simple Cycle and Aero Units (cont.)
Energy, FRM, and Real-time Reserve Market Compensation
Day-Ahead Market
Clear for energy if DA Offer ≤ Day-ahead LMP adjusted for LOE and scarcity. Financial position where revenues = MW x (DA LMP – RT LMP) Startup costs amortized if the unit is offline and ignored if the unit is online Offer adjusted for Daily Threshold Price as appropriate 30% of capacity assigned TMNSR 70% of capacity assigned TMOR
Real-time Market
If RT Offer ≤ Real-time LMP: Clear for energy (no reserves) Compensation based on real-time LMP and unit capacity (single offer block) If RT Offer > Real-time LMP: Do not clear for energy Clear for reserves 30% of capacity designated TMNSR 70% of capacity designated TMOR Compensation for reserves depends on whether it is an FRM hour FRM hour: FRM price Non-FRM hour: real-time reserves price

## Slide 50: Preliminary CONE E&AS Offsets: Combined Cycle Dispatch Methodology
Cost Assumptions
Next-day gas price at Algonquin City Gates RGGI prices SO2 prices
Unit Characteristics
Size, heat rate, VOM, emissions, and $11,000 startup cost Physical characteristics: 2-hour minimum run time, quick start capability Duct-firing capability can provide synchronized reserves
Economic Offer Price
Two offer blocks Block 1: baseload capacity (MW total) Block 2: Duct firing ( MW total) If offline, dispatch considers amortized startup cost and energy costs over its 2-hour minimum run time If online, dispatch only considers incremental production costs
Market Offer Price
Offer Price = economic offer Offer price is the same in day-ahead and real-time markets Day-ahead award is a financial position Combined cycle does not participate in the FRM

## Slide 51: Preliminary CONE E&AS Offsets: Combined Cycle Dispatch Methodology (cont.)
Energy and Real-time Reserve market compensation
Day-Ahead Market
Clear for energy if DA Offer ≤ Day-ahead LMP adjusted for LOE and scarcity. Financial position where revenues = DA MW x (DA LMP – RT LMP) Startup costs amortized if the unit is offline and ignored if the unit is online Offer adjusted for Daily Threshold Price as appropriate
Real-time Market
If RT Offer block ≤ Real-time LMP: If block 1 clears for energy, the 2nd block is designated as TMSR If block 1 and block 2 both clear for energy, the unit cannot provide TMSR If RT Offer > Real-time LMP: Does not clear for energy Is not designated for TMSR

## Slide 52: Preliminary CONE E&AS Offsets: Summary of Preliminary E&AS Offsets for CONE Units
2025$/kW-mo | E&AS Revenues Without FRM | E&AS Revenues With FRM | Energy/Reserve Scarcity Revenue Adjustment | Pay-for-Performance Adjustment | Total Offsets Without FRM | Total Offsets With FRM
Combined Cycle | $4.99 | $4.99 | $1.17 | $0.48 | $6.64 | $6.64
Simple Cycle | $2.75 | $3.40 | $1.25 | $0.84 | $4.84 | $5.49
Aeroderivative | $0.73 | $2.09 | $1.17 | $0.48 | $2.39 | $3.74
Notes
ESI adjustments not included PFP includes a value of $5,455 as a placeholder consistent with the current Tariff value

## Slide 53
Questions

## Slide 54
Preliminary ORTP Energy and Ancillary Services Offsets

## Slide 55: Preliminary ORTP E&AS Offset Onshore Wind
82.5 MW onshore only wind facility located in central New Hampshire
Onshore wind generation profile
  Based on generation of installed onshore wind facilities in Maine and New Hampshire
  Adjusted upward to achieve 43.1% capacity factor
  Generation in simulation based on 24-hour generation profile, one for each month (12 total)
Onshore wind facility sells only energy in the New Hampshire Zone
  Half of the onshore wind facility’s simulated generation is offered into the day-ahead energy market
  All of the onshore wind facility’s simulated generation is offered into the real-time market
  Energy offered at -1 times the REC price and VOM assumed to be zero

## Slide 56: Preliminary ORTP E&AS Offset: Offshore Wind
800 MW offshore only wind facility located in a Massachusetts Offshore lease area in Southeastern Massachusetts, interconnecting at Brayton Point
Offshore wind generation profile
  Use onshore wind generation profile
  Adjusted upward to achieve a 47% capacity factor
  Generation in simulation based on 24-hour generation profile, one for each month (12 total)
Offshore wind facility sells only energy in the SEMA Zone
  Half of the offshore wind facility’s simulated generation is offered into the day-ahead energy market
  All of the offshore wind facility’s simulated generation is offered into the real-time market
  Energy offered at -1 times the REC price and VOM assumed to be zero

## Slide 57: Preliminary ORTP E&AS Offsets Solar
20 MW solar facility located in Windham County, Connecticut
Solar generation profile
  Based on generation of installed solar facilities in Massachusetts and Connecticut installed on or after January 2016
  17.2% capacity factor
  Generation in simulation based on 24-hour generation profile, one for each month (12 total)
Solar facility sells only energy in the Connecticut Zone
  Half of the solar facility’s simulated generation is offered into the day-ahead energy market
  All of the solar facility’s simulated generation is offered into the real-time market
  Energy offered at -1 times the REC price and VOM assumed to be zero

## Slide 58: Preliminary ORTP E&AS Offset: Battery Storage
150 MW/300 MWh lithium ion battery storage facility in Kent County, Rhode Island
Providing reserves was found to be preferable to energy arbitrage
Similar dispatch logic to the Simple Cycle and Aero except battery charges from grid in off-peak hours if dispatched for energy
$10/MWh assumed VOM on charging energy
Battery charges 5% of nameplate from the grid in off peak hours once a month to “top off” battery

## Slide 59: Preliminary ORTP E&AS Offset: Battery Dispatch Methodology Overview
Cost Assumptions
$10/MWh VOM for charging to reflect amortized battery warranty and degradation costs Battery re-charges in next HE 3-5 if dispatched in real-time
Unit Characteristics
150 MW battery with 300 MWh storage 86% roundtrip efficiency FRM award assumes 100% of unit can provide TMNSR Zero startup cost Battery is limited to one complete cycle per day (maximum generation of 0.86*300 = MWh per day)
Economic Offer Price
Single offer block based on economic costs If offline, dispatch considers amortized startup cost and energy costs over one hour If online, dispatch only considers incremental production costs
Market Offer Price
Offer price is 95th percentile in each year in the day-ahead and real-time markets, respectively given the assumed mode of operation Dispatch/commitment is determined in the real-time market Day-ahead award is a financial position
FRM Hour
Offer Price = Max {economic offer, Daily Threshold Price}
Non-FRM Hour
Offer Price=economic offer

## Slide 60: Preliminary ORTP E&AS Offset: Co-located Resource
  Co-located resource located in Bristol County, Massachusetts
    5 MW PV
    5 MW/10 MWh lithium ion battery with $10/MWh VOM on charging energy
    PV and battery are AC-coupled with two 5 MW DC-to-AC inverters
  Co-located resource market participation
    Sells only energy in the SEMA zone and offers at negative REC price
    For purposes of ISO-NE energy/AS market and Forward Capacity Market participation, the PV and battery are separate assets (non-dispatchable PV and a Continuous Storage Resource). This does not affect the financial model calculations.
    Each facility has its own interconnection agreement with rights to inject up to 5 MW into the ISO-NE grid
    Battery will charge exclusively from the PV array to capture the ITC. Onsite charging will occur without any interaction with the ISO-NE grid. REC revenue will accrue at 17.2% x nameplate x 8760 (solar CF)

## Slide 61: Preliminary ORTP E&AS Offset: Co-located Dispatch Methodology Overview
Cost Assumptions
PV: $0/MWh VOM Battery: $10/MWh VOM for onsite charging to reflect amortized battery warranty and degradation costs
PV array
Generation based on solar generation profile First 10 MWh generated is used to charge battery Any excess PV generation above 10 MWh (after battery charged) is injected into grid when generated
Battery
10 MWh battery is fully charged and discharged daily Injects 1/3 of stored energy in HE 18-20 (10 MWh total over 3 hours)
Market Participation
Offer = negative REC price Half of co-located facility’s generation is offered into the day-ahead market All of the co-located facility’s generation is offered into the real-time market

## Slide 62
2025$/kW-mo (Nameplate) | E&AS Revenues Without FRM | E&AS Revenues With FRM | Energy /Reserve Scarcity Revenue Adjustment | Pay-for-Performance Adjustment | REC Revenue | Total Without FRM/With FRM
Combined Cycle | $4.54 | N/A | $0.64 | $0.39 | $0 | $5.58
Simple Cycle | $2.46 | $3.23 | $0.64 | $0.39 | $0 | $3.50/$4.27
Onshore wind | $13.43 | N/A | $0.64 | $0.39 | $6.86 | $21.33
Offshore wind | $14.86 | N/A | $0.64 | $0.39 | $7.48 | $23.37
Solar | $4.95 | N/A | $0.64 | $0.39 | $2.74 | $8.73
Battery | $1.76 | $2.33 | $0.64 | $0.39 | $0.00 | $2.80/$3.37
Co-located | $2.10 | N/A | $0.64 | $0.39 | $1.37 | $4.51
Preliminary ORTP E&AS Offset: Summary of Preliminary E&AS and REC Offsets for ORTP Units
Notes
ESI adjustments not included PFP includes a value of $5,455 as a placeholder consistent with the current Tariff value

## Slide 63
Questions

## Slide 64
Summary and Next Steps

## Slide 65: Summary and Next Steps
Next Steps:
Continue to refine our evaluation and analysis of technologies for CONE and ORTP calculations
Present recommended financial assumptions
Deliverables for August Markets Committee meeting:
  Incorporate ESI assumptions and analysis into CONE and ORTP models
  Review financial assumptions
  Review DR and EE analysis and preliminary findings

## Slide 66
Appendices

## Slide 67: Proposed Costs for CONE Calculations: Combined Cycle Capital Cost Estimating Basis Summary
  Detailed cost estimate for construction based on modern construction techniques in fourth quarter 2019 dollars
  Costs developed utilizing the confidential MM cost estimating database which consists of actual cost estimates for several hundred power projects including both simple and combined cycle projects
  Combined Cycle Scope
    1x1 7HA.02-based Combined Cycle unit with an air-cooled condenser
    Located in New London County Connecticut
    Gas turbine quotation from OEM obtained
    A combined control, administration, warehouse building provided, all else is outdoors

## Slide 68: Proposed Costs for CONE Calculations: Combined Cycle Capital Cost Estimating Basis Summary
  Estimate scope broken up into major categories to reflect subcontract structure typical for the power industry in New England
  Direct Costs
    Major equipment prices from MM confidential database of costs, with specific gas turbine quotes for this estimate
    Labor rates based on union labor rates for the New London County, Connecticut area. Field construction installation labor hours for major equipment installation were developed from MM’s experience in estimating other projects

## Slide 69: Proposed Costs for CONE Calculations: Combined Cycle Capital Cost Estimating Basis Summary
  Indirect Costs
    Includes Construction Management, Temporary Facilities and Utilities, Construction Equipment and Operators, Indirect Construction Services, Insurance, Taxes, Permits, and Other Expenses, A/E Engineering, Startup and Testing, EPC Contractor Contingency, and Subcontractor Overhead & Profit
      Construction management includes a detailed listing of the planned construction management team for the EPC Contractor. Subcontract management costs are included within the indirect costs of the three major Subcontractors
      It is assumed that, as is typically the case today, the EPC contractor would subcontract some or all civil, mechanical, and electrical and I&C work and function as the general contractor. Therefore, in addition to the mark-up for all of the subcontractors, the EPC contractor includes a fee on top of the subcontractors as its fee for monitoring their work under the total EPC contract
  Owner’s Costs
    Owner’s Project Costs, Interest During Construction, Plant Spare Parts, and Facility Furnishings