## Slide 1
December 15, 2020 Reliability Committee Meeting
Dan Schwarting
(413) 535-4073 | dschwarting@iso-ne.com
Revisions For Alignment With NERC RAS Definition And NERC Standard PRC-012-2
Revisions To Planning Procedures 5-5, 5-0, and 5-1

## Slide 2
Project Title: Revisions To Planning Procedure 5-5
Proposed Effective Date: January 2021
Proposed changes to Planning Procedure 5-5 (PP5-5) will align New England’s planning procedures with upcoming changes in NERC requirements and terminology
  Change from “Special Protection System” (SPS) to “Remedial Action Scheme” (RAS)
  Align PP5-5 requirements with NERC Standard PRC-012-2 (effective January 1, 2021), including a new Attachment 1 for data collection
  Minor conforming changes also required in PP5-0 and PP5-1
Today’s presentation finalizes revisions to PP5-5, based on feedback received during and after the November 18 RC meeting

## Slide 3: Proposal
PP5-5 title and terminology will be changed to use RAS rather than SPS
  Individual RASs/SPSs may still use the term “SPS” to avoid the need to change nomenclature in the field
New Attachment 1 to PP5-5 will be created because PRC-012-2 requires the collection of information on new and functionally modified RASs
Each RAS-Entity will be required to submit a completed Attachment 1 for each existing RAS within 6 months of the effective date of PP5-5, in order for ISO-NE to populate a RAS Database

## Slide 4: Updates Since November 18 RC Meeting
Incremental changes to the Planning Procedures in response to stakeholder feedback

## Slide 5: Responses to Feedback at November 18 RC
Clarifications on definition of Automatic Control Scheme (ACS)
  Automatic under-frequency load shedding (UFLS), out-of-step tripping, and power swing blocking schemes are not considered ACSs
  Automatic sectionalization schemes (for example, restoring load tapped from a faulted line by re-energizing the non-faulted section) are considered ACSs
How will the requirements of PP5-5 apply to RASs located on or affecting non-BES/non-BPS/non-PTF facilities?
  Language added to refer to Section I.3.9 requirements
  Schemes located on facilities rated below 69 kV that could have a significant adverse impact on the transmission system or a Market Participant are subject to I.3.9 approval, but not NPCC/NERC review
Other wording changes and clarifications

## Slide 6: PP5-5 Changes Since November 18 RC
Procedure Section | Procedure Change | Reason for Change
Section I, ACS definition | Added exception for under-frequency load shedding (UFLS) schemes | UFLS schemes are not relied upon in normal system operations, and data on UFLS schemes is collected separately
Section I, ACS definition | Added exception for out-of-step tripping and power swing blocking schemes | These are schemes that do not detect faults, but are considered part of protection schemes.
Section 1, footnote 1 | Added example of load restoration from the non-faulted terminal of a faulted line as an example of an ACS | Schemes of this type could result in criteria violations if not adequately studied and considered in planning and operational decisions
Clarifications and changes to ACS definition

## Slide 7: PP5-5 Changes Since November 18 RC
Procedure Section | Procedure Change | Reason for Change
Footnote 2 | “Consistent with Section I.3.9 of the Transmission, Markets and Services Tariff, these requirements apply to any RAS or ACS monitoring or acting on facilities rated 69 kV or above subject to control of a Market Participant or Transmission Owner. They also apply to any RAS or ACS monitoring or acting on facilities rated below 69 kV that may have a significant adverse impact on the stability, reliability, or operating characteristics of the Transmission Owner’s transmission facilities, the transmission facilities of another Transmission Owner, or the system of a Market Participant.” | New footnote to clarify applicability of PP5-5 to RASs and ACSs that monitor or act upon non-BES, non-BPS, or non-PTF elements
Applicability of PP5-5 to non-BES/BPS/PTF RASs and ACSs

## Slide 8: PP5-5 Changes Since November 18 RC
Procedure Section | Procedure Change | Reason for Change
Section I | “… must meet the requirements of Section I.3.9 of the … Tariff and is subject to the Application Guidelines in Section III and Requirements in Section V of this procedure.” | Clarification that section V, covering review of additions, changes, and retirement of RASs, also applies to ACSs
Section III | Change from “failure to operate or misoperation” to “inadvertent operation or failure to operate” | Alignment with language used by NPCC and NERC
Section V | Addition of “or ACSs” to title | Clarification that Section V also applies to ACSs
Other clarifications & wording changes

## Slide 9: PP5-5 Changes Since November 18 RC
Procedure Section | Procedure Change | Reason for Change
Section V | Rewording of language pertaining to PRC-012 and Directory 7 | PRC-012 and Directory 7 apply to RASs, but not ACSs
Footnote 3 | Extended the definition of “functional modification” to ACSs | The footnote previously provided a definition of “functional modification” for RASs, but not for ACSs.
Notes | Addition of “for Tables I, II, and III on the following pages” | Clarification that these notes apply to the tables
Other clarifications & wording changes

## Slide 10: PP5-5 Changes Since November 18 RC
Procedure Section | Procedure Change | Reason for Change
Attachment 1 | In list of additional documentation, added an asterisk to the item pertaining to functional testing | This information is only required for NERC PRC-012, and not for ISO-NE’s review of ACSs or non-BES/non-BPS RASs
Attachment 1 | “These items are also not required for submissions related to ACSs, or for submissions for RASs that do not remediate, or for which an inadvertent operation or a failure to operate does not cause, performance issues on the BES or BPS.” | Certain items in the list of additional documentation are required by NERC PRC-012, but are not required in order for ISO-NE to review additions or changes. ISO-NE will collect this documentation only for BES/BPS RASs, where required by NERC/NPCC.
Attachment 1 changes

## Slide 11: Changes Discussed At Previous Meetings

## Slide 12: Summary of Proposed Changes: PP5-5
Procedure Section | Procedure Change | Reason for Change
Throughout PP5-5 | Replacement of “Special Protection System” or “SPS” with “Remedial Action Scheme” or “RAS” (and, in some instances, “Automatic Control Scheme” or “ACS”) | Consistency with NERC and NPCC terminology
Section I | Replacement of SPS definition with an abbreviated version of NERC’s RAS definition | Consistency with NERC and NPCC definition
Introduction of “RAS” Terminology

## Slide 13: Summary of Proposed Changes: PP5-5
Procedure Section | Procedure Change | Reason for Change
Section I | “In existing documentation on individual schemes, and in existing Planning Procedures and other documents, the term ‘Special Protection System’ may continue to be used. The use of this term does not indicate that a scheme is, or is not, classified as a RAS. Most, but not all, schemes whose name includes the term SPS also meet the NERC and NPCC definition of a RAS.” | Clarifies that the use of “SPS” in a scheme’s name does not affect its classification as a RAS. The term “SPS” is being retained only to avoid nomenclature changes for equipment in the field.
Use of “Special Protection System”

## Slide 14: Summary of Proposed Changes: PP5-5
Procedure Section | Procedure Change | Reason for Change
Section I | “An Automatic Control Scheme (ACS) is defined as any scheme that automatically changes system topology and is not classified as a RAS according to NERC and NPCC’s definitions, with the exception of any of the following types of schemes:” | Defines “Automatic Control Scheme” as a term for schemes that are similar to RASs but not classified as RASs.
Section I | Schemes that detect faults and clear faulted elements | Fault protection schemes are not considered ACSs.
Section I | Protection schemes that trip an element operating outside of its capabilities, unless that scheme is intended to allow planning or operation of the system in a state where the element would be loaded beyond its capabilities | The intent is not to classify all over-current protection schemes as ACSs. However, if this system is relied upon to allow operation beyond its limits, then it will be classified as an ACS.
How will “Non-RAS” schemes be treated?

## Slide 15: Summary of Proposed Changes: PP5-5
Procedure Section | Procedure Change | Reason for Change
Section I | Automatic reclosing schemes that re-energize an entire protection zone after a temporary fault has been cleared | Automatic reclosing is common on overhead transmission lines, and is not considered an ACS.
Section I | Controls that automatically switch shunt reactive devices in order to regulate system voltage or dynamic reactive device output | Standard automatic controls on shunt devices will not be considered ACSs.
Footnote 1 | Footnote provides examples of the types of schemes defined as ACSs. | Intended to clarify the definition of an ACS.
Section I | “ACSs are not RASs, and thus are not subject to NERC PRC-012 or NPCC Directory 7.” | Clarification of applicability of NERC, NPCC, and ISO-NE documents to ACSs
Section I | Updates to titles and designations of planning criteria documents NERC TPL-001, NPCC Directory 1, and ISO-NE PP3 | Updates for consistency with current titles and designations
How will “Non-RAS” schemes be treated?

## Slide 16: Summary of Proposed Changes: PP5-5
Procedure Section | Procedure Change | Reason for Change
Section II | Added reference to requirements in Sections IV and V | Clarification to the purpose of PP5-5
Section III | Clarification that effects of Type I SPSs may or may not be entirely within New England | Minor clarification
Section III | Replacement of name and definition of Type III SPS with Limited Impact RAS | Consistency with NERC and NPCC criteria
Section IV | New section, with requirement for RAS-Entities to submit Attachment 1 data within six months of PP5-5 implementation | Information is required for ISO-NE to populate a RAS Database, as per NERC PRC-012-2 Requirement R9
Change from “Type III SPS” to “Limited Impact RAS”

## Slide 17: Summary of Proposed Changes: PP5-5
Procedure Section | Procedure Change | Reason for Change
Section V, 1. | Proponents of new or functionally modified RASs must submit Attachment 1 data to ISO-NE | Data is required to analyze RAS design and populate the RAS Database
Section V, 2. | Proponents of new or functionally modified RASs must resolve any issues identified in ISO-NE’s review | Mitigation of any reliability risks introduced by the new RAS
Section V, 3. | Specific events to be examined in a System Impact Study (SIS) for an addition, functional modification, or a retirement of a RAS | Alignment of ISO-NE SIS with NERC’s requirements for review of RAS changes, as per PRC-012-2
Section V, 4. | New or functionally modified RASs must not be implemented before the ISO-NE and NPCC review processes are complete | Review ensures that the new or modified RAS does not cause an unacceptable risk to reliability
Requirements for Review of Additions, Changes, or Retirements

## Slide 18: Summary of Proposed Changes: PP5-5
Procedure Section | Procedure Change | Reason for Change
Tables I, II, and III | “For the purposes of this table, ‘RAS’ also refers to any other scheme subject to Section III of this procedure, as defined in the second paragraph of Section I.” | Clarification that application guidelines apply to non-RAS schemes as well as RASs
Table III | Removed reference to NPCC Directory 7 | Type III SPSs/Limited Impact RASs are specifically excluded from Directory 7’s security and dependability requirements
Attachment 1 | New attachment, consisting of a data collection form | Data collection required by NERC PRC-012-2 R1
Tables and Attachments

## Slide 19: Summary of Proposed Changes: PP5-0
Procedure Section | Procedure Change | Reason for Change
Introduction | Conforming change to the title of PP5-5 | Conformance with PP5-5’s new title
Introduction | Replacement of “Special Protection System” with “Remedial Action Scheme” | Consistency with NERC and NPCC terminology
Introduction | Updated description of PP5-5’s purpose | Consistency with PP5-5’s new purpose

## Slide 20: Summary of Proposed Changes: PP5-1
Procedure Section | Procedure Change | Reason for Change
References | Added reference to PP5-5 | PP5-5 is now referenced in Section 2.4 of PP5-1
Section 2.4 | “Any addition of, functional change in, or retirement of a Remedial Action Scheme or Automatic Control Scheme (as described in Section 1 of Planning Procedure 5-5) requires submission of a Proposed Plan Application.” | Previous language was overly broad, and could be read to require I.3.9 approval for any protection system change

## Slide 21: Conclusion
PP5-5 revisions will ensure ISO-NE’s compliance and RAS-Entities’ compliance with NERC Standard PRC-012-2
Information collection will allow ISO-NE to maintain an up-to-date and complete RAS Database
  This information would also help ISO-NE to appropriately evaluate the impacts of RASs on the power system, as required by PRC-012-2 and NPCC Directory 7

## Slide 22: Stakeholder Schedule
Stakeholder Committee and Date | Scheduled Project Milestone
Reliability Committee October 20, 2020 | Introduction and review of proposed revisions
Reliability Committee November 18, 2020 | Review of updates to proposed revisions
Reliability Committee December 15, 2020 | Final review of proposed revisions and vote
Participants Committee January 7, 2021 | Vote

## Slide 23
Dan Schwarting
(413) 535-4073 | dschwarting@iso-ne.com