## Slide 1
January 19, 2021 | Joint MC/RC webex
Carissa P. Sedlacek
Director, Planning Services | system planning
Initial Feedback on Modeling and Ability to Perform Phase 1 Studies
Future Grid Reliability Study

## Slide 2: Background
Since fall 2020, stakeholders at the NEPOOL Markets Committee (MC) and Reliability Committee (RC) have been developing a Framework document supporting their Future Grid Reliability Study (FGRS)
  The ISO has participated in the joint MC/RC meetings in an advisory role, answering technical questions as they arose
  At the September 1, 2020 meeting, the ISO explained its technical ability to support the various studies that may comprise the FGRS
On December 29, 2020, NEPOOL formally asked ISO-NE for feedback on the proposed FGRS Framework document studies and if the ISO had the capability to undertake the study work described as “Phase 1,” which would include:
  Production Cost Simulations
  Ancillary Services Simulations
  Resource Adequacy Screen
  Probabilistic Resource Availability Analysis

## Slide 3: Study Assessment Overview
The ISO agrees the FGRS is likely to uncover information useful to performing a gap analysis on what the future system might need in terms of operational needs and revenue sufficiency
It is the ISO’s understanding that stakeholders are focused on starting the Phase 1 study work as soon as possible
The ISO has the software tools to perform most, if not all, of the Phase 1 studies
  Gridview, EPECS, and MARS
To leverage expertise from past annual Economic Studies, with the exception of the Probabilistic Resource Availability Analysis, the study would use the ISO-NE staff that normally performs Economic Studies in accordance with Attachment K of the Tariff

## Slide 4: Study Assessment Overview, cont.
To support the Phase 1 studies as described, and within the timeframe requested, the ISO will not be able to support additional 2021 Economic Studies this year
  If a 2021 Economic Study was received, it would be performed after both the 2020 Economic Study is complete and FGRS Phase 1 is complete
When elements of the Phase 2 requests are further developed, the ISO will consider the requests regarding transmission modeling, particularly as the 2050 Transmission Study becomes more fully fleshed out
  The 2050 study may serve the same purpose as the Phase 2 transmission work, and the ISO may not be able to support concurrent studies in this area
As noted previously, the Phase 2 capacity market modeling work is not currently within the ISO’s toolbox, so the ISO recommends that stakeholders contract with an appropriate consultant

## Slide 5: Study Assessment Overview, cont.
This presentation outlines the ISO’s initial thoughts on the request to assess the extent and timing of its ability to fully conduct the FGRS Phase 1 study work
  Stakeholder feedback is welcome
Overall, the Framework document outlines the intentions of the FGRS, but certain assumptions will need additional clarity
  See next slides
Currently, the ISO anticipates being able to perform both its planned evaluation of the Pathways as directed by the Board (kicking off next month) and the FGRS Phase 1
  This assumes the scope of FGRS Phase 1 remains similar to that described in the Framework document, and that further details on the assumptions can be expeditiously and collaboratively resolved
    Additional Economic Study requests will impact the ISO’s ability to do all studies simultaneously
  Potential involvement of the ISO in FGRS Phase 2, other study requests, and/or orders from FERC may impact the ISO’s timing and ability to complete all tasks
    The ISO anticipates discussing the convergence of these study efforts further at the February PC meeting

## Slide 6: Detailed Feedback
Study Objective/Scope: Says “…current state energy and environmental laws…” but should also mention if current market rules should be in effect too
  ISO suggests setting the date for current laws and Tariff rules as December 31, 2020
Resource Adequacy Screen: Suggested language change. See red font. “Determine Installed Capacity Requirement (ICR) for each future scenario in preparation for the energy market simulation to ensure that LOLE is met for expected system loads (not peaks). Include the creation of marginal reliability index demand curves.”

## Slide 7: Detailed Feedback, cont.
Revenue Sufficiency Analysis: Says “For some matrix and alternative scenarios selected by the MC/RC, conduct a Forward Capacity Market simulation for a few “bookend” prices.”
  As stakeholders flesh out the framework as it relates to FGRS Phase 2, clarify what is intended and how it might be accomplished

## Slide 8: Detailed Feedback, cont.
System Security – Phase 2: General modeling considerations that stakeholders should be aware of are below:
  To the ISO’s knowledge, there is currently no model yet in existence for studying the detailed, operational dispatch needs of a system with significant inverter-based resources, interaction between the transmission and distribution systems, and evolving load profiles that may occur in the future
  The ISO is embarking on developing this model internally, but it is significantly more time-intensive and will be a multi-year effort
  The ISO plans to build an enhanced simulator model between 2020-2023, in phases and with staged deliverables, and looks forward to sharing more information on its plan with stakeholders
    The ISO is currently in the planning stage and intends to build a sustainable and robust model that can be used for a variety of simulations
System Security – Phase 2: As stakeholders flesh out the framework as it relates to FGRS Phase 2, determine/clarify the relationship to the 2050 Transmission Study and if the assumptions should be aligned

## Slide 9: Detailed Feedback, cont.
Stability Analysis: Suggest revising the sub-section to read as follows to better describe how the study should be done as peak load conditions may be very different than minimum load (spring, weekend, mid-day) conditions
  “Methods: Use the secure cases with respect to thermal capability and voltage to test what frequency response would look like with no changes to current practices. New England remains part of the Eastern Interconnection, but does not lean on neighbors for inertial pick-up because the underlying assumption is that the decline in rotating machines and growth in inverter-based resources in New England will also happen in neighboring control areas. Start with minimum load conditions (i.e., spring, weekend, mid-day) and consider also testing at peak loads.”
Stability Analysis: It may be useful, since a consultant is likely to perform this study work, to be more specific in the consequences to be avoided such as unintended tripping of load or generation, unintended protective relay operation, voltage or angular instability leading to a breakup of the grid, etc.

## Slide 10: Detailed Feedback, cont.
Alternative Case #5: Additional clarity regarding the consideration of new or under construction resources would be in the model
General comment regarding the resource mix for all scenarios: Detail seems to be missing. Need to know the location/interconnection point of all of new resources proposed to be studied.
General comment regarding Study Year: It is strongly recommended to use a single year such as 2040 rather than 2035 for some scenarios and 2040 for others. This would result in an efficiency in performing the analyses. Also, helps in comparing study results.

## Slide 11: Detailed Feedback, cont.
Assumptions Table: Clarify the use of the most up-to-date forecast. Given the study timing, the 2021 CELT load forecast could be used instead of the 2020 CELT load forecast.
Assumptions Table: Additional detail is needed to determine how load growth rate should be determined.
Assumptions Table: Demand reductions for EE, BTM-PV, etc. do not clearly indicate the metrics for reduction. More specifically, when the scenario indicates a reduction, there is a need to indicate what the reduction is from. For example, summer peak daytime hour?
Assumptions Table: Battery Storage resource characteristics are missing. Need to specify the type of battery to be used (e.g., 1, 2, 4 or more hour discharge, grid charged).
Assumptions Table: Clarify topology e.g. FCA 16 topology as a base modeling assumption? Add any transmission projects from the project list? Use 2019 NESCOE Eco Study transmission buildout? Include Cape Cod Cluster Study?
Assumptions Table: Clarify what the existing resource mix is based on. Perhaps FCA 15 results?

## Slide 12: Detailed Feedback, cont.
Assumptions Table: It is not clear if ISO-NE acquired DNV-GL solar and wind profiles should be used, as appropriate, in this study.
Assumptions Table: For the MARS runs, proxy units need to be defined. They may be multiple types of resources, if desired. Resource characteristics will need to be defined.
Assumptions Table: Should additional resource retirements be considered if certain resources or resource types do not run in the Gridview simulations? Or is having these low/no capacity-factor resources remain in the MARS model acceptable?

## Slide 13: Detailed Feedback, cont.
Section VI - Timing - Preliminary Schedule – Phase 1: The schedule seems aggressive but achievable if there are no delays or changes in assumptions/scenarios. However, it should be noted that:
  The ISO is conducting the 2020 National Grid Economic Study request with an anticipated finish date of June 1, 2021.
  FGRS assumptions are defined but raw and need further refinement before any studies can commence. This may take 1-2 months at the onset of the Phase 1 work.

## Slide 14: Detailed Feedback, cont.
Deliverables: Says “…deliverables will include: 1) periodic status updates to and consultations with the MC/RC ; 2) a PowerPoint presentation and written report on the preliminary production cost simulation results; and 3) a final PowerPoint presentation and written report on the Study results and key findings and observations.” Deliverables should clarify if there is a separate report for Phase 1 work and Phase 2 work.
  With regards to Phase 1 study work, the ISO plans on reporting its progress monthly at the RC, similar to how working groups report on their assignments. Detailed presentations of interim and final results could be held via additionally scheduled MC/RC meetings, with advance notice to members.

## Slide 15: Closing Thoughts
The FGRS Phase 1 studies are well within the ISO’s area of expertise and the ISO is willing to perform these analyses
Timing to conduct the FGRS Phase 1 study will depend on the final clarity of the assumptions and ability to provide necessary model input data in a timely manner
The ISO looks forward to continued discussions with stakeholders as the FGRS Framework document is finalized

## Slide 16: Next Steps
The ISO will continue to review the FGRS Phase 1 portion of the Framework document to identify additional areas of clarification
  It may take 2-3 months to fully develop and define all study inputs
  Stakeholders to designate whom the ISO should work with in this regard
For the February MC/RC meeting, the ISO will develop a detailed plan for conveying FGRS Phase 1 study updates
  Interim updates
  Draft results
  Final results
Stakeholders may consider submitting a request to ISO-NE to perform the FGRS Phase 1 studies as 2021 Economic Request
  Due April 1