## Instructions
Alternative Scenario Proponents:
1 | Please use this form to submit your assumptions for your alternative scenario.
2 | In the blank row below the three main scenarios, please only include information for assumptions that differ from any of the three base scenarios.
3 | A blank cell for your alternative scenario means that the specific assumption from the base scenario will be used.
For example, if the alternative scenario is based on a different assumption for new ties than what is included in the three base scenarios, then the alternative scenario proponent should fill in the cell for new ties. That alternative assumption would then take the place of the external ties assumption in the three base scenarios for purpose of the alternative case. If the alternative scenario is not based on a different assumption for new ties than what is included in the three base scenarios, then the alternative scenario proponent should leave the cell blank in the column for new ties.

## Assumptions
| Load-Related | [5 empty] | Infrastructure | Resource Portfolio | [12 empty] | Marginal Cost Inputs
Scenario | Gross Load | Energy Efficiency | Behind-the-Meter Distributed Energy Resources | Storage | Heating | Transportation | Transmission Toplogy / Interface Transfer Limits | Existing Resources | Existing External Ties Import Limits | Existing External Ties Export Limits | New Ties | Retirements | Additions | Storage Approach | Resource Availability | Profiled Resource Production | Weather Year | Active Demand Response | Curtailment Prices / Threshold Prices | Reserve Margin / Capacity Assessment | Fuel Price Forecasts | Seasonal Volatility Adjustments | Emission Allowance Price Forecasts
Matrix Scenario 1 | Gross load to be calculated from 2021 CELT extrapolated with a 3-year CAGR to 2040 Net Load will be calculated after as: Gross – EE – BTM + transport + heat; Both subject to change according to profile used which is scaled using peak load value | Peak Reduction and MW Annual Energy Reduction to be calculated based on 2021 CELT | Peak Reduction and nameplate MW to be calculated based on 2021 CELT | Incremental Storage: 2000 MW Aggregated by RSP Zone based on grid-scale storage in the ISO-NE queue 4-hour duration 86% efficiency for battery storage Responds to LMP Provides System Capacity Provides regulation and reserves | Peak: 5,214 MW Demand: 9.6 TWh Projections by load zone Profile based on 2015 weather year but can be adjusted 2035 building heat electrification assumptions represent a top-down projection of primarily air-source heat pump (ASHP) adoption resulting in electrification of ~18% of non-electric building heat (compared to <1% today) and including a 14% decline in building heat demand due to efficiency gains. | Peak: 1,817MW Demand: 7.3TWh Hourly shapes, broken down by subarea proportional to population; Generally charging is lowest in the morning and peaks at hour ending 18:00; Flex charing per ISO's proposed methodology, amount TBD 2035 EV assumptions represent a top-down projection of electric vehicle adoption. It focuses on light-duty vehicles and is absent of significant incremental policy support, including policies designed to impact EV charge timing. The EV load represents 2.2 million light-duty vehicles electrified by 2035 in ISONE (~19% of vehicle stock, 50% of new sales). | Assume unconstrained internal transmission but interfaces at the Regional System Plan zonal level will be monitored at 2029 limits (FCA 16 topology) | FCA 15 resources with a CSO, Modeled at their SCC value (or CSO if no SCC) | Historical flows on external ties with existing limits monitored; NY exchange at 0MW | Historical flows on external ties with existing limits monitored; NY exchange at 0MW | NECEC at 1,200 MW nameplate | FCA 15 cleared retirements plus, all New England coal units, and 75% of the conventional New England oil, including dual-fuel units, based on age | Incremental Additions: 1,330 MW Land-Based Wind 8,009 MW Offshore Wind (assumes existing 29MW for Block Island) 6,425 MW Solar PV, >5MW (assumes existing 1666MW and 697MW assumed by ISO for 2020) Renewable additions include announced additions, as well as generic additions to bridge the gap between what is announced and what may be required to meet announced policy needs (i.e. RPS/CES requirements). Generic utility-scale PV, onshore wind, and offshore wind installed quantities/locations selected based on implied needs in policies goals to achieve a balanced portfolio across renewables types and zones that could plausibly be constructed. Offshore Wind interconnected proportional to ISO-NE’s queue at NESCOE 2019 Economic Study locations for scenario 8000_1 | See Storage under Load Assumptions; $3/MWh variable O&M costs in each directions will be reflected in the dispatch of batteries; pumped storage will be modeled consistent with historical experience | Same as used in FCA 15 Need for MARS runs only (EFORd and Maintenance Hours) | DNV-GL weather profiles for onshore wind, offshore wind, and PV | 2019 | FCA 15 | Import Priority | 120% of the first contingency in ten minutes split between Ten-Minute Spinning Reserve (TMSR) = 50% Ten-Minute Non-Spinning Reserve (TMNSR) = 50% | EIA’s 2020 AEO Base Forecast | Consistent approach pending agreement | NOX = $ 4.00 /ton SOX = $ 2.00 /ton CO2 = $33.52 /ton
Matrix Scenario 2 | Gross load to be calculated from 2021 CELT extrapolated with a 3-year CAGR to 2040 Net Load will be calculated after as: Gross – EE – BTM + transport + heat; Both subject to change according to profile used which is scaled using peak load value | Peak Reduction and MW Annual Energy Reduction to be calculated based on 2021 CELT | Peak Reduction and nameplate MW to be calculated based on 2021 CELT | New Storage Capacity: 3,940 MW Range of 1-hr to 8-hr discharge capability at 90% efficiency. All storage in-market, responds to LMP. | Heating Peak MW 2,991 MW Heating Demand: 6.6 TWh Heat pump forecasts based on heating sector emission targets combined with census population data kW peak and annual kWh per heat pump based on ISO “Final Draft 2020 Heating Electrification Forecast” | EV contribution to winter 8PM peak: 3,578 MW EV Demand: 18.5 TWh EV stock based on forecast total vehicle miles and transportation sector emission targets EV demand profiles based on ISO-NE “Final Draft 2020 Transportation Electrification Forecast”, adjusted to account for more coordinated charging | Assume unconstrained internal transmission but interfaces at the Regional System Plan zonal level will be monitored at 2029 limits | Same as Scenario 1 | Historical flows on external ties with existing limits monitored | Historical flows on external ties with existing limits monitored | NECEC (1,200 MW nameplate) and one additional 1,000 MW tie injecting into Northern New England | Retirements: 8,400 MW fossil fuel units (including all remaining coal & oil). Fossil fuel unit retirements based on age, heat rate, market revenues, and emissions targets. | Incremental Additions: 7,290 MW Utility Scale PV 9,469 MW Distributed PV 1,500 MW Onshore Wind 7,904 MW Offshore Wind Total Capacity: 8,820 MW Utility Scale PV 11,899 MW Distributed PV 2,803 MW Onshore Wind 7,934 MW Offshore Wind | Storage capacity added as needed as a balancing resource Storage operation is not on a fixed schedule, charge/discharge is an output of hourly model driven by wholesale energy prices. $3/MWh variable O&M costs in each directions will be reflected in the dispatch of batteries; pumped storage will be modeled consistent with historical experience | Same as Scenario 1 | Same as Scenarios 1 and 3. DNV-GL weather profiles for onshore wind, offshore wind, and PV | final determination based on review of DNV-GL dataset | Same as Scenario 1 | Consistent approach pending agreement | Same as Scenario 1 | EIA’s 2020 AEO Base Forecast | Same as Others | Same as Others
Matrix Scenario 3 | Net Summer Peak Load: 39,985 MW (July at 6pm) Net Winter Peak Load: 42,525 MW (January at 6pm) Annual Net Load: 182.5 TWh (including Energy Efficiency, Rooftop Solar PV*, and new Heating and Transportation loads) (Total energy 198.5 TWh less Rooftop Solar PV 16 TWh = 182.5 TWh) Hourly, zonal load forecast for 2040 from EnergyPATHWAYS model output from MA EEA 80x50 – adjusted to move rooftop solar PV to load side. EnergyPATHWAYS is a scenario analysis tool that is used to develop economy-wide energy demand scenarios. It is used to determine the demand for fuels (electricity, pipeline gas, diesel, etc.) over time, subject to economy-wide emissions constraints. also produces an hourly (8760) electricity load shape for each of the six New England states. | n/a Energy Efficiency is already reflected in the net load forecast discussed above (estimated amounts are unavailable) | Rooftop Solar PV: 12,671 MW Nameplate Total (~16.1 TWh Annual Gen) (8,870 MW Nameplate Incremental Rooftop Solar PV) Both Rooftop PV and Ground Mounted PV modeled as supply in capacity expansion model. However, Rooftop PV is included in Net Demand calculation. | Flexible Load representing approximately 50% of EVs with capability to delay charging by up to 8 hours. Values provided in data file with month-hour average flexible load impacts for each state. Values should be added to the 8760 load profile. | 38.9 TWh (embedded in load forecast from EnergyPATHWAYS) (Primary fuel type emissions reduced by approximately two-thirds relative to 2020) | Transportation 40.0 TWh (embedded in load forecast from EnergyPATHWAYS) (Primary fuel type emissions reduced by approximately two-thirds relative to 2020) | Zonal transfer limits from RIO[1] model results were mapped to the system topology used in this study: RIO had six New England state zones, plus New York, Hydro Quebec, and New Brunswick. RIO included economic transmission expansion from 2020-2050 based on $/MW-mile cost assumptions drawn from ReEDS[2] documentation | Same as Others - FCA 15 resources with a CSO, Modeled at their SCC value (or CSO if no SCC) - Resource Mix from RIO model output from MA EEA 80x50 | Historical flows on external ties with existing limits monitored | Historical flows on external ties with existing limits monitored | NECEC (1,200 MW nameplate) and one additional 1,000 MW tie injecting into Northern New England 450 MW increase in transfer limit between NY and ISO-NE (subject to continued review of zonal transfer limits from RIO model results) | FCA 15 cleared retirements plus, all remaining Coal, Oil and Refuse (subject to continued review of resource mix from RIO model results) | Total Capacity: 15,467 MW GroundMount PV 8,032 MW Offshore (Fixed) 8,601 MW Offshore (Floating) 600 MW Battery Storage (subject to continued review of resource mix from RIO model results) | Batteries (600MW) Similar to other scenarios, preference for Pumped Storage and Batteries to be economically dispatched. $3/MWh variable O&M costs in each directions will be reflected in the dispatch of batteries; pumped storage will be modeled consistent with historical experience. Interested in sensitivity with $2/MWh variable O&M costs for battery storage and $0.60/MWh for pumped storage. | Same as Others | Same as Others – DNV-GL weather profiles for onshore wind, offshore wind, and PV | RIO - 2012 Weather Year (open to comparability) (Preference for latest available resource production) | Same as Others (See also Flexible Load under Storage) | Open to adopting consistent approach | Same as Scenarios 1 and 2 | Same as Others | Same as Others | Same as Others
Alternative Scenario A Bi-Directional Transmission (National Grid) | [8 empty] | Historical flows for existing external ties to Quebec as in the B_Track sensitivity of the 2020 Economic Study (see Dec 17 PAC presenation p. 24-25); NY exchange at 0MW | NY exchange at 0MW | Add uncapped exchange between Quebec and NEMA; Use iterative approach for modeling exchange profile and tracking storage accounting according to 2020 Economic Study sensitivities presented at Dec PAC
Alternative Scenario B Vehicle to Grid (Multi Sector A) | Same as NESCOE 2040, but EE included in Gross Load for study purposes only. Still assumed as a supply resource in markets for the capacity screen. Amount of cleared EE vs. total EE in the same proportion as we see today. |  | see: EV storage | [9 empty] | EV storage: 100 GW at 2 hours available to grid. Based upon one quarter of a 100 kWh battery per vehicle. 8 million EV in New England by 2040 | Charging focused on periods of renewable curtailment; discharging at a price slightly lower than natural gas-fired resources
Alternative Scenario C Nuclear Retirement (NextEra/Dominion) | [11 empty] | Retire all remaining nuclear by 2035
Alternative Scenario D 100% clean electricity (Anbaric) | same as Matrix Scenario 3 | same as Matrix Scenario 3 | same as Matrix Scenario 3 | same as Matrix Scenario 3 on supply side to accommodate additions & retirements | same as Matrix Scenario 3 | same as Matrix Scenario 3 | same as Matrix Scenario 3 open to matching others | same as others upon reaching consensus values here the additions can be adjusted to be 'net' rather than 'total' values |  |  | same as Matrix Scenario 3 | same as Matrix Scenario 3 plus retire all remaining fossil | (based on Matrix Scenario 3 total net load of 169.8 TWh) final resource mix (can be adjusted to 'net' additions need final resource mix assumption) 26,300 MW OSW 1,400 MW LBW 52,100 MW solar PV 600 MW hydro 970 MW hydro imports from (NECEC) similar mix can be prepared for National Grid 2035 & Eversource 2040 cases based on their annual net load tally; seems to be 150 TWh and 139.1 TWh respectively w. common basis as Matrix Scenario 3 = 169.8 TWh (please confirm) | (based on Matrix Scenario 3 total net load of 169.8 TWh) 7,000 MW 4hr storage 10,000 MW 8hr storage 60,700 MW 36hr storage total: 2,293.2 GWh of battery storage similar mix can be prepared for National Grid 2035 & Eversource 2040 cases based on their annual net load tally; seems to be 150 TWh and 139.1 TWh respectively w. common basis as Matrix Scenario 3 = 169.8 TWh (please confirm) | same as others | willing to use same as others preference to use DNV GL 20 year load & production data for weather year (Stochastic Engine work @ ISONE) | present additions and storage values based on 2018; would prefer common weather year for all studies and willing to use consensus weather year (determines load profile, resource mix & storage)
Alternative Scenario E onshore/ offshore grids (Anbaric) | same as Alternative Scenario #5 | same as Alternative Scenario #5 | same as Alternative Scenario #5 | same as Alternative Scenario #5 | same as Alternative Scenario #5 | same as Alternative Scenario #5 | approach to topology is same as others -- more OSW interconnected to Boston and CT (can advise once base case assumptions on geographic split of OSW interconnection MW is available) | same as Alternative Scenario #5 |  |  | same as Alternative Scenario #5 | same as Alternative Scenario #5 | same as Alternative Scenario #5 more OSW interconnected to Boston and CT (can advise once base case assumptions on geographic split of OSW interconnection MW is available) | same as Alternative Scenario #5 | same as Alternative Scenario #5 | same as Alternative Scenario #5 | same as Alternative Scenario #5
[7 empty] | [1] | RIO is a capacity expansion model that uses hourly reserve margin constraints by zone and optimizes the portfolio for operations and investment decisions, subject to Renewable Portfolio Standard and power sector carbon emissions constraints, among others.
[7 empty] | [2] | The Regional Energy Deployment System (ReEDS) is a National Renewable Energy Laboratory's capacity planning model for the power sector. For more information, see https://www.nrel.gov/analysis/reeds/.
[7 empty] | [1] | The RIO resource mix results from the MA EEA 80x50 study were optimized every five years from 2020-2050, with the 2040 resource mix represented here.