## Slide 1
September 1, 2021 | RC WEBEX
Fei Zeng
Technical manager | Resource Studies and Assessments
Reliability Committee Meeting
Tie Benefits Study Results For Capacity Commitment Period 2025-2026 Sixteenth Forward Capacity Auction (FCA 16)

## Slide 2: Objective
To review the tie benefits study results for the Capacity Commitment Period (CCP) 2025-2026, associated with Forward Capacity Auction (FCA) 16
  Total tie benefits for New England
  Tie benefits contribution associated with individual or group of interconnection(s)
    Maritimes (MT)
    HQ Phase II (Ph II)
    Highgate
    New York AC ties (NY-AC)
    Cross Sound Cable (CSC)
Note: Acronyms not defined are spelled out in Appendix V

## Slide 3: Background
The ISO presented its FCA 16 transmission transfer capabilities and Capacity Zone development to the Reliability Committee (RC) on March 16, 2021
  https://www.iso-ne.com/static-assets/documents/2021/03/a9_fca_16_transmission_transfer_capability_and_capacity_zonal_development.pdf
The ISO presented its determination of Capacity Zones for FCA 16 to the Power Supply Planning Committee (PSPC) on May 20, 2021
  https://www.iso-ne.com/static-assets/documents/2021/05/a02_2021-05-20_pspc_review_objective_criteria_testing_for_capacity_zone_determinations.pdf
  Import-constrained Capacity Zone of Southeast New England (SENE) (includes Northeast Massachusetts/Boston & Southeast Massachusetts/Rhode Island Load Zones)
  Export-constrained Capacity Zones of:
    Maine, and
    Northern New England (NNE) (includes Maine, New Hampshire and Vermont Load Zones)
The ISO presented detailed tie benefits study assumptions to the PSPC on June 29, 2021
  https://www.iso-ne.com/static-assets/documents/2021/06/a05_pspc_2021_06_29_tie_benefit_assumptions_to_be_used_in_fca16_icr_calculations.pptx
  Detailed study methodology and assumptions are included in Appendices I, II and III to this presentation

## Slide 4: Background, cont.
The ISO presented the detailed FCA 16 tie benefits study results to the PSPC on July 27, 2021
  https://www.iso-ne.com/static-assets/documents/2021/07/a02_pspc_2021_07_27_fca_tie_benefits.pptx
Transmission transfer capability limits associated with Capacity Zones are relaxed in the tie benefits study
Transmission transfer capability limit of Boston import (5,250 MW) is also relaxed in the tie benefits study
  The Boston and SENE import interfaces share the same N-1 transmission constraint
    338 (Tewksbury-Woburn) 345 kV line
  The constraint is addressed by a Local Sourcing Requirement for SENE as an import-constrained Capacity Zone

## Slide 5: Summary of Tie Benefits Study Results
Interconnection | FCA 16 Tie Benefits Amount (MW)
Maritimes | 478
HQ Phase II | 923
Highgate | 142
New York AC ties | 287
Cross Sound Cable (CSC) | 0
Total Tie Benefits | 1,830

## Slide 6: Recap of Tie Benefits Calculation Process*
Process 1
  Calculate the tie benefits values for all possible interconnection states using isolated New England system as the reference
Process 2
  Calculate initial total tie benefits for New England from all neighboring Control Areas
Process 3
  Calculate initial tie benefits for each individual neighboring control area
  Pro-rate tie benefits values of individual Control Areas based on the total tie benefits, if necessary
Process 4
  Calculate initial tie benefits for individual interconnection or group of interconnections
  Pro-rate tie benefits values of individual interconnection or group of interconnections based on the individual Control Area tie benefits, if necessary
Process 5
  Adjust tie benefits of individual interconnection or group of interconnections to account for firm capacity imports
Process 6
  Calculate the final tie benefits for each individual neighboring Control Area
Process 7
  Sum the final total tie benefits for New England from each individual neighboring Control Areas
*The tie benefits calculation process is documented in Section III.12.9 of the Tariff, available at: https://www.iso-ne.com/static-assets/documents/2014/12/mr1_sec_1_12.pdf

## Slide 7: FCA 16 Tie Benefits Study detailed calculations

## Slide 8: Process 1 Calculation of Tie Benefits for All Interconnection States
X – disconnected √ - connected
Interconnection State | Description | Interconnection Status |  |  |  |  | LOLE | Equivalent TB (MW)
 |  | Maritimes | Ph II | Highgate | NY-AC | CSC |  | 
1 | Cut All | x | x | x | x | x | 0.42009 | 0
2 | Cut None | √ | √ | √ | √ | √ | 0.09989 | 1,830
3 | Cut MT | x | √ | √ | √ | √ | 0.13961 | 1,385
4 | Cut Ph II | √ | x | √ | √ | √ | 0.19016 | 965
5 | Cut Highgate | √ | √ | x | √ | √ | 0.11072 | 1,695
6 | Cut NY-AC | √ | √ | √ | x | √ | 0.11068 | 1,695
7 | Cut CSC | √ | √ | √ | √ | x | 0.09989 | 1,830
8 | Cut MT & Ph II | x | x | √ | √ | √ | 0.25972 | 585
9 | Cut MT & Highgate | x | √ | x | √ | √ | 0.15226 | 1,255
10 | Cut MT & NY-AC | x | √ | √ | x | √ | 0.16143 | 1,175
11 | Cut MT & CSC | x | √ | √ | √ | x | 0.13961 | 1,385
12 | Cut Ph II & Highgate | √ | x | x | √ | √ | 0.20820 | 850
13 | Cut Ph II & NY-AC | √ | x | √ | x | √ | 0.23434 | 715
14 | Cut Ph II & CSC | √ | x | √ | √ | x | 0.19016 | 965
15 | Cut Highgate & NY-AC | √ | √ | x | x | √ | 0.12386 | 1,535
16 | Cut Highgate & CSC | √ | √ | x | √ | x | 0.11072 | 1,695
17 | Cut NY-AC & CSC | √ | √ | √ | x | x | 0.11068 | 1,695
18 | Cut MT, Ph II & Highgate | x | x | x | √ | √ | 0.27907 | 490
19 | Cut MT, Ph II & NY-AC | x | x | √ | x | √ | 0.36259 | 190
20 | Cut MT, Ph II & CSC | x | x | √ | √ | x | 0.25972 | 585
21 | Cut MT, Highgate & NY-AC | x | √ | x | x | √ | 0.18037 | 1,040
22 | Cut MT, Highgate & CSC | x | √ | x | √ | x | 0.15226 | 1,255
23 | Cut MT, NY-AC & CSC | x | √ | √ | x | x | 0.16143 | 1,175
24 | Cut Ph II, Highgate & NY-AC | √ | x | x | x | √ | 0.26584 | 555
25 | Cut Ph II, Highgate & CSC | √ | x | x | √ | x | 0.20820 | 850
26 | Cut Ph II, NY-AC & CSC | √ | x | √ | x | x | 0.23434 | 715
27 | Cut Highgate, NY-AC & CSC | √ | √ | x | x | x | 0.12386 | 1,535
28 | Cut MT, Ph II, Highgate & NY-AC | x | x | x | x | √ | 0.42009 | 0
29 | Cut MT, Ph II, Highgate & CSC | x | x | x | √ | x | 0.27907 | 490
30 | Cut MT, Ph II, NY-AC & CSC | x | x | √ | x | x | 0.36259 | 190
31 | Cut MT, Highgate, NY-AC & CSC | x | √ | x | x | x | 0.18037 | 1,040
32 | Cut Ph II, Highgate, NY-AC & CSC | √ | x | x | x | x | 0.26584 | 555

## Slide 9: Process 2 Calculation of Initial Total Tie Benefits
Compare state 1 (without any ties) and state 2 (with all the ties)
  Total tie benefits = 1,830 MW
  This value is subject to the adjustment later to account for firm capacity imports

## Slide 10: Process 3 Calculation of Initial Tie Benefits for Neighboring Control Areas
All interconnections connected to a given neighboring Control Area are grouped together to represent the state of interconnection between New England and that neighboring Control Area. The simple average of values for all the interconnection states represents the tie benefits of the target neighboring Control Area (four states for each area)
Individual Control Area tie benefits calculations
  Proration is required since the sum of the average contribution from each Control Area (470.0 + 1047.5 + 282.5 = 1,800) is not equal to the total tie benefits of 1,830 MW calculated in Process 2
 | Tie Benefits Contribution under Different Scenarios |  |  |  | Average | After Proration
Maritimes (MW) | 1 vs 32 | 2 vs 3 | 12 vs 18 | 17 vs 23 | 470.0 | 470.0 x 1,830/1,800 = 478
 | 555 | 445 | 360 | 520 |  | 
Quebec (MW) | 1 vs 23 | 2 vs 12 | 3 vs 18 | 17 vs 32 | 1,047.5 | 1,047.5 x 1,830/1,800 = 1,065
 | 1,175 | 980 | 895 | 1,140 |  | 
New York (MW) | 1 vs 18 | 2 vs 17 | 3 vs 23 | 12 vs 32 | 282.5 | 282.5 x 1,830/1,800 = 287
 | 490 | 135 | 210 | 295 |  | 

## Slide 11: Process 4 Calculation of Tie Benefits for Individual or Group of Interconnections
Each individual interconnection or group of interconnections subject to the individual tie benefits contribution calculation is treated independently. The simple average of values for all the interconnection states represents tie benefits of the target interconnection or group of interconnections
Interconnections with Maritimes
  No individual interconnection is subject to the calculation
Interconnections with Quebec
  HQ Phase II and Highgate are subject to the calculation
  Proration is required since the sum of the average contribution (907.5 + 140 = 1,047.5) is not equal to the total control area tie benefits of 1,065 MW calculated in Process 3
 | Tie Benefits Contribution under Different Scenarios |  |  |  |  |  |  |  | Average | After Proration
Phase II (MW) | 1 vs 31 | 2 vs 4 | 3 vs 8 | 5 vs 12 | 9 vs 18 | 17 vs 26 | 23 vs 30 | 27 vs 32 | 907.5 | 907.5 x 1065/1047.5 = 923
 | 1,040 | 865 | 800 | 845 | 765 | 980 | 985 | 980 |  | 
Highgate (MW) | 1 vs 30 | 2 vs 5 | 3 vs 9 | 4 vs 12 | 8 vs 18 | 17 vs 27 | 23 vs 31 | 26 vs 32 | 140 | 140 x 1065/1047.5 = 142
 | 190 | 135 | 130 | 115 | 95 | 160 | 135 | 160 |  | 

## Slide 12: Process 4 cont.
Interconnections with New York
  NY-AC ties and CSC are subject to the calculation
  Proration is required since the sum of the average contribution (282.5 + 0 = 282.5) is not equal to the total control area tie benefits of 287 MW calculated in Process 3
 | Tie Benefits Contribution under Different Scenarios |  |  |  |  |  |  |  | Average | After Proration
NY-AC (MW) | 1 vs 29 | 2 vs 6 | 3 vs 10 | 7 vs 17 | 11 vs 23 | 12 vs 24 | 18 vs 28 | 25 vs 32 | 282.5 | 282.5 x 287/282.5 = 287
 | 490 | 135 | 210 | 135 | 210 | 295 | 490 | 295 |  | 
CSC (MW) | 1 vs 28 | 2 vs 7 | 3 vs 11 | 6 vs 17 | 10 vs 23 | 12 vs 25 | 18 vs 29 | 24 vs 32 | 0 | 0 x 287/282.5 = 0
 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 

## Slide 13: Process 5 Adjustment to Initial Tie Benefits Values to Account for Firm Capacity Imports
Tie benefits determined in Process 4 for individual interconnection or group of interconnections are adjusted to account for firm capacity imports
  Since there are no existing capacity imports for FCA 16, no adjustments are needed to the tie benefits as determined in Process 4 for individual interconnection or group of interconnections

## Slide 14: Process 6 Calculation of Final Tie Benefits for Individual Neighboring Control Area
Final tie benefits for each neighboring Control Area are the sum of the tie benefits from the individual interconnections or groups of interconnections with that Control Area, after accounting for the adjustments for firm capacity imports as determined in Process 5
  Maritimes = 478 MW
  Quebec = 923 + 142 = 1,065 MW
  New York = 287 + 0 = 287 MW

## Slide 15: Process 7 Calculation of Final Total Tie Benefits for New England
Final total tie benefits from all neighboring control areas are the sum of the Control Area tie benefits after accounting for any adjustment for capacity imports as determined in Process 6
  Total tie benefits = 478 + 1,065 + 287 = 1,830 MW

## Slide 16: Summary of Tie Benefits Study Results
For FCA 16, the total tie benefits are 1,830 MW, with the following contributions
Interconnection | FCA 16 Tie Benefits Amount (MW)
Maritimes | 478
HQ Phase II | 923
Highgate | 142
New York AC ties | 287
CSC | 0

## Slide 17: Comparison of FCA 16 & FCA 15 Tie benefits

## Slide 18: Comparison of FCA 16 & FCA 15 Tie Benefits
Interconnection | FCA 16 (MW) | FCA 15 (MW) | DELTA (MW) (FCA 16 minus FCA 15)
Maritimes | 478 | 454 | 24
HQ Phase II | 923 | 883 | 40
Highgate | 142 | 140 | 2
New York AC ties | 287 | 258 | 29
CSC | 0 | 0 | 0
Total Tie Benefits | 1,830 | 1,735 | 95
Note: FERC accepted the tie benefits for the 2024-2025 CCP associated with FCA 15 on January 21, 2021. See: https://www.iso-ne.com/static-assets/documents/2021/01/er21-496-000.pdf

## Slide 19: Sensitivity Analysis and Observations
The ISO has identified the major assumption updates/changes in New England and the neighboring Control Areas, and conducted additional simulations to quantify their impacts on the tie benefits study results
Updated reconstitution methodology for passive demand resources (PDR) was used in the development of the New England load forecast for the first time this year
  Has no impact on the tie benefits results
    New PDR reconstitution methodology results in a level shift of the load
    Because tie benefits are calculated using at-criterion condition, the change to load magnitude did not change the frequency and the amount of New England’s need for tie benefits

## Slide 20: Sensitivity Analysis and Observations, cont.
Modeling Boston import limit
  In the FCA 15 tie benefits study, the Boston import limit was assumed at 5,150 MW with proxy units added to the Boston subarea to satisfy the 0.1 days/year LOLE criterion
  In the FCA 16 tie benefits study, the Boston import limit (5,250 MW) was relaxed. If the Boston import limit had not been relaxed, the total tie benefits would have been approximately 1,730 MW, i.e., 100 MW lower
  This 100 MW difference should not be interpreted as the overall impact on tie benefits due to the modeling change of the Boston import limit from FCA 15 to FCA 16
  Quantifying the overall impact on tie benefits resulting from the modeling change of the Boston import limit is not easy
    Creating similar binding conditions to FCA 15 is difficult as they are affected not only by the changes to the interface limit, but also by resource and load assumptions in Boston, and the impact from proxy units

## Slide 21: Sensitivity Analysis and Observations, cont.
Modeling of behind-the-meter (BTM) photovoltaic (PV) in the New York system
  For the FCA 15 tie benefits study, New York provided a model in which it modeled BTM PV by using a single historical profile (2006)
  For the FCA 16 tie benefits study, New York provided a model in which it modeled BTM PV using 5 historical profiles (2015 to 2019)
    GE MARS randomly selected one of these profiles for each replication
  The total tie benefits for FCA 16 would have been ~55 MW lower if New York had used a single historical profile (2006) in its BTM PV model, as it did last year for FCA 15
    Using 5 historical profiles in the FCA 16 simulations introduces more load diversity between New England and New York, which results in higher tie benefits from New York.
    With the increased load diversity, New York and New England need emergency assistance at the same time less often and, as a result, the tie benefits contribution from Quebec and Maritimes increases for both New York and New England

## Slide 22: Sensitivity Analysis and Observations, cont.
In summary, the 95 MW increase of total tie benefits in FCA 16 is mainly attributed to the modeling change of BTM PV in the New York system (55 MW)

## Slide 24: Appendix I
FCA 16 Tie Benefits Study Methodology

## Slide 25: Study Methodology Calculation Process 1
Calculation of tie benefits values for all possible interconnection states
  Bring all interconnected areas to LOLE of 0.1 days/year simultaneously
  Calculate New England’s LOLE for all the possible interconnection states, e.g.
    with no interconnections (isolated state)
    With any single interconnection only
    With any of two interconnections
    With any of three interconnections
    …
  Calculate the equivalent tie benefits values for each interconnection state using the isolated state as reference
    As the equivalent MW to bridge the LOLE delta between these two states

## Slide 26: Study Methodology Calculation Process 2
Calculation of initial total tie benefits for New England
  Compare the following two interconnection states
    New England System with all interconnections with neighboring Control Areas connected
    New England System with all interconnections with neighboring Control Areas disconnected
  Total tie benefits for New England is the equivalent MW value to bridge the LOLE delta between these two states
  This initial total tie benefits value is subject to adjustment to account for firm capacity imports in Process 5

## Slide 27: Study Methodology Calculation Process 3
Calculation of initial tie benefits for each individual neighboring Control Area
  All interconnections connected to a given neighboring Control Area are grouped together to represent the state of interconnection between New England and that neighboring Control Area
  For each target neighboring Control Area, identify all the related interconnection states and calculate the equivalent tie benefits values for each of those states
    With a total of three neighboring control areas, there are four interconnection states for each neighboring Control Area
    Use the simple average of values for all the interconnection states to represent the tie benefits of the target neighboring Control Area
  If the sum of the individual control area tie benefits calculated above is different than the total tie benefits calculated in Process 2, each Control Area’s tie benefits shall be adjusted based on the ratio of the individual Control Area tie benefits to the total tie benefits
  These initial individual Control Area tie benefits are subject to further adjustment to account for firm capacity imports in Process 5

## Slide 28: Study Methodology Calculation Process 4
Calculation of initial tie benefits for individual interconnection or group of interconnections
  Each individual interconnection or group of interconnections subject to individual tie benefits contribution calculation is treated independently
  For each target interconnection or group of interconnections, identify all the related interconnection states and calculate the equivalent tie benefits values for each of these states
    Use the simple average of values for all the interconnection states to represent the tie benefits of the target interconnection or group of interconnections
  If the sum of tie benefits of the individual interconnections or group of interconnections calculated above is different than the relative Control Area’s tie benefits calculated in Process 3, tie benefits of the individual interconnection or group of interconnections shall be an adjusted ratio of the tie benefits of the individual interconnection or group of interconnections to the relative Control Area’s tie benefits
  These initial individual interconnection or group of interconnections’ tie benefits are subject to further adjustment to account for firm capacity imports in Process 5

## Slide 29: Study Methodology Calculation Process 5
Adjustment to the initial tie benefits for individual interconnection or group of interconnections to account for firm capacity imports
  Deduct firm capacity imports from the import capability of each individual interconnection or group of interconnections to determine the remaining available import capability to support tie benefits
    Firm capacity imports are the Qualified Existing Import Capacity for FCA 2024-2025
  Compare the tie benefits value of an individual interconnection or group of interconnections as determined in Process 4 to its remaining transmission import capability
    If the tie benefits value is greater than the remaining transmission import capability, the tie benefit value of the individual interconnection or group of interconnections is capped to the remaining transmission import capability value
    Otherwise, no adjustments are made

## Slide 30: Study Methodology Calculation Process 6
Calculate the final tie benefits for individual neighboring Control Areas
  Final tie benefits for each neighboring Control Area are the sum of the tie benefits from the individual interconnection or groups of interconnections with that Control Area, after accounting for any adjustment for firm capacity imports as determined in Process 5

## Slide 31: Study Methodology Calculation Process 7
Sum the final total tie benefits for New England
  Final total tie benefits from all neighboring control areas are the sum of the Control Area tie benefits after accounting for any adjustment for firm capacity imports as determined in Process 6

## Slide 32: Appendix II
FCA 16 Tie Benefits Study Assumptions – General

## Slide 33: Loads Assumptions
New England
  The New England load assumptions are consistent with the assumptions to be used for the calculation of the ICR-Related Values* for FCA 16 (please see Appendix III for details)
Neighboring Control Areas
  Load Forecast
  Based on their latest load models used in NPCC studies for the year 2025
  2002 hourly shape; consistent with current NPCC studies
  *The ICR, LSR, MCL, the MRI Demand Curves and HQICCs are collectively referred to as the ICR-Related Values
  For details on ICR-Related Values development, see ICR Reference Guide

## Slide 34: Resources Assumptions
New England
Model all FCA 16 Existing Qualified Capacity
  Ratings, EFORd, and maintenance weeks consistent with assumptions for the ICR-Related Values calculations for FCA 16 (see Appendix III for details)
Neighboring Control Areas
Model resources based on
  2020 NPCC Long Range Adequacy Overview data and 2021 NPCC Summer Assessment
    Quebec
    Maritimes
    New York
      2021 New York Gold Book
    Ontario & PJM (for the purpose of modeling the impacts of capacity imports/exports with Quebec and New York)

## Slide 35: Control Area Modeling
    Quebec, Maritimes, New England, and New York are simulated using the MARS multi-area model reflecting inter-area and intra-area transmission interface transfer limits
    An equivalent model is used to reflect the impacts of the known capacity import/export between New England’s directly interconnected neighboring Control Areas and their respective neighboring Control Areas (i.e., PJM and Ontario)

## Slide 36: Subarea Modeling and Transmission Transfer Capability Assumptions
New England
    RSP subarea representation
    Internal and external transmission interface transfer capabilities consistent with FCA 16 transmission transfer capabilities* reviewed at the March 2021 Reliability Committee meeting
    Interfaces associated with FCA 16 Capacity Zones** are not modeled
      Northern New England (“NNE” - Vermont, New Hampshire & Maine) – export-constrained
      Maine – nested within NNE, export-constrained
      Southeast New England (“SENE” - Northeast Massachusetts/Boston & Southeast Massachusetts/Rhode Island) – import-constrained
      Neighboring Control Areas
    Consistent with their latest model used in NPCC studies (please see Appendix)
* Based on transmission transfer capability limits presented at the March 16, 2021 Reliability Committee meeting. The presentation is available at: https://www.iso-ne.com/static-assets/documents/2021/03/a9_fca_16_transmission_transfer_capability_and_capacity_zonal_development.pdf
** For more info on the development of FCA 16 Capacity Zones, see: https://www.iso-ne.com/static-assets/documents/2021/05/a02_2021-05-20_pspc_review_objective_criteria_testing_for_capacity_zone_determinations.pdf

## Slide 37: New England Internal Interface Modeling in Tie Benefits Calculations
ISO Tariff Section III.12.9.2.2 requires the modeling of internal interfaces in tie benefits calculations
In calculating tie benefits, all New England internal transmission constraints that (i) are modeled in the most recent Regional System Plan resource adequacy studies and assessments and (ii) are not addressed by either a Local Sourcing Requirement or a Maximum Capacity Limit calculation shall be modeled, using the procedures in Section III.12.9.2.5 of the Tariff
The Boston and SENE import interfaces share the same N-1 transmission constraint – 338 (Tewksbury-Woburn) 345 kV line
This was noted last year during stakeholder discussions of the calculations of tie benefits for FCA 15

## Slide 38: New England Internal Interface Modeling in Tie Benefits Calculations, cont. SENE and Boston Import Constraint Modeling
The SENE and Boston import constraint is addressed by a Local Sourcing Requirement, the import constraints for both SENE and Boston will not be modeled for the tie benefits calculation for FCA 16 as discussed during agenda item 2 of the May PSPC meeting
The Boston import limit and Southeast import limit of 5,250 MW are both relaxed in the simulation (see the New England System Representation diagram in Appendix III)

## Slide 39: New England Internal Interface Transfer Capability Assumptions (MW)
Notes are discussed in the following presentation: https://www.iso-ne.com/static-assets/documents/2021/03/a9_fca_16_transmission_transfer_capability_and_capacity_zonal_development.pdf

## Slide 40: New England Internal Interface Transfer Capability (Notes)
a) Limits are for the summer period, except where noted to be winter
  The limits may not include possible simultaneous impacts, and should not be considered as “firm”
  For the years within the FCM horizon (CCP 2025-2026 and earlier), only accepted certified transmission projects are included when identifying transfer limits
  For the years beyond the FCM horizon (CCP 2026-2027 and later), transmission upgrades with an approved proposed plan are included according to their expected in-service dates

## Slide 41: New England Internal Interface Transfer Capability (Notes), cont.
b) Increase associated with the Southeast Massachusetts/Rhode Island (SEMA/RI) reliability project upgrades
c) Increase associated with the Greater Boston upgrades, with the Wakefield – Woburn 345 kV line in service (CCP 2022-2023 and later)
d) The transfer capability was decreased by updated load assumptions, updated Northern New England (NNE)-Scobie transfer capability and retirement of Mystic 7, 8 & 9 and then increased by the inclusion of the Boston Area Optimized Solution

## Slide 42: New England External Interface Import Capability Assumptions (MW)
Notes are discussed in the following presentation: https://www.iso-ne.com/static-assets/documents/2021/03/a9_fca_16_transmission_transfer_capability_and_capacity_zonal_development.pdf

## Slide 43: New England External Interface Import Capability (Notes)
Limits are for the summer period
  The limits may not include possible simultaneous impacts, and should not be considered as “firm” (the bases for these limits are subject to more detailed review in the future)
The electrical limit of the New Brunswick-New England (NB-NE) tie is 1,000 MW
  When adjusted for the ability to deliver capacity to the greater New England Control area, the NB-NE transfer capability is 700 MW
    This is because of downstream constraints; in particular Orrington South
The capability for the Highgate facility is listed at the New England AC side of the Highgate terminal

## Slide 44: New England External Interface Import Capability (Notes), cont.
The Hydro-Quebec Phase II interconnection is a DC tie with equipment ratings of 2,000 MW. Due to the need to protect for the loss of this line at full import level in the PJM and NY Control Areas’ systems, ISO-NE has assumed its transfer capability for capacity and reliability calculation purposes to be 1,400 MW
  This assumption is based on the results of loss-of-source analyses conducted by PJM and NY
Import capability on the Cross Sound Cable (CSC) is dependent on the level of local generation
New York interface limits
  These are without CSC and with the Northport Norwalk Cable at 0 MW flow
  Simultaneously importing into NE and SWCT or Connecticut can lower the NY-NE capability (very rough decrease = 200 MW)

## Slide 45: New England Transmission Interface Availability Assumptions
      New England
Internal transmission interfaces are modeled 100 % available because the power can be delivered using multiple paths
External transmission interface availability assumptions are based on values updated this year. The previous values used in FCA 15 are listed for comparison
      Please note that the GE MARS program only allows modeling the forced outage rate of a transmission interface. It is assumed that transmission maintenance needs will have minimum reliability impact because they are scheduled during periods when the system is reliable
      Neighboring Control Areas
    Consistent with their latest model used in the latest NPCC studies
 | Cross Sound Cable |  | Highgate |  | HQ Phase II |  | New Brunswick Ties |  | New York AC Ties | 
 | FCA 15 | FCA 16 | FCA 15 | FCA 16 | FCA 15 | FCA 16 | FCA 15 | FCA 16 | FCA 15 | FCA 16
Annual forced outage rate (%) | 0 | 0.2 | 0 | 0.1 | 1.3 | 1.6 | 0.1 | 0.1 | 0.5 | 0.6
Annual maintenance requirement (weeks) | 3.4 | 6.7 | 0.9 | 0.8 | 2.9 | 3.0 | 2.6 | 2.4 | 5.9 | 6.2

## Slide 46: Other Assumptions: Operating Reserves and Relief from Voltage Reduction
  New England
Assume 2,305 MW of system-wide operating reserves
  Allowed to deplete to a minimum of 700 MW as OP-4 actions progress prior to firm load shedding
  Locational reserve requirement is not assumed since the local reserve need is estimated to be zero for SWCT and CT and NEMA/Boston subareas
Voltage reductions
  Consistent with the ICR calculation, and the amount for subareas calculated as
    (90/10 subarea net peak load* MW minus all Active Demand Capacity Resources and passive demand resources) x 1.0%
  Neighboring Control Areas
Consistent with their latest model in NPCC studies
  *Net peak load is the gross load (including both transportation and heating electrification forecast) minus the load reduction associated with BTM PV

## Slide 47: Appendix III
FCA 16 Tie Benefits Study Assumptions – New England Specific (These are the same load and capacity resource assumptions associated with the FCA 16 ICR- Related Values calculations)

## Slide 48: Load Forecast Data Assumptions
Load forecast assumption from the 2021 Forecast Report of Capacity, Energy, Loads and Transmission (CELT) load forecast
The load forecast weather-related uncertainty is represented by specifying a series of multipliers on the peak load and the associated probabilities of each load level occurring
  The multipliers used to describe the load forecast uncertainty are derived from the 52 weekly peak load distributions described by the expected value (mean), the standard deviation, and the skewness
Note: The 2021 CELT load forecast is available at: https://www.iso-ne.com/static-assets/documents/2021/04/2021_celt_report.xlsx

## Slide 49: Load Forecast Data Assumptions, cont. Modeling of BTM PV
FCA 16 ICR calculations will use an hourly profile of BTM PV corresponding to the load shape for the year 2002, used by the Northeast Power Coordinating Council (NPCC) for reliability studies. For more information on the development of the hourly profile see: https://www.iso-ne.com/static-assets/documents/2017/06/pspc_6_22_2017_2002_PV_profile.pdf
  Used for all probabilistic ICR-Related Values calculations
  Modeled in GE MARS by groupings using the Regional System Plan (RSP) 13-subarea representation
  Includes an 8% transmission and distribution gross-up
  Peak load reduction uncertainty is modeled (randomly selected by MARS from a seven day window distribution)
The values of BTM PV published in the 2021 CELT Report are the values of BTM PV subtracted from the gross load forecast to determine the net load forecast
The published 90/10 net load forecast for the SENE sub-areas is used in the TSA
Note: For more info on the PV forecast, see https://www.iso-ne.com/static-assets/documents/2021/04/final_2021_pv_forecast.pdf

## Slide 50: Load Forecast Data Assumptions, cont. Modeling of Transportation and Heating Electrification
Transportation Electrification
  The ICR-Related Values calculations will use an hourly profile for the transportation electrification forecast
    Includes an 8% transmission and distribution gross-up
    Uncertainty is currently not modeled due to lack of performance data
  More information on the development of the transportation electrification forecast can be found at: https://www.iso-ne.com/static-assets/documents/2021/04/final_2021_transp_elec_forecast.pdf
Heating Electrification
  The ICR-Related Values calculations will use the 2021 CELT gross load forecast that include the heating electrification loads which occur during the winter months
    The hourly gross load forecast (2021 Forecast Data workbook) is inclusive of the heating electrification forecast. The heating electrification loads are weather sensitive and therefore, the uncertainties relating to weather also apply to these loads
  More information on the development of the heating electrification forecast can be found at : https://www.iso-ne.com/static-assets/documents/2021/04/final_2021_heat_elec_forecast.pdf

## Slide 51: Load Forecast Data Assumptions, cont. New England System Load Forecast
Probability Distribution of Seasonal Peak Load (MW)
Monthly Peak Load (MW) - Net of BTM PV
There is a distribution associated with each monthly peak. The distribution associated with the seasonal peak load forecast is shown below:
Corresponds to the reference forecast labeled “ISO-NE Control Area & New England States Monthly Peak Load Forecast“ from worksheet “4 Mnth Peak” of the 2021 Forecast Data
  https://www.iso-ne.com/static-assets/documents/2021/04/forecast_data_2021.xlsx
From Table 1.6 - Seasonal Peak Load Forecast Distributions (forecast is reference with reduction for BTM PV) of the 2021 CELT
https://www.iso-ne.com/static-assets/documents/2021/04/2021_celt_report.xlsx
CCP | JUN | JUL | AUG | SEP | OCT | NOV | DEC | JAN | FEB | MAR | APR | MAY
2025-2026 | 24,893 | 26,899 | 26,263 | 23,009 | 19,060 | 20,467 | 21,874 | 22,484 | 21,702 | 20,476 | 18,437 | 21,394
 | 10/90 | 20/80 | 30/70 | 40/60 | 50/50 | 60/40 | 70/30 | 80/20 | 90/10 | 95/5
Summer 2025 | 26,531 | 26,899 | 27,343 | 27,674 | 28,025 | 28,488 | 28,800 | 29,221 | 29,988 | 30,352
Winter 2025-26 | 22,633 | 22,735 | 22,823 | 22,897 | 22,989 | 23,129 | 23,302 | 23,455 | 23,662 | 23,859

## Slide 52
Resource Data Assumptions
Generating Capacity Resources (MW)
Qualified Existing Generating Capacity Resources for FCA 16 reflect:
  Significant decreases
  Resource retirements and known terminations
      Unconditional Permanent and Retirement De-List Bids
      Permanent De-List Bids that are at or above the Forward Capacity Auction Starting Price for FCA 16
  IPRs have both summer and winter values modeled; non-intermittent Generating Capacity Resources’ winter values provided for informational purpose
Load Zone | Non-Intermittent Generating Capacity Resources |  | Intermittent Power Resources |  | Total | 
 | Summer | Winter | Summer | Winter | Summer | Winter
MAINE | 3,055.870 | 3,239.197 | 274.892 | 328.854 | 3,330.762 | 3,568.051
NEW HAMPSHIRE | 4,064.064 | 4,308.469 | 79.239 | 161.805 | 4,143.303 | 4,470.274
VERMONT | 199.623 | 232.077 | 61.180 | 106.158 | 260.803 | 338.235
CONNECTICUT | 9,840.270 | 10,215.624 | 93.750 | 66.180 | 9,934.020 | 10,281.804
RHODE ISLAND | 1,899.569 | 2,051.291 | 50.104 | 41.741 | 1,949.673 | 2,093.032
SOUTH EAST MASSACHUSETTS | 4,778.498 | 5,118.294 | 285.234 | 358.085 | 5,063.732 | 5,476.379
WEST CENTRAL MASSACHUSETTS | 3,643.463 | 3,862.584 | 167.345 | 115.115 | 3,810.808 | 3,977.699
NORTH EAST MASSACHUSETTS & BOSTON | 1,307.215 | 1,405.944 | 54.931 | 44.081 | 1,362.146 | 1,450.025
Total New England | 28,788.572 | 30,433.480 | 1,066.675 | 1,222.019 | 29,855.247 | 31,655.499

## Slide 53: Resource Data Assumptions, cont. Import Capacity Resources (MW)
There are no Existing Import Capacity Resources qualified for FCA 16

## Slide 54
Resource Data Assumptions , cont.
Demand Capacity Resources (MW)
Notes:
Qualified Existing Demand Capacity Resources for FCA 16
Includes the 8% transmission and distribution loss adjustment (gross-up)
Load Zone | On-Peak Demand Resources |  | Seasonal Peak Demand Resources |  | ADCR |  | Total | 
 | Summer | Winter | Summer | Winter | Summer | Winter | Summer | Winter
MAINE | 210.184 | 207.947 | - | - | 137.803 | 155.699 | 347.987 | 363.646
NEW HAMPSHIRE | 136.442 | 138.504 | - | - | 48.407 | 47.687 | 184.849 | 186.191
VERMONT | 119.904 | 135.113 | - | - | 51.904 | 57.510 | 171.808 | 192.623
CONNECTICUT | 199.380 | 81.923 | 518.359 | 550.728 | 192.829 | 192.123 | 910.568 | 824.774
RHODE ISLAND | 270.227 | 240.576 | - | - | 44.737 | 41.207 | 314.964 | 281.783
SOUTH EAST MASSACHUSETTS | 405.098 | 334.120 | - | - | 59.395 | 57.566 | 464.493 | 391.686
WEST CENTRAL MASSACHUSETTS | 392.023 | 344.254 | 25.363 | 20.044 | 112.072 | 108.417 | 529.458 | 472.715
NORTH EAST MASSACHUSETTS & BOSTON | 643.330 | 490.020 | - | - | 99.802 | 99.903 | 743.132 | 589.923
Grand Total | 2,376.588 | 1,972.457 | 543.722 | 570.772 | 746.949 | 760.112 | 3,667.259 | 3,303.341

## Slide 55: Resource Availability Assumptions Non-Intermittent Generating Capacity Resources
Forced outages assumption
  Each generating unit’s Equivalent Forced Outage Rate on Demand (non-weighted EFORd) will be modeled
  Based on a 5-year average (January 2016 – December 2020) of Generation Availability Data System (GADS) data submitted by generators
  NERC GADS class average data will be used for immature/non-commercial units
Scheduled outage assumption
  Each generating unit’s weeks of maintenance modeled
  Based on a 5-year average (January 2016 – December 2020) of each generator’s actual historical average of planned and maintenance outages scheduled at least 14 days in advance
  NERC GADS class average data will be used for immature/non-commercial units

## Slide 56: Resource Availability Assumptions , cont. Non-Intermittent Generating Capacity Resources
Notes:
FOR for stand-alone battery is assumed as 5% based on MISO’s information: https://cdn.misoenergy.org/20180808%20RASC%20Item%2003b%20Capacity%20Determination%20for%20ESR263475.pdf
Average summer MW weighted EFORd and maintenance weeks are shown by resource category for informational purposes. In the LOLE simulations used for determining ICR-Related Values, individual unit assumptions will be modeled
Resource Category | Summer MW | Assumed Average EFORd (%) Weighted by Summer Ratings | Assumed Average Maintenance Weeks Weighted by Summer Ratings
Combined Cycle | 13,379 | 4.1 | 4.6
Fossil | 4,888 | 16.4 | 5.1
Combustion turbine | 3,337 | 9.7 | 2.9
Nuclear | 3,311 | 1.6 | 3.3
Hydros (includes pumped storage) | 3,109 | 2.3 | 5.9
Diesel | 112 | 10.6 | 2.8
Stand-alone battery | 600 | 5.0 | 0.0
Co-located battery | 30 | 0.0 | 0.0
Miscellaneous | 22 | 12.6 | 3.8
Total | 28,789 | 6.4 | 4.4

## Slide 57: Resource Availability Assumptions, cont. Intermittent Power Resources
Modeled as 100% available since their outages have been incorporated in their 5-year historical output used in calculating their existing Qualified Capacity

## Slide 58: Resource Availability Assumptions, cont. Battery Storage Resources
For FCA 16 ICR-Related Values calculations to be conducted in 2021, the ISO proposed to model battery storage resources as follows:
For details on the proposed changes to the modeling methodologies for battery storage resources, see June 2021 and May 2021 PSPC meeting materials
Resource Type | Availability Assumptions
Non-intermittent battery storage resources | 
Stand-alone battery storage | Use the class model available in GE MARS
Co-located battery storage | Model as 100% available
Intermittent battery storage resources | Model as 100% available

## Slide 59: Resource Availability Assumptions, cont. Demand Capacity Resources
Demand Capacity Resources average performance percentages will be applied to FCA 16 qualified Existing Demand Capacity Resources
Average of 2017 – 2020 historical summer and winter Demand Capacity Resource performance based on the new ADCR availability methodology
Modeled as a forced outage rate of 1-performance in blocks by Demand Capacity Resource type and Load Zone
Note: For calculation details on ADCR availability (performance), see June 2021 and May 2021 PSPC meeting materials
Load Zone | On-Peak Demand Resources |  | Seasonal Peak Demand Resources |  | ADCR |  | Total | 
 | Summer (MW) | Performance (%) | Summer (MW) | Performance (%) | Summer (MW) | Performance (%) | Summer (MW) | Performance (%)
MAINE | 210 | 100 |  |  | 138 | 97 | 348 | 99
NEW HAMPSHIRE | 136 | 100 |  |  | 48 | 89 | 185 | 97
VERMONT | 120 | 100 |  |  | 52 | 91 | 172 | 97
CONNECTICUT | 199 | 100 | 518 | 100 | 193 | 90 | 911 | 98
RHODE ISLAND | 270 | 100 |  |  | 45 | 80 | 315 | 97
SOUTH EAST MASSACHUSETTS | 405 | 100 |  |  | 59 | 87 | 464 | 98
WEST CENTRAL MASSACHUSETTS | 392 | 100 | 25 | 100 | 112 | 87 | 529 | 97
NORTH EAST MASSACHUSETTS & BOSTON | 643 | 100 |  |  | 100 | 81 | 743 | 97
Total New England | 2,377 | 100 | 544 | 100 | 747 | 88 | 3,667 | 98

## Slide 60: Resource Availability Assumptions, cont. Import Capacity Resources
System Import Capacity Resources
  The forced and planned outage assumptions will be based on the availability assumptions associated with the transmission line used to import the capacity resource. The following table shows the availability assumptions for the external ties based on external tie lines’ forced and scheduled outage rates:
Unit/Plant Import Capacity Resources
  The forced and planned outage assumptions will be based on the assumptions associated with the unit/plant supplying the import capacity
Please note, for FCA 16 there are no qualified existing Import Capacity Resources
External Ties | Forced Outage Rate (%) | Maintenance (Weeks)
Cross Sound Cable | 0.2 | 6.7
Highgate | 0.1 | 0.8
HQ Phase II | 1.6 | 3.0
New Brunswick Ties | 0.1 | 2.4
New York AC Ties | 0.6 | 6.2

## Slide 61: OP-4 Assumptions Action 6 & 8 - 5% Voltage Reduction (MW)
Note: Uses the 90-10 peak Gross load (including both transportation and heating electrification forecast) forecast minus BTM PV and all passive DR and ADCR, multiplied by the 1.0% estimated relief obtainable from OP-4 voltage reduction pursuant to Tariff Section III.12.7.4
 | 90-10 Peak Load (Net BTMPV) | Passive DR | ADCR | Actions 6 & 8 5% Voltage Reduction
June 2025-Sept 2025 | 29,988 | 2,920 | 747 | 263
October 2025-May 2026 | 23,662 | 2,543 | 760 | 204

## Slide 62: OP-4 Assumptions, cont. Minimum Operating Reserve Requirement (MW)
The system reserves assumption will be consistent with those needed for reliable system operations during Emergency Conditions
Modeled at 700 MW in the ICR calculations

## Slide 63: Appendix IV
FCA 16 Tie Benefits Study System diagrams for informational purposes

## Slide 64: Interconnected System Representation for 2025 (MW)
A
C
D
F
G
J
K
900 S
1,000 W
575 S
575 W
200
1,400
550
700
0
1,000
1,500
800
600
800
800
Total NY-NE
(Excludes CSC)
414
315
150
660
0
1,200 S
0 W
NOR
CT
W-MA
BHE
CMA
330
VT
0
Equivalent for PJM-NY boundary
300
600
New
York
Maritimes
Quebec
New
England
Mtl
100
230
300
1,400
1,400
660
9999
2,000
J3
J3
J4
K2
0
200
0
NB
0
NM
NS
PEI
300
300
9,999
350
150
ND
Que
Cent.
JB
MAN
Chur.
23,450
5,200
12,450
15,600
2,250
2,138
1
190 S
198 W
425
1,000
0
815
315
660
0
660
0
1,045
100
199
660
Cedars
RECO
0
315
140
550

## Slide 65: New York System Representation for 2025 (MW)
F
G
H
I
J
K
2,200
5,650
1,600
2,650
1,999
2,770 -
3,925*
1,600
5,400
1,999
1,999
7,375
8,450
1,999
4,350
235- 505 *
342
1,293
To VT
To WMA
To NOR
1,000
414
800
800
0
1,500
A
B
C
E
D
1,999
1,500
1,600
1,999
To Quebec
300
140
1,000
To CT
330
CE Group
5,000-5,650*
3,400
320
1,999
800
600
0
600
0
Total East
9,999
9,999
UPNY-SENY
99,999
7,150
1,613
29 –220 *
LI Sum
200
300
660
2,300
AG
9,999
PJM to G&J
9,999
2,000
99,999
134
LI West
J3
VFT
HTP
315
815
RECO
CPVVEC
0
1,999
5,693
DSY49Y50
1,000
425
Equivalent for PJM-NY boundary
0
CSC
To Cedars
2,650
9,999
2,300
1000
1,000
0
600
9999
500
* Rating a function of unit availabilities and/or area loads.
0
660
0
0
315
315
9999
150
0
J2
385
270 (s)
278 (w)

## Slide 66: New England System Representation for 2025 (MW)
East – West
3,500/3.000
Orrington South
Surowiec South
ME - NH
North – South
2,725 (relaxed)
Boston Import
5,250 (relaxed)
SEMA/RI Export/Import
3,400/1,800
Southwest CT Import
2,800
Connecticut
(Excludes CSC) 3,400
Norwalk - Stamford
9,999 In
NB - NE
Highgate
Phase II
To D
To F
To G
To K
To NB
To Quebec
To Quebec
RI
ME
BHE
SEMA
CMA/
NEMA
Boston
NH
SME
SWCT
CT
WMA
NOR
VT
200
1,200 S
0 W
1,400
700
550
0
800
800
800
1,325
1,500
1,900
To K
330 (CSC)
0
600
0
100
Total NY-NE
(Excludes CSC)
1,400
1,400
414
* Rating a function of unit availabilities and/or area loads.
0
Southeast Import
5,250 (relaxed)
(relaxed)

## Slide 67: Abbreviations of Subareas in Diagrams
Maritimes
NB 'NEW BRUNSWICK'
NS 'NOVA SCOTIA'
PEI 'PRINCE EDWARD ISLAND'
NM 'NORTHERN MAINE ISA'
Quebec
JB 'JAMES BAY'
Chur 'CHURCHILL'
MAN 'NORTH COAST/MANIC'
Que Cent. 'CENTRE (Que.)'
Mtl 'SOUTHWEST/MTL'
ND 'NICOLET-DESCANTONS'
CEDARS ' for cedar sale'
New York
A 'AREA_A'
B 'AREA_B '
C 'AREA_C'
D 'AREA_D'
E 'AREA_E'
F 'AREA_F'
G 'AREA_G'
CPVVEC 'AREA FOR CPV VEC'
H 'AREA_H '
I 'AREA_I '
J 'AREA_J '
J3 'LINDEN VFT CABLE'
J4 'HTP CABLE'
K 'AREA_K'
RECO 'RECO PJM'

## Slide 68: Abbreviations of Subareas in Diagrams, cont.
New England
BHE ‘Northeastern Maine’
ME ‘Western and central Maine and Saco Valley, New Hampshire’
SME ‘Southeastern Maine’
NH ‘Northern, eastern, and central New Hampshire; eastern Vermont; and southwestern Maine’
VT ‘Vermont and southwestern New Hampshire’
Boston ‘Greater Boston, including the North Shore’
CMA/NEMA ‘Central Massachusetts and Northeastern Massachusetts’
WMA ‘Western Massachusetts’
SEMA ‘Southeast Massachusetts and Newport, Rhode Island’
RI ‘Part of Rhode Island bordering Massachusetts’
CT ‘Northern and eastern Connecticut’
SWCT ‘Southwestern Connecticut’
NOR ‘Norwalk and Stamford, Connecticut’

## Slide 69: Appendix V
Acronyms*
*Not all acronyms are used in this presentation

## Slide 70: Acronyms
ADCR – Active Demand Capacity Resource
ALCC – Additional Load Carrying Capability
APk – Gross peak load net of BTM PV
ARA – Annual Reconfiguration Auction
ART – Annual Reconfiguration Transaction
BTM PV – Behind-the-meter Photovoltaic
CCP – Capacity Commitment Period
CDD – Cooling Degree Days
CELT – Capacity, Energy, Loads and Transmission
CSC – Cross Sound Cable
CSO – Capacity Supply Obligation
CT – Connecticut
DR – Demand Resource

## Slide 71: Acronyms, cont.
EE – Energy Efficiency
EFORd – Equivalent Forced Outage Rate on Demand
FCA – Forward Capacity Auction
FCM – Forward Capacity Market
FERC – Federal Energy Regulatory Commission
HQICCs – Hydro-Quebec Interconnection Capability Credits
ICR – Installed Capacity Requirement
ISO – ISO New England
LRA – Local Resource Adequacy
LSR – Local Sourcing Requirement
MARS -Multi-Area Reliability Simulation
MCL – Maximum Capacity Limit
MRI – Marginal Reliability Impact
NEMA – Northeast Massachusetts
NEPOOL – New England Power Pool
Net ICR – ICR minus HQICCs

## Slide 72: Acronyms, cont.
NNE – Northern New England
NPCC – Northeast Power Coordinating Council
OP-4 – Operating Procedure No. 4, Action During a Capacity Deficiency
PAC – Planning Advisory Committee
PC – Participants Committee
PK – Peak (gross load forecast)
PSPC – Power Supply Planning Committee
RC – Reliability Committee
RI – Rhode Island
SEMA – Southeast Massachusetts
SENE – Southeast New England
SWCT – Southwest Connecticut
TSA – Transmission Security Analysis
VR – Voltage Reduction
WEFORd – Weighted Equivalent Forced Outage Rated on Demand