## Slide 1
Alex Rost
Manager, Resource qualification
Forward Capacity Auction 18
Transmission Transfer Capabilities &
Capacity Zone Development
March 14, 2023 | NEPOOL Reliability Committee | Doubletree Hotel, Westborough, ma
Reliability Committee

## Slide 2: Topics
Review of interface transfer capabilities
Proposed Capacity Zone construct for Forward Capacity Auction (FCA) 18, which is associated with the 2027-2028 Capacity Commitment Period (CCP)

## Slide 3: FCA 18 – Capacity Zone Development: Steps So Far
ISO presented the FCA 18 Capacity Zone Development Preview at the December 2022 Planning Advisory Committee (PAC) meeting
  ISO presented the 2023 Forward Capacity Market Transmission Certifications at the January 2022 Reliability Committee (RC) meeting

## Slide 4: Review of interface transfer capabilities
Internal Interfaces

## Slide 5: Update on Review of Maine Interface Transfer Capabilities
The ISO informed the PAC during the December 2022 FCA 18 Capacity Zone Development Preview presentation that:
  It’s currently investigating the impacts of changes to NPCC A-10 (Criteria on the Classification of Bulk Power System Elements) on the transfer capabilities of interfaces in ME
  If completed in time (e.g. around the end of Q1/start of Q2 2023), the ISO will consider the results of this analysis for the FCA 18 Capacity Zone formation process
The analysis will not be completed in time for consideration in the FCA 18 Capacity Zone formation process
  Stability, voltage and thermal analyses to identify key system constraints and evaluate interactions among the Maine interfaces for transfers above the current A-10 limited transfer levels are ongoing
  Completion of the analysis is expected near the end of 2023

## Slide 6: A Note on the Boston/Southeast New England (SENE) Import Transfer Capabilities
Several system changes have affected the Boston/SENE import transfer capabilities
System Change | Boston/SENE N-1 Import Transfer Capability (MW)
Greater Boston Upgrades, except for the Wakefield-Woburn 345 kV line1 | 5,400
Updated load assumptions, updated Northern New England (NNE)-Scobie transfer capability and retirement of Mystic 7, 8 & 9, and with the Boston Area Optimized Solution 2 | 5,250
Wakefield-Woburn 345 kV line is a portion of the Greater Boston Upgrades. The in-service date has been updated to December 2023.
Accounts for all of the Greater Boston Upgrades, including the Wakefield-Woburn 345 kV line

## Slide 7: A Note on the Boston/SENE Import Transfer Capabilities, cont’d
Several system changes have affected the Boston/SENE import transfer capabilities
System Change | Boston/SENE N-1-1 Import Transfer Capability (MW)
Boston Area Optimized Solution1 | 4,550
Opening of the K Street Breaker | 4,850
Accounts for all of the Greater Boston Upgrades and the retirement of the Mystic units

## Slide 8: FCA 18 Internal Interface Transfer Capabilities (MW)
Notes are discussed on the following page

## Slide 9: FCA 18 Internal Interface Transfer Capabilities (Notes)
Limits are for the summer period, except where noted to be winter
  The limits may not include possible simultaneous impacts, and should not be considered as “firm”
  For the years within the Forward Capacity Market (FCM) horizon (CCP 2027-2028 and sooner), only accepted certified transmission projects are included when identifying transfer limits
  For the years beyond the FCM horizon (CCP 2028-2029 and later), proposed plan approved transmission upgrades are included according to their expected in-service dates
The transfer capability was decreased by updated load assumptions, updated Northern New England (NNE)-Scobie transfer capability and retirement of Mystic 7, 8 & 9, and increased by the completion of the Greater Boston upgrades (including the Wakefield – Woburn 345 kV line) and the Boston Area Optimized Solution, and increased by the inclusion of the opening of the K Street breaker for only the N-1-1 transfer capability
The East-West interface transfer capability has not changed; the value presented in the table is its margined limit, where the 3,500 MW value presented in earlier versions of this table is its unmargined limit

## Slide 10: Review of interface transfer capabilities
External Interfaces

## Slide 11: FCA 18 External Interface Import Capability (MW)
Notes are discussed on the following pages

## Slide 12: Notes on External Interface Import Capability
Limits are for the summer period
  The limits may not include possible simultaneous impacts, and should not be considered as “firm” (the bases for these limits are subject to more detailed review in the future)
The limit on scheduled energy transactions over the New Brunswick (NB)-New England (NE) Tie is 1,000 MW
  Historically, when adjusted for the ability to deliver capacity to the greater New England Control area, the NB-NE capacity import capability is 700 MW
    This is because of downstream constraints; in particular Orrington-South
The capability for the Highgate facility is listed at the New England AC side of the Highgate terminal

## Slide 13: Notes on External Interface Import Capability, cont’d
The Hydro-Quebec Phase II interconnection is a DC tie with equipment ratings of 2,000 MW. Due to the need to protect for the loss of this line at full import level in the PJM and New York (NY) Control Areas’ systems, ISO-NE has assumed its transfer capability for capacity and reliability calculation purposes to be 1,400 MW
  This assumption is based on the results of loss-of-source analyses conducted by PJM and NYISO
Import capability on the Cross Sound Cable (CSC) is dependent on the level of local generation
NY interface limits
  These are without CSC and with the Northport Norwalk Cable at 0 MW flow
  Simultaneously importing into NE and SWCT or Connecticut can lower the NY-NE capability (very rough decrease = 200 MW)

## Slide 14: Proposed Potential Zonal Construct for FCA 18

## Slide 15: Proposed Potential Zonal Construct for FCA 18
For FCA 18, the following potential zones (unchanged from the potential zones evaluated for FCA 17) will be evaluated using the Capacity Zone modeling objective criteria triggers in Section III.12.4 of the Tariff
  Potential export-constrained zones:
    Northern New England (“NNE” - Vermont, New Hampshire & Maine)
    Maine – nested within NNE
  Potential import-constrained zones:
    Southern New England (“SENE” - Northeast Massachusetts/Boston & SEMA/RI)
    Connecticut
Pursuant to Section III.12.4 (b) of the Tariff, the ISO must model out-of-service all Retirement De-List Bids and Permanent De-List Bids (including any received for the current FCA at the time of the calculation)
  The window for submitting these bids for FCA 18 is March 30 – April 6, 2023
    Submissions are based on the FCA Starting Price (which is dependent on the Cost of New Entry (CONE)) and the Capacity Performance Payment Rate (CPPR)

## Slide 16: Potential Capacity Zone Construct for FCA 18
Rest-of-Pool (West Central Mass, NY-AC & Phase II)
SENE (NEMA/
Boston & SEMA/RI)
Connecticut
Note that zones are modeled in the FCA only if the objective criteria in Section III.12 of the Tariff is triggered
Maine
NNE
Note:
Supply from New
Brunswick is modeled
as connected to Maine

## Slide 17: Interface Transfer Capabilities for Potential Capacity Zone Boundaries
FCA 17 Transfer Capabilities (MW) |  | FCA 18 Transfer Capabilities (MW) | 
SENE Import N-1 | 5,250 | SENE Import N-1 | 5,250
SENE Import N-1-1 | 4,850 | SENE Import N-1-1 | 4,850
Connecticut Import N-1 | 3,400 | Connecticut Import N-1 | 3,400
Connecticut Import N-1-1 | 2,200 | Connecticut Import N-1-1 | 2,200
North-South (NNE Boundary) N-1 | 2,725 | North-South (NNE Boundary) N-1 | 2,725
Maine-New Hampshire (Maine Boundary) N-1 | 1,900 | Maine-New Hampshire (Maine Boundary) N-1 | 1,900

## Slide 18: A Note on Dispatch Zones (Active Demand Capacity Resources)
Tariff Section III.12.4A. Dispatch Zones
  The ISO shall establish Dispatch Zones that reflect potential transmission constraints within a Load Zone that are expected to exist during each Capacity Commitment Period. Dispatch Zones shall be used to establish the geographic location of Active Demand Capacity Resources. For each Capacity Commitment Period, the ISO shall establish and publish Dispatch Zones by the beginning of the New Capacity Show of Interest Submission Window of the applicable Forward Capacity Auction, and those Dispatch Zones shall remain in place through the end of the Capacity Commitment Period for which they were established. The ISO will review proposed Dispatch Zones with Market Participants prior to establishing and publishing final Dispatch Zones.
The ISO is proposing no changes to the existing Dispatch Zones

## Slide 19: Next Steps
The potential Capacity Zone boundaries will be tested using the Step 2 objective criteria trigger calculations
  Results scheduled to be presented at the May 31, 2023 Power Supply Planning Committee
Zones that trigger the objective criteria will be modeled in FCA 18 and associated reconfiguration auctions
Whether any of the modeled zones bind in FCA 18 and experience price-separation will be determined during the auction itself

## Slide 21: Appendix
Methodology for Modeling Capacity Zones in FCM

## Slide 22: Developing Zonal Boundaries for the FCM
Included in section 14 of Attachment K of the ISO New England Open Access Transmission Tariff (OATT):*
  Annual assessment of transmission transfer capability
    Each year, the ISO shall issue the results of the annual assessment of transmission transfer capability, conducted pursuant to applicable NERC, NPCC and ISO New England standards and criteria and the identification of potential future transmission system weaknesses and limiting facilities that could impact the transmission system’s ability to reliably transfer energy in the planning horizon.
    Each annual assessment will identify those portions of the New England system, along with the associated interface boundaries, that should be considered in the assessment of Capacity Zones to be modeled in the FCM pursuant to ISO Tariff Section III.12.
    * The OATT is Section II of the ISO Tariff

## Slide 23: Zone Formation: A Two Step Process
Step ONE | Step TWO
Identify the potential zonal boundaries and associated transfer limits to be tested for modeling in the FCM | Use objective criteria* to conduct the test determining whether or not the zone meets the trigger to be modeled for the CCP
 | Import-constrained zone Trigger to model the zone is based on the quantity of surplus resources in the zone above the zonal requirement Export-constrained zone Trigger to model the zone is based on the quantity of existing and proposed new resources compared with the maximum capacity capability in the zone Adjacent load zones that aren’t import- or export-constrained are modeled together in the rest-of-pool zone
*Objective criteria are contained in Section III.12.4 of the ISO Tariff

## Slide 24: Zonal Modeling Timeline
Pursuant to Attachment K:
Conduct transfer analysis
Identify zones & boundaries to be evaluated in FCM preparation
Discuss with PAC
Present to RC
Nov | Dec | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Jan | Feb
SOI for FCA
FCA
Pursuant to Tariff Section III.12:
Calculate whether the zones identified pursuant to Attachment K should be modeled using the objective criteria
Develop Installed Capacity Requirement, Local Sourcing Requirement, Maximum Capacity Limit, tie benefits and demand curves
Discuss with Power Supply Planning Committee
Present to RC for vote
File modeled Capacity Zones at FERC as part of the FCA informational filing
Retirement / Permanent De-List
Bids that are received in this timeframe would be captured in the zone-modeling calculations
File new Capacity Zone boundary at FERC – if proposed
Preview boundary expectations for upcoming FCA cycle
Transmission Certifications

## Slide 25: External Import Capability Determinations For Use in FCM (Tariff Section III.12.9.2.4)
The import capability of all external interconnections with New England will be determined using studies of system conditions expected during the CCP:
  Forecast 90/10 peak load
  Existing Generating Capacity Resources at their Capacity Network Resource (CNR) Capability
  Existing Demand Resources reflecting their Capacity Supply Obligations
  Stressed Transfers
The system will be modeled in a manner that reflects the design of the interconnection
  If an interconnection and its supporting system upgrades were designed to provide incremental capacity into the New England Control Area, simulations will assume imports up to the level that the interconnection was designed to support
  If the interconnection was not designed to be comparably integrated, simulations will determine the amount of power that can be delivered into New England over the interconnection