2010 Regional System Plan

.

© ISO New England Inc.

October 28, 2010

Preface

ISO New England Inc. (ISO) is the not-for-profit corporation responsible for the reliable operation of New England’s power generation and  transmission system. It also administers the region’s wholesale electricity markets and manages the comprehensive planning of the regional power system. The planning process includes the preparation of an annual Regional System Plan (RSP) in accordance with Attachment K of the ISO’s Open Access Transmission Tariff (OATT), which is a part of the Transmission, Markets, and Services Tariff, approved by the Federal Energy Regulatory Commission (FERC). Regional System Plans (RSPs) meet the tariff requirements by including the following:

- Forecasts of future annual and peak loads (i.e., the demand for electricity) for a five- to 10-year planning horizon and the need for resources (i.e., capacity)

- Information about the amounts, locations, and characteristics of market responses that can meet the defined system needs to satisfy demand—systemwide and in specific areas

- Descriptions of transmission projects for the region that could meet the identified needs, as summarized in an RSP Project List, which also includes information on project status and cost estimates.

RSPs also must summarize the ISO’s coordination of its short- and long-term system plans with those of neighboring systems, the results of economic studies of the New England system, and information for improving the design of the regional power markets. In addition to these requirements, the RSPs identify the initiatives and other actions the ISO, state officials, regional policymakers, transmission owners (TOs), and other New England Power Pool (NEPOOL) market participants and stakeholders can take to meet the needs of the system.

The 2010 Regional System Plan (RSP10) and the regional system planning process were developed in accordance with the requirements established in Attachment K of the OATT for the region’s 10-year electricity needs from 2010 through 2019. Where applicable throughout RSP10, Attachment K requirements are included within text boxes to demonstrate how each ISO task complies with the requirements. RSP10 also refers to the RSP Project List.

Regional Transmission Planning Results

On the basis of the results and needs described in past RSPs and supporting reports, New England’s transmission owners have constructed transmission projects throughout the region. These projects reinforce transmission facilities serving areas that have experienced load growth, such as Vermont, southern Maine, and the New Hampshire seacoast area. The projects also reinforce the system’s critical “load pockets,” such as Southwest Connecticut (SWCT) and Boston, allowing the import of power from other parts of the system. New interconnections with neighboring power systems have also been placed in service. From 2002 through 2010, 341 projects will have been put into service, totaling approximately $4.3 billion of new infrastructure investment.

In addition to the need for transmission development, the region has responded to the need for electric energy and capacity resources. Almost 12,900 megawatts (MW) of new generating projects have been interconnected with the system since generators first submitted requests to the ISO to be interconnected to the New England power system in November 1997. Approximately 1,900 MW of demand resources currently are part of the regional power system. The New England markets continue to evolve and encourage the development of resources where and when they are needed. Past RSPs and market signals had identified the need for generation in load pockets, including “fast-start” resources, which can quickly reach rated capability to help meet reliability requirements and reduce the amount of time generators run uneconomically.

According to the U.S. Department of Energy (DOE) 2009 National Electric Transmission Congestion Study, which summarized the amounts of congestion throughout the Eastern Interconnection, the New England system currently experiences little system congestion. The report cited the region’s “multi-faceted approach,” which has spurred investment in new supply- and demand-side resources and the planning and development of extensive transmission upgrades. As a result, DOE removed New England as “an area of concern” for the identification of National Interest Electric Transmission Corridors.

RSP10 Review and Approval

The regional system planning process in New England is open and transparent and reflects advisory input from regional stakeholders, particularly members of the Planning Advisory Committee (PAC), according to the requirements specified in Attachment K. The PAC is open to all parties interested in regional system planning activities in New England.

The ISO and the PAC have discussed study proposals, scopes of work, assumptions, and draft and final results and other materials appearing in RSP10. From September 2009 through September 2010, the ISO hosted 12 PAC meetings, which were attended by 208 individuals representing 145 entities. A total of 665 stakeholders attended, signifying over 4,000 workforce hours of participation. The ISO also posted to its Web site PAC presentations, meeting minutes, and other materials.

As required by the OATT Attachment K, the ISO New England Board of Directors has approved the 2010 Regional System Plan.

# Contents

Preface	i

Figures	viii

Tables	x

Section 1
Executive Summary	1

1.1 Major Findings and Observations	1

1.1.1 Forecasting the Annual and Peak Use of Electric Energy and Load Growth	2

1.1.2 Identifying Needs for Capacity and Operating Reserves	2

1.1.3 Identifying Transmission System Needs and Solutions	3

1.1.4 Developing and Integrating Resources	6

1.1.5 Supporting State, Regional, and Federal Initiatives that Affect System Planning	9

1.2 Conclusions	9

Section 2
Introduction	11

2.1 Approach to Regional System Planning	12

2.2 Overview of the New England Electric Power System	15

2.3 Overview of the New England Wholesale Electricity Market Structure	17

2.4 RSP Subareas	19

Section 3
Forecasts of Annual and Peak Use of Electric Energy in New England	21

3.1 Short- and Long-Run Forecasts	21

3.2 Economic and Demographic Factors and Electric Energy Use	23

3.3 Load Forecast Methodology and Model Enhancements	26

3.4 Subarea Use of Electric Energy	27

3.5 The CELT Forecast and Passive Demand Resources	30

3.6 Summary of Key Findings	31

Section 4
Resource Adequacy and Capacity	32

4.1 Systemwide Installed Capacity Requirement	33

4.1.1 ICR Values for 2010/2011 through 2019/2020 Capacity Commitment Periods	34

4.1.2 Other Resource Adequacy Analyses	36

4.2 Forward Capacity Market	37

4.2.1 Forward Capacity Auction Qualification Process	37

4.2.2 Forward Capacity Auctions	38

4.2.3 Meeting Capacity Needs	42

4.3 Operable Capacity Analysis	45

4.3.1 Approach	45

4.3.2 Results	46

4.3.3 Observations	48

4.4 Generating Units in the ISO Generator Interconnection Queue	48

4.5 Summary	50

Section 5
Operating Reserves	51

5.1 Requirements for Operating Reserves	52

5.1.1 Systemwide Operating-Reserve Requirements	52

5.1.2 Forward Reserve Market Requirements for Major Import Areas	53

5.2 Demand-Response Reserves Pilot Program	56

5.3 Summary of Key Findings and Follow-Up	58

Section 6
Transmission Security and Upgrades	59

6.1 The Need for Transmission Security	60

6.2 Transmission Planning Process	60

6.2.1 Needs Assessments and Solutions Studies	61

6.2.2 Project Timing	61

6.2.3 Types of Transmission Upgrades	62

6.3 RSP Project List and Projected Transmission Project Costs	64

6.4 Transmission System Performance Needs Assessments and Upgrade Approvals	66

6.4.1 Northern New England	67

6.4.2 Southern New England	75

6.5 Transmission Improvements to Load and Generation Pockets Addressing Reliability Issues	84

6.5.1 Maine	85

6.5.2 Boston Area	85

6.5.3 Southeastern Massachusetts	86

6.5.4 Western Massachusetts	86

6.5.5 Springfield Area	86

6.5.6 Connecticut	86

6.5.7 Southwest Connecticut Area	86

6.6 Out-of-Merit Operating Situations	86

6.7 Other Needed and Elective Transmission Upgrades	87

6.7.1 Needed Market-Efficiency-Related Transmission Upgrades	87

6.7.2 Required Generator-Interconnection-Related Upgrades	88

6.7.3 Elective Transmission Upgrades and Merchant Transmission	89

6.8 Summary	89

Section 7
Fuel Diversity	91

7.1 System Capacity for 2010 and 2009 Fuel Mix	91

7.2 Winter 2009/2010 Operational Overview	93

7.3 Expanding Natural Gas Supply and Infrastructure	94

7.3.1 LNG Supply Facilities	95

7.3.2 Other Natural Gas Development	96

7.3.3 New Pipelines and Storage	96

7.4 Electric Power Sector Outlook	97

7.4.1 Lower Natural Gas and Oil Prices	97

7.4.2 Improved Supply Infrastructure, Including Renewables	98

7.4.3 Adequate Dual-Fuel Capacity	99

7.5 Remaining Risks and Mitigation	99

7.5.1 Resource Commitment Uncertainties	99

7.5.2 Unforeseen Events in Real-Time Operations	100

7.5.3 Gas Quality and Interchangeability	100

7.5.4 LNG Supply Risks	100

7.5.5 Communication Barriers	101

7.5.6 Price Exposure	101

7.5.7 Other Fuel-Supply Risks	101

7.6 Summary	103

Section 8
Environmental Regulatory Update	104

8.1 Update of Environmental Regulations	104

8.1.1 Ozone Attainment Measures	105

8.1.2 Greenhouse Gases	107

8.1.3 Cooling Water	108

8.1.4 Studies of Potential Generator Retirements	108

8.1.5 FCM Classification for Generation Retrofits Resulting from Environmental Regulations	109

8.2 New England Power Plant Emissions	109

8.3 Peak-Day NOx Analysis	112

8.4 Energy Efficiency in New England	113

8.4.1 Energy Efficiency Resources in the FCM	113

8.4.2 Overview of States’ Energy-Efficiency Programs	114

8.4.3 State Energy-Efficiency Reductions Summary in 2020	119

8.5 Renewable Portfolio Standards, Projected Requirements, and Potential Supply
from the ISO Queue	121

8.5.1 Related Renewable Resource and Energy-Efficiency Developments	125

8.5.2 Projected RPS and Renewable Resources in the ISO Queue	126

8.6 Summary	135

Section 9
New Technologies	136

9.1 Integration of Smart Grid Technologies	136

9.1.1 Operational Challenges and Opportunities	136

9.1.2 ISO Activities in Support of Developing and Implementing a Smart Grid	137

9.1.3 Dynamic Line Ratings	138

9.1.4 Flexible Alternating-Current Transmission Systems	139

9.2 Integration of Active Demand Resources under the FCM	139

9.2.1 Modifications to ISO New England Operating Procedure No. 4	141

9.2.2 Creation of Demand-Designated Entities	141

9.2.3 Operator Interfaces	141

9.2.4 Development of New Communications Infrastructure	141

9.2.5 Use of Active-Demand-Resource Dispatch Zones	142

9.3 Integration of Variable-Output Generation	142

9.3.1 Studies of Variable-Output Generation Resources	143

9.3.2 Wind Generation Technology and Integration	144

9.3.3 Solar Energy Technologies and Integration	147

9.4 Summary	152

Section 10
System Performance and Production Cost Studies	153

10.1 2030 Power System Study for New England Governors	153

10.2 New York ISO/ISO New England Economic Study	155

10.2.1 Modeling and Assumptions	157

10.2.2 Simulation Metrics	161

10.3 Economic Study Requests, 2010	162

10.4 Generic Capital Costs of New Resources	162

10.5 Observations	164

Section 11
Interregional Planning and Studies	165

11.1 Studies of the Eastern Interconnection	165

11.1.1 U.S. DOE Study of National Interest Electric Transmission Corridors	165

11.1.2 Eastern Interconnection Planning Collaborative	166

11.1.3 Electric Reliability Organization Overview	167

11.2 Interregional Coordination	167

11.2.1 IRC Activities	167

11.2.2 Northeast Power Coordinating Council	168

11.2.3 Northeastern ISO/RTO Planning Coordination Protocol	169

11.3 Summary of Interregional Planning	170

Section 12
State, Regional and Federal Initiatives	171

12.1 State Initiatives, Activities, and Policies	171

12.1.1 Connecticut	171

12.1.2 Maine	172

12.1.3 Massachusetts	172

12.1.4 New Hampshire	174

12.1.5 Rhode Island	174

12.1.6 Vermont	175

12.2 Regional Initiatives	175

12.2.1 Coordination among the New England States	175

12.2.2 Regional Policy Development	176

12.2.3 Forward Capacity Market Updates	177

12.2.4 Price-Responsive Demand	177

12.2.5 Consumer Liaison Group	178

12.2.6 Regional Smart Grid Projects	178

12.3 ISO Initiatives	179

12.3.1 Project Cost Estimation and Controls Working Group	179

12.3.2 RSP Planning Process Updates	180

12.4 Federal Initiatives	181

12.5 Summary of Regional Initiatives	182

Section 13
Conclusions and Key Findings	183

13.1 RSP Tariff Requirements	183

13.2 RSP10 Outlook	184

Appendix A
RSP Project List	188

Appendix B
List of Acronyms and Abbreviations	188

# Figures

Figure 2-1: 	Key facts about New England’s electric power system and wholesale electricity markets, 2009.	16

Figure 2-2: 	RSP10 geographic scope of the New England electric power system.	20

Figure 3-1: 	“Economy.com” forecasts of New England annual percentage change in real personal income
from 2008 and 2009 forecasts.	25

Figure 3-2: 	Historical and projected annual percentage change in real personal income for New England
compared with the United States as a whole, 1981 to 2020.	26

Figure 3-3: 	Historical and forecast annual summer-peak loads, 1980 to 2019.	30

Figure 3-4: 	Historical and forecast annual energy use, 1980 to 2019.	31

Figure 4-1: 	New resource qualifications for participation in the FCAs.	44

Figure 4-2: 	Projected summer operable capacity analysis, 2010 to 2019.	46

Figure 4-3: 	Capacity of generation-interconnection requests by RSP subarea.	48

Figure 4-4: 	Resources in the ISO Generator Interconnection Queue, by state and fuel type, as of April 1, 2010 (MW and %).	49

Figure 6-1: 	Map of constraints in southern New England.	77

Figure 7-1: 	Generation capacity mix by primary fuel type, 2010 summer ratings (MW and %).	92

Figure 7-2: 	New England electric energy production in 2009, by fuel type.	93

Figure 7-3: 	Recent generating capacity additions, 2000 to 2009.	98

Figure 7-4: 	Shift in New England’s fuel mix, from 2000 to 2009.	102

Figure 8-1: 	Average seasonal concentrations of ozone in the Northeast, 2007 to 2009 (ppb).	106

Figure 8-2: 	New England system generation hourly NOX emissions on the five highest peak-load days,
2005 to 2008.	112

Figure 8-3: 	Hourly NOX emissions for the last dispatched 500 MW of thermal generation
on the peak-load day, August 2, 2006.	113

Figure 8-4: 	Projected cumulative targets for renewables and energy efficiency based on RPSs
and related policies, 2010 to 2020.	128

Figure 8-5: 	Cumulative RPS targets for new renewable resource classes beyond 2009, by state (GWh).	130

Figure 8-6: 	Proposed New England renewable resources in the ISO Generator Interconnection Queue
as of April 1, 2010 (MW and %).	130

Figure 8-7: 	Estimated energy from proposed New England renewable resources in the ISO’s Generator Interconnection Queue (including affected non-FERC queue projects) as of April 1, 2010
(GWh and %).	132

Figure 8-8: 	Various levels of estimated cumulative electric energy from new renewable projects
in the ISO queue, as of April 1, 2010 (including affected non-FERC queue projects)
compared with RPS demand by year.	134

Figure 9-1: 	Active-demand-resource dispatch zones in the ISO New England system.	142

Figure 9-2: 	Planned and active wind projects in New England, 2010.	145

Figure 9-3: 	Annual average solar radiation in the United States, 1998 to 2005.	148

Figure 9-4: 	Estimated monthly output of a PV system based on a composite of solar data
for Boston and Hartford.	149

Figure 10-1: 	Transmission interfaces and RSP areas.	156

Figure 10-2: 	Transmission interfaces Group 1.	158

Figure 10-3: 	Transmission interfaces Group 2.	158

# Tables

Table 3-1 	Summary of the Short-Run Forecasts of New England’s Annual Use of Electric Energy and 50/50 Peak Loads	22

Table 3-2 	Summary of Annual and Peak Use of Electric Energy for New England and the States	23

Table 3-3 	New England Economic and Demographic Forecast Summary	24

Table 3-4 	Forecasts of Annual and Peak Use of Electric Energy in RSP Subareas, 2010 and 2019	27

Table 3-5 	Forecasts of Peak Use of Electric Energy for Load Zones and the New England States, 2010	28

Table 3-6 	Forecasts of Peak Use of Electric Energy for RSP Subareas, 2010	29

Table 4-1 	Actual and Representative Future New England Net Installed Capacity Requirements
for 2010–2019 and Resulting Reserves	35

Table 4-2 	LSRs and MCLs for the First Four FCAs	37

Table 4-3 	Total New Resources that Cleared in FCA #1, FCA #2, and FCA #3 by State (MW and %)	39

Table 4-4 	Summary of the First, Second, and Third FCA Obligations (MW)	40

Table 4-5 	Results of FCA #1, FCA #2, and FCA #3 by Capacity Zone (MW, $/kW-month)	40

Table 4-6 	States’ Capacity Supply Obligations for the 2012/2013 Capacity Commitment Period	41

Table 4-7 	Demand-Resource Capacity that Cleared in FCA #3 (MW)	42

Table 4-8 	Actual and Representative Future New England Net Installed Capacity Requirements
for 2010–2019 and Potential Surplus ICAP	43

Table 4-9 	New Capacity Qualified for FCA #4	44

Table 4-10 	New Generation and Demand Resources that Qualified in FCA #4, by State (MW)	45

Table 4-11 	Projected New England Operable Capacity Analysis for Summer 2010 to 2019,
Assuming 50/50 loads (MW)	47

Table 4-12 	Projected New England Operable Capacity Analysis for Summer 2010 to 2019,
Assuming 90/10 Loads (MW)	47

Table 4-13 	Summary of Queue Projects as of April 1, 2010	49

Table 5-1  	Representative Future Operating-Reserve Requirements in Major New England
Import Areas (MW)	54

Table 5-2 	DRR Pilot Summary Statistics	57

Table 6-1 	Regional Network Service Rate Forecast, 2011 to 2014	66

Table 6-2 	Net Commitment-Period Compensation by Type and Year (million $)	88

Table 7-1 	New England’s Generation Capacity Mix by Fuel Type Compared with the Nationwide
Capacity Mix (%)	92

Table 7-2 	New England’s 2010 Summer Generation Capacity Mix by Fuel Type and In-Service Dates	102

Table 8-1  	Total New England Generator Emissions (1,000 tons)	110

Table 8-2 	New England Generator Average Emissions Rates, 1999 to 2008 (lbs/MWh)	110

Table 8-3 	New England Generation Annual Marginal Emission Rates (lbs/MWh)	111

Table 8-4 	Comparison of Emission Rates of Three RTO/ISOs (lbs/MWh)	111

Table 8-5 	Energy-Efficiency Resources Clearing the Primary FCM Auctions	114

Table 8-6 	Connecticut’s Sources of Funding for Energy-Efficiency Programs, 2009	115

Table 8-7 	Massachusetts’s Approved Spending for Energy-Efficiency Programs, 2010 to 2012	116

Table 8-8 	Rhode Island’s Approved Spending for Energy-Efficiency Programs, 2009	116

Table 8-9 	Vermont’s Funding Sources for Energy-Efficiency Programs, 2009	117

Table 8-10 	New Hampshire’s Proposed Funding Levels for the CORE Energy-Efficiency Programs, 2010	118

Table 8-11 	Maine’s Proposed Funding Levels and Sources for Energy-Efficiency Programs, 2011 to 2013	118

Table 8-12 	Projected Reductions in Electric Energy Use Based on the RSP Forecast
of 2020 State Loads (GWh)	119

Table 8-13 	Key Facts on the New England States’ Energy-Efficiency Programs and Goals	120

Table 8-14 	Summary of Technologies Designated in Renewable Portfolio Standards in New England	122

Table 8-15 	Annual Percentages of Electric Energy Use by Affected Load-Serving Entities
for Meeting the States’ RPS Classes, 2010 to 2020	123

Table 8-16 	Estimated New England RPS and Related Targets for Renewables and Energy Efficiency
(GWh and %)	127

Table 8-17 	New England RPS and Related Targets for Renewables and Energy Efficiency, by Category (%)	128

Table 8-18 	Projected New England RPSs for “New” Renewables Beyond 2009 (GWh)	129

Table 8-19 	Estimated Energy from New England Renewable Energy Projects in the ISO Queue
as of April 1, 2010	131

Table 8-20  	Summary of All Projects and Wind Projects in ISO Queue as of April 1, 2010	133

Table 9-1 	Solar Policies in New England and Neighboring Areas	151

Table 10-1 	Interfaces Modeled	159

Table 10-2 	Generic Capital Cost Estimates for Generation and Demand Resources	164

# Executive Summary

The ISO New England (ISO) 2010 Regional System Plan (RSP10) presents the results of load, resource, and transmission analyses of New England’s electric power system for the 10-year planning period through 2019. The report describes the major factors influencing the development of the electric power system for these future years and how the region can provide a reliable and economic system in compliance with federal and state regulations and guidelines. In addition to complying with the ISO’s Transmission, Markets, and Services Tariff, approved by the Federal Energy Regulatory Commission (FERC), RSP10 meets the criteria and requirements established by the North American Electric Reliability Corporation (NERC), the Northeast Power Coordinating Council (NPCC), and the region. The ISO conducts the planning process in full compliance with Attachment K of its Open Access Transmission Tariff, which is part of the ISO tariff.

## Major Findings and Observations

This section presents an overview of the major findings of RSP10 load forecasts; supply and demand resource and transmission planning; market outcomes; economic studies; and other programs, projects, and initiatives that are part of the system planning process. The sections of the report that contain more details of these findings and observations are indicated.

For all RSP10 analyses, the ISO applied a number of assumptions, which are subject to uncertainty over the course of the planning period. Some factors subject to change, which may vary RSP10 results and conclusions, are as follows:

Demand forecasts

Resource availability

Timing of planned system improvements

Fuel price forecasts

Market rules and governmental policies

Technology development

The ISO conducts sensitivity analyses to account for these factors, which could influence the development of needed transmission. While each RSP is a snapshot in time, the planning process is continuous, and the results are revisited as needed, accounting for appropriately updated information, such as load forecasts.

### Forecasting the Annual and Peak Use of Electric Energy and Load Growth

The RSP10 forecasts incorporate the expected effects of federal energy-efficiency (EE) standards for appliances and commercial equipment that will go into effect in 2013 and the historical energy-efficiency savings. Increases in state-sponsored EE programs, enrolled with the ISO as “other demand resources” (ODRs), contributed to the declines in electric energy demand in 2008 and 2009. The increased energy savings attributable to ODRs reduced the growth in weather-normalized electric energy consumption by 50% from 2008 to 2009. The peak load forecasts also account for updates in the historical weather data. These forecasts reflect the growth of the summer cooling load and a lower rate of growth of the winter heating load. (Section 3)

The expected summer peak forecast is 27,190 megawatts (MW) for 2010, which grows to 30,730 MW for 2019. The ISO forecasts the 10-year growth rate to be 1.4% per year for the summer peak load, 0.5% per year for the winter peak load, and 0.9% per year for electric energy. The annual load factor (i.e., the ratio of the average hourly load during a year to peak hourly load) declines from 55% in 2010 to 53% in 2019. This decrease indicates the less efficient use of electric power system infrastructure. (Section 3)

The forecasts are lower mainly due to the economic recession that began in 2008, reached its low point in 2009, and is expected to begin a weak recovery in late 2010. The lower load forecast affects the need for new resources and may delay the timing of some transmission projects. (Section 3)

### Identifying Needs for Capacity and Operating Reserves

The ISO’s system planning process identifies the needs for capacity and operating reserves. These needs are met through the Forward Capacity Market (FCM) and the locational Forward Reserve Market (FRM).

#### Capacity

The regional development of generation and demand resources is expected to provide the capacity needed to meet resource adequacy requirements (i.e., the minimum amount of capacity the region will require, called the Installed Capacity Requirement; ICR). The net ICR is expected to grow from 31,110 MW in 2011 to a representative value of 34,818 MW by 2019. (Section 4)

Assuming the over 35,000 MW of resources that cleared the third Forward Capacity Auction (FCA #3) for the capacity commitment period for 2012/2013 remain in commercial operation beyond 2012, and no generation or demand resources retire or permanently delist, New England should have adequate resources through 2019. Recent modifications to the FCM require the procurement of resources that meet both resource adequacy and transmission security needs, which ensure adequate resources in import-constrained areas. (Section 4)

#### Operating Reserves

Resources participating in the locational Forward Reserve Market are helping to satisfy the operating-reserve requirements of the region overall and of major load pockets in New England to cover contingencies (i.e., the sudden loss of a generation or transmission power system element). As a result of transmission upgrades and other resource additions, the Greater Southwest Connecticut area is not expected to need any local operating reserve for 2010 to 2014. Over the same period, the forecasted need for the Greater Connecticut area is 700 to 1,250 MW, and the need for the BOSTON area is in the range of 0 to 150 MW. The addition of in-merit generation within the major import areas, improvements to the transmission system, or some combination of both would decrease the need to locate operating reserves within these areas. A Demand-Response Reserves Pilot Program, completed in June 2010, assessed the ability of demand resources to provide operating reserves; the ISO and regional stakeholders are developing a follow-up program based on the results of the pilot. (Section 5)

### Identifying Transmission System Needs and Solutions

Key inputs to the transmission planning process are peak demand and electric energy growth, as well as the development of resources, including renewable and demand resources. Upgrades to the transmission system since 2002 have improved the New England transmission infrastructure; maintained power system reliability in accordance with NERC, NPCC, and ISO criteria and standards; and further reduced congestion costs and other charges. (Section 6)

Transmission planning studies, done collaboratively with transmission owners (TOs) and other stakeholders, have identified future reliability needs of the region and transmission improvements to solve them. Projects currently being identified, planned, and implemented are also laying the foundation for integrating new resources, including renewable energy resources, and are improving the economic performance of the system. The RSP10 identifies the continued need for transmission development across the region and summarizes the status of ongoing transmission studies and the results of projects in various stages of implementation. (Section 6)

#### Transmission Projects

The RSP Project List is a summary of transmission projects under various stages of development (i.e., concept, planned, proposed, and under construction), as required under Attachment K of the OATT to meet regional system needs. It also includes information on project status and cost estimates. The descriptions of transmission projects in RSP10 are based on the June 2010 update, which includes 189 projects at a total cost of approximately $5 billion. On the basis of these costs, the Regional Network Service (RNS) transmission rate is expected to grow from $64.83/kilowatt-year (kW-year) in 2010 to $110.07/kW-year in 2014, an increase of almost 70%. (Section 6)

The ISO updates the RSP Project List at least three times per year, as improvements are identified and projects are completed or eliminated from the list. In addition, the ISO regularly discusses system needs and the justification for transmission improvements with the PAC and the Reliability Committee, which provide guidance and comment on study scopes, assumptions, and results. All transmission projects are coordinated with other regions as well. The ISO will continue to work with regional TOs to improve project management cost estimates, cost transparency, and cost controls and provide timely and accurate transmission project cost estimates throughout the development of transmission projects. (Section 6)

The status of several major projects under development is as follows:

- The Maine Power Reliability Program (MPRP), for which the Maine Public Utilities Commission (MPUC) has approved most of the components, establishes a second 345 kilovolt (kV) path in the north from Surowiec to Orrington and adds new 345 kV lines in southern Maine, creating a third parallel path from Surowiec to Three Rivers. These new paths will provide basic infrastructure necessary to increase the ability to move power into Maine from New Hampshire, improve the ability of the transmission system within Maine to move power into the local load pockets as necessary, and increase transfer capability through Maine. (Section 6)

- The New England East–West Solution (NEEWS) series of projects had been identified to improve system reliability: (Section 6)

- As a result of the Needs Assessments and Solutions Studies conducted by the ISO and the completion of the siting proceedings completed by the affected states (Massachusetts, Connecticut, and Rhode Island), the Springfield and Rhode Island components of NEEWS should be placed in service as soon as possible.

- The Interstate Reliability Project and the Central Connecticut Reliability Project were reevaluated to account for the RSP10 load forecast, system operating constraints, resources acquired and delisted through the Forward Capacity Auctions, the impact of the unavailability of the Kleen Energy facility in Connecticut, and the possibility that the Vermont Yankee plant will not remain operational.

- On the basis of studies that considered these and other factors, the Interstate Reliability Project is needed to meet national and regional reliably criteria and serve load throughout southern and eastern New England. One need is to ensure deliverability of FCA-cleared resources from western New England to eastern New England and vice versa. The system Needs Assessment also identified the need for relieving generator mechanical stress issues, reducing high short-circuit availability at key substations, and improving system resiliency to withstand extreme contingencies and the retirement of generating units. The final alternatives for the Interstate Reliability Project remain under study. (Section 6)

- The need for the Central Connecticut Reliability Project is also under study.

Plans call for discussing these remaining studies with the PAC by the first quarter of 2011.

At various times, generating units in New England load pockets have been in “must-run” situations to serve area load reliably. These load pockets include portions of Maine, the Boston area, southeastern Massachusetts (SEMA), western Massachusetts, the Springfield area, and Connecticut. In addition to improving reliability, transmission improvements placed in service have reduced load costs associated with second-contingency and voltage-control payments to generators. The Lower Southeastern Massachusetts (Lower SEMA) short-term upgrades are one example of transmission improvements that have improved reliability, reduced dependencies on generating units, and reduced “make-whole” payments to market participants with resources whose operating costs were higher than their energy market revenues over a 24-hour dispatch day. (Section 6)

Several developers have proposed elective and merchant transmission upgrades, which are in various stages of study and development. These projects could increase New England’s tie capability with its neighbors and improve access to renewable sources of energy. The ISO will continue to monitor projected system conditions and needs based on the outcomes of these upgrades. (Section 6)

#### Interregional Planning

ISO New England’s planning activities are closely coordinated among the six New England states and other New England stakeholders, as well as with neighboring systems and nationally with the U.S. Department of Energy (DOE), the Federal Energy Regulatory Commission, and NERC. The ISO has coordinated system plans and has proactively initiated planning studies with other regions. The Northeastern ISO/RTO (Independent System Operator/Regional Transmission Organization) Planning Protocol has further improved interregional planning among neighboring areas. Sharing more supply and demand resources with other systems will likely become necessary, particularly, to meet environmental emission initiatives (see below). Identifying the potential impacts that proposed generating units and transmission projects could have on neighboring systems is beneficial to support interregional reliability and economic performance. (Section 11)

In August 2009, a coalition of the regional planning authorities within the Eastern Interconnection formed the Eastern Interconnection Planning Collaborative (EIPC). The EIPC is a first-of-its-kind effort to address North American planning issues, coordinate plans, and conduct studies for the entire Eastern Interconnection through a transparent and collaborative process with input from a broad base of interested stakeholders. Participants include federal and state policymakers; Canadian provincial officials; consumer and environmental advocates; transmission owners and developers; generation owners; other suppliers; and representatives from transmission-dependent utilities, public power companies, and electric cooperatives within the Eastern Interconnection. ISO New England and other planning authorities throughout the Eastern Interconnection are principal investigators in the EIPC process. The EIPC proposes to use local and regional planning processes and studies as the basis for performing new interconnection-wide analyses of various transmission alternatives. (Section 11)

The ISO participates in several other national and regional system planning forums, such as the Electric Reliability Organization, the ISO/RTO Council, and the Northeast Power Coordinating Council. The ISO is conducting a joint production-cost study with the New York ISO (NYISO) and PJM Interconnection (PJM) based on stakeholder requests received in 2009. This study is identifying transmission constraints limiting interregional power transfers and showing the effects of relaxing these constraints throughout the ISO/RTO regions. ISO New England will continue to coordinate efforts with neighboring systems to plan projects jointly, explore the ability to import power from and export power to the eastern Canadian provinces and New York, and participate in national and regional planning activities. (Sections 10 and 11)

### Developing and Integrating Resources

In addition to identifying the need for capacity and operating reserves, the ISO’s system planning process assesses the impacts of fuel diversity and environmental initiatives. It also identifies and resolves issues related to developing and integrating renewable resources, demand-resource applications, and smart grid technologies.

#### Fuel Diversity

New England will remain heavily dependent on natural gas as a primary fuel for generating electric energy for the foreseeable future; natural gas plants currently represent 41% of the region’s capacity and provided about 42% of the system’s electrical energy in 2009. Recent improvements to the regional and interregional natural gas infrastructure have helped expand and diversify natural gas sources to meet New England’s increasing demand for natural gas to produce electric power. Also, the implementation of operating procedures and improved communications between electric power and natural gas system operators have decreased operational risks and improved the reliability and diversity of natural gas supply and transportation. These steps have mitigated electric power system reliability concerns. (Section 7)

#### Environmental Emissions Requirements

The region and neighboring areas face extensive state and federal environmental initiatives that cover air emissions, water intake requirements, and the handling of coal combustion products. These regulations will continue to increase fossil fuel plant operating costs for emission allowances, add capital costs for environmental controls, and require the use of low-emitting fuels, which may limit generation capacity or energy production. The limited availability of emission allowances also could constrain generation capacity and fossil-fueled energy production, which could lead to new generation dispatch and commitment patterns and shifting costs. The ISO will monitor and evaluate environmental initiatives as they occur or are proposed and provide feedback and input to environmental regulators on the impacts the initiatives could have on power system operations and reliability. (Section 8)

Over the past 10 years, generating units in the region have been using cleaner fuels, particularly natural gas, and have added emission controls. As a result, the region’s average and marginal emission rates for sulfur dioxide, nitrous oxides, and carbon dioxide have continued to decline. Total emissions for SO2 and NOX also have continued to decrease with time. (Section 8)

Some aging generation facilities may retire before 2019 (the last year of this 10-year plan) because of the impact of stricter environmental regulations. However, the FCM allows resources with a significant investment in environmental upgrades to qualify as new resources, making them eligible for established FCM revenues for up to five years. Much of the 1,671 MW of new generation resources that cleared FCA #3 are from enhancements to existing facilities retrofitting to meet environmental regulations. (Sections 4 and 8)

#### Renewables, Demand Resources, and the Smart Grid

- Environmental regulations and policies, such as the Regional Greenhouse Gas Initiative (RGGI) and Renewable Portfolio Standards (RPSs), are stimulating the need for and development of renewable resources and energy efficiency in the region. Other regional and industry efforts are assisting in the process to integrate renewables, demand resources, and smart grid technologies:

- Meeting State Targets for Renewables and Energy Efficiency—The New England states have targets for the proportion of electric energy to be met by renewable resources, such as wind and solar, and energy efficiency. These state targets will increase to approximately 30% of New England’s total projected electric energy use by 2020. This goal of 30.4% consists of 11% energy-efficiency programs and 19.4% Renewable Portfolio Standards and policies addressing renewable supply and EE goals. Possible solutions for meeting or exceeding the region’s RPSs include developing the renewable resources in the ISO Generator Interconnection Queue, importing renewable resources from adjacent balancing authority areas, building new renewable resources in New England not yet in the queue and small “behind-the-meter” projects, and using eligible renewable fuels in existing generators. If renewable resource development is not meeting the RPSs, the use of state-established Alternative Compliance Payments (ACPs) can serve as a means of addressing the shortfall. (Section 8)

- Integrating Renewable Resources—The ISO is conducting a major study of integrating wind resources into the New England system. This study is analyzing various planning, operating, and market aspects of wind integration; simulations that add wind resources up to 12,000 MW; and the conceptual development of a transmission system that can integrate large amounts of wind generation resources. The study, scheduled to be completed in 2010, is developing models of generation output for a hypothesized fleet of wind plants suitable for ISO studies. (Section 9)

- Integrating Demand Resources—The operational and market integration of active demand resources, from approximately 1,300 MW in 2010 to over 1,800 MW by 2012, requires careful planning and coordination. Accordingly, control room applications and ISO operating procedures have been modified, and a new communications infrastructure has been implemented. (Section 9)

- Developing New England’s Smart Grid—Smart grid technologies represent the next stage in the evolution of the power system to improve data acquisition, analysis, control, and efficiency of the electric power grid. In 2010, the DOE approved funding for the ISO and the New England transmission owners to add over 30 new phasor measurement units (PMUs), which will be used to improve the monitoring and operation of the system. The ISO and stakeholders also will support research and development efforts and the establishment of industry standards for integrating smart grid technologies. (Section 9)

#### Economic Studies of Resource Integration

One of the major economic studies of the power system the ISO conducted in 2009 analyzed the development and delivery of large amounts of renewable resources within New England. This study was conducted at the request of the New England governors, made through the New England States Committee on Electricity (NESCOE), who used the study to develop a blueprint for integrating large-scale renewable energy resources into the region’s electric power grid. The ISO study demonstrated that the region has abundant sites for developing resources well in excess of its renewable targets, but an appropriate transmission infrastructure needs to be built to interconnect such renewables. The study also showed that the aggressive pursuit of New England and nearby Canadian resources could make this region a net provider of low- or non-carbon-emitting resources to the Eastern Interconnection.
(Section 10)

In 2010, NESCOE requested the ISO to conduct a follow-up study of replacing aging coal- and oil-fired generating units with efficient, low-pollution-emitting, natural gas combined-cycle units; wind resources within New England; and renewable imports from Canada. This study will further inform government officials as they establish policies that affect the future planning and development of the system.
(Section 10)

### Supporting State, Regional, and Federal Initiatives that Affect System Planning

The ISO continuously works with a wide variety of state policymakers and other regional stakeholders to upgrade its planning process. Regional initiatives have improved the planning process, such as the transparency of transmission cost estimates and the provision of critical load levels in Needs Assessments. The quality and extent of interregional analyses with neighboring areas has also been evident, as shown by the issuance of the Northeast Coordinated System Plan and the recently formed EIPC. One recently begun initiative will assess the impacts of FCM demand resources and state EE programs on the load forecast, the regional planning studies and processes, and market systems. Stakeholders also have requested additional information on the factors affecting the degradation of the systemwide load factor and whether actions should and can be taken to improve it. Another new initiative will provide additional information on the ability of nontransmission alternatives (NTAs) to meet system needs. Stakeholders have also asked the ISO to consider the retirement of aging, environmentally challenged generating units and conduct transmission planning analyses for some of these scenarios. Plans call for discussing these issues with the PAC beginning in the fourth quarter of 2010 and providing an update on their status in RSP11. (Section 12)

- Active involvement and participation by all stakeholders, including public officials, state agencies, NESCOE, market participants, and other PAC members, are key elements of an open, transparent, and successful planning process. The ISO has continued to work with other representatives of the New England states, primarily through the PAC but also through designated representative organizations, such as the New England Conference of Public Utilities Commissioners (NECPUC), the New England Governors’ Conference (NEGC), and the Consumer Liaison Group (CLG). As needed, the ISO will work with these groups, as well as NEPOOL members and other interested parties, to support regional and federal policy initiatives. One of these initiatives is compliance with an upcoming FERC ruling, based on a Notice of Proposed Rulemaking on transmission planning and cost allocation. The ISO will continue to provide required technical support to the New England states and the federal government as they formulate policies for the region (Section 12)

## Conclusions

The ISO’s 2010 Regional System Plan provides information on the timing, location, and type of system resources as well as transmission projects necessary to serve load reliably throughout the region through 2019. The economic recession has slowed the growth in summer peak demand, while wholesale electricity markets and other factors have stimulated the successful development of supply and demand resources to meet the needs of the New England region. Assuming no major resource retirements, the need for new power system infrastructure could be delayed or eliminated over the next 10 years. However, the likelihood of power plant retirements and the expected realization of the region’s renewable resource potential will require additional consideration during the planning process to meet system needs.

The region’s heavy dependence on natural-gas-fired generation to supply its electricity needs is expected to grow. At the same time, environmental and economic incentives provided by the wholesale electricity markets and government policies are encouraging the development of clean, renewable resources, such as wind and solar. In addition, demand resources are expected to increase. Economic studies have shown the effects of these types of resources and possible new imports from Canada, providing useful information to guide the decisions of policymakers and resource developers. Also, smart grid technologies are being developed to improve the electric power system’s performance and operating flexibility.

RSP10 and its complementary RSP Project List, Needs Assessments, and Solution Studies provide detailed information on the system changes required for serving load reliably in New England for the next 10 years. Transmission projects are in various stages of development, and many have begun or have completed the siting process. Finally, elective and merchant transmission facilities, in various stages of development, have the potential to provide access to renewable resources in remote areas of the region and in neighboring areas.

# Introduction

As the Regional Transmission Operator (RTO) for New England, ISO New England (ISO) operates the region’s electric power system, administers the region’s competitive wholesale electricity markets, and is responsible for the regional planning process. It also coordinates planning efforts with neighboring areas. To carry out its planning responsibilities, the ISO works closely with members of the Planning Advisory Committee (PAC). PAC membership is open to all and currently includes representatives from governmental agencies, transmission owners (TOs), market participants, other New England Power Pool (NEPOOL) members, consulting companies, manufacturers, and other organizations, such as universities and environmental groups.

“The ISO shall develop the RSP . . . [which] is a compilation of the regional system planning process activities conducted by the ISO during a given year.” (Attachment K, § 1)

“The RSP shall be based on a five- to ten-year planning horizon, and reflect five- to ten-year capacity and load forecasts.” (Attachment K, § 3.3)

In compliance with Attachment K of its Open Access Transmission Tariff (OATT) and to provide information to stakeholders for developing supply and demand resources and transmission solutions to meet system needs, the 2010 Regional System Plan (RSP10) describes the ISO’s annual system resource and transmission planning activities for the 10-year period to 2019. It also summarizes the results of regional and local-area studies, as follows:

- Load forecasts for the annual and peak use of electric energy

- Analyses of the amount, characteristics, and locations of needed capacity and operating reserves

- Assessments of systemwide and local-area transmission system needs and solutions

- Simulations of the estimated economic and environmental performance of various future resource- and transmission-expansion scenarios.

RSP10 also summarizes information and activities concerning the status of the region’s fuel diversity; resource development and integration, including renewables, demand resources, and new technologies; environmental issues associated with power plant air emissions and water discharges; and the New England states’ energy-efficiency (EE) programs. The RSP also reports on state, regional, federal, and eastern Canadian initiatives relevant to New England’s power system planning and joint planning efforts with New York and other neighboring power systems.

Appendix A provides a link to the RSP Project List, which includes the status of transmission upgrades during a project’s lifecycle. RSP10 incorporates information from the June 2010 list. Appendix B is a list of acronyms and abbreviations used in RSP10. Italicized terms are defined within the text and footnotes. The text boxes included in this report contain Attachment K requirements and indicate the ISO’s compliance with the requirements. All Web site addresses are current as of the time of publication.

- This section summarizes the ISO’s regional system planning process per the requirements of the ISO’s tariffs. As background, the section provides an overview of the power system and wholesale market structure in New England and the RSP subareas used in system planning studies.

## Approach to Regional System Planning

The main objectives of the ISO’s regional system planning process are to identify system enhancements required to ensure the reliability of the system, facilitate the efficient operation of the markets, and provide information to regional stakeholders, who can use the information to conduct independent analyses and further develop system improvements. The development of needed supply and demand resources and transmission upgrades supports the reliable operation of the power system for the short and long term. The transmission upgrades also enhance the region’s ability to support a robust, competitive wholesale power market by reliably moving power from various internal and external sources to the region’s load centers. In addition to meeting regional reliability needs and supporting the markets, additional transmission infrastructure can build a foundation for integrating new resources, including renewables.

#### Working with the Planning Advisory Committee

”Specifically, the Planning Advisory Committee serves to review and provide input and comment on:  (i) the development of the RSP, (ii) assumptions for studies, (iii) the results of Needs Assessments and Solutions Studies, and (iv) potential market responses to the needs identified by the ISO in a Needs Assessment or the RSP. The Planning Advisory Committee, with the assistance of and in coordination with the ISO, serves also to identify and prioritize requests for Economic Studies to be performed by the ISO, and provides input and feedback to the ISO concerning the conduct of Economic Studies, including the criteria and assumptions for such studies.” (Attachment K, § 2.2)

“Any entity, including State regulators or agencies and, if in existence, a Regional State Committee or similarly situated entity, as specified in Attachment N of the OATT, may designate a member to the Planning Advisory Committee . . . ” (Attachment K, § 2.3)

“Meetings of the Planning Advisory Committee shall be held as frequently as necessary to serve the purposes stated in Section 2.2 of this Attachment and as further specified elsewhere in this Attachment, generally expected to be no less than four (4) times per year.” (Attachment K, § 2.4)

The primary means of conducting the system planning process is through the open and transparent stakeholder forum with the PAC. The ISO has worked closely with the region’s stakeholders through this process. Several PAC sessions for RSP10 focused on particular issues, such as the planning process (March 8), the effect of the economy on the load forecast (March 18), and environmental issues (May 25). For RSP10, the ISO and the PAC have discussed all draft study scopes of work, assumptions, draft results, and final study results. They also have discussed economic study proposals, scopes of work, assumptions, and draft and final results. For RSP10, as in past years, feedback from the PAC has been referred to NEPOOL technical committees.

#### Forecasting Demand and Determining System Needs

“The RSP shall address needs of the PTF system determined by the ISO through Needs Assessments initiated and updated on an ongoing basis by the ISO to:  (i) account for changes in the PTF system conditions; (ii) ensure reliability of the PTF system; (iii) comply with national and regional planning standards, criteria and procedures; and (iv) account for market performance and economic, environmental and other considerations as may be agreed upon from time to time.”  (Attachment K, § 1)

“In addition, the RSP shall also provide information on a broad variety of power system requirements that serves as input for reviewing the design of the markets and the overall economic performance of the system.” (Attachment K, § 1)

“The ISO shall incorporate market responses that have met the criteria  . . into the Needs Assessments or the Regional System Plan (“RSP”) . . . Where market responses incorporated into the Need Assessments do not eliminate or address the needs identified by the ISO in Needs Assessments or the RSP, the ISO shall develop or evaluate . . . regulated transmission solutions proposed in response to the needs identified by the ISO.” (Attachment K, § 1)

“The RSP shall, among other things . . . (iii) specify the physical characteristics of the physical solutions that can meet the needs defined in the Needs Assessments and include information on market responses that can address them; (iv) provide sufficient information to allow Market Participants to assess the quantity, general locations, operating characteristics and required availability criteria of the type of incremental supply or demand-side resources, or merchant transmission projects, that would satisfy the identified needs or that may serve to modify, offset or defer proposed regulated transmission upgrades.” (Attachment K, § 3.1)

”On a regular and ongoing basis, the ISO, in coordination with the PTOs and the Planning Advisory Committee, shall conduct assessments (i.e., Needs Assessments) of the adequacy of the PTF system, as a whole or in part, to maintain the reliability of such facilities while promoting the operation of efficient wholesale electric markets in New England. A Needs Assessment shall also identify: (i) the location and nature of any potential problems with respect to the PTF and (ii) situations that significantly affect the reliable and efficient operation of the PTF along with any critical time constraints for addressing the needs of the PTF to facilitate the development of market responses and to initiate the pursuit of regulated transmission solutions.” (Attachment K, § 4.1)

The key drivers for determining whether and where system improvements are needed are the forecasts of the annual and peak use of electric energy over a five- to 10-year planning period. RSP10 projects electric energy use for 2010 to 2019.

To assess how to maintain the reliability of the New England power system, while promoting the operation of efficient wholesale electricity markets, the ISO and its stakeholders analyze the system and its components as a whole. They account for the performance of these individual elements and the many varied and complex interactions that occur among the components and affect the overall performance of the system. Specifically, the electric power planning process in New England assesses the amounts and general locations of resources the overall system and individual areas of the system need, the types of resources that can satisfy these needs, and any critical time constraints for addressing them.

#### Developing Transmission and Nontransmission Alternatives to Address System Needs

Using information on defined system needs developed during the system planning process, a variety of established signals from ISO-administered markets, and other factors, stakeholders responsible for developing needed resources can assess their options for satisfying these needs and commit to developing projects. Stakeholders can, for example, build a new power plant to provide additional system capacity, participate in ISO programs to reduce the amount of electric energy used, or provide merchant transmission upgrades. These merchant transmission and nontransmission alternatives (NTAs) could result in modifying, offsetting, or deferring proposed regulated transmission upgrades.

#### Developing Needs Assessments, Solutions Studies, and the RSP Project List

“The RSP Project List shall identify regulated transmission solutions proposed in response to the needs identified in a RSP or Needs Assessments conducted pursuant to Section 4.1 of this Attachment. The RSP Project List shall identify the proposed regulated transmission solutions separately as either a Reliability Transmission Upgrade or a Market Efficiency Transmission Upgrade. The RSP Project List will be updated by the ISO periodically by adding, removing or revising regulated transmission solutions or Transmission Upgrades in consultation with the Planning Advisory Committee and, as appropriate, the Reliability Committee.” (Attachment K, § 3.6)

To the extent that stakeholder responses to market signals are not forthcoming or adequate to meet identified system needs, the planning process requires the ISO, through the open stakeholder process, to conduct subsequent transmission planning to develop regulated transmission solutions that determine transmission infrastructure that can meet the identified needs. The ISO does not, however, have the authority to build needed resources or transmission. With input from stakeholders, the ISO prepares Needs Assessments, which identify the needs for transmission solutions, and Solutions Studies, which describe options for meeting the identified needs. Subsequent assessments report on the status of these solutions, which typically are implemented over several years. These transmission projects are part of the ISO’s RSP Project List (see Section 6.3), which is updated several times per year and can be accessed in Appendix A of this document.

#### Providing Information to Stakeholders

To provide the needed information to stakeholders, including developers interested in developing supply and demand resource alternatives to transmission projects, the ISO issues the comprehensive annual Regional System Plan, the RSP Project List, Needs Assessments, and Solutions Studies. In addition, the ISO posts on its Web site detailed supplemental information to the RSP process, such as the Annual Markets Report, presentations, and other reports. The ISO also makes available databases used in its analyses, consistent with FERC policies and the ISO Information Policy requirements pertaining to both confidential information and critical energy infrastructure information (CEII) requirements.

“The RSP shall also describe the coordination of the ISO’s regional system plans with regional, local and inter-area planning activities.”  (Attachment K, § 1)

Coordinating with Neighboring Areas

In developing the Regional System Plans, the ISO also is required to coordinate study efforts with surrounding RTOs and balancing authority areas and to analyze information and data presented in neighboring plans. This is achieved through a number of interregional agreements and joint studies with neighboring regions and across the entire Eastern Interconnection.

”The RSP shall conform to:  Good Utility Practice; applicable Commission compliance requirements related to the regional system planning process; applicable reliability principles, guidelines, criteria, rules, procedures and standards of the ERO, NPCC, and any of their successors; planning criteria adopted and/or developed by the ISO; Transmission Owner criteria, rules, standards, guides and policies developed by the Transmission Owner for its facilities consistent with the ISO planning criteria, the applicable criteria of the ERO and NPCC; local transmission planning criteria; and the ISO New England Planning Procedures and ISO New England Operating Procedures, as they may be amended from time to time (collectively, the “Planning and Reliability Criteria”).” (Attachment K, § 3.3)

Meeting All Requirements

In addition to complying with the ISO tariffs, which reflect the improvements to the regional planning process adopted in 2008 to comply with the planning principles required by FERC Order 890, RSP10 complies with North American Electric Reliability Corporation (NERC) and Northeast Power Coordinating Council (NPCC) criteria and standards, as well as ISO planning and operating procedures. RSP10 also conforms to transmission owner criteria, rules, standards, guides, and policies consistent with NERC, NPCC, and ISO criteria, standards, and procedures.

Regional system planning must account for the uncertainty in assumptions made about the next 10 years stemming from changing demand, fuel prices, technologies, market rules, and environmental requirements; other relevant events; and the physical conditions under which the system might be operating. The development and retirement of resources and changes in the load forecast are major factors affecting the development and timing of needed transmission facilities. While each RSP represents a snapshot in time, the planning process is continuous, and the results are revisited as needed as new information becomes available.

## Overview of the New England Electric Power System

Since 1971, New England’s electric power grid has been planned and operated as a unified system of its NEPOOL members. The New England system integrates resources with the transmission system to serve all regional load regardless of state boundaries. Most of the transmission lines are relatively short and networked as a grid. Therefore, the electrical performance in one part of the system affects all areas of the system.

As shown in Figure 2-1, the New England regional electric power system serves 14 million people living in a 68,000 square-mile area. More than 300 generating units, representing approximately 32,000 megawatts (MW) of total generating capacity, produce electric energy, measured in megawatt-hours (MWh). Most of these facilities are connected through over 8,000 miles of high-voltage transmission lines. Thirteen tie lines interconnect New England with neighboring New York State and the provinces of New Brunswick and Québec, Canada. Demand resources now play a significant role in operating the New England power system. As of summer 2010, approximately 1,900 MW of demand resources representing load reductions and “behind-the-meter” generators are registered as part of ISO’s Forward Capacity Market.

|  | - 6.5 million households and businesses; population 14 million - Over 300 generators - 32,000 MW of total generation - Over 8,000 miles of transmission lines - 13 interconnections to electricity systems in New York and Canada - About 1,900 MW of demand-resources - All-time peak demand of 28,130 MW, set on August 2, 2006 - More than 400 participants in the marketplace (those who generate, buy, sell, transport, and use wholesale electricity and implement demand resources) - $7.5 billion total market value; $5.3 billion energy market - More than $4.0 billion in transmission investment from 2002 through 2010 to enhance system reliability; approximately $5 billion planned over the next 10 years - Seven major 345-kilovolt projects constructed in four states |
| --- | --- |

Figure 2-1: Key facts about New England’s electric power system and wholesale electricity markets, 2009.

Note: The total load on August 2, 2006, would have been 28,770 MW had it not been reduced by approximately 640 MW, which included a 490 MW demand reduction in response to ISO Operating Procedure No. 4, Action during a Capacity Deficiency (OP 4); a 45 MW reduction of other interruptible OP 4 loads; and a 107 MW reduction of load as a result of price-response programs, which are outside of OP 4 actions. More information on OP 4 is available at http://www.iso-ne.com/rules_proceds/operating/isone/op4/OP4_RTO_FIN.doc. Also see Section 4.

The ISO’s all-time actual summer peak demand was 28,130 MW on August 2, 2006, which was due to extreme temperatures and humidity regionwide. In accordance with ISO operating procedures, demand-response programs were activated during this period, which lowered this peak by approximately 640 MW. Without these programs, the peak would have been approximately 28,770 MW. The 2009 summer peak was much lower at about 25,100 MW, primarily because of mild summer weather conditions, and would have been 682 MW higher without demand resources. The ISO’s all-time actual winter peak of 22,818 MW occurred on January 15, 2004. The 2009/2010 winter peak was much lower at 20,791 MW, also because of less extreme weather conditions, and would have been 766 MW higher without demand resources.

## Overview of the New England Wholesale Electricity Market Structure

New England’s wholesale electricity markets facilitate the buying, selling, and transporting of wholesale electricity, as well as ensure proper system frequency and voltage, sufficient future capacity, seasonal and real-time reserve capacity, and system restoration capability after a blackout. Stakeholders also have the opportunity to hedge against the costs associated with transmission congestion. As shown in Figure 2-1, in 2009, over 400 market participants completed transactions in New England’s wholesale electricity markets totaling $7.5 billion. The wholesale electricity markets and market products in New England are as follows:

- Day-Ahead Energy Market—allows market participants to secure prices for electric energy the day before the operating day and hedge against price fluctuations that can occur in real time.

- Real-Time Energy Market—coordinates the dispatch of generation and demand resources to meet the instantaneous demand for electricity.

- Forward Capacity Market (FCM)—ensures the sufficiency of installed capacity, which includes demand resources, to meet the future demand for electricity by sending appropriate price signals to attract new investment and maintain existing investment both where and when needed.

- Financial Transmission Rights (FTRs)—allows participants to hedge against the economic impacts associated with transmission congestion and provides a financial instrument to arbitrage differences between expected and actual day-ahead congestion.

- Ancillary services

- Regulation Market—compensates resources that the ISO instructs to increase or decrease output moment by moment to balance the variations in demand and system frequency to meet industry standards.

- Forward Reserve Market (FRM)—compensates generators for the availability of their unloaded operating capacity that can be converted into electric energy within 10 or 30 minutes when needed to respond to system contingencies, such as unexpected outages.

- Real-time reserve pricing—compensates on-line generators that offer their electric energy above the marginal cost for the increased value of their energy when the system or portions of the system are short of reserves. It also provides efficient price signals to generators when redispatch is needed to provide additional reserves to meet requirements.

- Voltage support—compensates resources for maintaining voltage-control capability, which allows system operators to maintain transmission voltages within acceptable limits.

The market structure for conducting wholesale electric energy transactions in New England is Standard Market Design (SMD). One key feature of SMD is locational marginal pricing, which is a way for electric energy prices to reflect the variations in supply, demand, and transmission system limitations effectively at every location where electric energy enters or exits the wholesale network. In New England, wholesale electricity prices are set at approximately 900 pricing points (i.e., pnodes) on the power grid. Locational marginal prices (LMPs) differ among these locations as a result of each location’s marginal cost of congestion and marginal cost of line losses.

The congestion cost component of an LMP arises because of transmission system constraints that limit the flow of the least-cost generation, which results in the need to dispatch more costly generation. Line losses are caused by physical resistance in the transmission system as electricity travels through transformers, reactors, and other types of equipment, which produces heat and results in less power being withdrawn from the system than was injected. Line losses and their associated marginal costs are inherent to transmission lines and other grid infrastructure as electric energy flows from generators to loads. As with the marginal cost of congestion, the marginal cost of losses affects the amount of generation that must be dispatched. The ISO operates the system to minimize total system costs, while recognizing physical limitations of the system. If the system were entirely unconstrained and had no losses, all LMPs would be the same, reflecting only the cost of serving the next megawatt increment of load by the generator with the lowest-cost electric energy available, which would be able to flow to any point on the transmission system.

The pricing points on the system include individual generating units, load nodes, load zones (i.e., aggregations of load pnodes within a specific area), and the Hub. The Hub is a collection of locations that has a price intended to represent an uncongested price for electric energy, facilitate trading, and enhance transparency and liquidity in the marketplace. In New England, generators are paid the LMP for electric energy at their respective nodes, and participants serving demand pay the price at their respective load zones.

Import-constrained load zones are areas within New England that do not have enough local resources and transmission-import capability to serve local demand reliably or economically. Export-constrained load zones are areas within New England where the available resources, after serving local load, exceed the areas’ transmission capability to export the excess electric energy. New England is divided into the following eight load zones used for wholesale market billing: Maine (ME), New Hampshire (NH), Vermont (VT), Rhode Island (RI), Connecticut (CT), Western/Central Massachusetts (WCMA), Northeast Massachusetts and Boston (NEMA), and Southeast Massachusetts (SEMA).

A capacity zone is a geographic subregion of the New England Balancing Authority Area that may represent load zones that are export constrained, import constrained, or contiguous—neither export nor import constrained. Capacity zones are used in the Forward Capacity Auctions (FCAs) (see Section 4.2). The region also currently has four reserve zones—Connecticut (CT), Southwest Connecticut (SWCT), NEMA/Boston, and the rest of the system (Rest-of-System, ROS) (i.e., the area excluding the other, local reserve zones). Additionally, the region is divided into 19 demand-resource dispatch zones, which are groups of nodes used to dispatch real-time demand-response resources or real-time emergency generation (RTEG) resources (see Section 4.2.1.1).

## RSP Subareas

To assist in modeling and planning electricity resources in New England, the ISO established 13 subareas of the region’s electric power system. These subareas form a simplified model of load areas connected by the major transmission interfaces across the system. The simplified model illustrates possible physical limitations to the reliable flow of power that can evolve over time as the system changes.

Figure 2-2 shows the ISO subareas and three external balancing authority areas. While more detailed models are used for transmission planning studies and for the real-time operation of the system, the subarea representation shown in Figure 2-2 is suitable for RSP10 studies of resource adequacy, production cost, and environmental emissions.

|  | Subarea Designation | Region or State |
| --- | --- | --- |
|  | BHE | Northeastern Maine |
|  | ME | Western and central Maine/ Saco Valley, New Hampshire |
|  | SME | Southeastern Maine |
|  | NH | Northern, eastern, and central New Hampshire/eastern Vermont and southwestern Maine |
|  | VT | Vermont/southwestern New Hampshire |
|  | Boston (all capitalized) | Greater Boston, including the North Shore |
|  | CMA/NEMA | Central Massachusetts/ northeastern Massachusetts |
|  | WMA | Western Massachusetts |
|  | SEMA | Southeastern Massachusetts/ Newport, Rhode Island |
|  | RI | Rhode Island/bordering Massachusetts |
|  | CT | Northern and eastern Connecticut |
|  | SWCT | Southwestern Connecticut |
|  | NOR | Norwalk/Stamford, Connecticut |
|  | NB, HQ, and NY | New Brunswick (Maritimes), Hydro­Québec, and New York external balancing authority areas |

Figure 2-2: RSP10 geographic scope of the New England electric power system.

Notes: Some RSP studies investigate conditions in Greater Connecticut, which combines the NOR, SWCT, and CT subareas. This area has similar boundaries to the State of Connecticut but is slightly smaller because of electrical system configurations near the border with western Massachusetts. Greater Southwest Connecticut includes the southwest and western portions of Connecticut and consists of the NOR and SWCT subareas. NB includes New Brunswick, Nova Scotia, and Prince Edward Island (i.e., the Maritime provinces) plus the area served by the Northern Maine Independent System Administrator (USA).

# Forecasts of Annual and Peak Use
of Electric Energy in New England

“The RSP shall, among other things …. (ii) provide the projected annual and peak demands for electric energy for a five- to ten-year horizon.” (Attachment K, § 3.1)

“The RSP shall be based on a five- to ten-year planning horizon, and reflect five- to ten-year capacity and load forecasts.” (Attachment K, § 3.3)

Load forecasts provide key inputs for evaluating the reliability and economic performance of the electric power system under various conditions and for determining whether and when improvements are needed. This section summarizes the short- and long-run forecasts of the annual and peak use of electric energy, New England-wide and in the states and subareas. The section describes the economic and demographic factors that drive the forecasts and explains the forecast methodology. It also summarizes the recent review of the ISO’s forecast methodology, which reflects input from stakeholders and includes suggestions for improved transparency and technical accuracy.

## Short- and Long-Run Forecasts

The ISO forecasts are estimates of the total amounts of electric energy that will be needed in the New England states annually and during seasonal peak hours. The short-run forecast projects peak load and annual energy use for 2010 and 2011. The long-run forecast provides load data for 2012 through winter 2019/2020. Each forecast cycle updates the data for the region’s historical annual and peak use of electric energy by including an additional year of data, the most recent economic and demographic forecasts, and resettlement adjustments that include meter corrections.

The current economic recession dominates the changes in the annual and seasonal peak-load forecasts. The economic analysis used by the ISO shows the national and regional recession, which started in mid-2008, to be more severe than forecasted for the 2009 Regional System Plan (RSP09). The load forecasts are based on economic forecasts from November 2009 that projected the low point of the recession occurring in late 2009 and the economy starting to recover in 2010.

Similar to the annual and seasonal peak-load forecasts, the current economic recession dominates the changes in the short-run forecasts, which are shown in Table 3-1 for 2010 and 2011. Electric energy use is forecast to decline by 0.6% in 2010 but recover and grow by 0.8% in 2011. The summer peak load is forecast to decline by 0.1% in 2010 but recover and grow by 1.7% in 2011. The winter peak load is forecast to grow by 0.2% in 2010 and by 0.6% in 2011.

Table 3-1
Summary of the Short-Run Forecasts of New England’s
Annual Use of Electric Energy and 50/50 Peak Loads

| Parameter | 2009(a) | 2010 | 2011 | % Change 2009–2010 | % Change 2010–2011 |
| --- | --- | --- | --- | --- | --- |
| Annual use of electric energy (1,000 MWh) (NEL) | 132,045 | 131,305 | 132,370 | −0.6 | 0.8 |
| Summer peak (MW) | 27,220 | 27,190 | 27,660 | −0.1 | 1.7 |
| Winter peak (MW)(b) | 22,030 | 22,085 | 22,225 | 0.2 | 0.6 |

(a)	The weather-normal actual load is shown for the 2009 annual energy use and summer peak load.

(b)	The winter peak could occur in the following year.

The net energy for load (NEL) shown in Table 3-1 is the net generation output within an area, accounting for electric energy imports from other areas and electric energy exports to other areas. It also accounts for system losses but excludes the electric energy consumption required to operate pumped-storage plants. The seasonal peak load and annual energy forecasts also do not reflect or subtract the peak and electric energy savings attributable to passive demand resources (PDRs) (i.e., demand resources, such as energy-efficiency measures, designed to save electric energy) treated as capacity based on FCM obligations and as resources in resource adequacy and transmission planning studies (see Section 3.5 and Section 4.2.1.1). The effects of long-term state EE goals are not fully captured in the ISO load forecast, but this is an open issue discussed in Sections 8.4 and 12.3.2.

The 50/50 “reference” case peak loads shown in Table 3-1 have a 50% chance of being exceeded because of weather conditions. For the reference case, the summer peak load is expected to occur at a weighted New England-wide temperature of 90.2ºF, and the winter peak load is expected to occur at 7.0ºF. The 90/10 “extreme” case peak loads have a 10% chance of being exceeded because of weather (see Table 3-2). For the extreme case, the summer peak is expected to occur at a temperature of 94.2ºF, and the winter peak is expected to occur at a temperature of 1.6ºF.

Table 3-2
Summary of Annual and Peak Use of Electric Energy for New England and the States

| State(a) | Net Energy for Load (1,000 MWh) |  |  | Summer Peak Loads (MW) |  |  |  |  | Winter Peak Loads (MW) |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | 50/50 |  | 90/10 |  |  | 50/50 |  | 90/10 |  |  |
|  | 2010 | 2019 | CAGR(b) | 2010 | 2019 | 2010 | 2019 | CAGR(b) | 2010/11 | 2019/20 | 2010/11 | 2019/20 | CAGR(b) |
| CT | 32,675 | 34,465 | 0.6 | 7,240 | 8,050 | 7,865 | 8,760 | 1.2 | 5,710 | 5,835 | 5,880 | 6,010 | 0.2 |
| ME | 11,975 | 12,975 | 0.9 | 2,030 | 2,315 | 2,165 | 2,485 | 1.5 | 1,915 | 1,965 | 1,975 | 2,025 | 0.3 |
| MA | 60,305 | 66,510 | 1.1 | 12,620 | 14,315 | 13,555 | 15,415 | 1.4 | 10,065 | 10,590 | 10,375 | 10,900 | 0.5 |
| NH | 11,620 | 12,940 | 1.2 | 2,410 | 2,815 | 2,590 | 3,040 | 1.8 | 1,990 | 2,160 | 2,070 | 2,240 | 0.9 |
| RI | 8,315 | 8,845 | 0.7 | 1,825 | 2,045 | 2,035 | 2,290 | 1.3 | 1,365 | 1,430 | 1,410 | 1,475 | 0.5 |
| VT | 6,415 | 6,780 | 0.6 | 1,060 | 1,185 | 1,100 | 1,235 | 1.3 | 1,040 | 1,085 | 1,055 | 1,100 | 0.5 |
| New England | 131,305 | 142,520 | 0.9 | 27,190 | 30,730 | 29,310 | 33,225 | 1.4 | 22,085 | 23,070 | 22,765 | 23,750 | 0.5 |

- A variety of factors cause state growth rates to differ from the overall growth rate for New England. For example, New Hampshire has the fastest-growing economy in New England, and Connecticut has the slowest-growing economy in the region.

- CAGR stands for compound annual growth rate.

Table 3-2 summarizes the ISO’s long-run forecasts of annual electric energy use and seasonal peak load (50/50 and 90/10) for New England overall and for each state. The price of electricity and other economic and demographic factors (see Section 3.2) drive the annual use of electric energy and the growth of the seasonal peak. The compound annual growth rate (CAGR) for electric energy use is 0.9% for 2010 through 2019. The CAGR for the summer peak load is 1.4% per year for 2010 through 2019, while the CAGR for the winter peak is 0.5%. The systemwide load factor (i.e., the ratio of the average hourly load during a year to peak hourly load) declines from 55% in 2010 to 53% in 2019. The decline is attributable to several factors—the increased penetration of cooling load (e.g., air conditioning), which increases the summer peak load; the loss of industry with less variability in its load throughout the year; and the addition of energy-efficient lighting, which decreases load during low-load periods—all of which indicate the less efficient use of electric power system infrastructure.

## Economic and Demographic Factors and Electric Energy Use

The ISO’s forecasts of electric energy use in New England and each state are based on a total energy-use concept, which sums the total electric energy used residentially (about 40%), commercially (about 40%), and industrially (about 20%). Real income and the real price of electricity, which serve as proxies for overall economic and demographic conditions, are the primary factors applied to determine electric energy use. Table 3-3 summarizes these and other indicators of the New England economy.

Table 3-3
New England Economic and Demographic Forecast Summary

| Factor | 1980 | 2009 | CAGR | 2010 | 2019 | CAGR |
| --- | --- | --- | --- | --- | --- | --- |
| Summer peak (MW) | 14,539 | 27,220 | 2.2 | 27,190 | 30,730 | 1.4 |
| Net energy for load (1,000 MWh) | 82,927 | 132,045 | 1.6 | 131,305 | 142,520 | 0.9 |
| Population (thousands) | 12,378 | 14,337 | 0.5 | 14,369 | 14,685 | 0.2 |
| Real price of electricity (¢/kWh, 1996 $)(a) | 11.990 | 11.617 | −0.1 | 11.691 | 11.484 | −0.2 |
| Employment (thousands) | 5,485 | 6,810 | 0.7 | 6,718 | 7,340 | 1.0 |
| Real income (millions, 2005 $) | 281,871 | 629,265 | 2.8 | 627,438 | 765,697 | 2.2 |
| Real gross state product (millions, 2000 $) | 277,035 | 626,220 | 2.9 | 640,226 | 841,344 | 3.1 |
| Energy per household (MWh) | 18.954 | 23.101 | 0.7 | 22.944 | 23.712 | 0.4 |
| Real income per household (thousands) (2005 base year) | 64.425 | 113.332 | 2.0 | 112.680 | 130.750 | 1.7 |

(a) kWh stands for kilowatt-hour.

The forecast for 2010 to 2019 of the retail electricity price assumes increases will be held to the rate of inflation (2.4% average annual growth) and will incorporate the assumed transition costs from the FCM Settlement Agreement and assumed capacity costs from the Forward Capacity Market ($1.9 billion in 2010, decreasing to $1.75 billion in 2019). The assumed capacity costs of the FCM are based on RSP09’s projected systemwide requirements for installed capacity and a capacity clearing price of $4.50/kW-month after adjustments for peak energy rent (PER) in 2010, $3.60/kW-month in 2011, and $2.95 in 2012.

The “Economy.com” November 2009 economic forecast of real personal income was used as a surrogate for overall economic activity in the RSP10 forecast models. Figure 3-1 compares the percentage change in the forecasted real personal income for New England used in the RSP10 and RSP09 load and peak-load forecasts. The November 2009 forecast shows that economic activity started to decline in 2008 and reached its low point in late 2009; a weak recovery is forecast to begin in late 2010. Figure 3-2 presents historical and projected annual percentage changes in real personal income for New England compared with the United States as a whole. The forecast assumes the present credit crisis is resolved and the federal economic stimulus bill, the American Recovery and Reinvestment Act of 2009 (ARRA), passed in February 2009, is successful in turning the economy around.

Figure 3-1: “Economy.com” forecasts of New England annual percentage change in real personal income from 2008 and 2009 forecasts.

Source: Moody’s Analytics, Economy.com.

Figure 3-2: Historical and projected annual percentage change in real personal income for New England compared with the United States as a whole, 1981 to 2020.

Source: Moody’s Analytics, “Real Personal Income: Annual Percent Changes,” Economy.com.

## Load Forecast Methodology and Model Enhancements

No changes to the forecast methodology have been made for RSP10. However, the forecasts of annual and peak energy use continue to include the impacts of new federal electric appliance efficiency standards that will go into effect in 2013 and would not be captured by the econometric models. As part of RSP11 efforts, the ISO will work with stakeholders to assess the impacts that FCM demand resources and state EE programs have on the load forecast. The ISO also will initiate more thorough analysis to determine the reasons for the decrease in the systemwide load factor and how it can be improved.

The historical weather data used to develop the weekly peak load distributions and seasonal peaks have been updated from 1963–1999 to 1968–2008, resulting in June and July being not quite as hot but August being slightly hotter (all changes are within a few tenths of a degree). For example, the temperature/ humidity index used to forecast the 50/50 summer peak decreased from 80.13 to 79.88, and the 90/10 summer peak decreased from 82.00 to 81.96.

## Subarea Use of Electric Energy

Much of the RSP10 reliability and production cost analyses depend on forecasts of the annual and peak use of electric energy in the subareas. These forecasts are summarized in Table 3-4 and provide important market information to stakeholders. Table 3-5 shows the forecasts for the peak use of electric energy for the New England states and load zones. Table 3-6 shows the forecast for the RSP subareas and their relationship to the load zones and states.

Table 3-4
Forecasts of Annual and Peak Use of Electric Energy in RSP Subareas,
2010 and 2019

| Area | Net Energy for Load (1,000 MWh) |  |  | Summer Peak Loads (MW) |  |  |  |  | Winter Peak Loads (MW) |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | 50/50 Load |  | 90/10 Load |  |  | 50/50 Load |  | 90/10 Load |  |  |
|  | 2010 | 2019 | CAGR | 2010 | 2019 | 2010 | 2019 | CAGR | 2010/11 | 2019/20 | 2010/11 | 2019/20 | CAGR |
| BHE | 1,890 | 2,030 | 0.8 | 325 | 360 | 345 | 385 | 1.2 | 315 | 330 | 325 | 340 | 0.5 |
| ME | 6,670 | 7,210 | 0.9 | 1,135 | 1,295 | 1,210 | 1,390 | 1.6 | 1,110 | 1,140 | 1,145 | 1,175 | 0.3 |
| SME | 3,175 | 3,435 | 0.9 | 575 | 660 | 610 | 710 | 1.7 | 490 | 500 | 505 | 515 | 0.2 |
| NH | 9,715 | 10,915 | 1.3 | 1,985 | 2,325 | 2,130 | 2,510 | 1.8 | 1,655 | 1,785 | 1,720 | 1,850 | 0.8 |
| VT | 7,205 | 7,855 | 1 | 1,250 | 1,405 | 1,310 | 1,480 | 1.4 | 1,195 | 1,265 | 1,220 | 1,290 | 0.6 |
| BOSTON | 26,425 | 28,585 | 0.9 | 5,565 | 6,225 | 5,975 | 6,700 | 1.3 | 4,320 | 4,530 | 4,455 | 4,660 | 0.5 |
| CMA/NEMA | 8,475 | 9,500 | 1.3 | 1,795 | 2,120 | 1,925 | 2,285 | 1.9 | 1,430 | 1,525 | 1,475 | 1,570 | 0.7 |
| WMA | 10,280 | 11,225 | 1 | 2,030 | 2,305 | 2,180 | 2,480 | 1.4 | 1,775 | 18,70 | 1,830 | 1,920 | 0.5 |
| SEMA | 13,440 | 14,595 | 0.9 | 2,875 | 3,250 | 3,095 | 3,505 | 1.4 | 2,255 | 2,360 | 2,325 | 2,430 | 0.5 |
| RI | 11,445 | 12,460 | 0.9 | 2,500 | 2,815 | 2,750 | 3,110 | 1.4 | 1,880 | 1,985 | 1,940 | 2,045 | 0.6 |
| CT | 15,875 | 16,870 | 0.7 | 3,450 | 3,825 | 3,750 | 4,165 | 1.2 | 2,780 | 2,835 | 2,860 | 2,920 | 0.2 |
| SWCT | 10,885 | 11,685 | 0.8 | 2,370 | 2,665 | 2,575 | 2,895 | 1.3 | 1,905 | 1,960 | 1,965 | 2,020 | 0.3 |
| NOR | 5,830 | 6,145 | 0.6 | 1,345 | 1,475 | 1,460 | 1,605 | 1.1 | 970 | 985 | 1,000 | 1,015 | 0.2 |
| ISO total | 131,305 | 142,520 | 0.9 | 27,190 | 30,730 | 29,310 | 33,225 | 1.4 | 22,085 | 23,070 | 22,765 | 23,750 | 0.5 |

Table 3-5
Forecasts of Peak Use of Electric Energy for Load Zones
and the New England States, 2010

| Load Zone(a) | State | 2010 Summer Peak-Load Forecast |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  |  | 50/50 Load |  | 90/10 Load |  |
|  |  | MW | State Peak Load, % | MW | State Peak Load, % |
| CT | Connecticut | 7,240 | 100 | 7,865 | 100 |
| ME | Maine | 2,030 | 100 | 2,165 | 100 |
| NEMA/Boston | Massachusetts | 5,485 | 43 | 5,895 | 43 |
| SEMA |  | 3,550 | 28 | 3,810 | 28 |
| WCMA |  | 3,590 | 28 | 3,855 | 28 |
| Massachusetts subtotal |  | 12,620 |  | 13,555 |  |
| NH | New Hampshire | 2,410 | 100 | 2,590 | 100 |
| RI | Rhode Island | 1,825 | 100 | 2,035 | 100 |
| VT | Vermont | 1,060 | 100 | 1,100 | 100 |
| Total(b) |  | 27,190 |  | 29,315 |  |

- (a) The total load-zone projections are similar to the state load projections and are available at the ISO’s “2010 Forecast Data File;” http://www.iso-ne.com/trans/celt/fsct_detail/index.html; tab #2, “ISO-NE Control Area, States, Regional System Plan (RSP10) Subareas and SMD Load Zones Energy and Seasonal Peak-Load Forecast.”

- (b) Totals may not add because of rounding and may not exactly match the results for other tables in this section.

Table 3-6
Forecasts of Peak Use of Electric Energy for RSP Subareas, 2010(a)

| RSP Subarea | Load Zone | State | 50/50 Summer Peak Load |  |  | 90/10 Summer Peak Load |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | MW | % of RSP Subarea | % of State | MW | % of RSP Subarea | % of State |
| BHE | ME | Maine | 325 | 100.0 | 16.4 | 345 | 100.0 | 16.3 |
| ME | ME | Maine | 1,086 | 95.7 | 53.2 | 1,158 | 95.7 | 53.2 |
|  | NH | New Hampshire | 49 | 4.3 | 2.0 | 52 | 4.3 | 2.0 |
|  |  |  | 1,135 |  |  | 1,210 |  |  |
| SME | ME | Maine | 575 | 100.0 | 28.1 | 610 | 100.0 | 28.1 |
| NH | ME | Maine | 47 | 2.4 | 2.3 | 51 | 2.4 | 2.3 |
|  | NH | New Hampshire | 1,866 | 94.0 | 77.5 | 2,005 | 94.1 | 77.3 |
|  | VT | Vermont | 72 | 3.6 | 6.8 | 74 | 3.5 | 6.8 |
|  |  |  | 1,985 |  |  | 2,130 |  |  |
| VT | NH | New Hampshire | 334 | 26.7 | 13.8 | 360 | 27.5 | 13.9 |
|  | VT | Vermont | 916 | 73.3 | 86.2 | 950 | 72.5 | 86.2 |
|  |  |  | 1,250 |  |  | 1,310 |  |  |
| BOSTON | NH | New Hampshire | 76 | 1.4 | 3.1 | 83 | 1.4 | 3.2 |
|  | NEMA/ Boston | Massachusetts | 5,489 | 98.6 | 43.5 | 5,892 | 98.6 | 43.5 |
|  |  |  | 5,565 |  |  | 5,975 |  |  |
| CMA/NEMA | NH | New Hampshire | 85 | 4.7 | 3.5 | 92 | 4.8 | 3.5 |
|  | WCMA | Massachusetts | 1,710 | 95.3 | 13.5 | 1,833 | 95.2 | 13.5 |
|  |  |  | 1,795 |  |  | 1,925 |  |  |
| WMA | VT | Vermont | 75 | 3.7 | 7.0 | 78 | 3.6 | 7.0 |
|  | CT | Connecticut | 77 | 3.8 | 1.1 | 83 | 3.8 | 1.1 |
|  | WCMA | Massachusetts | 1,878 | 92.5 | 14.9 | 2,019 | 92.6 | 14.9 |
|  |  |  | 2,030 |  |  | 2,180 |  |  |
| SEMA | RI | Rhode Island | 153 | 5.3 | 8.4 | 171 | 5.5 | 8.4 |
|  | SEMA | Massachusetts | 2,722 | 94.7 | 21.6 | 2,924 | 94.5 | 21.6 |
|  |  |  | 2,875 |  |  | 3,095 |  |  |
| RI | RI | Rhode Island | 1,674 | 67.0 | 91.6 | 1,864 | 67.8 | 91.6 |
|  | SEMA | Massachusetts | 826 | 33.0 | 6.5 | 886 | 32.2 | 6.5 |
|  |  |  | 2,500 |  |  | 2,750 |  |  |
| CT | CT | Connecticut | 3,450 | 100.0 | 47.7 | 3,750 | 100.0 | 47.7 |
| SWCT | CT | Connecticut | 2,370 | 100.0 | 32.7 | 2,575 | 100.0 | 32.7 |
| NOR | CT | Connecticut | 1,345 | 100.0 | 18.6 | 1,460 | 100.0 | 18.6 |

(a) Numbers may not add because of rounding and may not exactly match the results for other tables in this section.

## The CELT Forecast and Passive Demand Resources

The seasonal peak load and energy forecast, as published in the 2010–2019 Forecast Report of Capacity, Energy, Loads, and Transmission (2010 CELT Report) and used for calculating the Installed Capacity Requirement (ICR), fully reflects historical passive demand resources and future federal appliance standards. The load forecast does not reflect the peak and energy savings of the passive demand resources that have cleared the Forward Capacity Auctions and are listed in the CELT Report as capacity and are assumed held constant for years beyond FCA #3. The impacts these PDRs have on the systemwide load forecast is demonstrated in the following plots of annual electric energy use and summer peaks. Figure 3-3 shows the ISO’s 50/50 historical summer peak loads and the forecasted load with and without passive resources. Figure 3-4 shows the ISO’s historical net energy for load and the forecasted net energy for load with and without passive resources. Stakeholders have suggested that demand resources could show additional growth beyond FCA #3 and state EE programs could lead to additional savings, especially beyond 2012.

Figure 3-3: Historical and forecast annual summer-peak loads, 1980 to 2019.

Note: Additional information is available at “CELT Forecasting Details 2010;” http://www.iso-ne.com/trans/celt/fsct_detail/index.html, and “CELT Report 2010;” http://www.iso-ne.com/trans/celt/report/index.html.

Figure 3-4: Historical and forecast annual energy use, 1980 to 2019.

## Summary of Key Findings

The RSP10 forecasts of annual and peak use of electric energy are key inputs in establishing the system needs discussed in Sections 4 through 12. The RSP10 forecasts are lower than those for RSP09, mainly because of the severity of the current recession. The key points of the forecast are as follows:

The recession, although more severe than forecasted for RSP09, is forecast to end by mid to late 2009, followed by weak economic growth in 2010. The economy is forecast to rebound through 2012 and then return to a long-run sustainable growth rate. The recovery assumes the resolution of the credit crisis and the success of the economic stimulus program.

The 50/50 summer peak forecast is lower than in RSP09 by 970 MW in 2010, 795 MW in 2013, and 530 MW in 2018. The 90/10 summer peak forecast is lower than in RSP09 by 800 MW in 2010, 630 MW in 2013, and 340 MW in 2018. The forecasts reflect the projected growth of the summer cooling load.

The updating of the historical weather (from 1963–1999 to 1969–2008) used in the peak load forecasts accounts for approximately 240 MW of the difference in the 50/50 summer peak from RSP09 but only 45 MW of the difference in the 90/10 summer peak from RSP09.

The 50/50 and 90/10 winter peak forecast have not significantly changed from RSP09.

While historical load forecasts have been accurate, the ISO will continue working with stakeholders to examine ways for further improvement.

# Resource Adequacy and Capacity

“The RSP shall identify: . . . (ii) the requirements and characteristics of the types of resources that may satisfy PTF system reliability and market efficiency needs to provide stakeholders an opportunity to develop and propose efficient market responses to meet the needs identified in Needs Assessments.” (Attachment K, Overview)

“The RSP shall, among other things: . . .(ii) provide the projected annual and peak demands for electric energy for a five- to ten-year horizon, the needs for resources over this period and how such resources are expected to be provided; (iii) specify the physical characteristics of the physical solutions that can meet the needs defined in the Needs Assessments and include information on market responses that can address them . . .” (Attachment K, § 3.1)

“The RSP shall be designed and implemented to: . . .((ii) identify facilities that are necessary to meet Planning and Reliability Criteria; (iii) avoid the imposition of unreasonable costs upon any Transmission Owner, Transmission Customer or other user of a transmission facility; and (vi) properly coordinate with market responses, including, but not limited to generation, merchant transmission and demand-side responses.” (Attachment K,, § 3.4)

“Needs Assessments may examine resource adequacy . . .” (Attachment K, § 4.1.d)

“Specifically, the ISO shall incorporate or update information regarding resources in Needs Assessments that have been proposed and (i) have cleared in a Forward Capacity Auction pursuant to Market Rule 1 of the ISO Tariff, (ii) have been selected in, and are contractually bound by, a state-sponsored Request For Proposals, or (iii) have a financially binding obligation pursuant to a contract.”  (Attachment K,, § 4.2)]

The amount of capacity the New England power system needs to meet its resource adequacy and reliability requirements is called the Installed Capacity Requirement. To ensure the power system has adequate capacity resources to meet its requirements under a wide range of existing and future system conditions, the ISO forecasts future electricity demand and identifies the quantity of resources needed to meet this demand after accounting for uncertainties, contingencies, and resource performance. It also must procure these resources through the Forward Capacity Market. Collectively, this process is referred to as the Resource Adequacy Process. Both supply-side and demand-side resources participate in the FCM, and both are used to effectively meet the resource needs of the New England region.

Through the FCM, which consists of a series of auctions and bilateral trading periods, the specific resources committed to meet the New England ICR and related values are identified. Purchased capacity resources must be available in the specified timeframe to ensure the region has adequate resources to meet regional resource needs. Because of the present capacity surplus and the ongoing operation of the market, which allows resource owners to acquire, trade, and dispose of capacity supply obligations (CSOs), the specific mix of resources committed to the New England system for any particular delivery period changes over time. Because of this ongoing operation of the market, no static report such as this one can possibly capture the “latest” available information. All the data in this report are accurate as of the date they were presented before the PAC, but specific results may have changed by the time this report becomes available.

This section describes the requirements for resource adequacy over the planning period, the analyses conducted to determine specific systemwide and local-area resource adequacy needs, the results and findings of these analyses, and the region’s efforts to meet the need for resources through the FCM and the ISO’s Generator Interconnection Queue. Some of the new and evolving features of the Forward Capacity Market are discussed. This section also addresses the net operable capability assessments necessary for determining whether sufficient resources will be available under a variety of scenarios examining deterministic stressed-system conditions.

Specifying the need for capacity resources over the 10-year period and providing sufficient information to assess the quality, general locations, and types of supply- or demand-side resources that can either satisfy the defined needs or potentially modify, offset, or defer regulated transmission upgrades complies with Section 3.1 of the OATT Attachment K.

## Systemwide Installed Capacity Requirement

To ensure the system continually has adequate capacity resources, each year the ISO must determine the regional Installed Capacity Requirement, which forms the basis of the systemwide total amount of new and existing resources the annual Forward Capacity Auctions must procure as part of the FCM. The ICR is determined using the well-established probabilistic loss-of-load-expectation (LOLE) analysis. The LOLE analysis identifies the amount of installed capacity (MW) the system needs to meet the NPCC and ISO resource adequacy planning criterion to not disconnect firm load more frequently than once in 10 years. To meet this “once-in-10-years” LOLE requirement, the region’s power system needs installed capacity in an amount equal to the expected demand plus additional capacity to handle any uncertainties associated with load or the performance of the capacity resources.

The analysis for calculating the ICR for New England examines system resource adequacy using assumptions for the load forecast, resource availability, and possible tie-reliability benefits (i.e., the receipt of emergency electric energy from neighboring regions). The model also accounts for the load and capacity relief that can be obtained from implementing operating procedures, including demand-response programs. The ICR calculation, which uses a single-bus model, does not consider the transmission system constraints within New England. In addition to resources located in New England, the ICR analysis models all existing qualified imports, as reported in the ISO’s 2010 CELT Report.

RSP10 presents the established ICR values for the 2010 through 2013 capacity commitment periods and shows representative net ICR values for the 2014 through 2019 periods. The projected net ICR values do not indicate the definitive amount of capacity the region must purchase for that period but provide stakeholders with a general forecast of the likely resource needs of the region. The assumptions used to develop the ICR values published in RSP10 were presented to and discussed thoroughly with the Power Supply Planning Committee (PSPC), the Reliability Committee (RC), and the Planning Advisory Committee.

### ICR Values for 2010/2011 through 2019/2020 Capacity Commitment Periods

Table 4-1 summarizes the 50/50 peak load forecast, the net ICR values for the 2010/2011 through 2013/2014 capacity commitment periods, the representative net ICR values for the 2014/2015 through 2019/2020 periods, and the percentage of the resulting reserves. The net ICR values for the 2010/2011 through 2013/2014 capacity commitment periods, which are calculated as the ICR minus the value of Hydro-Québec Interconnection Capability Credit (HQICC) for the particular capability year, reflect the latest ICR values established for those years. The ICR and HQICC values for the 2010/2011 through 2013/2014 commitment periods have been approved by FERC. The representative net ICR values for 2014/2015 and beyond were calculated by the ISO with stakeholder input using the following assumptions:

The availability of 1,700 MW of total tie-line benefits from the three neighboring balancing authority areas of Québec, the Canadian Maritime provinces, and New York

2010 CELT load forecast

Generating and demand-resource capability ratings, availability, and performance metrics, based on the values used to calculate the ICR for the fourth FCA (FCA #4) for the 2013/2014 capability period

Table 4-1
Actual and Representative Future New England Net Installed Capacity Requirements for 2010–2019 and Resulting Reserves

| Year | Forecast 50/50 Peak (MW) | Actual and Representative Future Net ICR(a) (MW) | Resulting Reserves (%) |
| --- | --- | --- | --- |
| 2010/2011 | 27,190 | 31,110(b) | 14.4 |
| 2011/2012 | 27,660 | 31,741(c) | 14.8 |
| 2012/2013 | 28,165 | 31,965(d) | 13.5 |
| 2013/2014 | 28,570 | 32,127(e) | 12.5 |
| 2014/2015 | 29,025 | 32,672(f) | 12.6 |
| 2015/2016 | 29,450 | 33,178(f) | 12.7 |
| 2016/2017 | 29,785 | 33,604(f) | 12.8 |
| 2017/2018 | 30,110 | 34,025(f) | 13.0 |
| 2018/2019 | 30,430 | 34,434(f) | 13.2 |
| 2019/2020 | 30,730 | 34,818(f) | 13.3 |

(a) 	“Representative Future Net ICR” is the representative ICR for the region, minus the tie-reliability benefits associated with the HQICCs.

(b) 	The ICR value for 2010/2011 reflects the value for the third Annual Reconfiguration Auction (ARA #3) approved by FERC in its February 12, 2010, Order Accepting ISO New England’s Proposed Installed Capacity Requirement, Hydro Québec Interconnection Capability Credits, Related Values, and Tariff Changes, Subject to Condition (http://www.iso-ne.com/regulatory/ferc/orders/2010/feb/er10-438-000_2-12-10_icr_jump_ball_order.pdf).

(c) 	The ICR value for 2011/2012 reflects the ARA #2 value accepted for filing by FERC in its March 29, 2010, Order Accepting for Filing the Installed Capacity Requirement, Hydro Québec Interconnection Capability Credits and Related Values for the Second Reconfiguration Auction for the 2011/2012 Capability Year (http://www.iso-ne.com/regulatory/ferc/orders/2010/mar/er10-714-000_3-29-10_ltr_order_accept_2011-2012_icr.pdf).

(d) 	For the 2012/2013 capability year, the net ICR value represents the value approved by FERC in its August 14, 2009, Filing of Installed Capacity Requirement, Hydro-Québec Interconnection Capability Credits and Related Values for the 2012/2013 Capability Year (http://www.iso-ne.com/regulatory/ferc/orders/2009/aug/er09-1415-000_8-14-09_accept%202012-2013%20icr.pdf).

(e) 	For the 2013/2014 capacity commitment period, the net ICR value represents the value filed with FERC on May 4, 2010. Representative net ICR values are presented for the 2014/2015 through 2019/2020 capability years, reflecting the amount of capacity resources needed to meet the resource adequacy planning criterion.

(f) 	The 2014/2015 through 2019/2020 capability years’ representative net ICR values reflect the amount of capacity resources needed to meet the resource adequacy planning criterion.

As shown in Table 4-1, the percentage of resulting reserves associated with the net ICR values for 2010/2011 and 2011/2012 is 1% to 2% higher than the percentage values for the rest of the years. This is because the load forecasts used to calculate these net ICRs were slightly higher than the RSP10 load forecasts used to calculate the percentages of resulting reserves for the later years. The table also shows that the annual resulting reserves calculated using the net ICR values increase from 12.5% in 2013 to 13.3% by 2019/2020. This increase in the percentage of resulting reserves is a result of assuming a fixed amount of tie benefits through time. As the system load increases and the tie benefits stay constant, the installed capacity needed to meet the resource adequacy planning criterion increases as a percentage of the peak load.

### Other Resource Adequacy Analyses

While the ICR addresses New England’s total capacity requirement, assuming the system overall has no transmission constraints within the region, certain subareas within New England are affected by limitations in the ability to export or import power within the region. To address the subarea reliability impacts of these constraints, the ISO determines the maximum capacity limit (MCL) and local sourcing requirement (LSR) for certain subareas within New England. An MCL is the maximum amount of capacity that can be procured in an export-constrained load zone to meet the total ICR for the New England region. An LSR is the minimum amount of capacity that must be electrically located within an import-constrained load zone to meet the ICR. Areas that have either a LCR or a MCL and that meet other tests in the market are designated as capacity zones. These designations help ensure that the appropriate amount of capacity is procured within these capacity zones to satisfy the ICR and contribute effectively to total system reliability. The remaining areas in New England are designated as the “Rest of Pool” capacity zone.

On February 22, 2010, as part of a larger package of proposed changes, the ISO filed rule changes to revise the methodology for calculating the LSR for import-constrained capacity zones starting with FCA #4. Because the system must meet both the resource adequacy and transmission security requirements, the rule changes would require both resource adequacy and transmission security constraints to be respected for each import-constrained zone. These revisions consider both the use of the probabilistic local resource adequacy criteria previously used to determine the LSR for capacity zones and the deterministic transmission security criteria the ISO uses to maintain system operational reliability when reviewing delist bids for the FCA (i.e., bids submitted by existing capacity resources interested in being removed from the FCA; see Section 4.2.2.1). The LSR for an import-constrained zone is now defined as the amount of capacity needed to satisfy the higher of the probabilistic local resource adequacy (LRA) requirement or the deterministic transmission security analysis (TSA) requirement.

The LSR and MCL values are included in Table 4-2 for the first four capacity commitment periods; only the FCA #4 values for the LSR were calculated using “the higher of” methodology.

Table 4-2
LSRs and MCLs for the First Four FCAs(a)

| Capacity Commitment Period |  | LSR (MW) |  | MCL (MW) |
| --- | --- | --- | --- | --- |
|  |  | CT | NEMA/Boston | Maine |
| 2010/2011 | FCA #1 | 6,496 | 1,838 | 3,697 |
| 2011/2012 | FCA #2 | 5,666 | 1,956 | 3,140 |
| 2012/2013 | FCA #3 | 6,640 | 2,019 | 3,257 |
| 2013/2014 | FCA #4 | 7,419 | 2,957 | 3,187 |

(a) 	Sources: “Summary of ICR, LSR, and MCL for FCM and the Transition Period,” available at http://www.iso-ne.com/markets/othrmkts_data/fcm/doc/summary_of_icr_values.xls. ARA values were used for the 2010/2011 and 2011/2012 capacity commitment periods.

## Forward Capacity Market

The purpose of the FCM is to procure the required amount of installed capacity resources to maintain system reliability, consistent with the region’s ICR. Qualified resources are procured through annual Forward Capacity Auctions governed by the market rules. The first FCA (FCA #1) took place in February 2008, procuring the capacity needed for the 2010/2011 capacity commitment period. The second FCA (FCA #2) occurred in December 2008, procuring the capacity needed for the 2011/2012 capacity commitment period. The third FCA occurred in October 2009, procuring capacity for the 2012/2013 capacity commitment period. The fourth FCA occurred in August 2010, procuring capacity for the 2013/2014 capacity commitment period. The operational use of FCM resources began on June 1, 2010.

This section summarizes the features of the Forward Capacity Market for procuring capacity resources. It presents the results of the first three Forward Capacity Auctions and the amount of capacity that will be supplied by generating, import, and demand resources in the region. The effectiveness of adding new resources in various locations of the power system also is addressed.

### Forward Capacity Auction Qualification Process

To enter into a Forward Capacity Auction, all capacity resources, supply side and demand side, must comply with the qualification and financial-assurance requirements of the FCM. Each resource type, including variable-output (i.e., intermittent) generation such as wind and solar generation, must meet a specific set of rules for qualification to participate in the FCM. For new resources to qualify, each potential bidder of a new capacity resource must submit a predefined package of qualification materials to the ISO before each auction. Each package specifies the location and capacity of the bidder’s resources and potential projects that could be completed by the beginning of the capacity commitment period.

#### Types of Capacity Available from Demand Resources

June 1, 2010, marked the beginning of the first FCM capacity commitment period as well as the beginning of the only mechanism for demand resources to receive a payment for load-curtailment initiatives in the New England markets. Two categories of FCM demand resources exist—passive and active demand:

- Passive Resources (e.g., energy efficiency) are principally designed to save electric energy (MWh). The electric energy that passive projects save during peak hours also helps to fulfill the ICR. These projects are in place at all times and do not reduce load based on real-time system conditions or ISO instructions. The FCM includes two types of passive projects:

  - On peak—passive, non-weather-sensitive loads, such as efficient lighting

  - Seasonal peak—passive, weather-sensitive loads, such as efficient heating and air conditioning (HVAC)

- Active Resources (e.g., demand response) are designed to reduce peak loads in electric energy use and are considered capacity resources (MW). These resources can reduce load based on real-time system conditions or ISO instructions. The FCM includes two types of active projects:

  - Real-time demand response—active, individual resources, such as active load management and distributed generation at commercial and industrial facilities

  - Real-time emergency generation—active, emergency distributed generation

#### Implementation of an Overlapping Impact Standard for Demand Resources

Under the FCM market rules, new generating capacity resources are qualified at levels at which they can operate without requiring the redispach of other capacity resources to respect transmission system constraints. Beginning with the qualification for 2014/2015, the overlapping impact analysis for qualifying new generating capacity resources will be extended to cover active demand resources.

### Forward Capacity Auctions

The FCM’s Forward Capacity Auctions are designed to procure capacity roughly three years (40 months) in advance of the commitment period. This lead time allows capacity suppliers to develop new capacity resources and enables the ISO to plan for these new resources.

Existing capacity resources are required to participate in the FCA and are automatically entered into the capacity auction. However, these resources may indicate a desire to be removed from the FCA by submitting a delist bid before the qualification deadline for existing capacity. For example, high-priced capacity resources may choose to submit delist bids, indicating the resources do not want the capacity supply obligation below a certain price. Since the obligation to participate in the New England energy market is assigned only to resources with a capacity supply obligation, delisted resources are not obligated to supply energy, although they are allowed to voluntarily supply electric energy at market prices. Reconfiguration auctions also may procure any quantities not purchased in the FCA as a result of delisting at specific price thresholds. These auctions allow adjustments that reflect changes in the ICR, and they facilitate the trading of individual commitments made in the previous FCA. The effects of the delist bids for FCA #3 and FCA #4 on the need for transmission facilities is discussed in Section 6.6.

Unless an existing capacity resource follows specific criteria to become delisted each year, it will be assigned a one-year capacity supply obligation. New capacity that bids in the FCA can choose a capacity commitment period obligation between one and five years. The FCM requires all new and existing capacity resources that obtain a capacity supply obligation (i.e., that clear the auction) to perform during shortage events, which occur when the region is not able to meet its load and operating-reserve requirements (see Section 4.4). Purchased resources that fail to perform during a shortage event receive a significantly reduced capacity payment, a measure intended to improve the alignment between resource needs and available capacity.

#### New Resource Qualifications

Table 4-3 shows the locations of new resources that qualified for and then cleared the first, second, and third FCAs.

Table 4-3
Total New Resources that Cleared in FCA #1, FCA #2, and FCA #3 by State (MW and %)

| State | FCA #1 |  | FCA #2 |  | FCA #3 |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | MW | % | MW | % | MW | % |
| CT | 62 | 6.9 | 1,169 | 37.3 | 235 | 8.4 |
| MA | 458 | 50.9 | 243 | 7.8 | 1,636 | 58.5 |
| RI | 45 | 5.0 | 55 | 1.8 | 21 | 0.8 |
| VT | 111 | 12.4 | 12 | 0.4 | 24 | 0.8 |
| NH | 53 | 5.9 | 76 | 2.4 | 24 | 0.8 |
| ME | 170 | 18.9 | 49 | 1.5 | 40 | 1.5 |
| Imports | 0 | 0 | 1,529 | 48.8 | 817 | 29.2 |
| Total(a) | 900 | 100 | 3,134 | 100 | 2,797 | 100 |

(a) The totals may not equal the sum of the rows because of rounding.

#### Capacity Supply Obligations for the First Three FCAs

Table 4-4 shows the results of the FCAs for 2010/2011, 2011/2012, and 2012/2013 and provides the capacity supply obligation totals (i.e., the total amount procured) for FCA #1, #2, and #3. This table also includes some details on the types of capacity obligations procured, including the total real-time emergency generation, self-supply obligation values that reflect bilateral capacity arrangements, and import capacity supply obligations from neighboring balancing authority areas. Comparisons of the results of the third FCA with representative future net ICR values show when the region may need capacity or have a surplus in the future. Subsequent auctions will procure resources to address any needs identified in the future.

Table 4-4
Summary of the First, Second, and Third FCA Obligations (MW)(a)

| Commitment Period | ICR | HQICC | Net ICR(b) | Capacity Supply Obligation | RTEG Capacity Supply Obligation | RTEG Utilization Ratio | Self-Supply Obligation | Import Capacity Supply Obligation |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 2010/2011 | 33,705(c) | 1,400 | 32,305 | 34,077 | 875 | 0.686 | 1,593 | 934 |
| 2011/2012 | 33,439(d) | 911 | 32,528 | 37,283 | 759 | 0.791 | 1,696 | 2,298 |
| 2012/2013 | 32,879 | 914 | 31,965 | 36,996 | 630 | 0.952 | 1,935 | 1,900 |

  - Information regarding the results of annual reconfiguration auctions is available at http://www.iso-ne.com/markets/othrmkts_data/fcm/doc/summary_of_icr_values.xls.

  - The ICR minus the HQICC is equal to the net ICR. The ICR is for the FCA, not the reconfiguration auction.

  - For the third annual reconfiguration auction for this commitment period, the ICR was adjusted to 32,510 MW.

  - For the second ARA for this capacity commitment period, the ICR was adjusted to 32,652 MW.

#### FCA Results by Capacity Zone and State

Table 4-5 contains the totals for each capacity zone. The capacity supply obligation total has been adjusted to reflect the market rule’s real-time emergency-generation limit of 600 MW, which is the maximum quantity of this capacity resource type that can be counted toward the ICR. The capacity zones for the first three auctions include Maine and the Rest-of-Pool. The auctions did not model any import-constrained capacity zones because each potential import-constrained area was determined to have sufficient existing capacity to meet the local sourcing requirements.

Table 4-5
Results of FCA #1, FCA #2, and FCA #3 by Capacity Zone (MW, $/kW-month)(a)

| Commitment Period | Modeled Capacity Zone Name | Maximum Capacity Limit | Capacity Supply Obligation | RTEG Capacity Supply Obligation | Self-Supply Obligation | Capacity Clearing Price | Payment Rate | RTEG Payment Rate |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | (MW) |  |  |  | ($/kW-month) |  |  |
| 2010/2011 | Rest-of-Pool |  | 30,572 | 838 | 1,584 | 4.500 | 4.25 | 2.92 |
| 2010/2011 | Maine | 3,855 | 3,505 | 37 | 9 | 4.500 | 4.25 | 2.92 |
| 2011/2012 | Rest-of-Pool |  | 33,468 | 727 | 1,687 | 3.600 | 3.12 | 2.47 |
| 2011/2012 | Maine | 3,395 | 3,815 | 32 | 9 | 3.600 | 3.12 | 2.47 |
| 2012/2013 | Rest-of-Pool |  | 33,099 | 597 | 1,925 | 2.951 | 2.535 | 2.413 |
| 2012/2013 | Maine | 3,257 | 3,897 | 33 | 9 | 2,951 | 2.465 | 2.347 |

(a)	Values are rounded.

Table 4-6 shows the location, by state, of total capacity supply obligations (in number of resources and megawatts) for FCA #3. The obligation amounts for each state are categorized according to resource status (i.e., new or existing resources) and capacity resource type (generation or demand resources). The table also shows the resources imported from neighboring regions.

Table 4-6
States’ Capacity Supply Obligations for the 2012/2013 Capacity Commitment Period

| State | Resource Status | Generation(a) |  | Demand(a) |  | Total(b) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Number of Resources | Total MW | Number of Resources | Total MW | Number of Resources | Total MW |
| MA | Existing | 183 | 11,399 | 202 | 1,096 | 385 | 12,495 |
|  | New | 11 | 1,490 | 39 | 146 | 50 | 1,636 |
|  |  | 194 | 12,889 | 241 | 1,242 | 435 | 14,132 |
| CT | Existing | 98 | 8,225 | 980 | 768 | 1,078 | 8,993 |
|  | New | 8 | 171 | 13 | 64 | 21 | 235 |
|  |  | 106 | 8,396 | 993 | 831 | 1,099 | 9,227 |
| RI | Existing | 23 | 2,612 | 33 | 175 | 56 | 2,787 |
|  | New |  |  | 7 | 21 | 7 | 21 |
|  |  | 23 | 2,612 | 40 | 196 | 63 | 2,808 |
| NH | Existing | 118 | 4,166 | 38 | 100 | 156 | 4,266 |
|  | New | 2 | 8 | 15 | 16 | 17 | 24 |
|  |  | 120 | 4,174 | 53 | 116 | 173 | 4,290 |
| VT | Existing | 86 | 924 | 37 | 94 | 123 | 1,018 |
|  | New | 3 | 2 | 6 | 22 | 9 | 24 |
|  |  | 89 | 926 | 43 | 116 | 132 | 1,042 |
| ME | Existing | 103 | 3,231 | 47 | 325 | 150 | 3,556 |
|  | New |  |  | 11 | 40 | 11 | 40 |
|  |  | 103 | 3,231 | 58 | 366 | 161 | 3,597 |
| Imports | Existing |  |  |  |  | 7 | 1,083 |
|  | New |  |  |  |  | 8 | 817 |
|  |  |  |  |  |  | 15 | 1,900 |
| Totals(c) | Existing | 611 | 30,557 | 1,337 | 2,558 | 1,955 | 34,198 |
|  | New | 24 | 1,671 | 91 | 309 | 123 | 2,797 |
| Grand total(c) |  | 635 | 32,228 | 1,428 | 2,867 | 2,078 | 36,996 |

(a)	Demand-resource amounts include real-time emergency generation capped at 600 MW per Market Rule 1.

(b)	The totals include external imports.

(c)	Values are rounded; the sum may not agree with the totals.

Several hundred demand resources, representing 2,867 MW, cleared in the third FCA. This total reflects the total RTEG market rule limit of 600 MW. An additional 30 MW of RTEGs above the 600 MW cap were procured, resulting in a total amount of demand resources of 2,897 MW. In addition, 24 new generation resources, representing 1,671 MW, are expected to be on line by June 1, 2012.

#### Demand Resources that Cleared FCA #3

Of the 2,867 MW of demand resources that cleared in FCA #3 and will count toward satisfying the ICR for the 2012/2013 delivery year, passive demand resources represent 1,072 MW, or 37%, and active demand resources represent 1,794 MW, or 63%. To meet the ICR requirements imposed under the market rules, the value for active demand response includes a 600 MW cap placed on the use of emergency generators. Table 4-7 shows the types and locations of demand resources that cleared in FCA #3.

Table 4-7
Demand-Resource Capacity that Cleared in FCA #3 (MW)(a)

| Resource Type | ME | NH | VT | MA | CT | RI | Total |
| --- | --- | --- | --- | --- | --- | --- | --- |
| On-peak demand resource | 60 | 63 | 75 | 418 | 114 | 69 | 799 |
| Real-time demand-response resource | 274 | 41 | 33 | 524 | 273 | 49 | 1,194 |
| Real-time emergency-generation resource(b) | 32 | 11 | 8 | 279 | 194 | 76 | 630 |
| Seasonal-peak demand resource | 0 | 0 | 0 | 21 | 251 | 2 | 273 |
| Total | 366 | 116 | 116 | 1,256 | 841 | 200 | 2,897 |

(a)	All megawatt values include the loss adjustment. Totals may not equal the sum because of rounding.

(b)	The use of real-time emergency-generation resources to meet the ICR is limited to 600 MW, but the 600 MW cap has not been applied to the values in this table.

### Meeting Capacity Needs

Table 4-8 shows that no additional physical capacity would be needed to meet the representative future ICR during the study period. This projection assumes all resources with supply obligations through FCA #3 are in commercial service by the start of the third capacity commitment period commencing in June 2012 and that all existing resources interconnected within New England as of that date remain in service.

Table 4-8
Actual and Representative Future New England Net Installed Capacity Requirements for 2010–2019 and Potential Surplus ICAP (MW)

| Year | Forecast 50/50 Peak | Representative Future Net ICR(a) | Assumed Existing ICAP(b) | Potential Surplus ICAP(c) |
| --- | --- | --- | --- | --- |
| 2010/2011 | 27,190 | 31,110(d) | 32,678 | 1,568 |
| 2011/2012 | 27,660 | 31,741(e) | 33,030 | 1,289 |
| 2012/2013 | 28,165 | 31,965(f) | 37,026 | 5,061 |
| 2013/2014 | 28,570 | 32,127(g) | 35,440 | 3,313 |
| 2014/2015 | 29,025 | 32,672(h) | 35,440 | 2,768 |
| 2015/2016 | 29,450 | 33,178(h) | 35,390 | 2,212 |
| 2016/2017 | 29,785 | 33,604(h) | 35,218 | 1,614 |
| 2017/2018 | 30,110 | 34,025(h) | 35,112 | 1,087 |
| 2018/2019 | 30,430 | 34,434(h) | 35,112 | 678 |
| 2019/2020 | 30,730 | 34,818(h) | 35,112 | 294 |

(a) 	“Representative Future Net ICR” is the representative ICR for the region, minus the tie-reliability benefits associated with the HQICCs.

(b)	“Assumed Existing ICAP” for 2010/2011 through 2012/2013 reflect the most recent FCM obligations as of March 12, 2010, for those years but without reserve-margin gross ups (i.e., credits to account for reducing power system losses), if any, from both New York Power Authority (NYPA) imports and demand resources. The values for 2013/2014 and beyond are based on the 2012/2013 obligations as of March 12, 2010, but with nongrandfathered capacity imports removed and the full amount of RTEGs included.

(c)	“Potential Surplus ICAP” represents an approximation of the future capacity situation, assuming no resource additions or attritions during the study period. Capacity that assumed FCA #3 obligations, excluding the nongrandfathered capacity imports and adjusted for other factors described in note (b), is assumed to be in service in 2012 and will continue to be in service until the end of the study period.

(d)	The net ICR value for 2010/2011 reflects the value for ARA #3 approved by FERC in its February 12, 2010, Order Accepting ISO New England’s Proposed Installed Capacity Requirement, Hydro Québec Interconnection Capability Credits, Related Values, and Tariff Changes, Subject to Condition (http://www.iso-ne.com/markets/othrmkts_data/fcm/doc/summary_of_icr_values.xls).

(e) 	The net ICR value for 2011/2012 reflects the ARA #2 value accepted for filing by FERC in its March 29, 2010, Order Accepting for Filing the Installed Capacity Requirement, Hydro Québec Interconnection Capability Credits and Related Values for the Second Reconfiguration Auction for the 2011/2012 Capability Year (http://www.iso-ne.com/regulatory/ferc/orders/2010/mar/er10-714-000_3-29-10_ltr_order_accept_2011-2012_icr.pdf).

(f) 	For the 2012/2013 capability year, the net ICR value represents the value approved by FERC in its August 14, 2009, order regarding the Filing of Installed Capacity Requirement, Hydro-Québec Interconnection Capability Credits and Related Values for the 2012/2013 Capability Year (http://www.iso-ne.com/regulatory/ferc/orders/2009/aug/er09-1415-000_8-14-09_accept%202012-2013%20icr.pdf).

(g) 	For 2013/2014 period, the net ICR value represents the value approved by FERC in its June 25, 2010, letter order regarding the Filing of Installed Capacity Requirement, Hydro Québec Interconnection Capability Credits, and Related Values for the 2013/2014 Capability Year (http://www.iso-ne.com/regulatory/ferc/orders/2010/jun/er10-1182_6-25-10_ltr_ordr_accept_2013-2014_icr.pdf).

(h) 	For the 2014/2015 to 2019/2020 capability years, representative net ICR values are presented reflecting the amount of capacity resources needed to meet the resource adequacy planning criterion.

The actual amounts of capacity to be procured through the FCM process for future years will continue to be determined according to established FCM market rules. The amount of additional capacity and the installation timing to meet the future requirements will depend on future expected system load and resource conditions. Any changes in these conditions will be reflected in future RSPs and FCAs.

Table 4-9 shows the total megawatts of qualified new resources by capacity resource type for the 2013/2014 capacity commitment period, as of May 4, 2010, the date of FERC’s Informational Filing for Qualification in the Forward Capacity Market.

Table 4-9
New Capacity Qualified for FCA #4

| Resource Type | MW(a) |
| --- | --- |
| Generation | 886 |
| Demand Resources | 1,011 |
| Imports | 1,244 |
| Total | 3,140 |

(a) 	The total includes real-time emergency-generation resources for which qualification packages were submitted. Values are effective as of May 4, 2010. Totals may not add because of rounding.

Overall, the qualification of new resources for participation in FCA #4 has declined compared with previous auctions. The amount of qualified new generating capacity is about half of what it has been in previous FCAs, while the amount of qualified imports has remained about the same and the quantity of qualified demand resources has nearly doubled from FCA #3. The smaller size of the proposed projects and project disqualifications due to overlapping impacts also contributed to decreased resource qualifications for FCA #4. Despite the decreased interest by new generating resources, interest from new resources overall remains strong, as illustrated in Figure 4-1.

Figure 4-1: New resource qualifications for participation in the FCAs.

Table 4-10 shows the qualified FCA #4 resources by location. A total of 638 MW of new active demand resources and 372 MW of new passive demand resources qualified. Participation by natural gas units remains strong at 83% of the total of 886 MW of generation resources.

Table 4-10
New Generation and Demand Resources that Qualified in FCA #4,
by State (MW)

| State | Sum of New FCA-Qualified Generation Capacity | Sum of New FCA-Qualified Demand-Resource Capacity |
| --- | --- | --- |
| CT | 599.804 | 265.734 |
| MA | 157.491 | 283.385 |
| ME | 24.867 | 281.374 |
| NH | 65.070 | 42.638 |
| RI | 0.000 | 62.117 |
| VT | 38.800 | 75.450 |

## Operable Capacity Analysis

Using a deterministic approach, the ISO analyzes the systemwide operable capacity to estimate the net capacity that will be available under specific scenarios. The analysis identifies operable capacity margins (i.e., the amount of resources that must be operational to meet peak demand plus operating-reserve requirements) under assumed peak-load conditions. The results of these examinations show either a positive or negative operating margin in meeting system operating requirements. A negative margin for a specific scenario indicates the extent of possible mitigation actions that would be required through predefined protocols, as prescribed in ISO Operating Procedure No. 4 (OP 4), Action during a Capacity Deficiency, or Operating Procedure No. 7 (OP 7), Action in an Emergency.

For RSP10, the ISO conducted a systemwide operable capacity analysis for 2010 to 2019, which does not account for RSP subareas. This section discusses the methodology used to conduct this analysis and summarizes its results.

### Approach

The operable capacity analysis is performed with both the 50/50 and 90/10 peak-load forecasts. The systemwide capacity assumed is the actual or the representative net ICR values for the region (described in Table 4-1).

A total of 2,000 MW of operating reserves were assumed to reflect the largest loss-of-source (LOS) contingency at 1,400 MW plus one-half of a large (1,200 MW) generating unit operating equivalent to 600 MW. A total of 2,100 MW of resource outages were assumed on the basis of historical performance observations of supply resources. The results are a direct comparison of the operable capacity system requirements with the total capacity assumed available (in this case, the net ICR values).

### Results

Figure 4-2, Table 4-11, and Table 4-12 show the results of the systemwide operable capacity analysis. The results show that if the loads associated with the 50/50 forecast were to occur, New England could experience a negative operable capacity margin of approximately 180 MW as early as summer 2010 and would need to rely on OP 4 actions for demand and supply relief. This negative operable capacity margin would increase to approximately 550 MW by summer 2013 and then decrease to approximately 10 MW by summer 2019, assuming the system has no surplus capacity resources above the net ICR.

Figure 4-2: Projected summer operable capacity analysis, 2010 to 2019.

Note: Each year indicates the starting year for the respective capacity commitment period.

Table 4-11
Projected New England Operable Capacity Analysis
for Summer, 2010 to 2019, Assuming 50/50 loads (MW)

| Capacity Situation (Summer MW) | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Load (50/50 forecast) | 27,190 | 27,660 | 28,165 | 28,570 | 29,025 | 29,450 | 29,785 | 30,110 | 30,430 | 30,730 |
| Operating reserves | 2,000 | 2,000 | 2,000 | 2,000 | 2,000 | 2,000 | 2,000 | 2,000 | 2,000 | 2,000 |
| Total requirement | 29,190 | 29,660 | 30,165 | 30,570 | 31,025 | 31,450 | 31,785 | 32,110 | 32,430 | 32,730 |
| Capacity | 31,110 | 31,741 | 31,965 | 32,127 | 32,672 | 33,178 | 33,604 | 34,025 | 34,434 | 34,818 |
| Assumed unavailable capacity | −2,100 | −2,100 | −2,100 | −2,100 | −2,100 | −2,100 | −2,100 | −2,100 | −2,100 | −2,100 |
| Total net capacity(a) | 29,010 | 29,641 | 29,865 | 30,027 | 30,572 | 31,078 | 31,504 | 31,925 | 32,334 | 32,718 |
| Operable capacity margin(b) | −180 | −19 | −300 | −543 | −453 | −372 | −281 | −185 | −96 | −12 |

(a)	The net capacity values are consistent with Table 4-1.

(b) “Operable capacity margin” equals “total net capacity” minus “total requirement.”

Table 4-12
Projected New England Operable Capacity Analysis
for Summer 2010 to 2019, Assuming 90/10 Loads (MW)

| Capacity Situation (Summer MW) | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Load (90/10 forecast) | 29,310 | 29,835 | 30,390 | 30,840 | 31,340 | 31,810 | 32,180 | 32,545 | 32,895 | 33,225 |
| Operating reserves | 2,000 | 2,000 | 2,000 | 2,000 | 2,000 | 2,000 | 2,000 | 2,000 | 2,000 | 2,000 |
| Total requirement | 31,310 | 31,835 | 32,390 | 32,840 | 33,340 | 33,810 | 34,180 | 34,545 | 34,895 | 35,225 |
| Capacity | 31,110 | 31,741 | 31,965 | 32,127 | 32,672 | 33,178 | 33,604 | 34,025 | 34,434 | 34,818 |
| Assumed unavailable capacity | −2,100 | −2,100 | −2,100 | −2,100 | −2,100 | −2,100 | −2,100 | −2,100 | −2,100 | −2,100 |
| Total net capacity(a) | 29,010 | 29,641 | 29,865 | 30,027 | 30,572 | 31,078 | 31,504 | 31,925 | 32,334 | 32,718 |
| Operable capacity margin(b) | −2,300 | −2,194 | −2,525 | −2,813 | −2,768 | −2,732 | −2,676 | −2,620 | −2,561 | −2,507 |

(a)	The net capacity values are consistent with Table 4-1.

(b)  “Operable capacity margin” equals “total net capacity” minus “total requirement.”

Similarly, Figure 4-2 and Table 4-12 show that New England could experience larger negative operable capacity margins of approximately 2,300 MW as early as summer 2010 if the 90/10 peak loads occurred. Thus, starting in 2010, New England would need to rely on load and capacity relief from OP 4 actions under the projected 90/10 peak loads. Assuming the exact amount of resources needed to meet the once-in-10-years LOLE is purchased in the FCA, this negative operable capacity margin would increase to approximately 2,800 MW by 2013 and then decrease to approximately 2,500 MW by 2019.

### Observations

On the basis of representative net ICR values, resources that cleared FCA #3 with supply obligations will be sufficient to meet the regional resource adequacy planning criterion during the 10-year study period, assuming no attrition of the existing capacity within New England and new FCM resources meet their planned in-service dates.

On the basis of the deterministic systemwide operable capacity analysis and assuming, under the FCM, the ISO purchases the minimum amount of capacity needed to meet the once-in-10-years LOLE criterion, New England will require approximately 2,200 to 2,800 MW of load and capacity relief from OP 4 actions if the 90/10 peak load occurred during the study period.

## Generating Units in the ISO Generator Interconnection Queue

The interconnection requests in the ISO’s Generator Interconnection Queue reflect the region’s interest in building new generation capacity. Figure 4-3 shows the capacity of the 84 active generation-interconnection requests in the queue by RSP subarea as of April 1, 2010. The four areas with the most proposed capacity additions are in the SEMA, WMA, CT, and ME subareas. Together, these subareas have about 5,321 MW under development out of a total of 8,809 MW of active projects for New England. A total of 2,937 MW is proposed for the three subareas in Connecticut.

Figure 4-3: Capacity of generation-interconnection requests by RSP subarea.

Notes: All capacities are based on the projects in the ISO Generator Interconnection Queue as of April 1, 2010, that would interconnect with the ISO system. Projects involving only transmission or that did not increase an existing generator’s capacity were excluded. Projects with more than one listing in the queue, representing different interconnection configurations, were only counted once.

A summary of the projects in the queue as of April 1, 2010, is shown in Table 4-13. Since the first publication of the Generator Interconnection Queue in November 1997, 64 generating projects (12,871 MW) out of 300 total generator applications (totaling 67,147 MW) have become commercial. Since the queue’s inception, proposed projects totaling approximately 45,467 MW have been withdrawn, reflecting a megawatt attrition rate of 68%. The 84 active projects in the queue total 8,809 MW. Figure 4-4 shows the resources in the ISO Generator Interconnection Queue, by state and fuel type, as of April 1, 2010.

Table 4-13
Summary of Queue Projects as of April 1, 2010

| Category of Projects | Projects | Total Capacity (MW) |
| --- | --- | --- |
| Commercial | 64 | 12,871 |
| Active | 84 | 8,809 |
| Withdrawn | 152 | 45,467 |
| Total | 300 | 67,147 |

Figure 4-4: Resources in the ISO Generator Interconnection Queue, by state and fuel type, as of April 1, 2010 (MW and %).

Notes: The total for the State of Connecticut (3,195 MW) is greater than the total for the subareas, CT, SWCT, and NOR (2,937 MW; see Figure 4-3), because the area of the state is greater than the total area used for the subareas. The “Other Renewables” category includes wood, refuse, landfill gas (LFG), other bio gas, and fuel cells. A total of 38 MW of hydro is included in the 1,224 MW total of hydro and pumped storage. The totals for all categories reflect all queue projects that would interconnect with the system and not all projects in New England.

As part of the FCA-qualification process, generators are subject to a review that evaluates whether transmission upgrades are needed to ensure the new generating capacity is incrementally useful within each capacity zone. Previous RSP and FCM studies have confirmed that interconnecting new resources close to the Connecticut, Boston, and SEMA load centers would improve the overall reliability of the system and could potentially defer the need for transmission improvements. However, individual system impact studies are necessary to fully assess the electrical performance of the system and determine reliable interconnections of generation resources.

## Summary

On the basis of the results of FCA #3 and assuming no resource retirements, New England will have adequate resources through 2019. While some retirements are likely, the ISO is optimistic that adequate demand and supply resources will be purchased through the FCM auctions and will be installed in time to meet the capacity needs established by future ICRs.

By design, the level of the ICR specified for New England could necessitate the use of specific OP 4 actions because the load relief provided by these actions is included as resource offsets in the ICR calculation. The frequency and extent of OP 4 actions would vary based on several factors, including the amount of the net ICR, tie-line benefits, and actual system load. Study results show that the need for load and capacity relief by OP 4 actions will range from approximately 2,200 to 2,800 MW during extremely hot and humid summer peak-load conditions. The FCM will continue to provide incentives for developing resources in the desired quantity and needed locations. Because Forward Capacity Auctions are held more than three years in advance of the delivery period, future resources will be better known in advance, which will facilitate and improve the planning process.

Resources are being planned in needed locations near load centers. A total of 1,871 MW of the new FCM resources procured in FCA #3 are located in Connecticut and Massachusetts. Of this total, 1,661 MW are new generation resources. In the ISO Generator Interconnection Queue, 2,937 MW of new resources are proposed for Greater Connecticut. In addition, demand-resource programs have been implemented successfully, and future additions of demand resources have been planned as part of the FCM process.

# Operating Reserves

“The RSP shall, among other things: (i) describe, in a consolidated manner, the assessment of the PTF system needs, the results of such assessments, and the projected improvements; (ii) provide the projected annual and peak demands for electric energy for a five- to ten-year horizon, the needs for resources over this period and how such resources are expected to be provided; (iii) specify the physical characteristics of the physical solutions that can meet the needs defined in the Needs Assessments and include information on market responses that can address them;  and (iv) provide sufficient information to allow Market Participants to assess the quantity, general locations, operating characteristics and required availability criteria of the type of incremental supply or demand-side resources, or merchant transmission projects, that would satisfy the identified needs or that may serve to modify, offset or defer proposed regulated transmission upgrades.” (Attachment K, § 3.1)

“The RSP shall be designed and implemented to: (ii) identify facilities that are necessary to meet Planning and Reliability Criteria; (iii) avoid the imposition of unreasonable costs upon any Transmission Owner, Transmission Customer or other user of a transmission facility; and (vi) properly coordinate with market responses, including, but not limited to generation, merchant transmission and demand-side responses.” (Attachment K, § 3.4)

“A Needs Assessment shall also identify: (ii) situations that significantly affect the reliable and efficient operation of the PTF along with any critical time constraints for addressing the needs of the PTF to facilitate the development of market responses and to initiate the pursuit of regulated transmission solutions.” (Attachment K, § 4.1)

“The ISO shall reflect proposed market responses in the regional system planning process. Market responses may include, but are not limited to, resources (e.g., demand-side projects and distributed generation) and Merchant Transmission Facilities.”  (Attachment K, § 4.2)

In addition to needing a certain level of resources for reliably meeting the region’s actual demand for electricity, as discussed in Section 4, the system needs a certain amount of resources that can provide operating reserves. The overall mix of resources providing operating reserves must be able to respond quickly to system contingencies stemming from equipment outages and forecast errors. These resources also may be called on to provide regulation service for maintaining operational control or to serve or reduce peak loads during high-demand conditions. A suboptimal mix of resources with limited amounts of these operating-reserve characteristics could lead to the need for the system to use more costly resources to provide these services. In the worst case, reliability would be degraded.

Several types of resources in New England have the operating characteristics to provide operating reserves for responding to contingencies, helping to maintain operational control, and for serving peak demand. The generating units that provide operating reserves can respond to contingencies within 10 or 30 minutes by offering reserve capability either synchronized or not synchronized to the power system. Synchronized (i.e., spinning) reserves are on-line reserves that can increase output. Nonsynchronized (i.e., nonspinning) reserves are off-line, “fast-start” resources that can be electrically synchronized to the system and quickly reach rated capability. Dispatchable asset-related demand (DARD) (i.e., demand that can be interrupted within 10 or 30 minutes in response to a dispatch order) also can provide operating reserves, meet or reduce peak demand, and avert the need to commit more costly resources to supply operating reserves.

This section discusses the need for operating reserves, both systemwide and in major import areas, and the use of specific types of fast-start and demand-response resources to fill these needs. An overview of the locational Forward Reserve Market (FRM) and a forecast of representative future operating-reserve requirements for Greater Southwest Connecticut, Greater Connecticut, and BOSTON are provided. This section also describes a pilot program evaluating the use of demand-response resources to provide operating reserves. Attachment K requires the RSP to specify the physical characteristics of solutions that can meet system needs, which include the general locations, operating characteristics, and type of supply-side or demand-side resources.

## Requirements for Operating Reserves

During daily operations, the ISO determines operating-reserve requirements for the system as a whole as well as for major transmission import-constrained areas. The requirement for systemwide operating reserves is based on the two largest loss-of-source contingencies within New England, which typically consist of some combination of the two largest on-line generating units or imports on the Phase II interconnection with Québec. The operating reserves required within subareas of the system depend on many factors, including the economic dispatch of generation systemwide, the projected peak load of the subarea, the most critical contingency in the subarea, possible resource outages, and expected transmission-related import limitations. ISO operations personnel analyze and determine how the generating resources within the load pockets must be committed to meet the following day’s operational requirements and withstand possible contingencies. The locational Forward Reserve Market is in place to procure these required operating reserves.

### Systemwide Operating-Reserve Requirements

A certain amount of the power system’s resources must be available to provide operating reserves to assist in addressing systemwide contingencies, as follows:

Loss of generating equipment within the ISO New England Balancing Authority Area or within any other NPCC balancing authority area

Loss of transmission equipment within or between NPCC balancing authority areas, which might reduce the capability to transfer energy within New England or between the New England balancing authority area and any other area

The ISO’s operating-reserve requirements, as established in Operating Procedure No. 8, Operating Reserve and Regulation (OP 8), protect the system from the impacts associated with a loss of generating or transmission equipment within New England. According to OP 8, the ISO must maintain a sufficient amount of reserves during normal conditions in the ISO New England Balancing Authority Area to be able to replace within 10 minutes the first-contingency loss (N-1) (see Section 2.3). Typically, the maximum first-contingency loss is between 1,300 and 1,700 MW. In addition, OP 8 requires the ISO to maintain a sufficient amount of reserves to be able to replace within 30 minutes at least 50% of the second-contingency loss (N-1-1). Typically, 50% of the maximum second-contingency loss is between 600 and 750 MW.

In accordance with NERC and NPCC criteria for power system operation, ISO Operating Procedure No. 19 (OP 19), Transmission Operations, requires the system to operate such that when any power system element is lost (N-1), power flows remain within applicable emergency limits of the remaining power system elements. This N-1 limit may be a thermal, voltage, or stability limit of the transmission system. OP 19 further stipulates that within 30 minutes of the loss of the first-contingency element, the system must be able to return to a normal state that can withstand a second contingency. To implement these requirements, OP 8 requires operating reserves to be distributed throughout the system. This ensures that the ISO can use them fully for any criteria contingency without exceeding transmission system limitations and that the operation of the system remains in accordance with NERC, NPCC, and ISO New England criteria and guidelines.

### Forward Reserve Market Requirements for Major Import Areas

To maintain system reliability, OP 8 mandates the ISO to maintain certain reserve levels within subareas that rely on resources located outside the area. The amount and type of operating reserves a subarea needs depend on the system’s reliability constraints and the characteristics of the generating units within the subarea. Subarea reserve requirements also vary as a function of system conditions related to load levels, unit commitment and dispatch, system topology, and special operational considerations. If maximizing the use of transmission import capability to meet demand is more economical, the subarea will require more local operating reserves to protect for the N-1-1 contingency. If using import capability to meet demand is less economical, generation located outside the subarea could be used to provide operating reserves, thus reducing operating-reserve support needed within the subarea.

Table 5-1 shows representative future operating-reserve requirements for Greater Southwest Connecticut, Greater Connecticut, and BOSTON. These estimated requirements are based on the same methodology used to calculate the requirements for the locational FRM. The estimates account for representative future system conditions for load, generation availability, N-1 and N-1-1 transfer limits, and the largest generation and transmission contingencies in each subarea. The representative values show a range to reflect the load and resource uncertainties associated with future system conditions. Actual market requirements are calculated immediately before each locational FRM procurement period and are based on historical data that reflect actual system conditions. The table also shows the existing amount of fast-start capability located in each subarea as a result of the fast-start resource offers into the past FRM auctions.

Table 5-1 
Representative Future Operating-Reserve Requirements
in Major New England Import Areas (MW)

| Area/Improvement | Market Period(a) | Range of Fast-Start Resources Offered into the Past Forward Reserve Auctions (MW)(b) | Representative Future Locational Forward Reserve Market Requirements (MW) |  |
| --- | --- | --- | --- | --- |
|  |  |  | Summer (Jun to Sep)(c) | Winter (Oct to May)(c) |
| Greater Southwest Connecticut(d) | 2010 | 301–505 | 0(e) | 0(e) |
|  | 2011 |  | 0 | 0 |
|  | 2012 |  | 0 | 0 |
|  | 2013 |  | 0 | 0 |
|  | 2014 |  | 0 | 0 |
| Greater Connecticut(f, g) | 2010 | 659–1,262(h) | 1,225(e) | 925(e) |
|  | 2011 |  | 1,000–1,250 | 600–1,050 |
|  | 2012 |  | 700–1,250 | 500–950 |
|  | 2013 |  | 700–1,250 | 450–900 |
|  | 2014 |  | 750–1,250 100 to 650 with NEEWS | 450–900 0 with NEEWS |
| BOSTON(g, i) | 2010 | 0–441 | 0(e) | 0(e) |
|  | 2011 |  | 0 to 100 | 0 |
|  | 2012 |  | 0 to 125 | 0 |
|  | 2013 |  | 0 to 125 | 0 |
|  | 2014 |  | 0 to 150 | 0 |

(a) 	The market period is from June 1 through May 31 of the following year.

(b) 	These values are the range of the megawatts of resources offered into the past forward-reserve auctions. The amount offered into the auctions for BOSTON decreased in recent years as the reserve requirements for the market decreased. A summary of the forward-reserve offers for the past auctions is available at
http://www.iso-ne.com/markets/othrmkts_data/res_mkt/cal_assump/index.html.

(c) 	“Summer” means June through September of a capability year; “winter” means October of the associated capability year through May of the following year (e.g., the 2010 winter values are for October 2010 through May 2011). The representative values show a range to reflect uncertainties associated with the future system conditions.

(d) 	The assumed N-1 and N-1-1 values to reflect transmission import limits into Greater Southwest Connecticut are 3,200 MW and 2,300 MW, respectively.

(e) 	These values are actual locational forward-reserve requirements. Requirements for future years are projected on the basis of assumed contingencies.

(f)  	For Greater CT, the assumed import limits reflect an N-1 value of 2,500 MW but does not account for the New England East–West Solution (NEEWS) project (see Section 6.4.2). The assumed N-1-1 value is 1,300 MW. These limits are assumed to increase to 3,600 MW and 2,500 MW, respectively, in 2014 if the NEEWS project were placed in-service.

(g)  In some circumstances when transmission contingencies are more severe than generation contingencies, shedding some load may be acceptable.

(h) 	These values include resources in Greater Southwest Connecticut.

(i)  The assumed N-1 and N-1-1 values to reflect transmission import limits into BOSTON are 4,900 MW and 3,700 MW, respectively. The operating-reserve values for BOSTON would be lower without consideration of the common-mode failures of Mystic units #8 and #9 that were assumed to trip up to 1,400 MW because of exposure to a common failure of the fuel supply to the units.

The estimates for operating reserve requirements were based on expected future operating conditions, but annual market requirements are based on the actual previous seasonal system conditions. If the summer 2010 actual conditions are similar to the well-below-normal demand levels of summer 2009, the locational FRM requirements for Greater Connecticut could be lower than the RSP10 forecast for summer 2011.

Because the local contingency requirements in Greater SWCT are nested within CT (i.e., operating reserves meeting the Greater SWCT requirement also meet the Greater Connecticut requirement), installing the resources in the Greater SWCT area also would satisfy the need for resources located anywhere in Greater Connecticut.

#### Greater Southwest Connecticut

With the completion of the SWCT Reliability Project in 2008, the import limit into this area increased by approximately 850 MW. This transmission upgrade gave system operators more flexibility to use generation located within and outside the subarea to meet both load and local 30-minute operating-reserve requirements. As shown in Table 5-1, Greater SWCT can have its operating reserves met from outside the area through 2014. Both economic energy transfers to serve load and the reserve support necessary to cover the second contingencies can be provided from outside the Greater SWCT area as a result of the transmission improvements.

#### Greater Connecticut

Past RSPs and market signals had identified the need for economical and fast-start resources in Greater Connecticut to meet reliability requirements and reduce out-of-merit market costs. As a result of resource development, Greater Connecticut is projected to have adequate fast-start resources, and the economical performance of that area is expected to improve. A total of 1,262 MW of fast-start resources was offered into the 2010 summer auction for Greater Connecticut, which exceeds the 1,225 MW of the reserve requirement established for the FRM. The local reserve requirements for the next several years are expected to decrease. This is the result of planned additions of economical baseload generation within Greater Connecticut procured through the FCM. The Interstate components of the New England East–West Solution (see Section 6.4.2) are currently under study but were shown to provide additional relief for the local reserve requirements.

#### BOSTON

The FRM requirements for the BOSTON subarea are shown in Table 5-1. These requirements reflect the increased import limits resulting from the implementation of the NSTAR 345 kV Transmission Reliability Project (Phase I and Phase II) transmission upgrades. The analysis also reflects the possible contingency of the simultaneous loss of Mystic units #8 and #9. With the increased import limits due to the completion of the NSTAR 345 kV Transmission Reliability Project Phase I and Phase II, operators should be able to optimize the use of regional generation to meet both load and reserve requirements. If the transmission lines were fully utilized to import lower-cost generation into BOSTON, this subarea would need to provide operating reserves to protect against the larger of (a) the loss of the largest generation source within the subarea, or (b) the loss of a transmission line into the subarea. The amount of fast-start resources offered into the FRM auctions in recent years was small because the reserve requirements established for this zone were very low. However, the amount of offers into the auction was as high as 441 MW when the requirement was higher. The expected amount of existing fast-start resources located in BOSTON will likely meet the 0 to 150 MW of representative local reserve requirements for BOSTON during the study timeframe.

#### Summary of Forward Reserve Market Requirements in Major Load Pockets

New England must meet its overall operating-reserve requirements and have sufficient reserves in load pockets to meet reliability requirements. The recent additions of fast-start resources in Greater Connecticut provide needed operating flexibility as well as operating reserves. Planned fast-start resources as well as baseload resources that are on line most of the time would also decrease the amounts of reserves required within the subareas of Greater Connecticut. Existing fast-start resources will likely be used to meet the locational reserve requirements for BOSTON, and new resources will likely participate in the locational FRM for this area. Any reduction in traditional baseload resources in either area would serve to increase the locational FRM requirement.

## Demand-Response Reserves Pilot Program

The ISO is assessing the Demand-Response Reserves Pilot Program (DRR Pilot) to determine whether the demand-response resources in New England are interested in and capable of providing a reserve product functionally equivalent to the type of reserves provided by central generating stations, combustion turbines, and other fast-start resources. The program began its initial two-year phase in October 2006 and its second phase in October 2008.

The DRR Pilot program tested the ability of demand resources to reliably provide an operating-reserve-like response. The pilot used the Internet-Based Communication System Open Solution (IBCS OS) to dispatch these resources and to provide near real-time data to system operators. Table 5-2 summarizes program participation and the number of events that occurred throughout the entire DRR Pilot.

Table 5-2
DRR Pilot Summary Statistics

| Season | Participation (# of assets) | Participation (MW)(a) | # of Activations | # of Statistically Significant Reductions |
| --- | --- | --- | --- | --- |
| Winter 2006/2007 | 47 | 14.9 | 19 | 19 |
| Summer 2007 | 90 | 30.3 | 18 | 13 |
| Winter 2007/2008 | 77 | 13.7 | 17 | 13 |
| Summer 2008 | 90 | 28.6 | 16 | 13 |
| Winter 2008/2009 | 0 | 0.0 | 0 | 0 |
| Summer 2009 | 57 | 34.5 | 18 | 18 |
| Winter 2009/2010 | 40 | 16.0 | 19 | 19 |

(a) 	During the first phase of the DRR Pilot, participating assets were required to enroll at their claimed capability (i.e., a generator’s maximum level of production or output or a demand-resource’s maximum amount of load reduction). During the second phase of the DDR Pilot, participating assets were able to nominate the level of reduction to be provided. This contract amount could be less than the demand resource’s claimed capability.

Throughout the DRR Pilot, the participation was below the 50 MW limit of total resources established by the ISO. With the implementation of the Forward Capacity Market, the dispatch and near real-time telemetry has changed from the IBCS OS to a remote terminal unit (RTU) connected to the ISO’s communications front end (CFE) system. Before moving forward with any additional pilots or market rules changes, the ISO is awaiting certain FERC orders and the completion of other demand-resource market design changes.

A critical step in determining the amount of interruption provided by demand-response resources is the estimation of what a customer’s load would have been without the reductions providing operating reserves. Several different methodologies for determining the customer baseline load shapes were compared with the baseline methodology used in the DRR Pilot to evaluate their relative accuracies. Independent analysis of the initial DRR pilot program methodology concluded that the methodology the ISO initially used was appropriate with some adjustments made to the customer baseline. The adjustments were based on the differences between the actual load of the customer and the customer baseline for the two hours preceding the interruption event.

Demand-resource performance during the second phase of the pilot was measured using a customer baseline that was adjusted upward or downward symmetrically depending on the customer’s actual load in the two-hour period preceding the start of the activation. The symmetrical adjustments matched the customer baseline with the actual load just before the start of the activation (even if the customer’s actual load was running higher or lower than normal). This change more accurately indicated the actual load reduced during reserve activations.

The early results of the program showed that demand resources in New England could respond to numerous interruption instructions over a season. Some demand resources responded within 30 minutes. The ISO observed that a response within 10 minutes may be practical for some resources. However, the number of demand resources interested in and capable of providing operating reserve appears to be limited because the pilot has never been fully subscribed. Many issues remain to be resolved that are related to other demand-resource issues being discussed with stakeholders and that will influence whether demand resources are able to participate in the reserve market and how they will do so.

## Summary of Key Findings and Follow-Up

Fast-start resources with a short lead time for project development can satisfy near-term operating-reserve requirements while providing operational flexibility to major load pockets and the system overall. Locating economical baseload generation within major load pockets decreases the amount of reserves required within the load pocket. Transmission improvements also can allow for the increased use of reserves from outside these areas. The Demand-Response Reserves Pilot program has demonstrated the level of response that demand resources could be expected to provide when providing operating reserves. This information on the performance of these resources, in conjunction with standards established in FERC Order 719 and the final rules emanating from the recently issued FERC NOPR on Demand Response Compensation in Organized Wholesale Energy Markets, will shape how the ISO formulates the participation of demand response in the real-time energy market.

# Transmission Security and Upgrades

“The regional system planning process described in this Attachment provides for the ISO to undertake assessments of the needs of the PTF system on a systemwide or specific area basis. These assessments shall be referred to as Needs Assessments, as described in Section 4.1 of this Attachment. The ISO shall incorporate market responses that have met the criteria specified in Section 4.2(a) of this Attachment into the Needs Assessments or the Regional System Plan (“RSP”), described below. Where market responses incorporated into the Needs Assessments do not eliminate or address the needs identified by the ISO in Needs Assessments or the RSP, the ISO shall develop or evaluate, pursuant to Section 4.2(b) of this Attachment, regulated transmission solutions proposed in response to the needs identified by the ISO.” (Attachment K, Overview)

“On a regular and ongoing basis, the ISO, in coordination with the PTOs and the Planning Advisory Committee, shall conduct assessments (i.e., Needs Assessments) of the adequacy of the PTF system, as a whole or in part, to maintain the reliability of such facilities while promoting the operation of efficient wholesale electric markets in New England.”  ((Attachment K, § 4.1)

The ISO and regional stakeholders have made progress analyzing the transmission system in New England, developing solutions to address existing and projected transmission system needs, and implementing these solutions. Fourteen major 345 kV projects have emerged from these efforts, all of which are critical for maintaining transmission system reliability. These transmission upgrades also will improve the economic performance of the system.

Seven of the 14 projects have been placed in service. These include the two Southwest Connecticut Reliability Projects (Phase 1 and Phase 2), the Northeast Reliability Interconnection (NRI) Project, the two phases of the Boston 345 kV Transmission Reliability Project (Phase 1 and Phase 2), the Short-Term Lower SEMA Upgrades, and the Northwest Vermont (NWVT) Reliability Project. Four of the 14 projects currently are in siting or are expected to be in siting by the end of 2010. These include the Maine Power Reliability Program (MPRP), the Long-Term Lower SEMA Upgrades, and two of the four components of the New England East–West Solution (NEEWS) series of projects—the Springfield and Rhode Island components. The last three of the 14 projects are the Vermont Southern Loop project, which has received its siting approval and is currently under construction, and the Interstate and Central Connecticut components of NEEWS. These NEEWS components are being studied to account for a reduced load forecast, new supply and demand resources, and sensitivity to the unavailability of generating units affecting the project.

Also, the addition of the 345 kV substations in Wachusett, Ward Hill, Wakefield Junction, and West Amesbury, Massachusetts; the expansion and creation of the 345 kV substations in Scobie and Monadnock, New Hampshire, respectively; and the expansion of the 345 kV substations in Barbour Hill, Haddam, and Killingly, Connecticut, have improved the ability of the transmission system to meet load growth. One additional project in the final stages of construction includes improvements at the 345 kV Keene Road substation in northern Maine. All these and other projects will help maintain system reliability and enhance the region’s ability to support a robust, competitive wholesale power market by reliably moving power from various internal and external sources to the region’s load centers.

This section discusses the need for transmission security and the performance of the transmission system in New England. It addresses the need for transmission upgrades accounting for known plans for the addition of resources. It also updates the progress of the current major transmission projects in the region. Information regarding the detailed analyses associated with many of these efforts can be found in previous RSPs, various PAC presentations, and other ISO reports.

## The Need for Transmission Security

A reliable, well-designed transmission system is essential for complying with mandatory reliability standards and providing regional transmission service that provides for the secure dispatch and operation of generation and that delivers numerous products and services, as follows:

Capacity

Electric energy

Operating reserves

Load-following

Automatic generation control

Immediate contingency response to sudden generator or transmission outages

A secure transmission system also plays an important role in the following functions:

Improving the reliability of and access to supply resources

Regulating voltage and minimizing voltage fluctuations

Stabilizing the grid after transient events

Facilitating the efficient use of existing regional supply and demand resources

Reducing the amount of reserves necessary for the secure operation of the system

Facilitating the scheduling of equipment maintenance

Assisting neighboring balancing authority areas, especially during major contingencies affecting their reliability

## Transmission Planning Process

”The RSP shall conform to:  Good Utility Practice; applicable Commission compliance requirements related to the regional system planning process; applicable reliability principles, guidelines, criteria, rules, procedures and standards of the ERO, NPCC, and any of their successors; planning criteria adopted and/or developed by the ISO; Transmission Owner criteria, rules, standards, guides and policies developed by the Transmission Owner for its facilities consistent with the ISO planning criteria, the applicable criteria of the ERO and NPCC; local transmission planning criteria; and the ISO New England Planning Procedures and ISO New England Operating Procedures, as they may be amended from time to time (collectively, the “Planning and Reliability Criteria”).” (Attachment K, § 3.3)

The electric power system’s mandatory reliability standards define what constitutes adequate regional transmission service, the foundation for ISO’s responsibility for regional transmission planning. All proposed system modifications, including transmission and generation additions or significant load reductions or additions, must be analyzed and designed to ensure systemwide coordination and continued system reliability in compliance with these standards.

Infrastructure throughout many parts of the system, which was planned, designed, and built many years ago, is becoming increasingly inadequate. The system contains relatively old, low-capacity 115 kV lines, many of which were converted from 69 kV design. Additionally, a number of aging 345/115 kV transformers are connected to the 115 kV system. The continued use of this aging equipment increases the risk of the system experiencing extended equipment outages that cannot be repaired or replaced quickly. Many of the transmission system projects underway in the region are being designed to improve the operation of those areas of the system currently complicated by, for example, restrictions on generator dispatch, the use of special protection systems (SPSs), sensitivity to varying load levels, and facility outages resulting from unplanned contingencies and maintenance conditions.

### Needs Assessments and Solutions Studies

“The ISO shall develop the RSP based on periodic comprehensive assessments (conducted not less than every third year) of the PTF systemwide needs to maintain the reliability of the New England Transmission System while accounting for market efficiency, economic, environmental and other considerations, as agreed upon from time to time. The ISO shall update the RSP to reflect the results of ongoing Needs Assessments conducted pursuant to Section 4.1 of this Attachment. The RSP shall also account for projected improvements to the PTF that are needed to maintain system reliability in accordance with national and regional standards and the operation of efficient markets under a set of planning assumptions.” (Attachment K, § 3.1)

“Each RSP shall be built upon the previous year’s RSP.” (Attachment K, § 3.1)

Through an open stakeholder process, the ISO develops plans for the region’s networked transmission facilities to address future system needs. A Needs Assessment determines the adequacy of the power system, as a whole or in part, to maintain the reliability of the facilities while promoting the operation of efficient wholesale electric markets in New England. After the results of a Needs Assessment are made available for stakeholder input, the potential transmission system solutions are evaluated thoroughly to determine the most cost-effective one for the region. These study efforts and the proposed transmission solutions are documented in Solutions Studies, which also are subject to stakeholder review and input. These studies, in aggregate, provide the basis to update the ISO’s Regional System Plans and ensure an ongoing 10-year plan for the region consistent and in compliance with the standards and criteria of NERC and the NPCC.

### Project Timing

The ISO periodically reviews the need for and timing of projects, as stakeholders provide new information and input and as system parameters change this review and any necessary adjustments, to ensure that all plans can be implemented without degrading the performance of the New England System, the NPCC region, or the remainder of the Eastern Interconnection. The ISO conducts sensitivity analyses to account for factors such as generation unavailability, maintenance-outage conditions, and potential retirement scenarios, which could advance the need for transmission improvements, as well as the development of generation and demand resources, which can delay the need for transmission. The planning process identifies sufficient lead times for the construction of transmission solutions to ensure the region meets planning and operating criteria.

### Types of Transmission Upgrades

Attachment N of the OATT, “Procedures for Regional System Plan Upgrades,” defines several categories of transmission upgrades that can be developed to address various types of defined system needs, such as reliability and market efficiency.

#### Reliability Transmission Upgrades

Reliability Transmission Upgrades are necessary to ensure the continued reliability of the New England transmission system in compliance with applicable reliability standards. To identify the transmission system facilities required to maintain reliability and system performance consistent with the standards, the ISO determines whether the following factors are met using reasonable assumptions for forecasted load growth and the availability of generation and transmission facilities (based on maintenance schedules, forced outages, or other unavailability factors):

Known changes in available supply resources and transmission facilities, such as through anticipated transmission enhancements considering Elective Transmission Upgrades and merchant transmission facilities (as specified in Section 9 of Attachment K); the addition of demand-side resources or new or previously unavailable generators; or generator retirements

- Load growth

Acceptable stability response

Acceptable short-circuit capability

Acceptable voltage levels

Adequate thermal capability

Acceptable system operability and responses (e.g., automatic operations, voltage changes)

The ISO also relies on good utility practice, applicable reliability standards, and ISO procedures and practices. A Reliability Transmission Upgrade may also provide market efficiency benefits.

#### Market Efficiency Transmission Upgrades

Market Efficiency Transmission Upgrades (METUs) are primarily designed to reduce the total net production cost to supply the system load. The ISO categorizes a proposed transmission upgrade as a Market Efficiency Transmission Upgrade when it determines that the net present value of the net reduction in total cost to supply the system load is greater than the net present value of the carrying cost of the identified upgrade.

A Reliability Transmission Upgrade may qualify for interim treatment as a Market Efficiency Transmission Upgrade if market efficiency is used to advance the schedule for the implementation of the upgrade. This can take place if the ISO determines that the net present value of the reduction in total production cost to supply system load is greater than the net present value of the Reliability Transmission Upgrade after the schedule is advanced, minus the net present value of the upgrade for when it is projected to be needed for reliability.

In determining the net present value of power system resource costs, the ISO takes into account applicable projected economic factors, as follows:

Energy costs

Capacity costs

Cost of supplying total operating reserve

System losses

Known changes in available supply resources and transmission facilities, such as through anticipated transmission enhancements considering Elective Transmission Upgrades and merchant transmission facilities (as specified in Attachment K, Section 9); the addition of demand-side resources or new or previously unavailable generators; or generator retirements

Load growth

Fuel costs

Fuel availability

Generator availability

Release of locked-in generating resources

Present-worth factors for each project specific to the owner of the project

Present-worth period not to exceed 10 years

Cost of the project

Analyses may include the use of historical information, such as information in market reports, and special studies, and they should report cumulative net present value annually over the study period.

#### Generator Interconnection Upgrades and Generator Interconnection-Related Upgrades

A Generator Interconnection Upgrade is an addition to or modification of the New England transmission system for interconnecting a new or existing generating unit whose energy or capacity capability is materially changing and increasing, whether or not the interconnection is for meeting the Network Capability Interconnection Standard or the Capacity Capability Interconnection Standard. Generator Interconnection-Related Upgrades to the New England transmission system are included in the RSP Project List (see Section 6.3).

#### Elective Transmission Upgrades and Merchant Transmission Facilities

An Elective Transmission Upgrade (ETU) is an upgrade to the New England transmission system that is voluntarily funded by one or more participants that have agreed to pay for all the costs of the upgrade and is not one of the following types of other upgrades:

“The ISO shall reflect proposed market responses in the regional system planning process. Market responses may include, but are not limited to, resources . . . and Merchant Transmission Facilities.” (Attachment K, § 4.2(a))

Generator Interconnection-Related Upgrade

Reliability Transmission Upgrade (including a NEMA Upgrade, as appropriate)

Market Efficiency Transmission Upgrade (including a NEMA Upgrade, as appropriate)

- Project proposed as an ETU but that was already identified as a transmission project in the RSP before its proposal as an ETU

The Elective Transmission Upgrades study process is also the mechanism available to integrate merchant transmission facilities into the regional transmission system. Merchant transmission facilities are independently developed and funded and subject to the operational control of the ISO, pursuant to an operating agreement specific to each of these facilities.

## RSP Project List and Projected Transmission Project Costs

“The RSP Project List shall identify regulated transmission solutions proposed in response to the needs identified in a RSP or Needs Assessments conducted pursuant to Section 4.1 of this Attachment. The RSP Project List shall identify the proposed regulated transmission solutions separately as either a Reliability Transmission Upgrade or a Market Efficiency Transmission Upgrade.

Within each category of the RSP Project List, the following subcategories will be utilized to indicate the status of each proposed regulated transmission solution in the evaluation process. These subcategories include:  (i) Concept; (ii) Proposed; (iii) Planned; (iv) Under Construction; and (v) In-Service.” (Attachment K, § 3.6(a))

The RSP Project List is a summary of needed transmission projects for the region and includes information on project type, the primary owner, the transmission upgrades and their status, and the estimated cost of the PTFs. The list is updated at least three times per year, although the ISO regularly discusses the justification for transmission improvements with the PAC and the Reliability Committee, which provide guidance and comment on study scopes, assumptions, and results. The RSP Project List classifies projects as they progress through the study and stakeholder planning processes as follows:

Concept—a transmission project under consideration by its proponent as a potential solution to meet a need the ISO has identified in a Needs Assessment or the RSP but for which little or no analysis is available to support the transmission project.

Proposed—a regulated transmission solution that (1) has been proposed in response to a specific need the ISO identified in a Needs Assessment or the RSP, and (2) has been evaluated or further defined and developed in a Solutions Study, as specified in Section 4.2(b) of Attachment K but has not received ISO approval under Section I.3.9 of the tariff. The regulated transmission solution must include analysis sufficient to support an ISO determination, as communicated to the PAC, that it would likely meet the ISO-identified need included in the Needs Assessment or the RSP.

Planned—a transmission upgrade the ISO has approved under Section I.3.9 of the tariff. Both a Needs Assessment and a Solution Study have been completed for planned projects.

The ISO regularly updates the PAC on study schedules, scopes of work, assumptions, draft results and final results, with the status of all projects compiled in the RSP Project List. Projects are considered part of the Regional System Plan consistent with their status and are subject to transmission cost allocation for the region. RSP10 incorporates information from the June 2010 RSP Project List, which can be accessed in Appendix A of this document.

As of June 2010, the total estimated cost of transmission upgrades proposed, planned, and under construction was approximately $5 billion. The participating transmission owner (PTO) Administrative Committee (AC) provides annual updates to the ISO and NEPOOL on projected regional network service (RNS) transmission rates. The RNS transmission rate effective June 1, 2010, is $64.83/kW-year. The updated projected transmission rates for 2011 to 2014 are included in Table 6-1. On the basis of these costs, the RNS transmission rate is expected to increase almost 70% from 2010 to 2014.

Table 6-1
Regional Network Service Rate Forecast, 2011 to 2014(a. b. c)

|  | 2011 | 2012 | 2013 | 2014 |
| --- | --- | --- | --- | --- |
| Estimated additions in-service ($ millions) | 766 | 1,683 | 2,336 | 454 |
| Forecasted revenue requirement ($ millions) | 127 | 281 | 400 | 73 |
| Estimated RNS rate impact ($/kW-year) | 7 | 14 | 21 | 4 |
| Estimated RNS rate forecast ($/kW-year) | 71 | 86 | 106 | 110 |
| Estimated RNS rate forecast ($/kWh)(d) | 0.014 | 0.016 | 0.020 | 0.021 |

(a) 	The forecast is preliminary and for illustrative purposes only. It reflects gross costs and is based on a number of assumptions and variables, including, among others, estimated project need, design, scope, and labor and materials costs; inflation; site and permitting approvals; transmission in-service dates; estimated carrying charges; and coincident peak network loads. It does not include assumptions pertaining to savings (e.g., those associated with reduced congestion or capacity costs to load) or prior-year true-up adjustments. Therefore, such estimates and assumptions are expected to change as current data become available. Contact ISO Customer Service at (413) 540-4220 for additional information about the RNS rate forecast.

(b) 	The figures may be off slightly because of rounding.

(c)	 Information was taken from the PTO AC Work Group Presentation at the NEPOOL Reliability Committee/ Transmission Committee Summer Meeting (August 16–17, 2010); further details are available at http://www.iso-ne.com/committees/comm_wkgrps/trans_comm/tariff_comm/mtrls/2010/aug16172010/a11_rns_rate_forecast_%202010_2014.pdf.

(d) 	The estimated RNS rate forecast assumes a 60% load factor.

## Transmission System Performance Needs Assessments
and Upgrade Approvals

“The RSP shall, among other things:

describe, in a consolidated manner, the assessment of the PTF system needs, the results of such assessments, and the projected improvements;”

The following additional provisions are addressed by this section, which are supplemented by the detailed study documents referenced in this section,

“(iii) specify the physical characteristics of the physical solutions that can meet the needs defined in the Needs Assessments and include information on market responses that can address them; and

(iv) provide sufficient information to allow Market Participants to assess the quantity, general locations, operating characteristics and required availability criteria of the type of incremental supply or demand-side resources, or merchant transmission projects, that would satisfy the identified needs or that may serve to modify, offset or defer proposed regulated transmission upgrades.” (Attachment K, § 3.1)

Also, “The results of Solutions Studies will…be reflected in the RSP and/or its Project List . . . ” (Attachment K, § 4.2(e))

The New England power system provides electricity to a diverse region, ranging from rural agricultural areas to densely populated urban areas, and it integrates widely dispersed and varied types of power supply resources. The geographic distribution of New England’s summer and winter peak loads is approximately 20% in the northern states of Maine, New Hampshire, and Vermont and 80% in the southern states of Massachusetts, Connecticut, and Rhode Island. Although the land area in the northern states is larger than the land area in the southern states, the greater urban development in southern New England creates the relatively larger demand and corresponding transmission density.

The New England transmission system consists of mostly 115 kV, 230 kV, and 345 kV transmission lines, which in northern New England are generally longer and fewer in number than in southern New England. The New England area has nine interconnections with New York: two 345 kV ties, one 230 kV tie, one 138 kV tie, three 115 kV ties, one 69 kV tie, and one 330 MW, +/-150 kV high-voltage direct-current (HVDC) tie.

Currently, New England and New Brunswick are connected through two 345 kV ties, the second of which was placed in service in December 2007. New England also has two HVDC interconnections with Québec: a 225 MW back-to-back converter at Highgate in northern Vermont and a ±450 kV HVDC line with terminal configurations allowing up to 2,000 MW to be delivered at Sandy Pond in Massachusetts.

The following sections summarize the July 2010 status of several transmission planning studies and the need for upgrades.

### Northern New England

The northern New England (NNE) area encompasses the transmission system in Maine, New Hampshire, and Vermont. Studies of each of these states are being conducted to address the transmission system’s short- and long-term needs.

#### Northern New England Transmission

With the Northeast Reliability Interconnection in service, New England and New Brunswick now have two 345 kV interconnections leading into a 345 kV corridor at Orrington, Maine. The corridor spans hundreds of miles and eventually ties into Massachusetts. The transmission system throughout northern New England is limited in capacity; it is weak in places and faces numerous transmission security concerns. Underlying the limited number of 345 kV transmission facilities are a number of old, low-capacity, and long 115 kV lines. These lines serve a geographically dispersed load as well as the concentrated, more developed load centers in southern Maine, southern New Hampshire, and northwestern Vermont.

The two most significant issues facing the area have been to maintain the general performance of the long 345 kV corridor, particularly through Maine, and to maintain the reliability of supply to meet demand. The region faces thermal and voltage performance issues and stability concerns and is reliant on several SPSs that may be subject to incorrect or undesired operation. Rapid load growth has raised particular concerns in northwestern Vermont; the southern and seacoast areas of Maine and New Hampshire; various localized areas across Maine; and the tri-state “Monadnock” area of southeastern Vermont, southwestern New Hampshire, and north-central Massachusetts. The system of long 115 kV lines, with weak sources and high real- and reactive-power losses, is exceeding its ability to integrate generation and efficiently and effectively serve load. In many instances, the underlying systems of 34.5 kV, 46 kV, and 69 kV lines also are exceeding their capabilities and are being upgraded, placing greater demands on an already stressed 115 kV system.

Over the past several years, the addition of generation in Maine and New Hampshire, in combination with the area’s limited transfer capability and limited transmission expansion, has increased the likelihood of many northern New England interfaces operating near their limits, creating restrictions on northern resources. Because these interface limits depend on generation dispatch, the operation of the system becomes more complex. Additional concerns in northern New England include limited system flexibility to accommodate maintenance outages, limited dynamic reactive-power resources, and high real- and reactive-power losses. However, load growth in the north, in combination with other system changes, is easing the stresses on some northern New England interfaces, such as the interface between Maine and New Hampshire. In fact, the power flows on some interfaces, which historically have been from north to south, frequently have reversed and are moving from south to north during a significant number of hours each year, highlighting new emerging system weaknesses in addition to those already identified on the interfaces.

Load growth also is causing reliability concerns and has led to new or worsening situations in areas with localized dependence on existing generation. Additionally, limitations in the ability of special protection systems to operate correctly are at times leading to requirements to operate generation out of merit to ensure adequate SPS functioning.

#### Northern New England Transmission System Studies

Study efforts are progressing in various portions of Maine, New Hampshire, and Vermont to address a number of transmission system concerns. Some of these studies have focused on defining short-term needs and developing solutions, while others have made significant progress in evaluating potential system conditions 10 years into the future.

Maine. The long-term system needs of Bangor Hydro Electric (BHE) and Central Maine Power (CMP) have been identified. To improve the performance of the Bangor system, 115 kV transmission lines have been proposed. CMP is proposing 115 kV expansions in western Maine to address area thermal and voltage issues. Upgrades north of Augusta and near Rumford, including a new 115 kV substation, will reduce potential voltage concerns. System reinforcements at 115 kV, including the addition of the new substation at Maguire Road in southern Maine, will help serve southern Maine load in the near term. Projects proposed as part of the Maine Power Reliability Program must meet reliability requirements and be consistent with long-term planning objectives in both the BHE and CMP service territories. These projects include the addition of significant new 345 kV and 115 kV transmission facilities and new 345 kV autotransformers at key locations.

New Hampshire. A number of studies of the New Hampshire portion of the system have been conducted. The existing and midterm concerns of northern and central New Hampshire have been improved by closing the Y-138 tie with Maine (see below). A number of 115 kV transmission reinforcements already are under development in southern New Hampshire. Studies have indicated a midterm need for additional 345/115 kV area autotransformers at Deerfield. Longer-term studies are in progress to determine the reinforcements necessary to support load growth in these areas.

A 10-year, two-phase study of the New Hampshire area is in progress. The focus of this study is on serving New Hampshire loads while maintaining overall regional system performance. The first phase of this study was the Needs Assessment, which identified the needs for system improvements to serve load reliably in New Hampshire.

The New Hampshire Transmission System Needs Assessment identified several areas of weak performance and demonstrated the following transmission system needs:

Insufficient 345/115 kV transformation capacity—Thermal overloads occurred in the simulations on one of the Deerfield 345/115 kV autotransformers and one of the Scobie 345/115 kV autotransformers under certain contingencies before the Maine Power Reliability Program (MPRP) (see Section 6.4.1.3) was implemented, and were close to 100% of their rating post-MPRP. The reliability of the 115 kV system is dependent on the capacity and availability of these autotransformers.

Insufficient 115 kV transmission support for the seacoast area—This area represents a major load pocket with a dependence on local generation. Under certain dispatch and unit availability scenarios, this area had thermal and voltage violations on the remaining system and the potential for system voltage collapse.

Insufficient 115 kV transmission support for the southern area—This area also represents a major load pocket with a dependence on local generation and 345 kV transformation capabilities. Most of the thermal and voltage violations occurred when the local generation was not available.

Insufficient 115 kV transmission support for the central and the western areas—The central area relies almost entirely on power transfers from resources outside this area; the western area has lower capacity 115 kV lines. Transmission outages in these areas result in violations that stem from heavy load in relation to the transmission supply capability. Overloads can be exacerbated when flows from east to west increase.

The Needs Assessment analysis included the identification of the critical load level at which the voltage violations and thermal overloads would occur. Most of the voltage and thermal violations identified in the New Hampshire Needs Assessment were found at the forecasted 2009 peak load level under various system conditions. The Needs Assessment, coupled with the critical load level analysis, indicates the need to examine substantial transmission system upgrades to improve system performance.

Because of the poor system performance shown by the N-1 (first-contingency) assessment, an N-1-1 (second-contingency) analysis was not performed as part of the Needs Assessment. The N-1-1 analysis is being addressed as part of the Solutions Study.

The New Hampshire Transmission System Needs Assessment will be updated to reflect the 2010 CELT Report forecast and additional system conditions that may result within the next 10 years. This update is needed to reflect necessary changes to future assumptions within Vermont, such as the status of Vermont Yankee, which may have an impact on the performance of the New Hampshire transmission system. The completion of this Needs Assessment update, which has been combined with the Vermont update analysis, is targeted for the third quarter of 2010.

The New Hampshire Solutions Study is assessing the New Hampshire 345 kV and 115 kV transmission system expansion alternatives. Transmission upgrades for ensuring the reliability of the transmission system in New Hampshire will be identified to address the reliability needs found in the Needs Assessment. In general, the following transmission system upgrades will be considered:

Additional 345/115 kV autotransformers to support normal conditions—with all lines in service—and back-up conditions when one or more of the existing autotransformers are out-of-service

Additional upgrades to the 345 kV and 115 kV transmission lines to reinforce the network capability of the existing system to serve load under contingency conditions

Additional reactive compensation required to satisfy voltage criteria under contingency conditions

- The Solutions Study is projected to be completed in late 2010.

Vermont. A number of solutions have been studied to address concerns in southern Vermont, including issues with certain facilities—specifically between Bennington and Brattleboro—that have design voltages below 115 kV. Transmission upgrades in the Burlington area, known as the Burlington Project, have been designed to maintain adequate supply in the event of a transmission or underlying system outage, as well as to address load growth. A longer-term analysis conducted by the Vermont Electric Power Company (VELCO) confirmed Vermont state transmission system reliability concerns highlighted in previous analyses. The results of the 2006 Vermont Transmission System Long-Range Plan (2006 VT LRP) demonstrate a need for a combination of further expansion of the 115 kV and 345 kV transmission facilities. System reinforcements resulting from the 2006 VT LRP include the addition of 345 kV and 115 kV infrastructure in southern Vermont as part of the Southern Loop Project.

The Vermont system continues to be studied to assess and resolve potential reliability issues. Moreover, Vermont regulations require VELCO to develop a 10-year plan every three years. Collaborative efforts among the ISO, VELCO, National Grid, and Northeast Utilities have continued assessing the reliability of Vermont’s transmission system. The ISO posted the Vermont Transmission System Needs Assessment Study Scope in February 2010. VELCO published the 2009 Vermont Transmission System Long-Range Plan (2009 VT LRP) on July 1, 2009. Both studies identified several thermal and voltage violations, some severe and widespread, for multiple-element contingencies and facility-out conditions. Facility-out conditions included outages of key transmission lines, autotransformers, and resources in and around the state of Vermont. Among the alternatives that are continuing to be investigated to address the identified system needs are reactive compensation throughout Vermont; variations of new 345 kV or 230 kV facilities internal or external to the state, or both; and new or upgraded 115 kV facilities.

The Vermont Transmission Reliability Report Needs Analysis will be updated to reflect the 2010 CELT Report forecast and additional system conditions that may result within the next 10 years. The New York ISO (NYISO) has informed ISO New England and VELCO that the normal flow on the PV-20 line into Vermont may no longer be expected to be between 70 MW and 140 MW because of concerns in New York. In addition, system deficiencies were identified with Vermont Yankee in service, and the potential retirement of the plant can exacerbate these issues. Needs analyses will consider firm imports over the Highgate HVDC facility and will study scenarios with no megawatts flowing into Vermont across PV-20, as well as the potential retirement of Vermont Yankee. These scenarios will be studied independent of each other and in combination to determine the vulnerabilities for Vermont and surrounding areas, including portions of New Hampshire and New York. This Needs Assessment, which has been combined with the New Hampshire update, is targeted for completion in the third quarter of 2010.

The 2009 VT LRP and Vermont Transmission Reliability Report Needs Analysis identified widespread thermal and voltage violations for key contingencies with critical facilities out of service. A regional Solutions Study will evaluate alternatives that could address the system deficiencies in Vermont and those identified in the New Hampshire Needs Assessment. The regional Solutions Study also will evaluate the robustness of each alternative, most likely involving interstate facilities, and ascertain whether proposed transmission solution alternatives solely within each state are still needed. The completion of this solutions assessment is targeted for late 2010.

#### Northern New England Transmission Projects

The ISO has identified projects that address transmission system performance issues, either individually or in combination. Some of the projects, as described in the previous sections, address subregional reliability issues and also have the ancillary benefit of improving the performance of major transmission corridors and thus the overall performance of the system. The projects are as follows:

Burlington Project (i.e., the East Ave 115 kV Loop)—This project, as follows, was proposed to loop through the East Avenue substation and ensure that the outage of a 115 kV line does not result in loss of load in the Burlington area.

Disconnect the K-23 (Essex–Tafts Corner–Williston) line outside the Essex substation, construct a new five-mile 115 kV line to East Ave, and rebuild five miles of the existing K-25 (Essex–East Avenue) line.

Rebuild the East Avenue substation to a four-breaker ring connecting two 115 kV lines and two step-down transformers.

Construct a new three-breaker substation at Gorge connecting two 115 kV lines and one step-down transformer.

The majority of the project was completed in November 2009, and the remaining component, the Gorge 115 kV substation, is expected in service December 2010.

Southern Loop (i.e., the Coolidge Connector) Project—The 2006 Vermont Transmission System Long-Range Plan identified significant system performance concerns for key contingencies occurring under heavy import conditions. A number of components that address the thermal and voltage problems these contingencies would cause are expected to be in service late 2010:

Installation of the new Vernon–Newfane–Coolidge 345 kV line with requisite station upgrades

Installation of a new Vernon 345/115 kV substation, including a new 345/115 kV autotransformer

Installation of a new Newfane 345/115 kV substation

Expansion of the Coolidge 345 kV substation

Closing the Y-138 Line—This project, which came in service in the third quarter of 2009, addresses near-term central New Hampshire reliability needs and somewhat improves the Surowiec–South and Maine–New Hampshire voltage and thermal performance problems. This project adds a new through path from Saco Valley to White Lake.

Deerfield Substation Expansion Project—This project adds a second 345/115 kV autotransformer at the Deerfield substation in New Hampshire. Three new 345 kV circuit breakers will be added to eliminate problematic contingencies. Five 115 kV circuit breakers will be replaced, and one new 115 kV circuit breaker will be added. To mitigate area overloads, the Madbury to Deerfield (L175) 115 kV line will be rebuilt and the Dover to Madbury (M183) 115 kV line and Deerfield to Rochester (C129) 115 kV line will be reconductored. In addition, the Rochester substation will be expanded to accommodate a new radial line to a new North Rochester substation. The plan is to place this project in service in 2012 and shows the work at Rochester and North Rochester needed by 2015.

Littleton Reconfiguration Project—To improve system performance, this project adds 115 kV breakers at the Littleton substation in New Hampshire and relocates the Littleton 230/115 kV autotransformer from the 115 kV bus to a new bay position. The planned in-service date for the project is June 2011.

Rumford–Woodstock–Kimball Road (RWK) Corridor Transmission Project—The northwestern Maine transmission system is influenced heavily by pulp and paper industrial load, but it also has significant area generation, which presently is the area’s main source of voltage support. The need for additional transmission and voltage support has been identified. The RWK project upgrades include constructing a new transmission line, upgrading existing transmission lines, installing additional capacitor banks, and changing substation configurations. All these upgrades will increase the system reliability of the western Maine network. One aspect of the project has been changed because of the cancellation of local planned system expansion (the Railroad Street [NewPage] Project). This has altered the RWK project to replace the new 115 kV line between Rumford Industrial Park and Railroad Street with a new 115 kV line between Rumford Industrial Park and Rumford. While some pieces of the RWK project have been placed in service, the planned in-service date for the entire project is the end of 2010.

Heywood Road (formerly Benton) Project—Transmission upgrades are required to mitigate low voltages and voltage collapse in the Skowhegan–Waterville–Winslow area in Maine that could result from the contingent loss of critical lines in the area. A new switchyard connecting the Winslow−Wyman Hydro, Coopers Mills–Rice Rips, and Heywood–Wyman Hydro (lines 83, 67A, and 241, respectively) in a six-breaker ring-bus configuration will provide an additional path from Coopers Mills (formerly Maxcys) substation to the Waterville–Winslow area. This new switchyard will improve the system voltage performance. The upgraded Heywood Road switchyard will be located along an existing right-of-way where sections 67A and 83 can be joined at a common point. This project also includes the addition of a 20 megavolt-ampere reactive (MVAR) capacitor bank at the Heywood Road switchyard and an upgrade of portions of section 67A between the tap point of section 67 and the switchyard. The planned in-service date for this project is 2010.

Section 63 Area Voltage Support—Currently, all loads served by the Wyman–Livermore Falls 115 kV line (section 63) are exposed to contingency outages. Additionally, area voltages fall to unacceptable levels because of contingencies. To mitigate violations observed, a new switching station at the 63B tap, referred to as the Starks Switching Station, will be constructed, and two 18 MVAR capacitor banks will be added to that station. These upgrades have a proposed in-service date of December 2012.

Maine Power Reliability Program—The MPRP provides a 10-year look at the Maine transmission system and has identified the following inadequacies:

Insufficient 345 kV transmission—Maine currently has two 345 kV transmission paths from southern to central Maine and two 345 kV ties from northern Maine to New Brunswick. In the central part of the system, Maine has a single 345 kV path, which limits reliability performance and is a weak link in the system.

Insufficient 345/115 kV transformation capacity—The reliability of Maine’s 115 kV system depends on the capacity and availability of autotransformers at five locations. Overloads of the autotransformers with all lines in service illustrate insufficient transformation capacity.

Insufficient 345 kV transmission support for Portland and southern Maine—The largest load pocket in Maine is subject to thermal and voltage reliability issues.

Insufficient transmission infrastructure in western, central, and southern Maine regions—Each of these regions in Maine represents a major load pocket that depends on local generation to meet reliability standards.

Insufficient transmission infrastructure in midcoast and “downeast” Maine regions—These regions in Maine (i.e., Bucksport−Eastport) represent load pockets that have no local generation and fully depend on the transmission system.

MPRP Transmission Alternatives Study—This study identified transmission upgrades to serve load pockets and ensure the system will meet national and regional transmission reliability criteria. These projects will provide the ancillary benefit of facilitating the maintenance of the system in Maine. The selected alternative, referred to in the transmission alternatives study as “N5S1,” consists of significant additions of new 345 kV lines, 115 kV lines, 115 kV capacitors, 345/115 kV autotransformers, and line rebuilds, and the separation of circuits sharing common towers. The new 345 kV lines in the north create a 345 kV path from Orrington to Surowiec, while the new 345 kV lines in the south create a third parallel path from Surowiec to Three Rivers in southern Maine. While these new paths are expected to increase transfer capability out of Maine, they also will increase the ability to move power into Maine from New Hampshire and improve the ability of the transmission system within Maine to move power into the load pockets as necessary. The major 345 kV components of the plan are as follows:

New 345 kV line construction

- Orrington–Albion Road

- Albion Road–Coopers Mills

- Coopers Mills–Larrabee Road

- Larrabee Road–Surowiec

- Surowiec–Raven Farm

- South Gorham–Maguire Road

- Maguire Road–Three Rivers

New 345/115 kV autotransformers

- Albion Road

- Larrabee Road

- Raven Farm

- Maguire Road

- South Gorham

Separation of double-circuit towers (DCTs)

- 345 kV Kennebec River Crossing by the Maine Yankee−Buxton and Maine Yankee−Surowiec circuits (375/377)

- 345 kV Maine Yankee−Buxton and Coopers Mill−Maine Yankee (375/392)

Rerating of 345 kV transmission lines

- Section 378 (345 kV Maine Yankee–Mason)

- On July 1, 2008, CMP submitted a siting application for these MPRP projects to the Maine Public Utilities Commission (MPUC). In June 2010, the MPUC issued an order approving most of the MPRP. The 345 kV portions of the MPRP not approved were the installation of the autotransformer at Raven Farm, the reconfiguration of Maine Yankee substation, and the elimination of the double-circuit tower configuration, which exists on the Maine Yankee−Buxton and Coopers Mill−Maine Yankee (375/392) circuits. On July 26, 2010, PSNH and CMP filed a supplemental filing that provides additional information on the switching station near Three Rivers per the June 2010 MPUC order.

Chester Area Project—This project adds a 345/115 kV transformer at Keene Road in Chester, Maine, to provide necessary backup to the area load and allow for rebuilding the Keene to Enfield to Graham 115 kV section (line 64). Currently, section 64 needs to be rebuilt, and the area’s subtransmission system is incapable of supporting area loads while construction is underway. In addition, the section 64 rebuild and the installation of the Keene Road autotransformer will provide area support following the loss of both autotransformers at Orrington. This project is expected to be in service in late 2011.

Monadnock Region—The Monadnock region encompasses a three-state area of southeastern Vermont (Brattleboro to Bellows Falls and Ascutney), southwestern New Hampshire (Keene north to Claremont), and north-central Massachusetts (Pratts Junction to the northern border with New Hampshire). In addition to supplying local demand, the transmission facilities in this region are critical for supporting a wider area, including most of Vermont and northern New Hampshire. A new 345/115 kV substation at Fitzwilliam, New Hampshire, along the Amherst–Vermont Yankee 345 kV line, and a number of 115 kV upgrades have been developed to address existing and midterm voltage and thermal performance concerns. All these upgrades were completed in summer 2009. Studies indicate the likely need for future transmission system reinforcements in this area and will be reevaluated as part of the Vermont and New Hampshire 10-year assessments.

### Southern New England

The southern New England area encompasses the Massachusetts, Rhode Island, and Connecticut transmission system. Studies of these states are being conducted to address a wide range of transmission system concerns, both short and long term.

#### Southern New England Transmission

The 345 kV facilities that traverse southern New England comprise the primary infrastructure integrating southern New England, northern New England, and the Maritimes Balancing Authority Area with the rest of the Eastern Interconnection. This network serves the majority of New England demand, integrating a substantial portion of the region’s supply, demand, and import resources.

Although recent improvements have been made, the southern New England system continues to face thermal, low-voltage, high-voltage, and short-circuit concerns under some system conditions. The most significant concerns involve maintaining the reliability of supply to serve load and developing the transmission infrastructure to integrate generation throughout this area. In many areas, an aging low-capacity 115 kV system has been overtaxed and no longer is able to serve load and support generation reliably. Upgrades to the power system are being planned and developed to ensure the system can meet its current level of demand and prepare for future load growth (see Section 3).

#### Southern New England Transmission System Studies

Study efforts in southern New England have been progressing to address a wide range of system concerns. Major past and ongoing efforts have focused on the load areas with the most significant risks to reliability and threats to the system, particularly the Boston area and southwestern Connecticut. More recently, plans have been developed to address the reliability of other parts of the system, particularly Connecticut; the Springfield, Massachusetts, area; central and western Massachusetts; Rhode Island; and southeastern Massachusetts, including Cape Cod. The need for some of these plans currently is being reassessed to account for the lower load forecast, new supply and demand resources, and sensitivities to the unavailability of the Vermont Yankee generating facility. These efforts also are addressing the broader requirements of the overall east–west and west–east transmission systems.

Analyses of the Greater Boston and southwestern Connecticut areas, as well as of the Pittsfield area of western Massachusetts, continue to move forward. A new study has begun for the Hartford area, which will determine the area’s needs that are sensitive to the reassessments of the Interstate and Central Connecticut components of NEEWS. Another new study has begun for the Middletown area. This Needs Assessment will consider the issues associated with the single 345/115 kV autotransformer at the Haddam substation and the weak 115 kV links between this area and the surrounding areas. A southeast Massachusetts/Rhode Island study, referred to as the eastern REMVEC study, has also begun. Its major goal is to determine any long-term system needs required to integrally serve the broad SEMA, NEMA, and Rhode Island areas, and to ensure consistency and cohesiveness of planning and design. Other smaller, more local studies are scheduled for eastern Connecticut and the Manchester–Barbour Hill area of Connecticut. While many of the major efforts have focused primarily on near-term and midrange concerns, several longer-term analyses have been completed, and others are being conducted.

Southern New England Region. Before the start of siting hearings for the Rhode Island Reliability Project (RIRP), which is the first component of the four NEEWS components to proceed to siting, needs reassessments were begun for all four of the components—the RIRP, as well as the Greater Springfield Reliability Project (GSRP), the Interstate Reliability Project (IRP), and the Central Connecticut Reliability Project (CCRP). (See Section 6.4.2.3 for more details about these projects.) The need reassessments for the RIRP and the GSRP were relatively straightforward and were completed, presented to the PAC, and used eventually in both the RIRP and the GSRP siting proceedings.

As a result of new resources clearing in FCA #1 to FCA #3 within Connecticut and to the west of the New England East–West interface and the updated load forecast, the need for the IRP and the CCRP components required a significant amount of new analysis. The studies considered demand resources as part of the FCM resource mix and were not subtracted from the load forecast. The current CELT forecasted load for 2015 is higher than the critical load level included in previous analyses, which showed the criteria violations identified in the original Needs Assessment for NEEWS (i.e., Southern New England Transmission Reinforcement Study; SNETR).

The study work associated with the IRP component focused on addressing the following questions:

- Foremost, is the planned system for 2015 and 2020 capable of serving load reliably through the 10-year planning horizon in Rhode Island, western New England, Connecticut, and eastern New England areas under a variety of foreseen operating conditions?

- Will the 2015 and 2020 planned system allow the deliverability of FCA-cleared resources to and from western New England and eastern New England to help ensure a reliable supply to load?

- Will the Interstate component of NEEWS provide relief to the generator mechanical stress issues and reclosing problems in the area of the Lake Road generating plant?

- Will the Interstate component of NEEWS provide short-circuit-interrupt benefits by allowing the splitting of the West Medway 345 kV bus where substation equipment is approaching its short-circuit limits?

- Is the system response to extreme contingencies stable, and if not, will the Interstate component of NEEWS eliminate or reduce the severity of these issues?

- The New England east–west transfer limit has been stability limited at times and thermally limited at other times. Do the stability limits currently undercut the system’s thermal capability, and if so, will the Interstate component of NEEWS improve the system’s stability performance so that the higher thermal limit can be achieved?

- What impact would the closing of Vermont Yankee have on the results?

The results of the reassessment shows a substantial need for an integrated regional transmission solution to resolve transmission planning criteria violations in eastern New England, western New England, and Greater Rhode Island (GRI). The major driver is the need to reliably serve load in accordance with NERC, NPCC, and ISO planning standards and criteria in the areas of Rhode Island, western New England, Connecticut, and eastern New England. By addressing the transmission constraints along the Card Street to West Medway corridor (CT–RI–MA), both the aforementioned load-serving issues, as well as deliverability limitations in moving capacity from western New England and GRI to eastern New England and from eastern New England and GRI to western New England, will be resolved. Thus, about 2,000 MW along this corridor in the Greater Rhode Island area could be used to reliably serve load in both western and eastern New England over the long-term planning horizon. (See Figure 6-1.)

Figure 6-1: Map of constraints in southern New England.

The original need for the IRP component of NEEWS was based primarily on a deficiency in being able to move power from eastern New England to western New England and to Connecticut. While this need still exists, the new analysis shows an increased need to also move power from western New England to eastern New England. The study identified system constraints that exist to the east of the Greater Rhode Island area, which are more evident now with the increased resources in the west.

The simultaneous existence of load-serving needs in western New England and the deliverability limitations from western New England and GRI to eastern New England results in an overconstrained situation in western New England. The addition of resources in western New England to address load-serving capability would increase the amount of “locked-in” resources in western New England and Greater Rhode Island. Conversely, a combination of retirements and repowering outages in western New England would decrease “locked-in” resources but would increase the need to address load-serving capability in western New England. A transmission solution is necessary to bridge the gap between western New England load-serving requirements and western New England and GRI resource deliverability.

The preliminary Solutions Study shows that the original interstate project is effective at resolving the majority of the overload issues in Rhode Island, western New England, Connecticut, and eastern New England. However, it does not resolve all criteria violations for serving eastern New England load. Some additional modifications to the project will be necessary to complete the plan and will be identified when the ongoing studies are completed.

The CCRP component of NEEWS is still being reevaluated. Additionally, a long-term system Needs Assessment is underway to determine whether any additional needs or further solutions are necessary to reliably serve the broad SEMA, NEMA, and Rhode Island load areas. Past studies have indicated a need to further integrate the Brayton Point plant, perhaps via a new Brayton Point–Bridgewater 345 kV line, and to add transmission capacity to remove limits on moving generation into and around the West Medway substation.

Massachusetts. A long-term reliability Needs Assessment for 2013 and 2018 has been completed for the Greater Boston area. Criteria violations have been summarized into eight categories, which include areas to the north, the west, and the south, and in downtown Boston. Key outages in the north can cause overloads on the ties into Greater Boston and on 115 kV lines north of Boston. The 115 kV lines in the Tewksbury, Lexington, and Woburn areas overload when subjected to critical contingency outages. Additional contingencies cause overloads in the downtown area and on lines between Boston and Wakefield Junction. Overload issues arise between Holbrook and West Walpole for other outages. Lastly, outages result in overloaded lines and low voltages in the Sudbury, Marlboro, and Northborough areas. The year of need and the critical load level for each area of need have been tabulated.

Currently, two alternative plans are being given primary consideration. These may be supplemented or eliminated, and others may be added, as the results proceed through the stakeholder process. The initial two alternative plans are as follows:

Major components of Alternative A

Scobie–Tewksbury 345 kV line

Lexington–Waltham 230 kV line with a new 345/230 kV autotransformer at Lexington

Sudbury 230/115 kV autotransformer

Sudbury–Hudson 115 kV line

Holbrook–Walpole 115 kV line

Woburn–Mystic 115 kV line

Wakefield–Everett 115 kV line

Two Brighton–Waltham 115 kV cables

Major components of Alternative B

Seabrook–Ward Hill 345 kV line

Lexington–Waltham 345 kV line with a new 345/230 kV autotransformer at Waltham

Woburn–Lexington 115 kV line

Framingham–Speen 115 kV line

Conversion of 69 kV circuits and substation facilities to 115 kV in western suburbs of Boston

Woburn–Mystic 115 kV line

Wakefield–Everett 115 kV line

Two other options, which were initially considered, will not be pursued unless the two primary alternatives significantly expand in scope or are somehow inadequate.

Major components of Alternative C

Scobie–Woburn 345 kV line

Wakefield–Ward Hill 345 kV line

Lexington–Waltham 345 kV line with a new 345/230 kV autotransformer at Waltham

Waltham–Sudbury 115 kV line

Conversion of 69 kV circuits and substation facilities to 115 kV in western suburbs of Boston

Woburn–Mystic 115 kV line

Wakefield–Everett 115 kV line

Major components of Alternative D

Based on HVDC line with termination at the K Street substation.

Additional transmission upgrades for specific subareas to address remaining needs, drawing on upgrades from Plans A, B, and C, as appropriate

Although a previous analysis identified needs for the Berkshire County/Pittsfield area, this area has been reassessed using the latest available data, and a new report has been finalized and posted. The needs that require solutions are as follows:

Thermal overloads on the 115 kV corridor between Berkshire and Montague (1231/1361 lines) and on the A127-9 line (Montague to Cabot Junction)

Overloads on the Berkshire 2X autotransformer (345/115 kV) under certain system conditions

Thermal overloads on the Pleasant–Blandford–Granville Junction 115 kV corridor (1421/1512 lines)

Voltage violations (<0.95/unit of the nominal voltage) at several Pittsfield-area substations, as well as many Greenfield-area substations, which can go well below 0.90/unit under “low-hydro” conditions

Possible solutions to these needs include adding 345/115 kV autotransformers, upgrading considerable lengths of old 115 kV transmission lines, and installing additional capacitors to mitigate both thermal and voltage concerns. The selection of the final plan for this area is scheduled for late 2010 or early 2011.

Connecticut. The Needs Assessment phase of the Southwest Connecticut study currently is being completed and has identified the following issues:

A requirement for 115 kV reinforcements in the Bridgeport and New Haven areas

Low-voltage problems on the 115 kV system in the Naugatuck Valley area

Thermal overload problems along the 115 kV Stony Hill corridor

Thermal overload problems in the corridor down to Cos Cob

Impending short-circuit issues at the Pequonnock 115 kV substations

Two other study efforts have begun in Connecticut. Other analyses have revealed that transmission reliability deficiencies can exist in the Hartford area, under certain system conditions, and also in the Middletown area. The scope of the Hartford Needs Assessment, as presented to PAC, included both five- and 10-year analyses under various dispatches and system transfer levels. The Middletown Needs Assessment has been structured similarly. The Hartford transmission system can experience flow-through issues when its 115 kV circuits are called on, under contingency conditions, to carry the power normally supplied via the 345 kV system. Additionally, load supply issues exist under certain dispatch and transfer conditions. Both voltage and thermal issues have been identified in the Middletown area under future conditions when local generation is unavailable and when the Haddam 345/115kV autotransformer is out of service. Both the Hartford and the Middletown Needs Assessments will identify the problem conditions and the critical load levels at which they occur.

#### Southern New England Transmission Projects

About 10 transmission projects in various stages are underway in southern New England. The system performance in southern New England is complicated by many factors, such as load levels, system transfers, and unit commitment. The several projects identified for this area must function reliably under a wide variety of conditions, and their development must support the operation of the overall system.

NEEWS. The four components of the NEEWS project address the need for additional 345/115 kV transformation and contingency coverage in the Rhode Island area (Rhode Island Reliability Project), the need for reinforcements in the Springfield, Massachusetts, area (Greater Springfield Reliability Project), and the need for increased transfer capability into and through Connecticut (Interstate Reliability Project and Central Connecticut Reliability Project).

The specific needs for these components first identified are as follows:

The Springfield, Massachusetts, area experiences thermal overloads under forecasted normal conditions and significant thermal overloads and voltage problems under numerous contingencies. The severity of these problems increases when the system tries to move power into Connecticut from the rest of New England.

Regional east–west power flows and transfers into and out of Connecticut are limited and eventually may result in the inability to serve load under many probable system conditions.

East-to-west power flows inside Connecticut stress the existing system and could result in future thermal overloads under contingency conditions.

The Rhode Island system is overly dependent on limited transmission lines or autotransformers to serve its needs, resulting in thermal overloads and voltage problems for contingency conditions.

After considerable analyses of the alternatives, the following plan consisting of a number of projects was selected. The major upgrades for each of the four components of the plan are as follows:

Rhode Island component

A second West Farnum–Kent County 345 kV line

One additional Kent County 345/115 kV autotransformer

Springfield component

A new Ludlow–Agawam–North Bloomfield 345 kV line

Reconfiguration and expansion of the Ludlow 345 kV substation

Replacement of two 345 kV/115 kV autotransformers at Ludlow

A new 345 substation with two 345/115 kV autotransformers at Agawam

A second 345/115 kV autotransformer at North Bloomfield

A new 115 kV switching station at Cadwell

Reconfiguration of the Fairmont substation into a breaker-and-a-half arrangement

Two 345 kV 120 MVAR capacitor banks at Ludlow

Rebuilding and reconductoring numerous 115 kV circuits

Interstate component

A new Millbury–West Farnum–Lake Road–Card 345 kV line

Four 345 kV 120 MVAR capacitor banks at Montville

Central Connecticut component

A new North Bloomfield–Frost Bridge 345 kV line

Expansion of the Frost Bridge 345 kV substation, including the addition of a second 345/115 kV autotransformer

The plan also includes other projects ranging from relatively minor ones, such as upgrading terminal equipment at 115 kV substations and installing higher-rated circuit breakers, to more involved projects, such as reconfiguring, rebuilding, and reconductoring 115 kV lines. (See the Southern New England Region in Section 6.4.2.2 for the NEEWS reassessment results to date.)

Other transmission projects in southern New England are as follows:

Downtown Boston 345kV Reliability Project—The completion of the first and second phases of the Boston 345 kV Transmission Reliability Project occurred in early 2009. This project included the construction of a new Stoughton 345 kV switching station and the installation of three new underground 345 kV lines and associated 345/115 kV autotransformers. Two 17.5-mile cables connect the Stoughton and K Street substations, and one 11-mile cable connects the Stoughton and Hyde Park substations, significantly increasing the reliability to the downtown Boston area.

Merrimack Valley/North Shore Project—Engineering and construction of the last of the upgrades associated with the Merrimack Valley/North Shore Project currently is in progress. The new Wakefield Junction substation was placed in service in late 2009, and the Golden Hill substation was removed in early 2010. The remaining upgrades will be completed in the 2011 to 2014 timeframe.

Mystic and West Walpole Reactor Projects—The extensive light-load studies completed in 2008 concluded that additional static reactors in the Boston area could further help control steady-state high voltages and provide needed light-load reactive-compensation reserves. The first was installed at the Mystic station in early 2009 (345 kV, 160 MVAR) and the second at West Walpole mid-2010.

Bear Swamp–Pratts Junction 230 kV Refurbishment (E205 line)—Detailed field inspections revealed significant reliability issues with the condition of the equipment on this over-50-year-old line. Issues with wooden poles included checking, bowing, splitting, and woodpecker holes. Work on this major rebuild, which includes removing and replacing 300 to 400 structures, has begun. A similar rebuild is being engineered and scheduled for the A127 and B128 115 kV lines that run westerly from Millbury to the Harriman/Sherman substations.

Central/Western Massachusetts Upgrades—Past studies developed a 10-year plan for central Massachusetts and portions of western Massachusetts. This plan calls for adding a third autotransformer at the Wachusett 345/115 kV substation and a second 230/115 kV autotransformer at Bear Swamp, replacing transformers at Pratts Junction and Carpenter Hill substations, adding a new 115 kV line from Millbury to Webster, and implementing several other 115 kV upgrades.

Auburn Reliability Project—Past studies of the area surrounding the Auburn Street substation have found overloads of the existing 345/115 kV autotransformer and several 115 kV lines, voltage problems, and breaker overstresses. The solution to eliminate these identified reliability deficiencies includes a new bay configuration at the Auburn Street substation along with the installation of a second autotransformer and the replacement of a number of breakers. The 115 kV Auburn Street–Parkview and Bridgewater–East Bridgewater lines will be reconductored. Changes to the original Auburn substation equipment layout have been made through the engineering and design phases of the project. Additionally, a number of distribution substation changes are being discussed that could modify the original project and its subsequent cost. The Bridgewater–Easton 115 kV line (E1) will be extended to supply a new municipal substation in Mansfield. The new Avon substation will be constructed and tapped off the newly reconductored Auburn Street–Parkview line (A94). The addition of a second distribution transformer at Dupont requires associated terminal work.

Lower SEMA Short- and Long-Term Upgrades—Plans to eliminate the criteria violations in the lower southeastern Massachusetts (LSM) area, which includes Cape Cod, were separated into two phases. Phase one included the projects that could be put in place in an expedited time frame. Phase two includes those projects that would serve as the long-term solution for reliable supply but would require state siting hearings. The short-term upgrades were completed in 2009, and the long-term upgrades have now reached the siting stage. The short-term plan included the following system improvements:

Looping the Bridgewater–Pilgrim 345 kV line into the Carver substation

Adding a second Carver 345/115 kV autotransformer

Expanding the Carver 345 kV and 115 kV substations and the Brook Street and Barnstable 115 kV substations

Upgrading the Kingston terminal of the 191 line between Kingston and Auburn Street

Installing a second Carver–Tremont 115 kV line

Connecting the spare conductors of the Jordan Road–Auburn Street line as a new Brook Street–Auburn Street 115 kV circuit

Adding 115 kV breakers at Auburn Street

Reconnecting the Auburn Street–Kingston line to a new position at Auburn Street

Adding a static VAR compensator at Barnstable

The long-term plan includes adding a new 345 kV transmission line from the Carver substation to a new 345/115 kV substation. This new four-breaker ring-bus substation, which has been designated the Service Road Substation, will be located west of the Barnstable substation adjacent to the 115 kV line right of way. The Carver–Bourne section of the 345 kV line is new construction, and the Bourne–Barnstable portion of the new 345 kV line will use an existing 115 kV line built to 345 kV standards. The 115 kV line will be tapped into the new substation. The plan also involves placing the existing 345 kV Cape Cod Canal crossing on separate towers to eliminate a DCT contingency and reconductoring the 115 kV D21 line between Bell Rock and High Hill. In addition to these upgrades, a 115 kV line from Bourne to Barnstable is planned to address load growth on the Cape Cod peninsula.

Greater Rhode Island (Advanced NEEWS) Project—Reliability concerns with the 115 kV system in the Bridgewater–Somerset–Tiverton areas of southeastern Massachusetts and the adjoining area in Rhode Island had been identified previously. The solutions to these concerns were a group of upgrades that had been combined with the advanced Rhode Island upgrades (associated with NEEWS studies) to become what is now known as the Greater Rhode Island Transmission Reinforcements. The advanced NEEWS upgrades are now under construction; the two largest upgrades are the new Berry Street 345/115kV substation (MA) and the expansion of the Kent County substation (RI) with an additional 345/115 kV autotransformer. The proposed non-NEEWS GRI solutions in the Massachusetts area include, among other projects, the construction of new Brayton Point–Somerset and Somerset–Bell Rock 115 kV transmission circuits. These currently are scheduled for a 2014 in-service date and will be reexamined as part of the Eastern REMVEC study (discussed in Section 6.4.2.2). The proposed GRI advanced NEEWS solutions in Rhode Island also include the reconductoring of the Pawtucket–Somerset (MA) 115 kV line (placed in service in late 2009) and West Farnum breaker replacements.

Grand Avenue Substation Rebuild—A plan for rebuilding the Grand Avenue 115 kV substation has been developed and currently is in the engineering phase. A detailed engineering review of the existing substation determined that it was past its useful life and that upgrades were not practical when considering the capabilities of the bus work, the ground grid, disconnect switches, and other equipment. Maintenance of the existing equipment had become increasingly difficult with the clearances that existed and the extent of the outages that had to be secured for work to proceed.

## Transmission Improvements to Load and Generation Pockets Addressing Reliability Issues

The performance of the transmission system is highly dependent on embedded generators operating to maintain reliability in several smaller areas of the system. Consistent with ISO operating requirements, the generators may be required to provide second-contingency protection or voltage support or to avoid overloads of transmission system elements. Reliability may be threatened when only a few generating units are available to provide system support, especially when considering normal levels of unplanned or scheduled outages of generators or transmission facilities. This transmission system dependence on local-area generating units typically can result in relatively high reliability payments associated with out-of-merit unit commitments (see Section 6.6).

The areas that have or could potentially benefit from additional generators for local reliability support are as follows:

Maine

Massachusetts—the Boston area, the North Shore area, southeastern Massachusetts, western Massachusetts, and the Springfield area

Connecticut

The following sections describe several of the areas currently depending on generating units to some degree to maintain reliability. They also provide the status of the transmission projects that will either reduce or eliminate the need to run these units out of merit to respect reliability requirements.

### Maine

Generation in western Maine is required to provide voltage support for the 115 kV transmission system. Low-voltage conditions can develop in parts of western Maine, geographically and electrically distant from the 345 kV system during both pre- and post-contingency scenarios. Several 115 kV contingencies can result in unacceptably low voltages on many of the 115 kV buses in the western Maine area.

Generation also is required for maintaining system reliability following second contingencies involving flows from New Hampshire to Maine. In addition, in 2008, Sable Offshore Energy’s production facility sustained a series of problems that, on several occasions, disrupted the supply of gas to generators in Maine (see Section 7.2). This in turn depleted electric power capacity in Maine, which depends heavily on gas-fueled generation. In such scenarios, available generation in Maine must be on line to maintain system reliability in that state. The system did not experience any reliability problems because operating procedures helped anticipate the gas supply problems. Recently in 2009, the Canaport LNG facility was placed in service, decreasing the likelihood of such gas supply disruptions (see Section 7.3.1.3).

### Boston Area

The cost of operating local generation to control high voltages in Boston had been significant in previous years. An extensive high-voltage study of Boston was conducted to investigate whether the need to run local generation during light-load periods could be eliminated. The study concluded that the area can be operated reliably without any generation in the Boston area to control high voltages during light-load periods. It also concluded that no dynamic voltage control device would be needed with all lines in service and an additional static reactor in the Boston area could help control high voltages, especially during line-out conditions. The voltage control payments for this area in 2009 were eliminated to a large degree following the installation of additional planned reactors. Further reductions are likely after the second West Walpole variable-shunt reactor is installed, which is planned for mid-2010 (see Section 6.4.2.3).

Running local generation for second-contingency coverage under some conditions also had been needed in the past. This also has been eliminated to a large degree with the installation of the third cable from Stoughton to K Street (see Section 6.4.2.3).

### Southeastern Massachusetts

In the southeastern part of Massachusetts, the Canal generating units have been run to control the high-voltage conditions that exist during light-load periods and to provide for transmission security during virtually all load levels. These circumstances resulted in significant costs in 2007, which increased roughly 50% for 2008. As detailed in Section 6.4.2.2, the SEMA short-term upgrades are in service, and these recent improvements, coupled with recently experienced low load levels, already have significantly reduced the need for out-of-merit generation support. The long-term improvements, planned to begin siting in 2010, should eliminate the need entirely when placed in service in 2012.

### Western Massachusetts

The primary supplies for the Pittsfield area consist of the Berkshire autotransformer, the Bear Swamp autotransformer, and the Pittsfield generating units. The Pittsfield units are located in an extremely weak part of the system. Without these facilities, the area relies on a 115 kV transmission system, which is unable to provide adequate voltage support in the area under certain conditions. A new autotransformer has been placed in service at Berkshire that allows the older transformer to function as a spare, thereby reducing the risk of a long-term failure of this essential part of the supply to load in this area.

Studies of alternative transmission solutions surrounding the Berkshire substation are in process and should be completed by late 2010. Some out-of-merit costs will continue until improvements are made in the area.

### Springfield Area

Currently, the West Springfield station and Berkshire power generation plants are needed to support local reliability during peak hours and to avoid overloads in violation of reliability criteria. A solution for the Greater Springfield area has been formulated as part of the NEEWS study (see Section 6.4.2.2). The GRSP component of NEEWS has been approved by siting authorities in Connecticut and is expecting approval in Massachusetts later this year. This solution will accommodate load growth as well as reduce dependence on operating these local units for local reliability. It also may allow for the eventual retirement of the oldest of these generation units and provide the opportunity for new units to interconnect.

### Connecticut

Most of the existing generation in Connecticut is necessary to ensure reliable service until the new resources secured through the FCA are in place. Until that time, imports into Connecticut will be constrained by both thermal and voltage limits for contingency events. As a result of the resources committed from the FCA, the Interstate and the Central Connecticut components of the NEEWS project are under further review, including examination of the sensitivity to the unavailability of Vermont Yankee and Kleen Energy. New study efforts currently are establishing a final date of need.

### Southwest Connecticut Area

The need to run out-of-merit generation in southwest Connecticut has been virtually eliminated by placing in service the Glenbrook–Norwalk and Middletown–Norwalk projects in late 2008.

## Out-of-Merit Operating Situations

As part of the FCM rules (Section 4.2), the ISO reviews each delist bid to determine whether the capacity associated with the delist bid is needed for the reliability of the New England electric power system. Capacity determined not to be needed for reliability is allowed to delist.

For the third FCA, for the 2012/2013 capacity commitment period, 326 delist bids totaling approximately 2,291 MW of summer-qualified capacity were submitted. In accordance with Planning Procedure No. 10 (PP 10), Planning Procedure to Support the Forward Capacity Market, the ISO reviewed and analyzed these bids and determined that 581 MW, representing Salem Harbor Units #3 and #4, were needed for reliability. In a February 26, 2010, order, FERC accepted the ISO’s determination. For the fourth FCA, for the 2013/2014 capacity commitment period, 119 delist bids were received, representing 1,248 MW. FCA #4 was held in August 2010.

## Other Needed and Elective Transmission Upgrades

This section discusses several needed Market-Efficiency-Related Transmission Upgrades. It also provides information on several transmission upgrades developed and paid for by market participants. The transmission upgrades must meet reliability performance requirements.

### Needed Market-Efficiency-Related Transmission Upgrades

The purpose of and requirements for Market Efficiency Transmission Upgrades are described in Section 6.2.3.2. However, market-efficiency benefits also may be associated with Reliability Transmission Upgrades, particularly when out-of-merit operating costs are reduced.

#### Transmission Improvements to Mitigate Congestion

Recent experience has demonstrated that the regional transmission system has little congestion. The U.S. Department of Energy (DOE) recognized the regional investment in new supply- and demand-side resources, as well as planning and development of extensive transmission upgrades, and it removed New England as “an area of concern” for the identification of National Interest Electric Transmission Corridors (NIETC) (see Section 11.1.1). For most of the system in 2009, the mean difference between the congestion component of the LMP at the Hub and the regional energy zones was less than $0.21/MWh. However, in some areas of the system, the mean difference between the loss component of the LMP at the Hub and the energy zone was as much as $3.31/MWh. This signifies a fairly inefficient portion of the system due to high losses. The congestion costs are not significant enough to warrant mitigation by a transmission upgrade; however, planned Reliability Transmission Upgrades might help reduce congestion costs further. Similarly, planned Reliability Transmission Upgrades may also reduce transmission system losses.

#### Reliability Transmission Upgrade Improvements to Load and Generation Pockets

Transmission solutions have been and are being put in place where developers have not proposed adding new resources to relieve transmission system performance concerns. The ISO is studying many of these areas, and while transmission projects are still being planned for some areas, other areas already have projects under construction and in-service to mitigate dependence on the embedded generating units. While the transmission system modifications needed to address the system performance problems in these areas were Reliability Transmission Upgrades, these upgrades contributed to a substantial reduction in out-of-merit operating costs.

Generating units in load pockets may receive second-contingency or voltage-control payments for must-run situations. Table 6-2 shows the Net Commitment-Period Compensation (NCPC) by type and year. In 2009, the total amount of NCPC was reduced by approximately 90% from levels experienced from 2005 through 2008. This was in large part due to transmission upgrades that have improved the reliability of service to load pockets. One set of transmission improvements in Lower SEMA reduced NCPC to the entire SEMA Reliability Region by approximately $130 million from 2008 to 2009. Additional plans are in place to eliminate constraints in this area. Other contributing factors to lower NCPC in 2009 were low loads and inexpensive natural gas and fuel oil for generating units in the load pockets.

Table 6-2
Net Commitment-Period Compensation by Type and Year (million $)

| Year | Second Contingency(a) | Voltage | Total(b) |
| --- | --- | --- | --- |
| 2003(c) | 36.0 | 14.4 | 50.4 |
| 2004 | 43.9 | 68.0 | 111.9 |
| 2005 | 133.7 | 75.1 | 208.8 |
| 2006 | 179.9 | 19.0 | 199.0 |
| 2007 | 169.5 | 46.0 | 215.5 |
| 2008 | 182.5 | 29.4 | 211.9 |
| 2009 | 17.2 | 5.0 | 22.2 |

(a) 	NCPC for first-contingency commitment and distribution support are not included.

(b) 	Numbers may not add because of rounding.

(b) 	Recording of data began in March 2003.

At approximately $22 million of reliability NCPC payments in 2009, the current incentives are limited for pursuing transmission upgrades solely to reduce dependence on these generating units and improve the economic performance of the system.

### Required Generator-Interconnection-Related Upgrades

No significant transmission system upgrades resulted from the interconnection of generators. Most of the Generator-Interconnection-Related Upgrades are fairly local to the point of interconnection of the generator. The PTF upgrades are identified in the RSP Project List.

### Elective Transmission Upgrades and Merchant Transmission

Currently six projects are Elective Transmission Upgrades or merchant transmission facilities:

Two-terminal, 1,000 MW, 500 kV, DC line between Maine Yankee substation and South Boston, MA

HVDC line between Orrington, ME, and Boston, MA

345/230 kV DC line between Plattsburgh, NY, and New Haven, VT

345 kV tie line connecting Houlton, ME, and the Maine Electric Power Company (MEPCO)

345kV tie line connecting Bridgewater, ME, and MEPCO

These projects are all currently under study.

## Summary

To date, seven major 345 kV transmission projects have been completed in four states; one additional project has completed siting and is under construction; and four others have either completed siting, are in siting, or are expected to be in siting by the end of 2010. These projects reinforce critical load pockets, such as in Southwest Connecticut and Boston, and areas that have experienced significant load growth, such as Northwest Vermont. These projects also include a new interconnection to New Brunswick, which increases the ability of New England to import power from Canada. The replacement of existing underwater transmission cables (the NNC) between Connecticut and Long Island also has been completed recently to preserve the integrity of this tie line.

The Maine Power Reliability Program, for which the MPUC has approved most of the component projects, will establish a second 345 kV line in the north from Orrington to Surowiec. It also will add new 345 kV lines in southern Maine, creating a third parallel path from Surowiec to Three Rivers in southern Maine. This program will reinforce and augment the 345/115 kV transformation capability in various load centers of Maine for greater reliability to area loads. While these new paths provide basic infrastructure to increase transfer capability out of Maine, they also will increase the ability to move power into Maine from New Hampshire and improve the ability of the transmission system within Maine to move power into the load pockets as necessary.

The New England East–West Solution series of projects has been identified to improve system reliability. RSP10 shows that the Springfield and Rhode Island components should be placed in-service as soon as possible, while the 345 kV lines planned into Connecticut (i.e., the Interstate component) and through Connecticut (the Central Connecticut component) are under further review based on the latest forecast, FCM-obtained resources, and other factors. The need for the Interstate Reliability Project component of NEEWS has been established, but the final transmission alternatives remain under study. The need for the Central Connecticut Reliability Project is also under study.

Costs associated with second-contingency and voltage-control payments have been mitigated through transmission improvements. Additional transmission plans have been developed to further reduce the dependence on generating units needed for reliability. An example is the Lower SEMA projects whereby short-term improvements already have reduced dependence on the Cape Cod Canal generating units; further long-term improvements will eliminate the need to commit generation for second-contingency protection.

From 2002 through 2010, 341 projects will have been put into service, with an investment totaling approximately $4.3 billion. Additional projects, totaling approximately $5 billion, are summarized in the RSP Project List, which is updated periodically. All transmission projects are developed to serve the entire region reliably and are fully coordinated regionally and interregionally. Most projects on the RSP Project List remain subject to regional cost allocation.

As a result of transmission expansion, the ISO meets all required reliability requirements, and little congestion is evident on the system.

# Fuel Diversity

“[T]he RSP shall identify: (ii) the requirements and characteristics of the types of resources that may satisfy PTF system reliability and market efficiency needs to provide stakeholders an opportunity to develop and propose efficient market responses to meet the needs identified in Needs Assessments.” [T]he RSP shall also provide information on a broad variety of power system requirements that serves as input for reviewing the design of the markets and the overall economic performance of the system.“ (Attachment K, Overview)

“The RSP shall be designed and implemented to: . . .(ii) identify facilities that are necessary to meet Planning and Reliability Criteria; (iii) avoid the imposition of unreasonable costs upon any Transmission Owner, Transmission Customer or other user of a transmission facility; and (vi) properly coordinate with market responses, including, but not limited to generation, merchant transmission and demand-side responses.” (Attachment K, § 3.4)

For at least 10 years, New England’s power generation sector has had issues associated with the significant lack of fuel diversity. But actions over the past few years have improved the reliability of the fuel supply and associated generator performance. Although the region remains heavily dependent on natural gas as its primary fuel for power generation, recent natural gas infrastructure projects should satisfy the needs of New England’s gas and power markets for years to come. These improvements include the diversification of natural gas supply sources that include new fields and expanded natural gas pipelines, storage, and liquefied natural gas (LNG) import facilities. The improvements in the regional natural gas system, combined with the addition of both demand-side and renewable resources, are expected to mitigate historical reliability concerns over the lack of fuel diversity within New England.

This section discusses the status of issues associated with fuel diversity in New England and presents statistics on the current fuel mix and the amounts of electricity these fuels have generated. The section also summarizes regional enhancements to the natural gas system infrastructure, provides an electricity sector outlook of actions that are addressing fuel reliability issues, and identifies some fuel-related risks remaining within the generation sector that have been or currently are being addressed.

Attachment K requires the RSP to specify the physical characteristics of solutions that can meet system needs, including general locations, operating characteristics, and types of supply-side or demand-side resources. Attachment K also requires the ISO to consider market responses within its planning process.

## System Capacity for 2010 and 2009 Fuel Mix

Figure 7-1 depicts New England’s generation capacity mix by primary fuel type and percentage. On the basis of the ISO’s 2010 CELT Report, the total 2010 summer installed capacity is forecast to be 31,965 MW with the following fuel mix:

Fossil-fuel-based generation (22,803 MW) accounts for 71.3% of the installed capacity within the region.

Natural-gas-fired generation represents the largest component of total installed capacity at 41.2% (13,181 MW).

Oil-fired generation is second at 21.5% (6,866 MW).

Nuclear generation is third at 14.5% (4,629 MW).

Coal-fired generation is fourth at 8.6% (2,756 MW).

Hydroelectric capacity (1,712 MW) and pumped-storage capacity (1,679 MW) are at 5.4% and 5.2%, respectively.

Other renewable resources are at 3.6% (1,142 MW).

Figure 7-1: Generation capacity mix by primary fuel type, 2010 summer ratings (MW and %).

Note: The “Other Renewables” category of fuel sources includes landfill gas, other biomass gas, refuse (municipal solid waste), wood and wood-waste solids, wind, solar, black liquor, and tire-derived fuels. Black liquor is the spent cooking liquor that results from the process of converting wood to wood pulp to free the cellulose fibers.

Table 7-1 compares New England’s generation capacity mix by fuel type to that of the nation’s.

Table 7-1
New England’s Generation Capacity Mix by Fuel Type
Compared with the Nationwide Capacity Mix (%)(a)

| Fuel | New England | United States |
| --- | --- | --- |
| Coal | 8.6 | 30.6 |
| Natural gas | 41.2 | 41.5 |
| Oil (heavy and light) | 21.5 | 5.9 |
| Nuclear | 14.5 | 9.6 |
| Hydroelectric, pumped-storage, and other renewables | 14.2 | 12.2 |

(a) 	National figures are from the Energy Information Association (EIA). The raw data are available at http://www.eia.doe.gov/cneaf/electricity/page/capacity/capacity.html.

Figure 7-2 shows the production of electric energy by fuel type for 2009. As shown, natural gas, nuclear, and coal produced the majority of the region’s electricity. In total, fossil fuels were used for generating approximately 55% of the electric energy produced within New England in 2009. Natural gas generation produced the highest amount at 50,650 gigawatt-hours (GWh) at 42.4%. In 2009, New England imported 15,226 GWh of electric energy and exported 5,863 GWh of electric energy, which resulted in net imports of 9,363 GWh.

Figure 7-2: New England electric energy production in 2009, by fuel type.

Notes: The “Other Renewables” category of fuel sources includes landfill gas, other biomass gas, refuse (municipal solid waste), wood and wood-waste solids, wind, solar, black liquor, and tire-derived fuels. The figure excludes 9,377 GWh of net imports.

Fossil fuels produced 55% of the electric energy used in New England in 2009, compared with 69% of the electric energy used in the United States. Nationwide, coal produced 45%, compared with only 12% in New England, and natural gas produced 24% in the U.S., compared with 42% in New England. Additionally, nuclear fuel produced 20% of the nation’s electric energy in 2009 compared with 30% in New England. Renewable and hydroelectric resources provided 11% of the country’s electric energy in 2009, compared with 13% within the region. Production from petroleum fuels was under 1% both in New England and nationwide.

## Winter 2009/2010 Operational Overview

December 2009 was colder than normal, while January and February 2010 were warmer than normal. During winter 2009/2010, the system faced no major operational issues. The seasonal winter peak demand of 20,791 MW took place on December 17, 2009, at 6:00 p.m. at 15°F. During these three winter months, the ISO did not need to implement any OP 4 actions to manage a capacity deficiency. However, during the same three-month timeframe, the ISO invoked Master/Local Control Center Procedure No. 2, Abnormal Conditions Alert (M/LCC2) on 12 occasions. Four M/LCC2 declarations in December 2009 were to maintain sufficient operational capacity across all New England. The majority of the remaining M/LCC2 declarations in January and February were to curtail real-time electricity supply contracts to maintain operating reserves.

The ISO did not need to invoke a Cold Weather Watch, Warning, or Event, as defined within Appendix H of Market Rule 1—Operations during Cold Weather Conditions. Appendix H is triggered when severe winter weather occurs at the same time operable capacity is insufficient to supply projected demand. Since severe weather never materialized in winter 2009/2010 and the system had no major fuel-supply disturbances, operable capacity margins remained positive and Appendix H did not need to be invoked. Early communication between the ISO and market participants allowed time for preparing for approaching cold weather, and gas-fired unit availability was sufficient. Communication and coordination between the ISO and the gas-control divisions of the regional pipelines in preparation for cold weather was excellent. For most of the winter, very few oil-fired fossil units cleared in the Day-Ahead Energy Market, and the ISO needed to commit only a few units for reliability.

No major issues with regional fuel supplies of coal, oil, or natural gas occurred during winter 2009/2010. However, the Sable Offshore Energy Project (SOEP) experienced several unplanned outages at its natural gas production facilities in Atlantic Canada. During these temporary gas supply interruptions, the Canaport LNG facility was able to deliver additional natural gas supplies to the market. No prolonged fuel-supply curtailments to gas-fired units or major issues were associated with natural gas quality or interchangeability.

## Expanding Natural Gas Supply and Infrastructure

Before the 1990s, New England was served by only two interstate natural gas pipelines, Algonquin Gas Transmission (AGT) and the Tennessee Gas Pipeline (TGP). The Iroquois Gas Transmission System (IGTS) was commercialized in 1991/1992. The Portland Natural Gas Transmission System (PNGTS) and the Maritimes and Northeast (M&NE) Pipeline were both commercialized in 1999. These five interstate natural gas pipelines make up the majority of gas transportation capacity into and within the region. Several intrastate natural gas pipelines are located within New England, for example, the Vermont Gas System, Northern Utilities, and KeySpan Energy Delivery.

As a result of the forecast for the need for new, regional gas supplies, combined with the natural progression of market expansion, the natural gas industry has invested heavily in infrastructure enhancements in the northeastern United States and in eastern Canada. Some of these enhancements were driven by the need to deliver new LNG supplies to regional markets. More recently, work is being completed to access new gas supplies emanating from the Rocky Mountain basins and other new, unconventional natural gas supply sources, such as Marcellus Shale, which is geographically close to New England. In addition, development continues at the Deep Panuke project located in Atlantic Canada with a target commercial in-service date of sometime in 2011.

### LNG Supply Facilities

The reliability of natural gas supply to New England will be improved through the addition of new LNG terminals, natural gas pipelines, and regional gas storage facilities.

#### Distrigas Import Terminal

In 2009, Distrigas of Massachusetts LLC (DOMAC) supplied 22% of New England’s total annual gas consumption and up to 45% of the region’s natural gas requirements on winter peak days. The LNG import terminal located on the Mystic River in Everett, Massachusetts, owned and operated by DOMAC and part of GDF SUEZ Energy North America, Inc. began commercial operation in 1971. In 2009, Distrigas received 67 LNG cargoes, representing 38% of total U.S. LNG cargoes and 34% of total U.S. LNG volumes.

#### Northeast Gateway Deepwater Port

In May 2008, the Northeast Gateway Deepwater Port, located offshore Gloucester, Massachusetts, accepted its first commercial delivery of LNG. Excelerate Energy owns and operates Northeast Gateway, which is an LNG importer and provider of regasification services. The physical infrastructure of Northeast Gateway consists of a dual-submerged turret-loading buoy system with approximately 16 miles of lateral pipeline connecting into the HubLine Pipeline in Massachusetts Bay.

#### Canaport Import and Storage Facility

In November 2009, a new land-based LNG import and storage facility was commercialized in Saint John, New Brunswick. Canaport LNG has the capability to regasify and sustain approximately 1.0 billion cubic feet of gas per day (Bcf/d). The regasified LNG is delivered through the Brunswick Pipeline for delivery into the Canadian and U.S. gas markets via the M&NE Pipeline system. In 2009, the Canaport LNG facility received 13 LNG cargoes, had a maximum daily send out of 0.77 Bcf/d, and had an average daily send out of 0.19 Bcf/d. A third LNG storage tank was commercialized in May 2010, providing overall storage capability at approximately 10 Bcf.

#### Neptune Deepwater Port

Another LNG import terminal and provider of regasification services for the region is the new Neptune LNG deepwater port off the coast of Cape Ann. The facility, which is owned by Neptune LNG LLC, another subsidiary of GDF SUEZ Energy North America Inc, is ready to accept LNG deliveries. The first commissioning cargo arrived at the port in February 2010, and the second commissioning cargo arrived in August 2010.

### Marcellus Shale Gas Development

One major new development in regional gas supply is the potential for expanded natural gas production within the Marcellus Shale. Technical estimates project that this basin, proximate to New England, may hold from 250 to 500 trillion cubic feet (Tcf) of natural gas, although the actual recoverable supply will be driven in part by environmental constraints and economics. Land and water access, infrastructure development, and other environmental concerns may present further complications as more of the Marcellus Shale is developed. However, it remains a promising domestic source of natural gas for the foreseeable future.

### New Pipelines and Storage

The Northeast Gas Association (NGA) maintains a list of regional natural gas pipeline, LNG, and storage projects that have been or are scheduled to be commercialized. Some of the projects affecting New England are described below.

#### New Pipelines Projects

During 2009, several regional natural gas pipeline projects were completed. Others are scheduled for commercial operation in 2010. Some of these infrastructure additions that may have a direct or indirect impact on New England are as follows:

Iroquois Pipeline—2008/2009 Expansion Phase II and III; 2008/2009 (U.S. and Canadian multi-party ownership)

Maritimes & Northeast Pipeline—Phase IV Project; 2009 (Spectra Energy)

Algonquin Pipeline—J-2 Lateral Expansion; 2009 (Spectra Energy)

Tennessee Gas Pipeline—Concord Lateral Expansion; 2009 (El Paso)

Algonquin Pipeline—East-to-West Expansion Project; 2010 (Spectra Energy)

Some of these projects were designed to improve the deliverability of the new LNG supplies. Some projects provide access to new gas supplies, underground storage, and other (interconnected) pipelines, while others were designed to mitigate known constraints and maximize throughput into major market centers.

#### New Storage Projects

Natural gas storage is a critical part of the gas supply chain. The northeast U.S. has considerable underground storage, notably in Pennsylvania and New York. Some gas storage infrastructure projects are as follows:

Steckman Ridge Storage Project (12 Bcf), located in south-central Pennsylvania, was put into service in April 2009.

Wyckoff Gas Storage provides approximately 5.1 Bcf of working gas storage and is designed to inject and withdraw storage inventory throughout the year. On July 22, 2009, FERC announced approval of Wyckoff’s request to begin storage service from the Onondaga reef storage reservoir using the facilities approved for the Wyckoff Gas Storage Project (Phase I) in Steuben County, New York.

Thomas Corners Storage Project (7 Bcf), also located in Steuben County, New York, was put into commercial operation on April 1, 2010.

## Electric Power Sector Outlook

Resource diversity within New England is expanding. Renewable projects are under development across the region, in part as a result of state Renewable Portfolio Standards (RPSs) (see Section 8 for information on the states’ RPS targets). Approximately 200 MW of new wind energy projects have been commercialized, and over 2,650 MW are under development within the ISO New England area. In addition, the American Recovery and Reinvestment Act of 2009 (ARRA) has earmarked $8.5 billion (including loan guarantees) for renewable energy research and development. Another factor helping to address the need for fuel diversity is the addition of demand resources, which are being promoted by the states and are under development.

### Lower Natural Gas and Oil Prices

One historical issue has been the volatility of natural gas prices because they routinely set the price of regional wholesale electric power. Seasonal and weather variations, coupled with natural disasters, can create fuel-price volatility. In early to mid-2008, world oil prices increased dramatically, resulting in a proportional increase in natural gas prices. However, with the economic downturn, as consumer demand decreased and business activity slowed, inventories increased, and world oil and natural gas prices decreased substantially. As a result of this price volatility, system planners in both the gas and electric industries monitor and reassess their fuel forecast assumptions and sensitivities, while fully accounting for the expanding natural gas supply and infrastructure available to the New England region.

### Improved Supply Infrastructure, Including Renewables

Like the regional natural gas industry’s recent infrastructure development, the power generation sector is also being improved and expanded. As shown in Figure 7-3, most of the recent generating capacity additions either are renewables or gas-fired projects. Within the 8,809 MW of new resources that have requested interconnection studies, 3,115 MW are renewable projects and 4,367 MW are either single-fuel, gas-only projects or dual fuel (gas and oil) projects. Several factors have been instrumental in encouraging the development of renewable generation projects. These include the states’ Renewable Portfolio Standards and related programs (discussed in Section 8.5), which have increasing targets over the next 10 years for the amount of electrical energy provided by renewable resources. In addition, tax incentives and environmental regulations may increase the relative costs of electric energy production by fossil-fueled generation compared with renewable resources, potentially making renewable generation more economically viable in the future.

Figure 7-3: Recent generating capacity additions, 2000 to 2009.

Note: The “Other” category includes nuclear uprates, oil-fired generators, and various types of renewable resources. The 2008 value includes 14 MW of gas-fired generation.

The gas-fired projects in the ISO’s queue will be able to take advantage of the surplus natural gas supplies within the region. Improved fast-start and ramping characteristics of these new, gas-fired units will be required to balance the system changes that can result from the integration of variable-output resources, such as wind and solar projects. To achieve the goal of reliably dispatching this electrical generation, natural gas must be available when and where it is needed.

### Adequate Dual-Fuel Capacity

In recent years, the number of single-fuel, gas-only generators that have invested in dual-fuel capability has increased. These generators typically burn natural gas as their primary fuel but can switch to fuel oil if needed. Although for some generators, switching from using one fuel source to another is a complex process, having dual-fuel capability provides reliability benefits when primary fuel supplies are temporarily constrained.

Of the 41% of the New England generators that use natural gas as their primary fuel, about 43% (5,603 MW) are dual-fuel capable and use fuel oil as their secondary fuel source. In total, about 25.4% of New England’s overall generation (8,106 MW) consists of dual-fuel units that can burn a combination of natural gas and heavy or light oil as both a primary or secondary fuel source.

## Remaining Risks and Mitigation

Over the past few years, operational events have revealed reliability issues associated with the interrelationships between the natural gas and electricity markets in New England. The ISO and regional stakeholders have worked together to address and mitigate most of these risks; however, some issues remain.

### Resource Commitment Uncertainties

The ability of gas-fired resources to meet their electricity-side commitments depends on their ability to nominate appropriate levels of fuel in advance of the operating day. The market deadlines, and differences between them, already are known when comparing the natural gas and electricity industries. These timeline differences pose little problem during most days when electric power capacity margins and operational flexibility within the pipelines are sufficient. However, in very cold conditions or during abnormal events on the regional gas grid, pipelines usually have limited capacity to serve customers with nonfirm contracts. Natural gas scheduling and delivery requirements sometimes can restrict fuel deliveries to gas-fired generation, which then can limit energy production. These issues can add complexity to the ISO’s dispatch decisions required to ensure that energy production is sufficient for meeting electricity demands.

The ISO is modifying existing market rules to mitigate these risks. To improve real-time reoffers of electricity market supply, the ISO is planning to improve how suppliers can submit price and physical reoffers and dual-fuel supply offers. These changes will allow a resource to modify its commitment cost components (i.e., start-up and no load costs) of its supply offer, up to the time of commitment, and to modify the incremental energy cost component of those offers as frequently as hourly, with appropriate restrictions. These market rule changes currently are scheduled for implementation sometime in 2012.

### Unforeseen Events in Real-Time Operations

Unplanned events that have an impact on regional fuel supply chains, coupled with the general inflexibility of the regional generation fleet to deliver fast-start, off-line operating reserves, directly affect power system operations. These issues can decrease the quantity and quality of operating reserves used to provide power system reliability and maintain reliability if variable-output resources are lost or were not accurately forecast.

The ISO is modifying existing market rules to mitigate these risks. To improve the ability to manually adjust real-time reserve requirements when system operators are faced with an unusually large or unforeseen contingency exposure, the ISO is planning to modify the reserve monitor and reserve calculations for the Unit Dispatch System (UDS). Thus, when the real-time UDS is solving for reserve requirements, it will appropriately reflect the system operators’ decisions to commit supplemental or replacement reserves. These market rule changes currently are scheduled for implementation by 2011.

### Gas Quality and Interchangeability

Given the increased use of imported LNG to supplement North American domestic gas supplies, and because of the historical composition of domestic natural gas, new gas supplies may not be fully interchangeable with existing supplies, which could have an adverse impact on end-use customers. To address this issue, most of New England’s pipelines have revised their gas quality sections within their tariffs. In 2009, however, only a few gas-fired power generators within New England reported gas quality issues that temporarily disrupted power plant operations. In most cases, the problem was due to the sensitivity of new combustion technologies to variations in the heat (British thermal unit; Btu) content within the gas stream. Both the natural gas and electricity industries are exploring several options to further minimize the risk of variations in the heat content and composition of natural gas supplies.

### LNG Supply Risks

LNG supply risks now include factors associated with homeland security. During this past winter, concern was expressed over allowing Yemeni LNG cargoes into Boston Harbor. Subsequently, on February 23, 2010, with approval from the U.S. Coast Guard, Distrigas received its first LNG cargo from Yemen, under heightened security protocols.

In addition to security concerns, LNG supply risks stem from the potential market diversion of LNG shipments to other geographic regions as a result of the price variations created by international competition for LNG supply. Destination-flexible or noncontracted LNG cargoes are routinely diverted to more profitable markets around the globe. Firm contracts between gas suppliers and end-use customers help minimize these risks and ensure the continued delivery of fuel.

### Communication Barriers

The ability to operate the power system reliably depends, in part, on the ISO’s ability to recognize possible limitations on fuel deliveries to generating resources, while accounting for other potential contingencies. This risk calls for improved coordination and communication between regional fuel suppliers (oil, coal, and gas) and the electric power industry.

The ISO already has a good working relationship with the regional natural gas industry; however, more training and coordinated interindustry drills would improve existing communication protocols. On September 18, 2009, the ISO hosted a full-day training session at its headquarters for members of the Electric/Gas Operations Committee (EGOC). Before 2009/2010 winter operations, the ISO also met with representatives of both the regional oil and natural gas sectors to assess conditions and confirm communications procedures. Future plans call for further training and the identification of opportunities that would further improve the timely exchange of information between the electricity and natural gas sectors.

### Price Exposure

The ISO has developed and implemented remedial measures to successfully manage possible fuel-shortage events. The combined effects of a number of these following measures have diminished the operational risks associated with the high dependence on natural gas by New England’s electric generation sector:

Direct engagement and interaction with regional stakeholders

Improvements to market rules and procedures

New interindustry coordination and communications protocols

Prominent infrastructure additions within both sectors

Although most operational risks have been mitigated, economic risks still remain because, in New England, the wholesale price of natural gas is projected to have a direct impact on the wholesale price of electric power.

### Other Fuel-Supply Risks

Several other components of the regional fuel-supply chain, in addition to the natural gas industry, can have an impact on the electric power sector. Problems within regional oil markets, for both heavy and light oil; constraints on transporting and importing coal; problems within the nuclear fuel cycle; regional drought; or a combination of several of these problems can have an impact on New England’s electric power system operations and wholesale markets.

Table 7-2 shows New England’s 2010 summer generation capacity mix categorized by fuel type and in-service dates. As seen in the table, the majority of the oldest units on the system are hydroelectric units. Most of the 40- to 60-year old stations are either coal- or oil-fired, steam-based units. The majority of the 20- to 40-year old units are nuclear and pumped-storage stations. Natural-gas-fired generation is predominantly new (within the last 20 years), with the majority of those stations being constructed after electric utility deregulation in the late 1990s or early 2000s. This is illustrated in Figure 7-4, which compares the capacity and electric energy production for 2000 and 2009. While the capacity of oil units has been reduced from 34% in 2000 to 25% in 2009, their energy production decreased even further from 14.8% to 0.7%.

Table 7-2
New England’s 2010 Summer Generation Capacity Mix by Fuel Type
and In-Service Dates(a, b, c)

| Fuel Type | In-Service Date Before 1950 |  | In-Service Date 1951–1970 |  | In-Service Date 1971–1990 |  | In-Service Date 1991–2000 |  | In-Service Date 2001 and after |  | Total |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | # of Assets | MW | # of Assets | MW | # of Assets | MW | # of Assets | MW | # of Assets | MW | MW | % |
| Gas | 5 | 73 | 0 | 0 | 12 | 1,617 | 20 | 3,564 | 38 | 7,928 | 13,181 | 41.2 |
| Oil | 3 | 10 | 61 | 2,485 | 25 | 4,014 | 11 | 146 | 21 | 212 | 6,866 | 21.5 |
| Nuclear | 0 | 0 | 0 | 0 | 5 | 4,629 | 0 | 0 | 0 | 0 | 4,629 | 14.5 |
| Coal | 0 | 0 | 13 | 2,570 | 2 | 186 | 0 | 0 | 0 | 0 | 2,756 | 8.6 |
| Pumped storage | 1 | 29 | 0 | 0 | 6 | 1,649 | 0 | 0 | 0 | 0 | 1,679 | 5.2 |
| Hydro | 68 | 774 | 8 | 328 | 160 | 434 | 32 | 23 | 31 | 153 | 1,712 | 5.4 |
| Other renewables | 0 | 0 | 1 | 43 | 33 | 633 | 28 | 215 | 58 | 251 | 1,142 | 3.6 |
| Totals | 77 | 887 | 83 | 5,426 | 243 | 13,162 | 91 | 3,948 | 148 | 8,543 | 31,965 | 100.0 |
| Percentage of total MW |  | 2.8% |  | 17.0% |  | 41.2% |  | 12.3% |  | 26.7% |  |  |

- (a) 	Generator assets in this table may be power plants or individual units that make up power plants. Values do not include HQICC, demand resources, or external purchases and sales.

- (b) 	A total of 10,011 MW of new generation has been installed since the start of the markets in May 1999. This total is based on the claimed capability of these assets as of March 2, 2010, and projected capabilities of assets expected to be in service by summer 2010.

- (c) 	Totals may not equal sum because of rounding.

Figure 7-4: Shift in New England’s fuel mix, from 2000 to 2009.

Note: The “other” category primarily contains renewable resources.

Environmental initiatives that require reduced air and water emissions are placing increased economic pressure on aging coal- and oil-fired units to add environmental controls or to reduce run times (see Section 8). Given the age of these coal and oil units, these stations may likely retire and be replaced with efficient and relatively clean-burning natural-gas-fired units.

## Summary

While natural gas remains the dominant fuel within New England’s electric power generation sector, the region’s diversity and expected reliability of natural gas supply has improved. This is the result of the new Canaport LNG terminal that went into commercial operation in 2009 and the Neptune LNG facility that went operational in 2010. In addition, new pipeline expansion projects have been designed to improve the ability to deliver LNG and other sources of natural gas to the region.

Regional gas prices on the spot market, which reached about $15.00/million Btu (MMBtu) in mid-2008, have dropped by about 66% to approximately $5.00/MMBtu in summer 2010. Oil has shown a similar pattern but typically remains more costly than gas on the basis of thermal equivalency. To help mitigate the dependency on natural gas as a single fuel when gas prices are high or supplies are scarce, about 25% of the region’s generating plants have dual-fuel capability, the ability to switch between oil and gas as required.

Contingencies on the regional gas supply and transmission system could temporarily limit gas deliveries to generators anytime of the year. Effective communication between gas and electric industry operations helps mitigate these and other reliability concerns. Further flexibility of operation of gas-fired generating units would assist with the reliable integration of variable-output generation resources, such as wind- and solar-powered facilities.

Gas quality and interchangeability will remain a concern, yet minor to date, as more LNG is imported, which can result in different gas compositions that can affect the operation of some types of gas turbines. The natural gas and electric power industries are exploring options to minimize potential problems due to variations in gas quality.

Aging coal- and oil-fired generators are facing additional economic pressures from environmental initiatives. The possibility of these units being replaced or repowered with natural gas could increase the region’s dependency on natural-gas-fired generation. Other environmental initiatives are promoting the development of renewable resources and energy efficiency. The addition of these supply- and demand-side resources would reduce the region’s dependency on natural-gas-fired generation.

# Environmental Regulatory Update

“The RSP shall address needs of the PTF system determined by the ISO through Needs Assessments initiated and updated on an ongoing basis by the ISO to account for market performance and economic, environmental and other considerations as may be agreed upon from time to time.” (Attachment K, Overview)

“The ISO shall develop the RSP based on periodic comprehensive assessments (conducted not less than every third year) of the PTF systemwide needs to maintain the reliability of the New England Transmission System while accounting for market efficiency, economic, environmental and other considerations, as agreed upon from time to time.“ (Attachment K, § 3.1)

This section provides an update of environmental regulations and initiatives potentially affecting New England generators and the outlook for renewable resource development in the region. It builds on the information presented in RSP09, Section 7. Two new topics are included in this section: historical emissions of New England generation and an overview of the New England states’ energy-efficiency (EE) programs. Attachment K of the OATT requires the RSP process to account for, among other things, environmental considerations, which are discussed in this section.

## Update of Environmental Regulations

This section summarizes major environmental activities at the federal and regional levels over the last 12 months that may affect New England generators. The U.S. Environmental Protection Agency (EPA) has been very active during this period in reviewing and proposing new air quality standards and regulations. EPA’s actions, along with regional activities, cover the following topics:

Ozone attainment measures

  - Tighter National Ambient Air Quality Standards (NAAQS) for criteria pollutants that power plants emit or that are created as a byproduct of these emissions: sulfur dioxide (SO2), nitrogen dioxide (NO2), fine particulates (PM2.5), and ozone (O3)

  - Clean Air Interstate Rule (CAIR)

  - High Electric Demand Day (HEDD) voluntary measures to reduce ozone

Carbon dioxide (CO2) regulation

  - Regional Greenhouse Gas Initiative (RGGI)

  - Other regional and federal cap-and-trade programs

  - EPA’s CO2 regulation and future air regulation strategy

Power plant cooling water issues addressed by the Clean Water Act, Section 316b

Regional haze

National Emission Standards for Hazardous Air Pollutants (NESHAPs), including mercury

EPA’s proposed rule on coal combustion byproducts

The issues that likely can have the most significant impacts on New England’s power plant operations and costs over the next 10 years are discussed in this section. They include proposed ozone attainment measures, the RGGI cap-and-trade program, federal climate legislation and CO2 regulation, and cooling water issues.

### Ozone Attainment Measures

Proposed ozone attainment measures include the revised NAAQS, HEDD, and the CAIR replacement rule.

#### Revised Ozone Standard

The EPA has proposed revising the March 2008 ozone standard of 75 parts per billion (ppb) to a range of 60 to 70 ppb. As shown in Figure 8-1, more New England areas and the Northeast in general would experience greater degrees of nonattainment of the proposed ozone standard. The figure is based on eight-hour ozone concentrations taken at monitoring sites from 2007 to 2009, and most sites have values exceeding the proposed range for the revised standard (as indicated by the different-colored symbols in the figure, which reflect different ppb values at the monitoring sites). The proposed ozone revision could require further reductions in NOX emissions in the region and affect some of New England’s generators.

Figure 8-1: Average seasonal concentrations of ozone in the Northeast, 2007 to 2009 (ppb).

Source: Chris Salmi (NJ Department of Environmental Protection [DEP]), “Intro, AQ/Timeline Presentation,” Slide 2, Ozone Transport Commission (OTC) Stationary Area and Mobile Sources Meeting, Hartford (March 16, 2010); http://www.otcair.org/document.asp?fview=meeting#). Map created by Martha Webster, Maine DEP.

#### High Electric Demand Days

In addition to meeting the ozone standard, Connecticut is one of six states that signed an OTC commitment for NOX reductions of 11.7 tons during high electric demand days. The total HEDD NOX reduction commitment by the six states in the program is 135 tons/day. The HEDD Memorandum of Understanding (MOU) lists alternatives such as adding NOX controls, repowering or retiring units, reducing output, implementing energy-efficiency and demand-response measures, or capping emissions on HEDDs to reduce NOX and meet the HEDD commitment. Each state is developing its own strategy and regulations to implement its HEDD commitment; rules must be in place no later than 2012 according to the MOU.

#### CAIR Replacement Rule

The EPA established the Clean Air Interstate Rule in March 2005 to reduce precursors to ozone and particulates over 28 eastern states (including Connecticut and Massachusetts) and the District of Columbia. CAIR’s objective is to reduce sulfur dioxide and nitrogen oxides, both of which contribute to the formation of fine particulates. NOX emissions also contribute to the formation of ground-level ozone. CAIR was intended to cap NOX emissions at 1.5 million tons starting in 2009 and at 1.3 million tons in 2015. CAIR also capped SO2 levels at 2.5 million tons.

Connecticut and Massachusetts were the only two affected states in New England that would be required to reduce emissions in their states under the original CAIR NOX cap during the ozone season, which is May through September. These states had been relying on the provisions of CAIR to develop their own compliance rules for generators and had been proceeding with CAIR compliance plans. Generators in these states also had been taking steps toward compliance with these CAIR rules. Connecticut and Massachusetts were not subject to the original CAIR’s annual SO2 or annual NOX caps.

On July 11, 2008, the U.S. Court of Appeals for the District of Columbia Circuit vacated the entire Clean Air Interstate Rule. However, on December 29, 2008, the court reversed its July decision and reinstated CAIR indefinitely until the EPA amends the rule or parties appeal the court’s decision. On July 6, 2010, EPA proposed a CAIR replacement rule, labeled the Transport Rule. As proposed, this rule would only affect Connecticut and Massachusetts by requiring annual caps on SO2 and NOX emissions for each state and an ozone season cap starting in 2012 for Connecticut for compliance by larger electric generators.

The ISO will continue to monitor and evaluate developments relating to the proposed Transport Rule and any impacts this decision and related state rules could have on New England generators throughout the region.

### Greenhouse Gases

The Regional Greenhouse Gas Initiative is a 10-state CO2 cap-and-trade program that began in 2009 and affects electricity generators. In 2008, CO2 emissions from RGGI units totaled 153.5 million tons, almost 18% below the current RGGI cap (188.1 million short tons of CO2). Preliminary EPA data show the 2009 emissions from RGGI units to be even lower at 123.7 million tons (a 34% reduction from the RGGI cap). New England’s portion of the 2008 RGGI emissions was 44.3 million tons, almost 21% below its six-state cap allocation of 55.8 million tons. New England’s 2009 preliminary emissions were 39.3 million tons, almost 30% below the six-state cap allocation. The lower emissions could be the result of the lower energy consumption driven in part by the economic recession, lower natural gas prices, and the increase in energy production by natural gas units from 40.9% in 2008 to 42.4% in 2009. Adding some longer-term perspective, the 2018 RGGI cap of 169 million tons is 10% lower than the current RGGI cap and less than what proposed federal cap-and-trade bills in the U.S. Congress would require: a 17% reduction by 2020 from 2005 emissions.

The RGGI auction prices have dropped to about $2/allowance from over $3/allowance in the first auctions. Total revenues for the New England states from seven RGGI auctions were $177.3 million, of which about 93% or $165.2 million was allocated to these states’ energy-efficiency programs (see Section 8.4). A reevaluation of the RGGI program is planned for 2012.

Climate legislation is under development in Congress, with the Senate developing an alternate bill to the Waxman-Markey bill that passed in the House in June 2009. The timetable for when either of these bills could emerge as legislation is uncertain. Both bills are targeting a 17% reduction in greenhouse gas (GHG) emissions by 2020.

EPA had also established an annual GHG emissions reporting requirement for electric generating units with GHG emissions greater than 25,000 metric tons. This requirement started January 1 for the year 2010. EPA also has proposed a GHG permitting requirement for the generating units that would be part of the Clean Air Act Title V air permit renewal every five years. The permit would require the use of best available control technology (BACT) or energy-efficiency measures to reduce GHG, but EPA has not yet defined what these would be.

### Cooling Water

Cooling water intake requirements for power plants under the Clean Water Act, Section 316b potentially could require cooling tower retrofits on some power plants in the region. The revised requirements would result in fewer aquatic organisms being entrained or entrapped in the cooling systems. However, EPA must decide how it will apply a benefit/cost analysis in determining the best available technology (BAT) to make these reductions at power plants. Until this is determined, future requirements will be uncertain when water permits are renewed.

### Studies of Potential Generator Retirements

A report sponsored by the Clean Air Policy Initiative of the Clean Energy Group, a coalition of private electric generating companies, analyzed the impacts of EPA’s proposed air and water regulations on electric system reliability nationwide. The report concluded that, while the initiatives would result in generator retirements, the excess amount of capacity generally is sufficient to maintain system reliability.

NERC is conducting a study to evaluate the potential for retirements of fossil generators because of the estimated impacts of four environmental initiatives in particular—the Transport Rule; NESHAPs, including mercury; EPA’s proposed rule that would regulate coal combustion byproducts; and the Clean Water Act, Section 316b. The study is assessing the potential for individual unit retirements, comparing the total estimated costs for compliance with these potential requirements with the units’ estimated wholesale energy revenues in their region. The study also is assessing the potential impact of the retirements (i.e., the initiatives) on system reliability and potential mitigation strategies for units that appear to be uneconomic and possible candidates for retirement. This report is scheduled to be published by the end of 2010.

### FCM Classification for Generation Retrofits Resulting from Environmental Regulations

The FCM rules allow a resource to be treated as a “new” resource when its investment for complying with environmental regulations or permits is equal to or greater than $100/kW of its summer qualified capacity. This is applicable when the investment was or is made between January 1, 2007, and the conclusion of the first capacity commitment period associated with the resource’s capacity supply obligation. After the investment, the owner of the resource may elect the whole resource for participation in the Forward Capacity Auction as a new generating capacity resource. The $100/kW threshold (in base year 2008 dollars) will be adjusted annually in accordance with the most recent Handy-Whitman Index of Public Utility Construction Costs.

## New England Power Plant Emissions

Since 1993, the ISO has produced an annual Marginal Emission Analysis (MEA) Report. In response to the suggestion of several stakeholders, the ISO expanded the 2008 MEA Report and renamed it the New England 2008 Electric Generation Emissions Report. In addition to including the results of the 2008 marginal emissions analysis, the revised report summarizes a peak-day NOX emissions analysis the ISO performed at the request of state environmental regulators. The results of the emissions analyses are summarized below.

The total generation system emissions are shown in Table 8-1 for the New England generators administered by the ISO for 2001 to 2008. The table shows that total NOX, SO2, and CO2 emissions in 2008 were 32.6 ktons, 94.2 ktons, and 55,427 ktons, respectively.

Table 8-1
 Total New England Generator Emissions (1,000 tons)

| Year | NOX | SO2 | CO2 |
| --- | --- | --- | --- |
| 2001 | 59.73 | 200.01 | 52,991 |
| 2002 | 56.40 | 161.10 | 54,497 |
| 2003 | 54.23 | 159.41 | 56,278 |
| 2004 | 50.64 | 149.75 | 56,723 |
| 2005 | 58.01 | 150.00 | 60,580 |
| 2006 | 42.86 | 101.78 | 51,649 |
| 2007 | 35.01 | 108.80 | 59,169 |
| 2008 | 32.57 | 94.18 | 55,427 |

Table 8-2 shows the annual New England generation emission rates in lbs/MWh. Compared with 1999, the 2008 SO2 emission rate has declined by 67%, the NOX rate by 62%, and the CO2 rate by 12%. This is the result of using cleaner fuels, particularly natural gas, and adding emissions controls to generating plants over these 10 years.

Table 8-2
New England Generator Average Emissions Rates, 1999 to 2008 (lbs/MWh)

| Year | Total Generation (GWh) | NOX | SO2 | CO2 |
| --- | --- | --- | --- | --- |
| 1999 | 104,409 | 1.36 | 4.52 | 1,009 |
| 2000 | 110,199 | 1.12 | 3.88 | 913 |
| 2001 | 114,626 | 1.05 | 3.51 | 930 |
| 2002 | 120,539 | 0.94 | 2.69 | 909 |
| 2003 | 127,195 | 0.93 | 2.75 | 970 |
| 2004 | 129,459 | 0.78 | 2.31 | 876 |
| 2005 | 131,874 | 0.88 | 2.27 | 919 |
| 2006 | 128,046 | 0.67 | 1.59 | 808 |
| 2007 | 130,723 | 0.54 | 1.66 | 905 |
| 2008 | 124,749 | 0.52 | 1.51 | 890 |

Table 8-3 shows the annual historical marginal emissions for the three types of emissions since 1993. In this analysis, annual marginal rates are calculated by the total emissions of intermediate and peaking generation in New England divided by the annual energy in megawatt-hours for the same generation. In 2008, the New England system SO2 and NOX marginal rates each had declined by over 95%, and the CO2 marginal rate declined over 40% from 1993 marginal rates.

Table 8-3
New England Generation Annual Marginal Emission Rates (lbs/MWh)

| Year | SO2 | NOX | CO2 |
| --- | --- | --- | --- |
| 1993 | 12.60 | 4.40 | 1,643 |
| 1994 | 9.80 | 4.20 | 1,573 |
| 1995 | 7.00 | 3.20 | 1,584 |
| 1996 | 9.60 | 2.60 | 1,653 |
| 1997 | 9.40 | 2.60 | 1,484 |
| 1998 | 6.20 | 2.10 | 1,520 |
| 1999 | 7.20 | 2.00 | 1,578 |
| 2000 | 6.20 | 1.90 | 1,488 |
| 2001 | 4.90 | 1.70 | 1,394 |
| 2002 | 3.30 | 1.10 | 1,338 |
| 2003 | 2.00 | 0.70 | 1,179 |
| 2004 | 2.03 | 0.54 | 1,102 |
| 2005 | 1.75 | 0.54 | 1,107 |
| 2006 | 0.53 | 0.29 | 993 |
| 2007 | 0.57 | 0.28 | 1,004 |
| 2008 | 0.33 | 0.21 | 964 |

Table 8-4 shows that in 2008, New England generators had lower CO2 and NOX emission rates than PJM.

Table 8-4
Comparison of Emission Rates of Three RTO/ISOs (lbs/MWh)

|  | Annual Emission Rates |  |  | On-Peak Marginal Emission Rates(a) |
| --- | --- | --- | --- | --- |
|  | CO2 | SO2 | NOX | CO2 |
| ISO-NE (2008)(b) | 890 | 1.51 | 0.52 | 952 |
| NYISO (2009)(c) | 552 | 0.68 | 0.52 | N/A |
| PJM (2009)(d) | 1,137 | 5.78 | 1.68 | 1,823 |

(a) 	The calculation methods for the ISO and PJM were different for these on-peak marginal CO2 costs. The ISO method was based on all the oil and gas generation marginal units for the on-peak period. PJM’s method was based on the marginal unit or units that set the five-minute LMP over PJM’s on-peak period.

(b) 	2008 New England Electric Generator Air Emissions Report (August 18, 2010); http://www.iso-ne.com/genrtion_resrcs/reports/emission/index.html.

(c) 	P. Carney (NYISO) e-mail to M. Henderson (ISO) (April 28 2010).

(d) 	C, Liebold (PJM) e-mail to the Joint Independent System Operator/Regional Transmission Organization (ISO/RTO) Planning Committee (JIPC) (April 28, 2010). PJM, “PJM Reports New Carbon Dioxide Emissions Data,” news release (March 25, 2010); http://www.pjm.com/~/media/about-pjm/newsroom/2010-releases/20100325-pjm-reports-new-carbon-dioxide-emissions-data.ashx.

## Peak-Day NOx Analysis

At the request of stakeholders, the ISO has been conducting a NOX emissions analysis of the five-highest peak-load days for 2005 to 2008. While the ISO is in the process of refining the results for the five-highest peak-load days for 2009, some interim results are reported here.

Using mostly generator emissions from EPA market data and maps, with supplemental ISO calculations for smaller units, the ISO developed hourly NOX profiles for the five-highest peak-load days for 2005 to 2008, as shown in Figure 8-2. The figure shows that over the 20 peak-load days, the generator system NOX emissions during peak hours varied from about 6 to 13 tons/hour total. Cumulative 24-hour data show that the total daily NOX emissions varied from 122 to 225 tons/day over the 20 days.

Figure 8-2: New England system generation hourly NOX emissions on the five highest peak-load days, 2005 to 2008.

Sources: EPA and ISO New England.

The hourly generation bid blocks were also analyzed on these 20 peak days for the last 500 MW increment of fossil units dispatched on the system. Figure 8-3 shows the hourly NOX contributions by fuel type on the all-time New England peak-load day of August 2, 2006, for the last 500 MW of generation dispatched each hour. At the peak hours, the NOX emission rate for the last 500 MW of generation was 2.5 tons/hour (10 lbs/MWh). As seen in the figure, most of the additional emissions were from oil-fueled steam plants and combustion turbines. The analysis will be described in more detail in a peak-load day NOX report scheduled for completion in the fourth quarter 2010.

Figure 8-3: Hourly NOX emissions for the last-dispatched 500 MW of thermal generation on the peak-load day, August 2, 2006.

## Energy Efficiency in New England

Energy efficiency continues to be a significant factor in New England. New England states have been recognized nationally for their EE programs, which range from consumer incentives, such as rebates for purchasing efficient equipment, to energy audits.  Some states also have long-term energy-efficiency quantitative or qualitative goals. Additionally in New England, some EE resources choose to participate in the FCM. This section summarizes the status of EE in New England.

### Energy Efficiency Resources in the FCM

The EE resources that participate in the FCM are a specific subset of demand resources (see Section 4.2.1.1). Table 8-5 shows that energy-efficiency resources are a growing part of the FCM. Because the FCM considers passive resources, such as EE, to always be “in service,” they are assumed to be 100% available.

Table 8-5
Energy-Efficiency Resources Clearing the Primary FCM Auctions

| Load Zone State | Cleared MW Energy Efficiency(a) |  |  |
| --- | --- | --- | --- |
|  | FCA #1(b) | FCA #2(c) | FCA #3(d) |
| Connecticut | 183 | 287 | 365 |
| Massachusetts | 247 | 318 | 439 |
| Maine | 23 | 23 | 60 |
| New Hampshire | 36 | 48 | 63 |
| Rhode Island | 38 | 51 | 70 |
| Vermont | 46 | 57 | 75 |
| Grand total(e) | 572 | 784 | 1,073 |

(a) Source: 2010 CELT Report, Section 1.1; http://www.iso-ne.com/trans/celt/report/index.html. The values do not reflect reserve-margin mark ups.

(b) 	For the 2010/2011 capacity commitment period, the capacity supply obligations for the passive demand resources are current as of the posted results for the period of the third ARA during which bilateral trading was allowed.

(c) The PDR CSO values are current as of the posted results for the FCA #2 (2011/2012) proration, which provides credits for reducing system losses.

(d) The PDR CSO values are current as of the posted results for FCA #3 (2012/2013).

(e) Values may not add because of rounding.

### Overview of States’ Energy-Efficiency Programs

Each state has its own structure for planning and implementing EE programs, although all the programs generally cover the residential, commercial, and industrial sectors, and most states have EE programs to assist low-income residents. The state Public Utilities Commissions (PUCs) generally are responsible for approving EE program scope, costs, and implementation. Often, utilities manage the state-sponsored EE programs, although Vermont and Maine have separate entities that provide conservation services: “Efficiency Vermont” (EV) and “Efficiency Maine.” These are umbrella EE programs that deliver the EE services through contractors and not through the utilities. Connecticut and Massachusetts each have a separate board or council that oversees program planning and implementation and reports to the state PUC.

While planned EE budgets generally are increasing and are augmented by various sources, such as RGGI funds, federal stimulus funding, and system benefits charges (SBCs), fiscal conditions may shift funds out of EE programs and into the general state budgets, which would delay reaching higher levels of EE. On the contrary, states may exceed their anticipated EE goals.

#### Connecticut

Connecticut’s two public electric utilities and municipal utilities provide a portfolio of EE programs to their customers according to an annual plan approved by the state’s Energy Conservation Management Board (ECMB). The ECMB also administers the Connecticut Energy Efficiency Fund (CEEF), which receives its revenues from the system benefits charge. The ECMB members are appointed by the Connecticut Department of Public Utility Control (DPUC). The utilities administer the EE programs and implement them with their own resources and through contractors. Legislation in 2007 decoupled utility revenues from the volume of sales to support EE performance goals and required utilities to pursue all cost-effective EE resources as a first priority. In 2009, the state estimated that it saved approximately 237,000 MWh through its EE programs. Table 8-6 shows the sources of spending for EE programs in Connecticut in 2009.

Table 8-6
Connecticut’s Sources of Funding for Energy-Efficiency Programs, 2009

| Funding Source | Amount (millions) |
| --- | --- |
| System benefits charge | $91 |
| FCM revenues | $10 |
| RGGI revenues | $17 |
| CT’s RPS Class III Renewable Energy Certificates (RECs)(a) | $14 |
| Total | $132 |

(a) 	A Renewable Energy Certificate represents the environmental attributes of 1 MWh of electricity from a certified renewable generation source for a specific state’s RPS. Providers of renewable energy are credited with RECs, which usually are sold or traded separately from the electric energy commodity.

#### Massachusetts

The Green Communities Act (GCA) passed in 2008 established the Energy Efficiency Advisory Council (EEAC). The Massachusetts Department of Energy Resources (DOER) sets EE policy and promotes EE programs and is represented on the EEAC. Every three years, the EEAC must coordinate the development of a three-year plan by the public utilities, which must be submitted to the Department of Public Utilities (DPU) for approval. The most recent EE plans were submitted by National Grid, NSTAR, WMECO, Unitil, and the Cape Light Compact for 2010 through 2012, which the DPU approved in January 2010.

The EE goals of the utilities and the EEAC essentially are the same. The GCA requires the utilities to pursue all cost-effective EE measures with minimum administration costs. The utilities manage and implement their EE programs, and the state administers low-income EE programs. Table 8-7 shows approved spending from 2010 to 2012 on EE programs. Massachusetts estimates that over these three years, the total energy savings will equal approximately 2,649,000 MWh.

Table 8-7
Massachusetts’s Approved Spending for Energy-Efficiency Programs, 2010 to 2012

| Funding Source | Amount |
| --- | --- |
| System benefits charge | $364 million |
| FCM revenues | $34 million |
| RGGI revenues | $145 million |
| Outside(a) | $180 million |
| Energy-Efficiency Reconciliation Factor (EERF)(b) | $620 million |
| Total | $ 1.3 billion |

- “Outside” revenue is only an estimate for 2011 to 2012. Outside funding could include traditional lending sources, such as banks, or nontraditional sources, such as retailers and other private entities, with the program administrators bringing customers together with lenders to effect a loan for an energy-efficiency project. Outside capital might also be raised through the sale of tax-exempt bonds or other government initiatives and grants.

- The EERF is an EE surcharge by the utilities on the bills of all customer classes.

Massachusetts seeks a 25% cut in electricity capacity needs and energy use by 2020 using energy efficiency, demand response, load management, and distributed generation.

#### Rhode Island

In Rhode Island, National Grid’s subsidiary, Narragansett Electric, provides about 99% of the efficiency programs in the state, and the public utility, Paschoag Utility District, operates its own EE programs. The RI PUC reviews and authorizes EE program funding annually. The Rhode Island Comprehensive Energy Conservation, Efficiency and Affordability Act of 2006 increased the acquisition requirements for utility EE programs and required the acquisition of all cost-effective EE programs. The 2009 planned EE program estimated an annual energy savings of 79,300 MWh and an annual peak reduction of 12.5 MW. Table 8-8 shows Rhode Island’s approved spending for EE program for 2009.

Table 8-8
Rhode Island’s Approved Spending for Energy-Efficiency Programs, 2009

| Funding Source | Amount (millions) |
| --- | --- |
| System benefits charge | $21.8 |
| FCM revenues | $1.0 |
| Total | $22.8 |

#### Vermont

Vermont has a state-sponsored efficiency resource acquisition program called Efficiency Vermont, which administers the state’s EE programs. Since 2000, all ratepayer-funded acquisition of energy efficiency has been implemented through a statewide energy-efficiency utility. The Vermont regulators determine the funding level, and in 2008, Vermont had the highest per capita funding in the United States for energy-efficiency measures at $55.3. (Connecticut had the second-highest per capita funding at $30.5).

As the competitively solicited administrator of the Efficiency Vermont Program, and using staff, subcontractors, and partners, Burlington Electric provides EE services and products to all 340,000 customers throughout the state. A contract similar to a power supply contract is used for providing services of energy savings, mainly through technical assistance and financial incentives. Targeted areas are also selected where deeper savings are sought to help defer capital transmission and distribution investments otherwise needed for maintaining reliability. A central database is maintained for all customers in the state containing data on all EE measures installed, their costs and savings, and other information. For 2006 to 2008, EV exceeded its goal of 261,000 MWh, reaching 311,000 MWh. EV’s budget for 2009 to 2011 is $100 million, and its performance goals are 360,000 MWh annual savings, with a summer-peak reduction of 51 MW. In a targeted area, the goal is to reduce the summer peak by 8 MW. Table 8-9 shows Vermont’s EE funding sources for 2009.

Table 8-9
Vermont’s Funding Sources for Energy-Efficiency Programs, 2009

| Funding Source | Amount |
| --- | --- |
| System benefits charge | $22.6 million |
| FCM revenues | $1.4 million |
| RGGI revenues | $2.0 million |
| Total | $26.0 million |

#### New Hampshire

In 2002, New Hampshire launched “CORE” statewide EE programs common for the four state utilities: PSNH, Unitil, NH Electric Coop, and Granite State (NGrid). The utilities jointly present a state EE program to the NH PUC. A study of the potential opportunities for EE in NH estimated that an 8.5% reduction in peak load using a 2008 baseline could potentially be attained by 2018. Table 8-10 shows the proposed funding levels and sources for EE programs for 2010.

Table 8-10
New Hampshire’s Proposed Funding Levels for
the CORE Energy-Efficiency Programs, 2010

| Proposed Funding Sources | Amount |
| --- | --- |
| System benefits charge | $18.8 million |
| FCM revenues | $1.5 million |
| RGGI revenues | $7.5 million |
| Total | $27.8 million |

#### Maine

The Maine PUC initiated Efficiency Maine in 2003 as an umbrella for seven separate EE programs administered by the PUC that cover all electricity end uses in the state. Its programs covered residential products, performance and appliances, business products, new commercial construction, education, and solar and wind equipment incentives. In 2008, the expected peak reduction was 25 MW in the summer and 43 MW in the winter.

Efficiency Maine administered EE programs until July 1, 2010. After that date, the existing programs run by Efficiency Maine and the Energy and Carbon Savings Trust were grouped together and put under the control of the Efficiency Maine Trust (EMT). The trust will develop a three-year plan providing program design, planning, and implementation strategies for all energy-efficiency and alternative energy resources, for all fuel types, across all customer classes. Table 8-11 shows the proposed funding levels and sources for EE programs for 2011 to 2013.

Table 8-11
Maine’s Proposed Funding Levels and Sources
for Energy-Efficiency Programs, 2011 to 2013

| Proposed Funding Sources | Amount (millions) |
| --- | --- |
| System benefits charge | $60 |
| FCM revenues | $6 |
| RGGI revenues | $25 |
| American Recovery and Reinvestment Act | $62 |
| DOE grants | $1 |
| Solar/wind rebates | $2 |
| Total | $156 |

Maine’s legislative efficiency goals include the following:

Weatherize 100% of Maine residences and 50% of Maine businesses by 2030.

Achieve 30% electric energy savings, 30% natural gas savings, and 20% heating fuels savings by 2020.

Capture all cost-effective energy-efficiency resources available for electric and natural gas ratepayers.

Reduce greenhouse gas emissions from heating and cooling loads in Maine to at least 10% below 1990 levels by 2020, and ultimately 75 to 85% below 2003 levels.

### State Energy-Efficiency Reductions Summary in 2020

Table 8-12 illustrates various projected reductions in electric energy use by state based on RSP10’s 2020 forecast of annual electric energy use.

Table 8-12
Projected Reductions in Electric Energy Use
Based on the RSP Forecast of 2020 State Loads (GWh)

| State | Percentage Reduction of Load Forecast |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | 5% | 10% | 15% | 20% | 25% | 30% |
| CT | 1,735 | 3,471 | 5,206 | 6,941 | 8,677 | 10,412 |
| MA | 3,361 | 6,721 | 10,082 | 13,442 | 16,803 | 20,164 |
| ME | 655 | 1,310 | 1,964 | 2,619 | 3,274 | 3,929 |
| NH | 655 | 1,311 | 1,966 | 2,621 | 3,277 | 3,932 |
| RI | 446 | 892 | 1,337 | 1,783 | 2,229 | 2,675 |
| VT | 342 | 683 | 1,025 | 1,366 | 1,708 | 2,049 |
| Total | 7,193 | 14,387 | 21,580 | 28,774 | 35,967 | 43,160 |

Table 8-13 provides some basic information about the state programs and their current or recent EE plans.

Table 8-13
Key Facts on the New England States’ Energy-Efficiency Programs and Goals

|  | CT(a, b) | MA(c) | RI(d) | VT(e) | NH(f) | ME(g) |
| --- | --- | --- | --- | --- | --- | --- |
| Program name |  |  |  | Efficiency Vermont (EV) | CORE | Efficiency Maine Trust |
| Program plan (years) | 1 | 3 | 3 for planning/ 1 for procurement | 3-year contract for EE services | 1 | 3 |
| Electric utility participants | 2 + municipal utilities | 4 + 1 municipal aggregator | 1 | Statewide | 4 | Statewide |
| Long-term EE goal |  | 25% reduction by 2020 |  |  |  | 30% electric energy savings by 2020 |
| Annual MWh saved | 237,000 (2009) | 2,625,083 (2010–2012) | 79,331 (NGrid estimate 2009) | 360,000 (avg. 2009–2011) | 78,537 (2007) | 107,517 (2008) |
| Peak MW reduction (sum) | 37 (2009, excludes FCM demand resources) |  | 12.5 (NGrid planned, 2009) | 50 |  | 25 |
| Annual costs ($ million) | 73.4 (2009) |  | 32.7 (proposed, 2009) |  | 30.3 (2009) | 31.8 |
| Funding period | 2009 | 2010–2012 | 2009 | 2009 | 2010 | Proposed 2011–2013 |
| SBC rate (mils/kWh) | 3 | 2.5 | 2 | Varies | 1.8 | 1.5 |
| Revenue sources ($ millions) |  |  |  |  |  |  |
| SBC | 91 | 364 | 21.8 | 22.6 | 18.8 | 60 |
| RGGI | 17 | 145 |  | 2 | 7.5 | 25 |
| FCM | 10 | 34 | 1 | 1.4 | 1.5 | 6 |
| Other | 14 | 800 |  |  |  | 65 |
| Total revenue | 132 | 1,300 | 22.8 | 26 | 27.8 | 156 |
| Costs (¢/kWh) |  | 4.6 (lifetime) | 3.6 | 3.7 | 5.5 | 3.1 |
| Benefit/cost | 4 |  | 3.5 | 2.8 |  | 3.8 |
| Accountability | ECMB/PUC | DOER/ EEAC/ DPU | PUC | DPS annual audit; independent financial audit; third-party audit | PUC | PUC |

(a) 	Energy Conservation Management Board and CT PUC, An Investment in Connecticut Energy Efficiency, Report of the Energy Conservation Management Board: Year 2009 Programs and Operations (March 1, 2010); http://www.ctsavesenergy.org/files/Final%202009%20Legislative%20Report%202.19.10.pdf.

(b)	Connecticut presentation at the ISO’s Regional Energy-Efficiency Initiative (REEI) (March 5, 2009); http://www.iso-ne.com/committees/comm_wkgrps/othr/reei/mtrls/index.html.

(c) 	Massachusetts Department of Public Utilities Order 09-116 through 09-120 (January 28, 2010); http://www.env.state.ma.us/dpu/docs/electric/09-116/12810dpuord.pdf. Also see the 2010–2012 Massachusetts Joint Statewide Three-Year Electric Energy Efficiency Plan (October 28, 2010); http://www.ma-eeac.org/docs/DPU-filing/ElectricPlanFinalOct09.pdf.

(d) 	Nicholas S. Ucci (Rhode Island Public Utilities Commission), in letter to Eric Wilkinson (ISO New England), March 3, 2009, with attachment: 2009 Energy Efficiency Program Plan Summary.

(e) 	Efficiency Vermont presentation at the ISO’s REEI. Also, ACEEE’s Vermont Utility Sector Policies (2010); http://www.aceee.org/energy/state/vermont/vt_utility.htm.

(f) 	New Hampshire presentation at the ISO’s REEI.

(g) 	Efficiency Maine, 2008 Annual Report (December 5, 2008); http://www.efficiencymaine.com/pdf/EM_AnnualReport2009_FINAL.pdf. Also see the “Efficiency Maine Trust” Web site; http://www.efficiencymainetrust.org/triennial.html.

EE resources that participate in the FCM are treated like traditional supply resources when the ISO calculates the ICR (see Section 4.1). However, ISO’s load forecasting methodology does not incorporate projected energy savings from EE resources that do not participate in the FCM. The ISO’s energy forecast includes new federal appliance standards that will take effect in 2013 and the effect of historical energy-efficiency programs as they have lowered energy consumption over time.

New England’s state-sponsored EE programs will likely have an overall long-term impact on energy usage in the region. Because of the diversity in size, scope, and focus of the state-sponsored EE programs, calculating the cumulative impact of these programs is challenging. Other challenges include double-accounting concerns, monitoring and verification, “fatigue” by those repeatedly reducing energy use and choosing not to continue to reduce use, and the diversion of EE funding. The ISO will continue to work with stakeholders to gain a better understanding of these programs and their impact on the power system.

## Renewable Portfolio Standards, Projected Requirements, and Potential Supply from the ISO Queue

Five New England states have Renewable Portfolio Standards (RPSs), and Vermont has a goal for increasing energy usage from renewable resources. These Renewable Portfolio Standards represent state policy targets to be achieved by retail competitive suppliers and have been summarized in previous RSP reports. The retail electricity suppliers can meet the targets in a variety of ways, as discussed in this section.

Table 8-14 summarizes the technologies designated in Renewable Portfolio Standards in New England. Table 8-15 shows the annual percentages of electric energy consumption by affected LSEs for meeting the states’ RPS classes through 2020. This section highlights the RPS changes that occurred over the past year.

Table 8-14
Summary of Technologies Designated in Renewable Portfolio Standards in New England

| Technology | CT Classes |  |  | MA Classes(a) |  |  | ME Classes |  | RI | NH Classes |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | I | II | III | I | IIa | IIb | I | II |  | I | II | III | IV |
| Solar thermal |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Photovoltaic |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Ocean thermal |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Wave |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Tidal |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Marine or hydrokinetic |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Hydro | <5 MW | <5 MW |  | <25 MW | <5 MW |  | (b) |  | <30 MW | incremental |  |  | <5 MW |
| Wind |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Biomass, biofuels | Sustainable, advanced conversion low NOX emissions(c) |  |  | Low-emission, advanced technology(c) |  |  |  | (d) | Includes cofiring with fossil fuels | Low NOX, and PM emissions |  | <25 MW, Low NOX, and PM emissions |  |
| Landfill gas |  |  |  |  |  |  |  |  |  | (e) |  | (e) |  |
| Anaerobic digester |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Fuel cells(f) |  |  |  | w/ renewable fuels |  |  |  |  | w/ renewable resources |  |  |  |  |
| Geothermal |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Municipal solid waste |  |  |  |  |  |  |  | w/ recycling |  |  |  |  |  |
| Cogeneration, combined heat and power |  |  | Customer sites, minimum 50% fuel efficiency |  |  |  |  | (d) |  |  |  |  |  |
| Energy efficiency |  |  |  |  |  |  |  |  |  |  |  |  |  |

(a)	The Massachusetts Green Communities Act divides the state’s RPS into Class I and Class II resources, each of which allows primarily the same renewable technologies. Resources that began operating after December 31, 1997, are Class 1 renewables, and those that were in operation before that date are Class II renewables.

(b)	These resources can be pumped hydro units, and they must meet all federal and state fish-passage requirements.

(c)	These terms are explained in the state’s RPS legislation and regulations.

(d)	These can be high-efficiency units built through December 31, 1997.

(e)  This category also includes biologically derived methane gas from sources such as biodiesel, yard waste, food waste, animal waste, sewage sludge, and septage.

(f)	Fuel cells are a relatively new “renewable” energy technology. These units emit negligible amounts of SO2, NOX, and particulates such that Connecticut does not require fuel cell installations to obtain air permits. For Massachusetts, an RPS fuel cell using an "eligible biomass fuel" includes landfill or anaerobic digester methane gas, hydrogen derived from such fuels, or hydrogen derived using the electrical output of a qualified renewable generation unit. As shown in the table, RPS fuel cells in Rhode Island must use eligible renewable resources.

Table 8-15
Annual Percentages of Electric Energy Use by Affected Load-Serving Entities
for Meeting the States’ RPS Classes, 2010 to 2020

| Year | CT Classes(a) |  |  | MA Classes(b) |  |  | ME Classes(c) |  |  | RI Classes(d) |  | NH RPS Classes(e) |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | I | II | III | I | IIa | IIb | I |  | II | Existing | New | I | Ii | III |  | IV |
| 2010 | 7.0 | 3.0 | 4.0 | 5.0 | 3.6 | 3.5 | 3.0 | 30 |  | 2.0 | 2.5 | 1.0 | 0.04 | 5.5 | 1.0 |  |
| 2011 | 8.0 |  |  | 6.0 |  |  | 4.0 |  |  |  | 3.5 | 2.0 | 0.08 | 6.5 |  |  |
| 2012 | 9.0 |  |  | 7.0 |  |  | 5.0 |  |  |  | 4.5 | 3.0 | 0.15 | 6.5 |  |  |
| 2013 | 10.0 |  |  | 8.0 |  |  | 6.0 |  |  |  | 5.5 | 4.0 | 0.2 | 6.5 |  |  |
| 2014 | 11.0 |  |  | 9.0 |  |  | 7.0 |  |  |  | 6.5 | 5.0 | 0.3 | 6.5 |  |  |
| 2015 | 12.5 |  |  | 10.0 |  |  | 8.0 |  |  |  | 8.0 | 6.0 | 0.3 | 6.5 |  |  |
| 2016 | 14.0 |  |  | 11.0 |  |  | 9.0 |  |  |  | 9.5 | 7.0 | 0.3 | 6.5 |  |  |
| 2017 | 15.5 |  |  | 12.0 |  |  | 10.0 |  |  |  | 11.0 | 8.0 | 0.3 | 6.5 |  |  |
| 2018 | 17.0 |  |  | 13.0 |  |  | 10.0 |  |  |  | 12.5 | 9.0 | 0.3 | 6.5 |  |  |
| 2019 | 19.5 |  |  | 14.0 |  |  | 10.0 |  |  |  | 14.0 | 10.0 | 0.3 | 6.5 |  |  |
| 2020 | 20.0 |  |  | 15.0 |  |  | 10.0 |  |  |  | 14.0 | 11.0 | 0.3 | 6.5 |  |  |
| Use Generator Information System Renewable Energy Certificates? | Yes |  |  | Yes |  |  | Yes |  |  | Yes |  | Yes |  |  |  |  |
| Purchase of RECs from outside ISO New England allowed? | Yes, from adjacent areas, with confirmation of delivery of energy from the renewable energy source and reciprocal RPSs for NY, NJ, PA, MD, and DE. |  |  | Yes, from adjacent areas, with confirmation of delivery of energy |  |  | Yes, from adjacent areas |  |  | Yes, from adjacent areas |  | Yes, from adjacent areas, with confirmation of delivery of energy from the renewable energy source |  |  |  |  |

(a)	All Connecticut Class I technologies except LFG and fuel cells can be used to meet Class II requirements. For Class III, combined heat and power (CHP) facilities can be used to offset generation on the grid with the more efficient on-site use of fuel.

(b)	Class I has a minimum of 2% behind-the-meter resources. Class IIa is a minimum percentage for existing pre-1997 vintage LFG, hydro less than 5 MW, and biomass plants. Class IIb is a minimum percentage for pre-1997 vintage waste-to-energy plants.

(c)	The 30% requirement refers to electric energy delivered to affected LSEs.

(d)	Existing resources can make up no more than 2.0% of the RPS percentage.

(e)	Class I increases an additional 1% per year from 2015 through 2025. Classes II to IV remain at the same percentages from 2015 through 2025.

Massachusetts has made two major changes to its RPS since RSP09. One is that it has added a solar “carve-out” as part of the Class I RPS requirements. For 2010, the solar carve-out is set at 30 MW (DC current).  Each year, the requirement for the carve-out is calculated based on the previous year’s minimum requirement, increased by 30%. Once a maximum of 400 MW (DC) of solar is installed in the state, the carve-out requirement ends. The state also set a solar carve-out Alternative Compliance Payment (ACP) of $600 (see Section 8.5.2.3). As a minimum support for solar REC (S-RECs), the DOER has proposed an auction process to guarantee developers a minimum of $300/MWh and a long-term market for S-RECs. The second Massachusetts change is that new biomass has been suspended as a renewable resource option to meet the RPS. The development of new regulations is pending and will be based on a DOER study of what types of biomass are considered a sustainable resource.

Vermont’s Sustainably Priced Energy Enterprise Development (SPEED) program has a trigger window, from 2005 to 2012; if new load growth within the state is not met with new renewable generation, an RPS goal will be triggered. On the basis of the ISO’s 2010 load forecast, Vermont’s net load for energy is expected to be about 50 MW above 2005 levels in 2012. Vermont also has a legislative goal of meeting 20% of its energy needs with renewable resources by 2017. Vermont considers large hydro as renewable resources and allows hydro imports from New York and Canada. The ISO will monitor whether any additional legislative action may be taken at the conclusion of the trigger window and revise its projections as appropriate.

As shown in Table 8-15, Connecticut has three classes of renewable resources; New Hampshire has four classes; and Massachusetts, Maine, and Rhode Island have two classes each. The Maine Public Utilities Commission established regulations in 2007 that created a Class I and Class II for renewable sources of energy. Class II became the previous 30% RPS for existing resources. Under the Class I RPS, competitive suppliers in Maine must demonstrate that new renewable resources provide a percentage of their energy supply portfolio. This started at 1% in 2008 and increases 1% annually through 2017. Alternatively, in lieu of having sufficient resources, affected suppliers may use the ACP (see Section 8.5.2.3).

The main drivers for the growth of renewable resources in New England are the classes for new renewables: Rhode Island’s RPS; Massachusetts’s, Connecticut’s, and Maine’s Class I; and New Hampshire’s Classes I and II. The Massachusetts DOER issued a rulemaking in 2010 that determined that the maximum size of on-site solar generation comprising Class I solar carve-out resources would be 2 MW.

The classes for existing renewables include Connecticut’s, Massachusetts’s, and Maine’s Class II, and New Hampshire’s Classes III and IV. These existing classes are intended to retain the use of existing renewable resources for meeting the RPS, although the projected increase in electricity use for these states will increase the amount of electric energy that resources in these classes will need to provide. Some combination of increased energy efficiency and the use of CHP facilities that have a total fuel efficiency greater than 50% can be used to satisfy Connecticut’s Class III. The percentages for this class are shown in Table 8-15.

With its Green Communities Act, Massachusetts established a Class II RPS. In the state’s RPS regulations, the Massachusetts DOER developed two Class II requirements: a minimum of 3.6% for the technologies shown in Table 8-14 and a minimum of 3.5% for municipal solid waste plants, both applying to plants in operation before December 31, 1997.

The Massachusetts Green Communities Act also established an Alternative Portfolio Standard (APS) similar to the RPS. The APS sets electric energy consumption targets for competitive retail electricity supplies, which must use alternative technologies to meet the minimum APS percentage of their electric energy consumption. The technologies include CHP, flywheel storage, gasification with carbon sequestration, paper-derived fuel, and efficient steam technology. The Massachusetts DOER determined the APS percentages, starting in 2009, to be 1.0% and growing in increments of 0.5% per year to 2014, reaching 3.5%. The percentages would then increase at 0.25% increments per year, reaching 5% by 2020. Table 8-14 and Table 8-15 do not include the APS targets because this category of technologies does not strictly encompass renewable resources. In any case, the ISO estimates the APS target would reflect about 300 MW by 2020 (operating at an 80% capacity factor).

### Related Renewable Resource and Energy-Efficiency Developments

Another portion of the Massachusetts Green Communities Act is for the Secretary of Energy and Environmental Affairs to prepare a five-year plan for meeting the following renewable and energy-efficiency goals, some of which were discussed in Section 8.4.2:

- Meet at least 25% of the state’s electricity load by 2020 with demand resources that include energy efficiency, load management, demand response, and behind-the-meter generation.

- Have competitive LSEs meet at least 20% of their electricity load by 2020 through the use of new, renewable, and alternative energy generation. This goal encompasses the RPS target of 15%, plus the APS target of 5% by 2020.

- By 2020, reduce the amount of fossil fuels used in buildings by 10% from 2007 levels through increased efficiency.

- Plan to reduce total electric and nonelectric energy consumption in the state by at least 10% by 2017 through the development and implementation of a green communities program that encourages the use of renewable energy, demand reduction, conservation, and energy efficiency, as well as the progressive adoption of Massachusetts’s new Stretch Energy Code. This building energy conservation code is intended to reduce at least 20% of the average overall annual combined energy consumption per square foot by all new and existing buildings in the municipalities that have adopted the code.

### Projected RPS and Renewable Resources in the ISO Queue

This section presents a New England-wide projection of the states’ RPS electric energy targets for renewable resources and energy-efficiency goals. It then shows the outlook for meeting these electric energy targets with just the renewable resources in the April 1, 2010, ISO Generator Interconnection Queue. Although the retail electricity providers have a combination of means for meeting their RPS targets (see Section 8.5.2.3), the renewable resources in the ISO queue represent a large potential physical supply for RPS compliance in New England. Analysis of the amounts of these resources provides information on the potential need for additional renewable development.

#### Projected Targets for RPSs and Related Energy-Efficiency Policies

To provide a New England-wide outlook for the five states with RPSs and other related state policies, the ISO projected the electric energy targets for all the RPS classes and related state policies. It also projected the potential growth of the RPS targets for “new renewable” classes. The RPS projections were based on the ISO’s 10-year 2010 forecast for the electric energy demand for competitive retail suppliers and excluded relevant municipal utilities in states where these entities are exempt from meeting the RPSs. To obtain the RPSs’ projected targets for 2020, the energy forecast was extrapolated from 2019, assuming energy growth rates would be similar to those of the last year of the ISO’s forecast (from 2018 to 2019). Massachusetts’s Green Communities Act energy-efficiency goal of reducing the state’s overall use of electric energy 25% by 2020 was modeled as energy-efficiency percentages of statewide electric energy use. The percentages were projected to incrementally increase annually until the state achieves the 25% goal in 2020 (i.e., electric energy usage for competitive retail suppliers would be reduced by over 14,000 GWh). The Massachusetts RPS percentages were then applied to the reduced level of electric energy consumption to obtain the RPS energy requirements. For these analyses, the various state RPS classes and other policies have been grouped into four categories:

- Existing—RPS classes using existing renewable resources. This includes the Class II category for Maine, Connecticut, and Massachusetts; Rhode Island’s “existing” category; and New Hampshire’s Classes III and IV. Massachusetts’s new Class II has two components: one covering the technologies shown in Table 8-14 and in operation before December 31, 1997, and another class for just waste energy plants from the same time period. Table 8-15 shows the percentage targets for each component. All these classes have some growth in the use of renewable resources because of the ISO’s estimated growth in the total demand for electric energy for each state over the next 10 years. New Hampshire’s Classes III and IV also include, for several near-term years, some increase in the percentage targets shown in Table 8-15.

- New—RPS classes focusing on using new renewable resources. This category includes increases in new renewable resources and includes Class I for Maine, Connecticut, and Massachusetts; Rhode Island’s RPS class for new growth; and New Hampshire’s Classes I and II.

- Vermont goals for using new renewable resources—This category includes Vermont’s goal of renewable resources meeting 20% of the state’s electric energy demand by 2017, as well as the SPEED program. Since an implementation plan for 20% by 2017 has not been formally established, an increase in renewable penetration of 2.5% has been assumed for forecasting this target.

- Energy efficiency—New energy-efficiency RPS classes and policy goals. This includes Connecticut’s Class III targets, which also can be met by CHP and Massachusetts’s goal of meeting 25% of energy demand with new energy-efficiency measures by 2020. Although the new Massachusetts APS category includes CHP, the APS has not been projected in this analysis for reasons explained previously.

For each of these four RPS categories and for 2010, 2013, 2017, and 2020, Table 8-16 shows the RPS and policy goals based on the ISO’s 2010 10-year forecast for annual electric energy use by state (net of noncompetitive suppliers’ energy) and the corresponding RPS percentage requirements shown in Table 8-15. For each year, the table shows the total electric energy goal for each of these four categories of renewables. It also shows the totals of these categories as a percentage of the projected total electric energy demand in New England. For the figures presented in this section and data shown in Table 8-15, it has been assumed that Vermont’s SPEED program will be renewed beyond 2012.

Table 8-16
Estimated New England RPS and Related Targets for Renewables
and Energy Efficiency (GWh and %)

| Line # | Use/Requirement Category | 2010 | 2013 | 2017 | 2020 |
| --- | --- | --- | --- | --- | --- |
| 1 | 2010 ISO electric energy use forecast | 131,305 | 134,650 | 139,810 | 143,868 |
| 2 | Existing—RPS targets for existing renewables(a) | 8,980 | 9,132 | 9,167 | 9,157 |
| 3 | New—RPS targets for new renewables(b) | 5,231 | 8,584 | 13,662 | 17,136 |
| 4 | Vermont goals(c) | 160 | 695 | 1,516 | 1,662 |
| 5 | Energy efficiency—targets for new energy efficiency and CHP(d) | 3,316 | 6,617 | 11,369 | 15,770 |
| 6 | Total RPS targets for renewables and energy efficiency | 17,687 | 25,027 | 35,715 | 43,724 |
| 7 | Total RPS targets for renewables and energy efficiency as a percentage of New England’s projected electric energy use(e) | 13.5% | 18.6% | 25.5% | 30.4% |

(a)	This category includes CT Class II, new MA Class II, ME Class II, RI Existing, and NH Classes III and IV. This RPS category grows through time as a result of the growth in electricity demand. NH’s classes also include some growth in the use of renewable resources to meet the RPS percentage of electric energy use.

(b)	This category includes CT Class I, ME Class I, MA Class I, RI’s “new” category, and NH Classes I and II.

(c)	It has been assumed that Vermont’s SPEED program will be renewed beyond 2012. Thus, this category includes VT’s goal for renewable resources to meet 20% of the demand for electric energy by 2017 and assumed will meet 20% for 2020. Incremental increases up to 2017 were assumed for meeting this renewable goal.

(d)	This incorporates only CT Class III (energy efficiency and CHP) and MA’s goal of 25% energy efficiency by 2020 from its Green Communities Act.

(e) 	The numbers may not add to the totals shown because of rounding.

Figure 8-4 shows the projected cumulative targets for renewable resources and energy efficiency in New England based on RPSs and related policies similar to Table 8-16.

Figure 8-4: Projected cumulative targets for renewables and energy efficiency based on RPSs and related policies, 2010 to 2020.

Table 8-17 shows that to meet the RPS-related targets for 2017, these four categories of renewables (i.e., existing, new, Vermont’s, and energy-efficiency resources) need to supply about 25.5% of the total amount of electricity projected to be needed in New England and, similarly, about 30.4% for 2020. Table 8-17 shows the percentages for each of these categories of resources. Energy efficiency is only calculated for states with specific numerical targets.

Table 8-17
New England RPS and Related Targets for Renewables
and Energy Efficiency, by Category (%)

| Category | 2017 | 2020 |
| --- | --- | --- |
| Existing | 6.6 | 6.4 |
| New | 9.8 | 11.9 |
| Vermont goals | 1.1 | 1.2 |
| Energy efficiency/CHP | 8.1 | 11.0 |
| Total(a) | 25.5 | 30.4 |

(a) The numbers may not add to the totals because of rounding.

New renewable resources are the focus of the ISO’s assessment because these resources represent the growth required in renewable resources. Table 8-18 shows the RPS targets for incremental new renewable resources (as shown in Table 8-16, line 3). Table 8-18, lines 1 to 5, show the breakdown by state class of the RPSs for new renewable resources, and line 6 shows the 2009 total New England RPS. Assuming the 2009 targets for RPS classes for new renewables are met by existing renewable resources and then subtracting the 2009 “new” RPS (line 7) from the total (line 6), the new incremental RPS would range from 868 GWh of electricity annually for 2010 to 12,773 GWh for 2020 (line 8).

Table 8-18
Projected New England RPSs for “New” Renewables Beyond 2009 (GWh)(a)

| Line # | State | 2010 | 2013 | 2017 | 2020 |
| --- | --- | --- | --- | --- | --- |
| 1 | Connecticut Class I | 308 | 1,276 | 3,138 | 4,730 |
| 2 | Massachusetts Class I | 453 | 1,823 | 3,473 | 4,466 |
| 3 | Rhode Island “new” | 40 | 296 | 789 | 1,080 |
| 4 | New Hampshire Classes I and II(b) | 63 | 445 | 989 | 1,423 |
| 5 | Maine Class I | 4 | 381 | 911 | 1,075 |
| 6 | Total “new” RPS targets (from Table 8-16, line 3)(c) | 5,231 | 8,584 | 13,662 | 17,136 |
| 7 | 2009 “new” RPS | 4,363 | 4,363 | 4,363 | 4,363 |
| 8 | Incremental “new” RPS beyond 2009(d) | 868 | 4,221 | 9,229 | 12,773 |

(a) 	The projection is based on the ISO’s 2010 state electric energy use forecast deducting 5% for noncompetitive LSEs in CT, and similarly, 14% for MA and 0.6% for RI. Modest growth requirements in the “existing” and “other” categories are not included here.

(b)	New Hampshire’s Classes I and II will go into effect in 2009 and 2010, respectively. However, NH’s Class I requirement starts at 0.5% in 2009.

(c)	The numbers may not add to the totals shown because of rounding.

(d)	This assumes existing renewable projects in New England met the 2007 requirements for “new” renewable resources.

Figure 8-5 shows the annual cumulative RPS targets for new renewable resources included in Table 8-18 by state (lines 1 through 6) for each year of the forecast period. By 2020, the RPSs for Connecticut and Massachusetts will make up 72% of the total RPSs for new renewable resources for the New England states.

Figure 8-5: Cumulative RPS targets for new renewable resource classes beyond 2009, by state (GWh).

#### Incremental RPS Targets for New Renewables Compared with Renewable Projects in
the ISO Queue

Figure 8-6 shows the renewable resource projects in the ISO queue as of April 1, 2010. They total 3,515 MW, with wind projects comprising 87% of the total megawatts, and biomass projects, 11%. The remaining 2% of the projects comprises landfill gas, hydroelectric, and fuel cell projects.

Figure 8-6: Proposed New England renewable resources in the ISO Generator Interconnection Queue as of April 1, 2010 (MW and %).

Note: Totals include all queue wind projects in New England. The total amount of renewable resources is 3,515 MW.

To provide an estimate of the regional outlook for meeting the new incremental growth in the RPS Class I targets by 2020 with just resources in the ISO queue, Table 8-19 develops an estimate of total electric energy production from a total of 52 renewable energy projects in the queue (as of April 1, 2010). These projects are assumed to become qualified to meet the total of the states’ new RPS targets (line 8 of Table 8-18). The table shows estimates of the electricity that the proposed renewable projects in the queue might provide annually. These estimates are based on an assumed capacity factor for each type of renewable resource. The estimates also assume all the projects would be built as proposed and the New England states would certify them as RPS projects so that they can count as RECs toward compliance with the RPS. Figure 8-7 also shows the projected energy from these resources similar to Table 8-19.

Table 8-19
Estimated Energy from New England Renewable Energy Projects
in the ISO Queue as of April 1, 2010

| Type (#) of Projects | Nameplate Capacity (MW)(a) | Assumed Capacity Factor (%)(b) | Estimated Annual Electricity Production (GWh) |
| --- | --- | --- | --- |
| Hydro (6) | 38 | 25 | 83 |
| Landfill gas (2) | 36 | 90 | 284 |
| Biomass (11) | 380 | 90 | 2,996 |
| Wind onshore (29)(c) | 2,025 | 32 | 5,676 |
| Wind offshore (3) | 1,027 | 37 | 3,329 |
| Fuel cells (1) | 9 | 95 | 75 |
| Total (52) | 3,515 | 40(d) | 12,443 |

(a) 	Nameplate capacity is a facility’s megawatt capability designated and usually guaranteed by the manufacturer or developer.

(b)  Capacity factors are based on the ISO’s 2007 Scenario Analysis. The wind capacity factors were adjusted to account for a generic assumption that wind turbines have a 90% availability. See http://www.iso-ne.com/committees/comm_wkgrps/othr/sas/mtrls/elec_report/scenario_analysis_final.pdf.

(c) 	This includes wind projects in New England (including affected non-FERC queue projects) and ignores duplicate listings for projects with more than one potential interconnection point.

(d)  An equivalent capacity factor = [{total energy production (GWh) x 1,000}/{total capacity (MW) x  8,760 hours}].

Figure 8-7: Estimated energy from proposed New England renewable resources in the ISO’s Generator Interconnection Queue (including affected non-FERC queue projects) as of April 1, 2010 (GWh and %).

A comparison of the queue projects in Table 8-19 with the total resources in the “new” RPS category beyond 2009 (as shown in Table 8-18, line 8), indicates that the New England renewable energy resources proposed in the queue would not meet the New England RPS demand by 2020 even if all the projects in the queue were completed successfully. However, additional projects not yet within the ISO queue could help meet the regional RPS demand, and the higher RPS requirements going forward could provide an incentive to develop additional renewable projects that may then appear in the queue. Table 8-20 shows the amount and percentage of projects (in total projects and megawatts) that have gone commercial, are active, or have withdrawn from the queue since the queue started in June 1996. Since wind is the dominant type of renewable technology in the queue, the table also shows the total number and megawatts of wind projects that have gone commercial or are active or have been withdrawn from the queue. A total of 51% of the projects withdrew from the queue, which represent 68% of the total megawatts withdrawn. Similarly, the number of wind projects that withdrew is 40%, representing a decrease in total megawatts of 70%.

Table 8-20 
Summary of All Projects and Wind Projects in ISO Queue as of April 1, 2010

| Project Category | All Projects |  |  |  | Wind Projects |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | No. | % | MW | % | No. | % | MW | % |
| Commercial | 64 | 21 | 12,871 | 19 | 4 | 7 | 174 | 2 |
| Active | 84 | 28 | 8,809 | 13 | 32 | 52 | 3,052(b) | 29 |
| Withdrawn | 152 | 51 | 45,467 | 68 | 25 | 41 | 7,446 | 70 |
| Total(a) | 300 | 100 | 67,147 | 100 | 61 | 100 | 10,672 | 100 |

(a) Percentages may not sum to 100 because of rounding.

(b) This includes wind projects in New England (including affected non-FERC queue projects) and ignores duplicate listings for projects with more than one potential interconnection point.

Figure 8-8 shows the annual new cumulative RPS targets for renewables from 2010 to 2020 compared with the annual potential electric energy production by renewable projects in the queue on the basis of the projected commercial operation date for these projects and assuming the capacity factors shown in Table 8-19. Given the uncertainty of the success of renewable projects, most of which are wind, and using guidance from the PAC, Figure 8-8 shows three scenarios of estimated cumulative electric energy from the renewable resource projects in the queue: 20%, 40%, and 60% of assumed commercial operation. These reflect different assumed attrition levels of renewable projects of 80%, 60%, and 40%. These assumed levels cover a wider range of attrition of wind projects than historically occurred, as shown in Table 8-20. If only 20% of the electric energy from the queue projects became commercially available, other projects would be needed to meet the total RPS targets for new renewables. Starting in 2011, the RPS targets for renewables would start to increase significantly from what the 20% level could provide. Similarly, at a 40% level, the queue projects alone would meet the RPS through 2013. At a 60% level, the queue projects alone would meet RPS targets through 2015.

Figure 8-8: Various levels of estimated cumulative electric energy from new renewable projects in the ISO queue, as of April 1, 2010 (including affected non-FERC queue projects) compared with RPS demand by year.

Notes: Various percentages of electric energy availability from queue projects have been assumed and are not projections of the projects’ expected energy production. RPSs also can be met with behind-the-meter projects, imports, new projects not in the queue, and Alternative Compliance Payments.

#### Other Ways of Meeting New England’s Renewable Portfolio Standards

The ISO recognizes that renewable resources other than those projects in the ISO queue will be used to meet some of the RPS demand in New England. These additional renewable projects include small, on-site and behind-the-meter renewable resources not in the queue; renewable projects in New England not yet in the queue or under development; eligible renewable fuels in existing generators; and imported energy from renewable projects in adjacent balancing authority areas. In 2008, the Massachusetts RPS compliance resources from imports into New England amounted to 40%. The Alternative Compliance Payment is a default that affected LSEs also could use for meeting RPS targets. The ACP acts as an administrative cap on the cost of renewable sources of electric energy, and ACP funds are used to promote the development of new renewable resources and energy efficiency in the region.

To meet their RPS targets, Massachusetts and Connecticut have been certifying some existing renewable generators to qualify for the “new” RPS category and, in some cases, requiring technology upgrades. Retail competitive suppliers will likely continue to use these generators for partial compliance with RPS classes for new renewable resources.

## Summary

Providing electricity at a reasonable cost while meeting environmental goals for air and water quality can create competing requirements for reliably meeting New England’s demand for electricity. The region’s stakeholders, including the ISO, NEPOOL participants, and state environmental agencies, should collaborate on any needed planning to meet these environmental initiatives. The key issues for the region’s major power plants will be complying with the requirements to meet the ozone standard, potential climate change legislation, RGGI revisions, and EPA’s cooling water intake permit requirements.

The New England generation emissions analysis, covering average and marginal emission rates, shows a continuing decline in the region’s SO2, NOX, and CO2 emissions. Even the total emissions for SO2 and NOX have continued to decrease with time. This is the result of generating units using cleaner fuels, particularly natural gas, and adding emission controls to generating plants over the last 10 years.

The ISO also conducted a new analysis of NOX emissions on 20 historic peak-load days. The analysis determined that the increase in emissions for the last 500 MW of fossil fuel generation serving the peak loads ranged from 2 to 11 lbs/MWh over the 20 days. The ISO will issue a report covering this analysis of system peak-load NOX emissions.

A summary of the New England states’ energy-efficiency programs and goals shows a policy focus of achieving all cost-effective energy efficiency as the region’s energy resource of first priority. Increased funding for achieving this goal is coming from increased state energy-efficiency budgets, FCM revenues, and the majority of RGGI auction revenues. Measurement and verification of energy reductions will become more important to assess the extent that targeted reductions from the state programs are achieved. Analysis using this input and other information has the potential to improve the long-term accuracy of the ISO load forecast.

The total RPS and related energy-efficiency targets will increase to approximately 25.5% of New England‘s total projected energy use by 2017 and reach 30.4% by 2020. State energy-efficiency programs make up about a third of this by 2017; the remainder is attributable to Renewable Portfolio Standards and related policies.

The ISO recognizes the uncertainty of success for projects in the current queue. On the basis of assumptions used in the three scenarios presented, these projects would likely meet the incremental growth in the RPS classes for new renewables sometime between 2011 and 2015. For the 10-year planning horizon, the potential supply is greater than what is in the ISO queue (as of April 1, 2010). Most renewable projects have a short lead time of a few years, and many new projects are likely not yet in the queue. Also contributing to the greater supply are the development of small renewable projects “behind the meter” and the purchase of RECs from projects in neighboring balancing authority areas, which could help meet any shortfalls. Alternatively, affected LSEs can make Alternative Compliance Payments to the states’ clean energy funds, which help finance new renewable projects.

# New Technologies

“In addition, the RSP shall also provide information on a broad variety of power system requirements that serves as input for reviewing the design of the markets and the overall economic performance of the system.” (Attachment K, Overview)

“The RSP shall be designed and implemented to:. . . (ii) identify facilities that are necessary to meet Planning and Reliability Criteria; (iii) avoid the imposition of unreasonable costs upon any Transmission Owner, Transmission Customer or other user of a transmission facility; . . .and (vi) properly coordinate with market responses, including, but not limited to generation, merchant transmission and demand-side responses.” (Attachment K, § 3.4)

The ISO strives to keep up to date with new technologies that can have an impact on the region’s electric power grid. As policymakers set targets and allocate public funds to developing smart grid initiatives and renewable generation, the ISO analyzes the effects of these technologies on system operations and reliability. This section discusses several of the technology developments affecting the planning of the New England region. It summarizes some of the challenges of integrating smart grid equipment and discusses three technologies—active demand resources, dynamic line rating, and flexible alternating-current transmission system (FACTS) devices—that would support smart grid enhancements by increasing demand- and condition-based adjustments. The section also highlights two types of renewable resource generation, wind and solar, and their interconnection challenges.

Attachment K of the OATT requires the RSP to provide information useful for understanding the types and locations of resource and transmission technologies that developers should consider.

## Integration of Smart Grid Technologies

This section provides an overview of ongoing smart grid activities at ISO New England.

### Operational Challenges and Opportunities

Implementing smart grid initiatives has many challenges for successfully planning and operating the system. In addition to the need to develop the smart grid technologies, technical standards for smart grid equipment and operations are lacking. Uncertainty over business practices (e.g., cost allocation between transmission and distribution) complicates efforts to add new smart grid infrastructure. The shift from a centrally controlled grid, with relatively large, predictable resources, into a more distributed system that would rely on a greater number of smaller, variable-output resources—that in some cases would have the capability to increase or decrease energy automatically, on the basis of real-time information—will add significant complexity to power system operations.

New, sophisticated algorithms and control systems will be needed to co-optimize the secure and economical operation of existing supply and demand technologies with variable-output renewable resources and automated smart grid sense-and-respond devices. The volume of data is expected to increase exponentially with smart grid technologies, which will require the use of more sophisticated network solutions. System and capacity planning processes will need to be enhanced to account for smart grid resources, and system operators and planners will require extensive training in new “smart-grid-aware” tools and techniques.

### ISO Activities in Support of Developing and Implementing a Smart Grid

The evolution and application of new smart grid technologies already is well underway in New England, and the ISO is implementing several smart grid projects in line with the vision established in the Energy Independence and Security Act of 2007. In response to FERC Order 890 regarding the provision of regulation and frequency services by nongenerating resources, the ISO is conducting an Alternative Technology Regulation (ATR) Pilot Program. The goal of the ATR Pilot Program is to allow the ISO to identify the impact on the New England system of alternative technologies with new and unique performance characteristics that might previously have been unable to participate in the Regulation Market (see Section 2.3). It also aims to allow the owners of the ATR resources to evaluate the technical and economic suitability of their technologies as market sources of regulation service, such as flywheels, thermal storage, and vehicle-to-grid (V2G) technology.

The American Recovery and Reinvestment Act (ARRA) of 2009 provided the U.S. Department of Energy with funding to facilitate the development and implementation of smart grid technologies. In close partnership with New England’s transmission owners, the ISO applied for DOE funding to implement a synchrophasor infrastructure and data utilization (SIDU) smart grid project in New England. Synchrophasors are power system measurements created in devices known as phasor measurement units (PMUs). The units use global positioning satellite (GPS) technology to monitor the performance of the region’s electric power grid accurately and provide specific data for use in operating the grid and enhancing grid design.

The SIDU project will supplement the five existing PMUs in the region with at least 30 new PMUs at various substations around New England. The synchrophasors measured by the PMUs will be communicated to local control centers and the ISO. The synchrophasor data will be collected and concentrated in phasor data concentrators (PDCs) at the control centers. This system will be the technology platform upon which the next generation of monitoring and analysis tools will be developed. With this project, the entire New England region is expected to realize the following benefits:

- Improved reliability through enhanced situational awareness

- Faster response to real-time system events

- Increased capability of monitoring system stability and more accurate system models

- New capabilities in system restoration

DOE approved the $18 million project application on October 27, 2009, for which DOE will contribute $8 million and the ISO and the region’s transmission companies will pay $10 million over a three-year period. The ISO’s share of the project costs is approximately $2.5 million and will be paid through the capital budget; the transmission companies will pay about $7.5 million. This funding will enable the ISO’s smart grid efforts to be completed at a lower cost to the region and allow the region to realize the benefits of smart grid technology much sooner than without federal funding. This project officially began on July 1, 2010, and will serve as a backbone for regional smart grid efforts.

ISO New England also is actively participating in the development of the national smart grid interoperability standards, led by the National Institute of Standards and Technology (NIST), to establish protocols that provide common interfaces. Additionally, as a part of an ISO/RTO Council (IRC) project with other ISOs/RTOs, ISO New England is providing technical and other support for the development of demand-response-related standards by NIST and the North American Energy Standards Board (NAESB) (see Section 11.2.1).

The ISO also is interested in the potential for using energy storage as a type of smart grid technology, in particular, V2G technology. The implementation of a project using V2G technology is being planned as part of the ATR program.

### Dynamic Line Rating

Historically, on the basis of thermal limitations, transmission line elements have one set of defined seasonal limits (also called a static line rating, SLR) for normal and post-contingency operation. However, ambient temperature may affect these limits because it may increase or decrease the ability of a line to dissipate heat. Thus, the limit used in real-time systems operation could be adjusted if proper monitoring equipment were available, allowing for the use of dynamic line ratings (DLRs).

Smart grid DLR applications are growing, with the potential for DLR technology to economically and more accurately reflect the capacity of known constrained elements on a transmission system. This in turn can effectively improve reliability and possibly improve the efficiency of the wholesale markets by allowing additional transfers under some conditions. DLR technologies include the following:

  - Real-time conductor measurements, limit calculations, and telemetry

  - Calibrated load cells directly installed on the monitored conductor

  - Laser-based measurement of conductor sag similar to the technology used by land surveyors

Effective usage of DLR assumes that the limiting element is the conductor itself and not a substation element, such as a breaker, current transformer, wave trap, or relay setting. Additionally, DLR can only be directly effective for thermal overload conditions.

The ISO is committed to working with transmission owners to identify potential transmission circuits that can benefit from the use of DLR. Recent advances in the measurement techniques mentioned are promising in terms of return on investment. Before widespread implementation, standards that pertain to planning, testing, and system operator training would need to be in place to ensure the effective use of DLR on the transmission system.

### Flexible Alternating-Current Transmission Systems

One way to enhance the performance of the transmission system is to apply flexible alternating-current transmission system technology. FACTS is a combination of solid-state switches and computerized automation that enables nearly instantaneous customized control of power flows—far faster than traditional electromechanical switches. The devices can be used to accomplish a number of tasks:

- Precisely move power along transmission lines

- Provide dynamic voltage support

- Increase transfer limits

- Help stabilize the transmission system after a disturbance

- Relieve or even eliminate congestion

- Tie grids together

- Integrate distributed and variable-output generation resources into the grid

- Combat the phenomenon of loop flow

FACTS applications have the potential to provide a much-needed boost to the transmission system and some other technical advantages, especially when dynamic voltage support is needed. However, a thorough economic evaluation of the costs and system performance of proposed FACTS applications compared with alternative plans is required within the framework of the wholesale markets and transmission tariff. Studies that project the prices of electric energy, capacity, and ancillary services, as well as the potential effects on loop flow, are important considerations.

## Integration of Active Demand Resources under the FCM

Almost 1,900 MW of system demand were enrolled in the demand-resource programs for summer 2010. The FCM treats demand response, energy efficiency, and distributed generation as capacity resources, and demand resources (both active and passive) will represent 9% (almost 2,900 MW) of the representative capacity resources needed (i.e., the ICR) in the New England electric power system by 2012 (see Section 4). Of these total demand resources, approximately 6% of the ICR, or about 1,800 MW, are active demand resources. The implementation of significant amounts of demand resources into New England has many advantages:

Delaying or reducing the need to build additional transmission, generation, or distribution facilities, or a combination of new facilities

Reducing land use and adverse environmental impacts, such as air emissions and water discharges

Reducing the reliance on imported fuels and improving the diversity of system resources

To gain all these benefits, the ISO must be prepared to reliably integrate the high level of demand resources that clear in the FCAs into New England’s system planning, operation, and market administration without creating undue barriers to participation. The ISO has created new procedures to work toward integrating the FCM’s active-demand-resource products into system planning, system operations, and market operations.

To determine whether the expected levels of active demand resources that clear in the initial FCAs could be reliably integrated in New England without having a negative impact on market and system operations, the ISO performed an initial operable capacity analysis of active demand resources. The analysis focused on varying levels of participation by active demand resources during the initial FCM delivery years. This initial analysis showed that the 2010 active-demand-resource levels met the criteria needed for system reliability; however, the analysis of the outcome of FCA #2 for the 2011/2012 delivery year identified operational issues and the potential need to change FCM market rules. Specific concerns were as follows:

The ability of active demand resources to maintain reduction without fatigue during the anticipated hours of operation

Access to the resources outside the initially approved program hours and requirements

The appropriateness of reserve “gross-up” rules

Auction transparency during the annual auctions

Infrastructure and telemetering requirements for the active demand resources

The ISO led an open stakeholder process that included a review of the operable capacity analysis of active demand resources and revised FCM rules to accommodate these resources. This stakeholder process culminated with unanimous support at the NEPOOL Participants Committee and ultimately a filing with FERC on October 1, 2008, which FERC approved on October 28, 2008. The revised rule included provisions on the following areas of concern:

The dispatch and settlement rules governing active demand resources

The eventual elimination of the critical-peak resource category and the conversion of these resources into other categories of demand resources

Improved information to facilitate active-demand-resource participation in Forward Capacity Auctions

A clarification of the ISO’s ability to impose appropriate sanctions when market participants with active demand resources do not comply with their obligations

The ISO’s real-time operational practices have been revised to improve the integration of large quantities of active demand resources. These changes include modifications to OP 4 and operator interfaces, the creation of demand-designated entities that can aggregate the operation of active demand resources, the establishment of dispatch zones for active demand resources, and the implementation of new communications infrastructure.

### Modifications to ISO New England Operating Procedure No. 4

Before June 1, 2010, the implementation of OP 4 actions involved notifying stakeholders that the ISO was close to not meeting its full 10- and 30-minute operating-reserve requirements or had a transmission system problem preventing the ISO from maintaining first- or second-contingency coverage. The availability of active demand resources in large quantities and in shorter response times greatly expands the resources available to maintain operating reserves. As such, by reducing load in the appropriate locations, active demand resources can be used to free other supply resources for maintaining reserve requirements for a systemwide event and transmission security for local events. The ISO has modified OP 4, dividing the use of active demand resources into stages that more accurately reflect their level of contribution to system reliability.

### Creation of Demand-Designated Entities

Coordinating operations between the ISO and the demand-resource network operating centers has been enhanced by creating demand-designated entities (DDEs), similar to generator-designated entities. These active-demand-resource communication entities are responsible for receiving and acting on dispatch instructions from the ISO. DDEs are the only entities the ISO will communicate with regarding dispatch instructions for active demand resources.

In addition, the DDEs are required to participate in training activities with the ISO and local control center staff to gain confidence and expertise in how these resources fit into the overall operation of the interconnected systems.

### Operator Interfaces

The ISO has incorporated active demand resources into the dispatch management tools within the Energy Management System (EMS), allowing operator control over their dispatch similar to other resources, with real-time input from the rest of the software tools within the EMS. This is a structural improvement from the past condition, in which active demand resources were administered with a separate set of software tools. Operational staff have been trained in the new environment and can use these new tools to predict available reserves both pre- and post-application of active demand resources. This new environment also allows for improved auditing of active demand resources to ensure they can respond as bid into the FCM during a system event.

### Development of New Communications Infrastructure

The ISO has worked with stakeholders to replace the communication infrastructure for active demand resources throughout the region. The response of active demand resources is now modeled, monitored, and controlled by the ISO’s Energy Management System, giving system operators a secure and reliable means to dispatch these resources. This prevents single points of failure from rendering all active-demand-resource assets unusable during an emergency or economic dispatch. A final effort to enhance the communications infrastructure involved integrating the active-demand-resource assets within the ISO’s supervisory control and data acquisition (SCADA) functions.

### Use of Active-Demand-Resource Dispatch Zones

A demand-resource dispatch zone is a group of nodes (i.e., pricing points) within a load zone that is used to define and dispatch real-time demand-response resources or real-time emergency generation (RTEG) resources. These allow for a more granular dispatch of active demand resources at times, locations, and quantities needed to address potential system problems without unnecessarily calling on other active demand resources. Figure 9-1 shows the dispatch zones the ISO uses to dispatch FCM active demand resources.

Figure 9-1: Active-demand-resource dispatch zones in the ISO New England system.

## Integration of Variable-Output Generation

Two of the main types of variable-output generation resources are wind and solar technologies. The large-scale use of wind power is becoming a norm in many parts of the world due to the emissions-free electric energy wind power can generate; the speed with which wind power plants can be constructed; the generation diversity it adds to the resource mix (see Section 7); the long-term certainty of its fuel costs; and, in some instances, the cost-competitiveness of modern utility-scale wind power. Emissions-free generation helps meet environmental goals, such as RPSs and greenhouse gas reduction objectives (see Section 8). Wind power plants can be constructed in as little as three to six months in New England, which facilitates financing and quick responses to identified system needs. With a fuel cost fixed at essentially zero, wind power’s long-term fuel costs are known. If the costs of fossil fuels and environmental emission-allowance prices rise, wind power may become more attractive as a resource (see Section 10) and can help New England relieve its dependence on natural gas (see Section 7).

Solar photovoltaic (PV) technology is experiencing a high level of growth in the New England states, and the technology is making strong inroads in locally providing electricity at customer sites. As the New England states reach hundreds of megawatts of installed solar capacity, solar PV will begin to have a measurable impact on the power system load and operation.

Studies are being conducted to determine how to successfully integrate variable-output resources into the power generation system and plan for this integration. Some issues being addressed include projecting and modeling energy production and the capacity values for use in analyses; coordinating generation and transmission planning approaches; studying the effects of distributed resources; determining the need for changes in operating practices, such as changes in the amounts of operating reserves and regulation requirements; identifying possible needs for integrating large amounts of storage and demand response and successfully integrating those technologies; and resolving other planning and operating aspects of the development of large-scale variable-output resources. Results of several studies, other factors about integrating these resources and their growth in New England and adjacent areas, and state incentives and costs for using solar technologies follow.

### Studies of Variable-Output Generation Resources

Several studies conducted by NERC and the IRC have addressed the integration of variable-output generation resources.

#### NERC’s Integrating Variable Generation Task Force Report

In December 2007, the NERC Planning Committee and the NERC Operating Committee created the Integrating Variable Generation Task Force (IVGTF) and charged it to prepare a report addressing the following topics:

  - Raise industry awareness and understanding of the characteristics of variable-output generation

  - Review the planning and operations of integrating variable-output resources and identify high-level shortcomings of existing planning approaches

  - Broadly assess existing standards to identify possible gaps and requirements to ensure power system reliability

The ISO is actively participating as a member of the IVGTF. The IVGTF’s assignment includes the following tasks:

  - Developing collaboratively proposed NERC standards as a strawman for industry consideration

  - Conducting research and summarizing specific analyses and studies that identify operational and planning issues concerning the integration of large amounts of wind generation with the electric power system.

The IVGTF studied power system reliability issues surrounding the integration of large amounts of resources that possess variability and uncertainty and has issued several conclusions and recommendations for revising practices to accommodate higher levels of these resources on the system. First, power system planners must consider the impacts of variable-output generation in power system planning and design and must develop the necessary practices and methods to maintain long-term power system reliability. Second, operators will require new tools and practices to maintain power system reliability. Last, planners and operators will benefit from a reference manual describing required changes to the planning and operation of both the electric power and distribution systems to accommodate large amounts of variable-output generation.

The IVGTF recognizes that the impacts of variable-output generation resources like wind and solar power are region-specific because of regional differences in the characteristics of the wind and solar power resources, load, and the operating and planning of generation and transmission resources. It also recognizes that diversity of locations for variable-output resources would mitigate the adverse effects of variations in total wind and solar energy production.

The IVGTF has begun a second phase of work to investigate more deeply the conclusions drawn and the recommendations made as a result of the first phase of work. The ISO is actively participating in the IVGTF’s second phase.

#### IRC Report on Variable-Output Energy Resources

A recent report on variable-output energy resources by the ISO/RTO Council indicates the following three issues with these types of resources, such as solar and wind:

Uncertainty before the dispatch, as reflected in energy market forecast errors

Variability of production as the penetration of the resource grows

Lack of dispatch control of the variable-output resource

The report suggests that the large-scale integration of variable-output resources could have an adverse impact on system. The effects on other generation include less efficient unit commitment, higher system ramp ups and downs, increased load-following regulation and reserve requirements, and increased frequency and magnitude of the under- and over-generation events. The report discusses options to deal with these requirements.

### Wind Generation Technology and Integration

While wind can provide many system benefits, the variability of wind resources and the uncertainty with which the amount of power produced can be accurately forecast pose challenges for the reliable operation and planning of the power system. Many favorable sites for wind development in New England are remote from load centers. Development of these distant sites would likely require significant transmission development, which may not be economical and would further complicate the operations and planning of the system. The geographical diversity of wind power development throughout New England and its neighboring systems in New York and the eastern Canadian provinces would mitigate some of the adverse impacts of wind-resource variability on the overall system. Several Elective and Merchant Transmission Upgrades are in various stages of development to access this wind power as well as other renewable resources (see Section 6, Section 10, and Section 12)

As of April 2010, approximately 200 MW of utility-scale wind generation are on line in the ISO New England system, of which approximately 170 MW are biddable assets. New England has approximately 3,100 MW of larger-scale wind projects in the queue, of which over 1,000 MW represent offshore projects and 2,100 MW represent onshore projects. Figure 9-2 shows a map of planned and active wind projects in New England. New England holds the potential for developing over 215 gigawatts (GW) of wind generation.

Figure 9-2: Planned and active wind projects in New England, 2010.

The ISO is focusing on three main wind-integration activities: facilitating the interconnection process for new wind generators, actively participating in the NERC IVGTF Phase II, and conducting a study of large-scale wind integration operational effects—the New England Wind Integration Study (NEWIS).

#### Wind Generator Interconnection Facilitation

Developers of wind generation interested in interconnecting facilities to the ISO system face particular challenges because of the differences between wind power and conventional resources caused by the variability of wind power production. In recognition of this and because wind generation is a relatively new type of technology for the New England system, the ISO has developed a set of procedures to facilitate wind generator interconnection. ISO staff assist wind project developers through the interconnection process, including the following tasks:

  - Meeting all phases of the ISO’s specific commissioning protocol

  - Complying with voice, data, and telemetry requirements, depending on the type of markets in which the resource will be participating

  - Designating an entity that has complete control over the wind generation resource and that can be contacted at all times during both normal and emergency conditions

  - Submitting real-time self-scheduling information so that the ISO can account for this information when operating the system and conducting resource adequacy analyses (see Section 4.1)

  - Understanding operating requirements, which includes the provision of training, for how the ISO manages congestion, should it occur

Additionally, wind generators are notified that because the interconnection requirements are under review as part of the NEWIS (see below), the requirements are interim and may change once the study has finalized recommendations for interconnection requirements.

#### New England Wind Integration Study

The ISO is conducting the comprehensive New England Wind Integration Study that highlights the operational effects of large-scale wind integration in New England, including the effects of wind forecasting and large-scale wind power on the rest of the generation fleet. In 2009, the ISO publicly released a request for proposals (RFP) and selected an expert vendor—General Electric Energy Applications and Systems Engineering, with support from EnerNex, AWSTruewind, and WindLogics—to perform the study. All work is to be performed during 2009 and 2010. In addition to studying operational effects on large-scale wind integration, NEWIS will recommend potential corrective actions to mitigate adverse operating conditions created or exacerbated by the variability and uncertainty of wind power.

NEWIS captures the unique characteristics of New England’s electrical power system and wind resource—including historical load and ramping profiles, geography, topology, supply- and demand-side resource characteristics, and wind profiles—and the unique impacts that these characteristics can have on system operations and planning with increasing wind power penetration. In addition to ISO support staff and the vendors, NEWIS includes a Technical Review Committee (TRC) composed of ISO subject matter experts and external wind integration experts. The ISO provides regular updates to stakeholders. The TRC and stakeholder reviews help ensure that the study objectives, methodology, and results are scientific, objective, reasonable, and relevant.

The results of the complete NEWIS ultimately will form some of the basis for the ISO’s policies and practices that may result in changes to the ISO tariff, operating procedures, and manuals. The ISO has presented to stakeholders the work completed to date and will continue to work with stakeholders to discuss the study’s findings. It will then complete a full stakeholder process within New England to address modifications to market and reliability rules required to facilitate the large-scale integration of wind resources. The NEWIS is scheduled for completion in fall 2010.

Using the outcomes of the analysis, the ISO will embark on a project to implement the recommendations developed in the NEWIS. The majority of actions to be implemented in the near term will be derived from the NEWIS-identified technical requirements for interconnection. The balance of the integration efforts will be ranked by priority and completed in accordance with the ISO’s project implementation schedule.

### Solar Energy Technologies and Integration

The potential for using solar energy is based on the amount of solar radiation that reaches the earth’s surface, the variability of solar energy production during the day, the efficiency of solar energy technologies, and other factors.

About half of the solar radiation that reaches the earth’s atmosphere reaches the earth’s surface. Figure 9-3 is a map of solar potential in the United States showing that the solar insolation in the Northeastern region is 4 to 5 kWh/m2/day.

Figure 9-3: Annual average solar radiation in the United States, 1998 to 2005.

Source: National Renewable Energy Laboratory (NREL), DOE (2008); http://www.nrel.gov/gis/images/map_pv_national_lo-res.jpg

Solar technologies include solar thermal and water heating, photovoltaic systems, and solar concentrator systems, photovoltaic systems being the most widely used. About 80% of the market is served by crystalline silicon PV panels, which can achieve 20% efficiency, while thin films comprise the remaining 20% of the PV market, which can achieve up to 11% efficiency. PV systems are modular and can be sited, for example, on roofs, parking garages, the ground, and individual pieces of equipment, such as roadside lighting and signage. They can be used as distributed generation, avoiding electricity delivery costs through the transmission and distribution systems. They also are relatively simple to install, compared with other forms of generation, and have no carbon emissions.

Solar resource production is variable during the day and unavailable at night. It peaks at noon (or 1:00 p.m. during daylight savings time) and overlaps somewhat with the summer peak electricity load hours of 2:00 p.m. to 4:00 p.m. Figure 9-4 shows representative monthly estimated outputs of a PV system for New England, based on a composite of solar data from Hartford and Boston and assuming a mix of various solar technologies. The profile is suitable for ISO economic studies and has an estimated annual capacity factor of about 15%.

Figure 9-4: Estimated monthly output of a PV system based on a composite of solar data for Boston and Hartford.

Source: New England Electricity Scenario Analysis Report (August 2, 2007); http://www.iso-ne.com/committees/comm_wkgrps/othr/sas/mtrls/elec_report/scenario_analysis_final.pdf.

NERC’s report on integrating variable-output resources (see Section 9.3.1) notes that on partially cloudy days, operating PV systems has demonstrated the potential for substantial ramps in output of +/- 50% in a 30- to 90-second timeframe and +/- 70% in a five- to 10-minute timeframe. This suggests more variability with these systems than for wind turbines, which have less variation due to the inertia of their rotating mass.

#### Photovoltaic Development

In 2008, solar installations in the United States grew from 335 MW to almost 800 MW. California had the largest amount of PV installations in the country, with over 500 MW by the end of 2008. In New England in 2008, Connecticut and Massachusetts installed the eighth- and tenth-most PV capacity in the country, 9 and 8 MW, respectively. The total cumulative capacity in the six New England states that year was 18 MW.

According to the Electric Power Research Institute (EPRI), over 185,000 buildings in the United States have PV systems installed. In Massachusetts, the Green Communities Act allows electric utilities to own up to 50 MW of solar installations. NGRID, WMECO, and NSTAR combined have solar installations in their interconnection queues approaching a total of 100 MW.

#### Costs of PV Systems

The Massachusetts DOER estimates that historical installed costs of PV systems range from $6,000 to $8,000/kW in New England. These costs are expected to decrease as the technology matures, but they are consistent with national estimates. The cost of electricity from PV can be influenced by a number of factors, such as the size of the installation and location. The costs can range from $0.20/kWh to $0.80/kWh, although selected samples in major American cities show a smaller range of costs, from $0.28/kWh to $0.46/kWh, before federal investment tax credits are applied, and between $0.20/kWh and $0.32/kWh afterward.

#### Incentives for Solar Installations

All the New England states have incentives for solar installations. These incentives typically are in the form of rebates or grants covering part of the cost of PV installations. In addition, federal incentives of investment tax credits are in effect until 2016. Two types of revenue programs for encouraging solar and renewable resources in general are long-term purchase contracts (10 to 20 years) and feed-in tariffs (FITs), which pay a stated price for the electricity produced.

#### State Goals and Solar Programs

The New England states have a number of aspects to their renewable and solar programs. These include goals, RPS requirements, requests for proposals and FITs. RFPs and FITs generally apply to a variety of renewable projects. These aspects are summarized in Table 9-1. PV goals and programs from New York and Ontario are also included for comparison. Refer to Section 8.5 for more information on state solar energy goals and RPS classes.

Table 9-1
Solar Policies in New England and Neighboring Areas(a)

| State | Goal | Renewable Portfolio Standard | Request for Proposal (RFP)/Feed-In Tariff (FIT) | Net Metering (Size Range)(b) | Other |
| --- | --- | --- | --- | --- | --- |
| CT(c) |  | Class I | DPUC RFP and considering FIT | 2 MW max | CT Clean Energy Fund rebates and loans |
| MA(d) | 250 MW by 2017 | Class I solar carve-out ends when 400 MW are installed. Solar auction Renewable Energy Certificates (RECs) = $300/credit. Solar Alternative Compliance Payment is $600/MWh. |  | 60 kW to 2 MW | 23.5 MW awarded in rebates last 2 years |
| ME(e) |  | Class I | FIT and periodic RFP for 10 contracts | 0.66 max | Bill LD 336, passed in 2009, amended FIT. |
| NH |  | Class 3 0.3% by 2014 |  | 1 MW max | Proposal in the legislature |
| RI |  | Class 1 | RFP for 15-year contract. 3 MW solar. FIT bill introduced in 2008. | 1.65 to 3.5 MW; varies with entity |  |
| VT | 50 MW cap |  | 175 MW of solar for RFP of 12.5 MW. FIT= 30¢/kWh. | 2.2 MW max |  |
| NY(f ) | 2,000 MW by 2017 | NYSERDA RFP for RECs 10-year fixed-price contracts | Considering FIT bill | 25 kW max residential; 2 MW max nonresidential |  |
| Ontario(g) |  |  | FIT (2009) | 500 kW max | Small projects (<10 kW) receive 80.2¢/kWh or lower; larger projects (>10 kW) receive 44¢/kWh. |

(a) 	Sources: North Carolina State University, “Database of State Incentives for Renewables and Efficiency” (DSIRE) (DOE, NREL contract); http://www.dsireusa.org/. Also, Robert C. Grace, “Long-Term Contracting Policies for Renewable Energy in the Northeast,” and Wilson RIckerson, “Feed-In Tariffs in the Northeast” presentations at the Northeast Energy and Commerce Association’s Renewable Energy Conference, Boston (March 3, 2010); http://www.necanews.org/dev/documents/100303_grace_bob_1.pdf and http://www.necanews.org/dev/documents/100303_rickerson_wilson_1.pdf.

(b) Net metering is when a renewable resource generator, such as solar PV, generates more energy than is needed and sells the excess energy back to the electric power grid at some agreed to price.

(c) 	Connecticut Energy Information Line, Connecticut Energy Efficiency Fund, “Net Metering—Class I Renewable Energy” Web site (2010); http://www.ctenergyinfo.com/dpuc_net_metering.htm. Also, Connecticut Clean Energy Fund, “Clean Energy Incentives” Web site (n.d.); http://www.ctcleanenergy.com/CleanEnergyIncentives/tabid/57/Default.aspx.

(d) 	Refer to Section 8.5 for more information on Massachusetts.

(e) 	Resolve, Regarding Legislative Review of Chapter 313: Net Energy Billing Rule to Allow Shared Ownership, a Major Substantive Rule of the Public Utilities Commission, Maine State Legislature. LD 336 (September 30, 2009); http://www.mainelegislature.org/legis/bills/bills_124th/chappdfs/RESOLVE20.pdf.

(f) 	Solar Initiative of New York, New York’s Solar Roadmap (May 2007); http://www.neny.org/download.cfm/NENY_Membership_Application.pdf?AssetID=225. NYSERDA stands for the New York State Energy Research Development Authority.

(g) Ontario Power Authority (OPA), Feed-in Tariff Program: Program Overview (July 2010); http://fit.powerauthority.on.ca/Storage/101/11057_FIT_Program_Overview_July_6_10_version_1.3.1_final_for_posting.pdf. Also, Ontario Ministry of Energy and Energy Safety Authority, Net Metering in Ontario (n.d.); http://www.mei.gov.on.ca/en/pdf/renewable/NetMeteringBrochure.pdf.

The New York State Energy Research Development Authority (NYSERDA) provides financial incentives to grid-connected PV systems on a first-come, first-served basis. To fund this program, on October 28, 2008, the New York Public Service Commission allocated $20.6 million to the customer-cited tier of the state’s RPS. The program has requirements for interconnection and net metering and the use of eligible installers only. The program provides 40 to 45% of the PV system costs.

In Ontario, the Ontario Power Authority has the responsibility for what they consider to be North America’s first comprehensive FIT. Recently, OPA awarded 184 renewable projects, 76 of which are ground-mounted PV under its FIT program.

## Summary

The ISO actively is implementing several smart grid projects, and several smart grid technologies have successfully been integrated into the transmission system. Additional research and development efforts are necessary to develop technical standards and business practices to fully use smart grid technologies on the distribution system and at consumer locations. Developing standards of smart grid technologies is a major area of focus at the national level, which the ISO is following. The potential for use of phasor measurement systems is one smart grid technology of particular interest to the ISO. DOE has granted funding for a project that will install over 30 additional phasor measurement units in the region. Phasor measurement units can provide vital information that would improve the overall efficiency and security of power system operations.

The ISO has made progress on several projects that will improve the integration of new technologies. Large amounts of active demand resources are being successfully integrated into the New England system through improvements to the ISO’s markets, system planning, and system operations. Dynamic line rating and the use of FACTS hold promise for more reliable and economic operation of the power system.

Two industry studies, one by NERC and one by the IRC, have helped explore issues with integrating variable-output, renewable generation resources. New England currently has 200 MW of wind operating on the system, and the ISO queue has 3,100 MW of wind projects in the planning stage, two-thirds of which are onshore projects and one-third, offshore. The ISO is conducting a large-scale detailed wind integration study that will help indicate any changes that would be needed in operating procedures, manuals, and the tariff to accommodate the integration of larger amounts of wind to the system. New England has around 20 MW of solar PV installations. Some states in the region have goals for solar installations, and all states have some solar incentives, such as rebates, grants, and feed-in-tariffs.

# System Performance and Production Cost Studies

“The ISO shall, among other things . . . (iv) provide sufficient information to allow Market Participants to access the quantity, general locations, operating characteristics and required availability criteria of the type of incremental supply and demand-side resources, or merchant transmission projects, that would satisfy the identified needs or that may serve to modify, offset or defer proposed regulated transmission upgrades.” (Attachment K, § 3.1)

“The ISO’s stakeholders may request the ISO to initiate a Needs Assessment to evaluate potential regulated transmission solutions or market responses or investments that could result in (i) a net reduction in total production cost to supply system load based on the factors specified in Attachment N of this OATT, (ii) reduced congestion, or (iii) the integration of new resources and/or loads on an aggregate or regional basis (an “Economic Study”).” (Attachment K, § 4.1)

ISO New England conducts economic planning studies each year, as specified in Attachment K of the OATT. The economic studies provide information on system performance, such as estimated production costs, load-serving-entity energy expenses, estimates of transmission congestion, and environmental metrics. This information can assist market participants and other stakeholders in evaluating various resource and transmission options for participating in New England’s wholesale electricity markets. The studies may also assist policymakers who formulate strategic visions of the future power system.

The economic study process is consistent with ISO’s open stakeholder planning process. Stakeholders submit economic study requests to the ISO by April 1 of each year. The requests may be to study scenarios of general locations and resource types for resource expansion, resource retirements, and possible changes to transmission interface limits. By May 1 of each year, the proponents of these studies are provided an opportunity to present the PAC with the reasons for the suggested study. The ISO discusses a draft scope of work with the PAC by June 1 and reviews the study assumptions with the PAC at later meetings. The ISO then performs up to three economic studies and reviews all draft results with the PAC.

The economic studies use assumptions for factors such as fuel prices, unit availability, and load growth, all of which could affect system performance metrics. Because all the assumptions are uncertain, the modeling results indicate relative values and trends and are not intended to be accurate projections of future congestion, ultimate project economics, and environmental impacts.

This section provides an overview of the status of economic studies conducted in response to stakeholder requests received in 2009. Additional details and discussion of the simulation assumptions and results are documented in supplemental presentations made to the PAC and other reports. This section also discusses economic study requests received in 2010.

## 2030 Power System Study for New England Governors

As part of the economic study request by the New England governors in 2009, the ISO provided technical support for developing a “blueprint” for integrating large-scale renewable energy resources into the region’s electric power grid. The resources in this study primarily were wind resources within New England and imports of wind and hydroelectric power from eastern Canada. Additionally, for comparison purposes, the study assessed the regional impacts of large-scale wind development in the Midwest for long-distance delivery to the Northeast. The targeted level of wind integration, up to 12,000 MW of nameplate capacity, is consistent with the ISO’s wind integration study (see Section 9.3.2.2).

A scenario analysis, or “what-if” approach, was used to evaluate several resource scenarios and assumptions for a single year in the 2030 timeframe. A 20-year view was selected to allow for the consideration of large-scale development of wind and other emerging technologies. The study approach evaluated specific economic and environmental characteristics of a range of future resource scenarios; it did not add resources to meet projections of future demand for electricity, and it did not add specific types of resources to meet any particular state or federal policy objectives.

The states developed the study assumptions with technical support from the ISO. Assumptions were developed for the following factors:

- Demand and supply levels for New England

- Representative future Installed Capacity Requirements (see Section 4.1.1)

- Demand-resource amounts

- Penetration and charging characteristics of plug-in electric vehicles

- A Maine proposal for converting homes from oil to electric heat

- The level of existing resources (generation, demand resources, and imports)

- Multiple wind integration cases

- Electric energy storage

- The retirement of older oil- and coal-fired generators

- The expansion of interconnections with neighboring regions

The study evaluated a range for most assumptions (i.e., low, medium, and high).

The study’s primary findings indicate that New England has significant onshore and offshore wind resources that could be developed and added to the electric power system with appropriate transmission expansion. Analysis of the conceptual transmission required to support the integration of New England wind resources indicates that connecting certain offshore wind resources results in the most cost-effective use of new and existing transmission—because it also allows for the integration of some near-shore and onshore wind generation. Renewable and low-carbon resources located nearby in eastern Canada could be available to New England with transmission expansions to the Québec and New Brunswick power systems, which are relatively modest expansion scenarios compared with the other conceptual transmission-expansion scenarios between New England and the Midwest.

The 2009 study was issued in September 2009 to coincide with the governors’ “blueprint” (see Section 12.2.2) and was subsequently posted as a final report in February 2010.

## New York ISO/ISO New England Economic Study

Another economic study request in 2009 was from the PAC and interregional stakeholders from the Inter-Area Planning Stakeholder Advisory Committee (IPSAC) to coordinate production cost models with neighboring systems and examine the overall interregional system performance. Similar to the planning process requirements of ISO New England’s OATT Attachment K, the planning processes of NYISO and PJM (each a NERC-registered planning authority) require a forum for stakeholder review of economic studies. The studies provide information on system performance, such as estimated production costs, load-serving-entity energy expenses, estimates of transmission congestion, and other metrics.

The NYISO/ISO New England economic study will analyze a series of scenarios for 2013 to account for planned load, resource expansion and retirements, and transmission configurations that could affect both regions and PJM. The study will conduct joint production cost analyses with both NYISO and PJM and will assess effects of relaxing various combinations of constrained transmission interfaces in increments of 500 to 1,000 MW. The goal of this analysis is to identify where major interfaces are constraining interregional transfers by modeling NYISO, ISO New England, and the eastern portion of PJM with approximate representations for their neighboring areas. This economic study is one of the many ongoing efforts that are improving interregional coordination (see Section 11).

The NYISO/ISO New England study initially will use the Interregional Electric Market Model (IREMM) production cost program, a simplified interregional model. The analysis will produce various metrics, including production cost, load-serving-entity energy expenses, environmental emissions, and locational marginal prices of “load bubble” areas, which represent the RSP subareas (see Section 2.4), NYISO, PJM, and the interconnected system (see Figure 10-1). Follow-up analysis will use a more detailed representation of the interregional network.

Figure 10-1: Transmission interfaces and RSP areas.

Note: The light yellow bubbles represent the New England RSP bubbles, and the orange bubbles show areas in New England with energy efficiency, demand response, and emergency generators (RTEGs). The names in the bubbles for New England are consistent with RSP subarea names (see Section 2.4). The subarea names used for New York (in the light orange bubbles) are consistent with the names used for its resource adequacy studies (e.g. “NY A” refers to Zone A). The G1 and F1 light orange bubbles represent additional bubbles in New York that contain generation near the New England border. The red boxes represent transmission interface names used within NYISO. The gray bubbles show controlled ties interconnecting New York with its neighbors where phase-angle regulators, HVDC, or variable-frequency transformers (VFTs) are used to control power. The PJM names (in the green bubbles) are consistent with those used for NPCC resource adequacy studies. The light blue bubbles represent equivalents for neighboring systems. The dark blue bubbles represent offshore wind, and the dark green bubbles represent onshore (inland) wind.

The study results are scheduled for completion by the end of 2010. The results may identify areas where transmission upgrades would promote interregional transfers. The final identification of transmission upgrades would require follow-up transmission planning analysis and detailed production cost simulations. A possible outcome could be a recommendation for conducting follow-up studies of additional interconnection capability, such as a southern New England–southeast New York–New Jersey tie.

### Modeling and Assumptions

The simulations of the Northeast ISO/RTOs were conducted using IREMM. The model was used to produce a base-case simulation and then to develop sensitivity cases with differing specific assumptions. The data, assumptions, and modeling inputs reflect stakeholder input and were based on the following factors:

  - Load forecast—The New England load and electric energy forecasts used in this analysis were based on the data for 2013 presented in Table 3-2 of RSP09, which are different from those used in Section 3 of this report. The loads and resources for PJM and New York were obtained from their respective publications produced in 2009.

  - System generation—The supply resources for the New England system were based on the April 2009 CELT report plus the new supply resources that cleared in FCA #2 for 2011/2012 (see Section 4.2.2). Resources for PJM and NYISO were provided by those areas.

  - Demand resources—Demand resources were one of the types of supply resources included in the RSP09 case. Three types of demand resources were modeled on the basis of the results of FCA #2: 983 MW of passive demand resources, which were represented as energy efficiency; 1,195 MW of near-peak demand resources, which were activated when the load approached seasonal peaks; and 759 MW of emergency generation activated in OP 4 at Action 12 (to implement voltage reductions). Active demand resources were assumed present for lower New York State with 1,700 MW in Zone J.

  - Controllable transmission—A number of controllable transmission elements were assumed to have a constant power flow across them. These are shown in Figure 10-1 and comprise links where the same amount of power withdrawn from one transmission bubble is injected into an associated bubble. For example, a 1,000 MW fixed transfer, known as the “PJM wheel,” has 1,000 MW injected into a bubble adjacent to New York Zone G and withdrawn adjacent to New York Zone J. This is a simplification of a transaction that includes several phase-angle regulators.

  - Transmission interfaces—Figure 10-2 and Figure 10-3 show the 20 interfaces modeled in the study, and Table 10-1 shows the interface values modeled.

Figure 10-2: Transmission interfaces Group 1.

Figure 10-3: Transmission interfaces Group 2.

Table 10-1
Interfaces Modeled

| Number | Interface Name | Interface Abbreviation | Forward (MW) |  | Reverse (MW) |  | Forward Direction |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Color Codes |  |  |  |  |
|  |  |  | Same as MARS Data(a) | Economic Transfer Limit |  | Unlimited |  |
| 1 | New York's Central East plus Marcy South | CE GRP | 4,550 |  | 3,400 |  | To the southwest |
| 2 | New York's Total East | Total-ES | 6,425 |  | 1,999 |  | From west to east |
| 3 | Dunwoodie South plus lines Y49 and Y50 | DSY49Y50 | 99,999 |  | 99,999 |  | To New York City |
| 4 | New England's East–West | East–West | 2,800 |  | 9,999 |  | Boston toward New York |
| 5 | New York– New England | NY–NE | 1,250 |  | 1,250 |  | New York to New England |
| 6 | New England North–South Interface | N to S | 2,700 |  | 9,999 |  | New Hampshire to Massachusetts |
| 7 | Connecticut import (AC only) | CT-IMPEX | 2,500 |  | 9,999 |  | Into Connecticut |
| 8 | PJM West–Central | PJM West–Central | 4,250 |  | 4,250 |  | From the west into central PJM |
| 9 | PJM Central–East | PJM Central–East | 6,450 |  | 6,450 |  | From the central into eastern PJM |
| 10 | Dysinger East (between Buffalo and Rochester) | DY Singer | 2,850 |  | 1,999 |  | From Buffalo, NY, to the east |
| 11 | New Brunswick– New England | NB–BHE | 1,000 |  | 550 |  | From New Brunswick |
| 12 | Suroweic–South | Suroweic–South | 1,200 |  | 9,999 |  | From central Maine to southern Maine |
| 13 | Orrington–South | Orrington–South | 1,150 |  | 9,999 |  | From Bangor, Maine, to central Maine |
| 14 | Maine–New Hampshire | Maine–New Hampshire | 1,525 |  | 9,999 |  | From southern Maine to New Hampshire |
| 15 | Boston import | Boston Import | 4,900 |  | 9,999 |  | Into Boston |
| 16 | Ontario–New York | Ontario to New York | 3,000 |  | 3,000 |  | From Ontario into New York |
| 17 | Upper New York– Consolidated Edison | G–SENY | 6,000 |  | 2,499 |  | From NY G toward New York City |
| 18 | Total import into New York City | J–Import | 99,999 |  | 99,999 |  | Import into New York City |
| 19(b) | Eastern PJM– Southern New York | PJ_G&PJ_J | 1,500 |  | 2,000 |  | Eastern PJM toward New York City |
| 20 | Total Import into Long Island (AC only) | LI SUM | 1,190 |  | 300 |  | Into Long Island from New York |

- “MARS” stands for multiarea reliability simulator.

- The 1,000 MW “PJM wheel” uses part of the 1,500 MW capability of Interface 19.

A coordinated production cost model was developed using several assumptions. Resource data for PJM and NYISO were initially developed from the comprehensive data filing of DOE’s 2008 Energy Information Administration (EIA) Form 860. The respective planning authorities reviewed and updated the data to reflect expected 2013 resources. These updates were merged with the 2009 economic study data (the Governor’s Study). One of the key pieces of information needed was heat-rate data for each unit. The most recent publicly available and comprehensive heat-rate data were available in the 1995 EIA Form 860, which was used to populate as many of the resources as possible. Generic heat-rate data were substituted for resources that were not included in this older data set. Additional study assumptions were made regarding the physical infrastructure, participant bidding behavior, and system loads:

- Resource expansions, retirements, and replacements reflect ISO/RTO expansion plans based on capacity markets and other “firm” plans for generation expansion.

- Dispatch costs are consistent with assumptions, such as fuel prices, heat rates, and emission-allowance dispatch adders.

- Transmission interface limits consistent with planning criteria were used for major interfaces that connect load bubbles or groups of load bubbles to allow energy to flow between them. The load-bubble grouping is similar to the approach used in other studies, such as resource adequacy studies.

- Load levels and profiles are based on 50/50 forecasts developed in 2009: the ISO New England RSP09 10-year forecast, the NYISO 2009 Load and Capacity Data Report, and the PJM 2009 load forecast report.

Additional study assumptions were made for fuel prices, allowance prices, and emission rates, all of which were reviewed by the PAC and IPSAC:

- Fuel-price forecast: The fuel-price forecast was based on DOE’s 2009 Annual Energy Outlook (AEO). The fuel prices (in 2007 dollars) were useful in establishing the base cases from which the relative impacts of each of the sensitivity cases could be determined.

- Allowance prices: The emission values were modeled in the dispatch cost. SO2 values were based on the assumptions used in the 2009 AEO energy forecast. NOX values were modeled for the ozone season and were based on early-year 2009 prices. These NOX values were applied only to resources in Connecticut, Massachusetts, New Hampshire, and Rhode Island. The CO2 emissions allowance price for all cases was assumed to be $10/ton.

- Emission rates: SO2 rates were based on the percentage of sulfur in the fuel currently used in a generating unit and any sulfur control technology at a plant. Most coal-fueled resources were assumed to have installed some form of scrubber control technology by 2012. CO2 rates were based on the fuel type and standard EPA conversion rates. NOX rates were based on a survey of emission data sources internal and external to the ISO.

### Simulation Metrics

The production cost simulation metrics provide a variety of results that summarize the economic performance of the system and the environmental emissions of generating units.

#### Production Simulation Metrics

The key metrics used to compare the cases are production cost and LSE electric energy expense. The absolute values of these metrics are not the focus of this analysis because the aim is to quantify relative changes. Values for Financial Transmission Rights (FTRs) and Auction Revenue Rights (ARRs) were also calculated (see Section 2.3).

The production cost metric is based on the summation of dispatch costs for each unit multiplied by the amount of electric energy produced. This calculation is performed for all New England resources used to serve customer demands. Production costs for resources located in external areas are not included in this metric.

LSE electric energy expense is calculated by taking the hourly marginal energy cost (e.g., the LMP) in an RSP area and multiplying it by the hourly load in that same RSP area. New England’s total LSE energy expense is the summation of each RSP area’s LSE energy expense, including the effects of congestion.

Within an import-constrained subarea, the one source of electric energy not paid the LMP, effectively, is a purchase brought into the congested subarea from an external subarea. The purchase of energy from an external subarea is modeled through a complex process that allows a certain amount of energy to flow into the constrained subarea and to be valued at essentially the selling area’s LMP. The rights associated with this transmission path are referred to as Financial Transmission Rights. A portion of the revenues associated with these FTRs may flow back to the LSEs as their share of the Auction Revenue Rights. Thus, a third metric is the “FTR/ARR” congestion estimate. FTR/ARR congestion values are equal to the product of the constrained interface flow and the price differential across the constrained interface.

The analysis did not include other costs that wholesale electricity customers would pay, such as Forward Capacity Market payments, ancillary service costs, Renewable Energy Certificates and Alternative Compliance Payments associated with Renewable Portfolio Standards (see Section 8.5), transmission costs, and other costs.

#### Environmental Metrics

The environmental metrics are the total tons of CO2, NOX, and SO2 emissions. While these are informative metrics, under cap-and-trade programs (regional and federal), the total number of tons emitted in the long term likely will equal the cap because the supply and demand for the allowances will affect the allowance prices and ensure that all the allowances will be used.

## Economic Study Requests, 2010

The following entities submitted requests for economic studies and presented their requests to the PAC on April 27, 2010.

The New England States Committee on Electricity (NESCOE) submitted a request for an economic study for a single year in the 20-year timeframe that would assume status quo market and reliability constructs. The study will assume existing state and federal energy and policy requirements, such as compliance with state Renewable Portfolio Standards, energy-efficiency goals, and the influence of the price of carbon. The request seeks to build on the results of the 2009 study and provide a baseline for the states to evaluate expansion scenarios that will be performed as part of the Eastern Interconnection Planning Collaborative (EIPC) initiative (see Section 11.1.2). The request includes two additional studies: (1) market-sourced replacement or repowering of older coal- and oil-fired generators, and (2) replacement of the same fossil units through the competitive procurement of renewable resources from New England, neighboring Canadian provinces, or both areas.

The New England Independent Transmission Company (NEITC) submitted a request for a study of a transmission line to enable renewable generation in the queue for northern New Hampshire to reach the regional market. The study seeks to quantify the production cost savings and congestion savings of adding 700 MW in Coos County, NH.

Sea Breeze Atlantic Regional Transmission System, whose cofounder, Boundless Energy, LLC, was one of the developers of the undersea New Jersey–Long Island Neptune transmission cable, submitted a request for an economic study of its proposed “NewSeaBos” submarine HVDC cable transmission project.

The ISO discussed the scope of work for new economic studies with the PAC and developed a final study plan, also discussed with the PAC. The scope of work examines several scenarios showing the effects of retiring coal and oil generating plants and replacing them with efficient natural-gas-fired generation, renewable resources, and imports from neighboring regions. The study also identifies the need for higher transmission transfer limits for each of the scenarios. The study is scheduled for completion by the end of 2010.

## Generic Capital Costs of New Resources

The actual capital costs of new resources may be highly variable because of a number of factors, including the following:

  - The state of technology development

  - Changes in the costs of materials, labor, and overhead

  - Specific site requirements

  - Geographic cost differences

  - Difficulties in obtaining site and technology approvals

As a complement to the economic studies, the ISO developed generic capital costs for new resources. The main focus was on those resource technologies in the ISO Interconnection Queue and participating in the FCM (see Sections 4.2 and 4.4). The ISO developed the generic estimates, with stakeholder input, on the basis of a limited review of recent reports and published information on resource costs, including actual projects and information provided by experts. The ISO also obtained information from the State of Connecticut’s RFPs in support of its Integrated Resource Plan (see Section 12.1.1).

The ISO analysis confirmed the approximate generic capital costs of generating units developed for the ISO’s 2007 Scenario Analysis Report. These costs were escalated to reflect 2010 costs. Demand-resource costs were determined using the costs of state and utility programs throughout New England. The ISO updated the generic capital cost estimates from the Scenario Analysis and included the costs of the Connecticut plan for comparison, as shown in Table 10-2. The estimates are similar except for the costs of wind resources. Recent construction experience in New England suggests a cost for wind generation ranging from $2,000/kW to approximately $3,400/kW, with an average about $2,600/kW.

Table 10-2
Generic Capital Cost Estimates for Generation and Demand Resources

| Generation Type(a) | Scenario Analysis for Generation and Demand-Resource Program Costs (2010 $/kW)(b) | CT Integrated Resource Plan(c) (2010 $/kW) |
| --- | --- | --- |
| Wind onshore | 1,600–2,140 | 2,000–2,550 |
| Wind offshore | 2,140–2,670 | 4,500–5,500 |
| Natural gas combined cycle (NGCC) | 850–1,070 | 906 |
| Combustion turbine | 530–750 | 576 |
| Biomass | 2,670–3,740 | 500–3,500 |
| Solar photovoltaic | 4,270–6,410 | 5,200–6,200 |
| Passive demand resources | 2,000–3,000 | 2,160 |
| Distributed resources (CHP) | 1,070–1,600 | Not provided |
| Distributed resources (fuel cells) | 3,740–4,270 | 3,500–4,600 |

(a) 	According to input from the PAC, generators in New England would not likely be able to develop resources that use nuclear or coal fuels.

(b) 	Scenario Analysis costs were in 2006 dollars and escalated to 2010 dollars by a GDP inflator (1.068).

(c) 	The Brattle Group, Connecticut Light and Power, and the United Illuminating Company, Integrated Resource Plan for Connecticut (January 1, 2010).

## Observations

This section provides an overview of the production costs and environmental results of the economic studies conducted in 2009, within New England and interregionally. Additional details and discussion of these simulations, assumptions, and results are documented in supplemental reports, as indicated.

The purpose of these studies is to “test” future resource supplies, transmission upgrades, and the effect of transmission constraints in a “what-if” context. While these studies do not identify specific Market Efficiency Transmission Upgrades (see Section 6.2.3.2), the results can be used to identify the need for additional targeted studies. Although the analyses are based on uncertain assumptions and thus provide only general trends for particular scenarios, the economic study results provide useful information to stakeholders and policymakers.

“The RSP shall also describe the coordination of the ISO’s regional system plans with regional, local and inter-area planning activities.” (Attachment K, Overview)

“The RSP shall be designed and implemented to: . . . (ii) identify facilities that are necessary to meet Planning and Reliability Criteria . . . (v) provide for coordination with existing transmission systems and with appropriate inter-area and local expansion plans . . .” (Attachment K, § 3.4)

“A Needs Assessment shall analyze whether the PTF in the New England Transmission System:  (i) meet applicable reliability standards; (ii) have adequate transfer capability to support local, regional, and inter-regional reliability . . .” (Attachment K, § 4.1)

“The regional system planning process shall be conducted and the annual RSP shall be developed in coordination with the similar plans of the surrounding ISOs/RTOs and Control Areas pursuant to the Northeastern ISO/RTO Planning Coordination Protocol and other agreements with neighboring systems and NPCC. Inter-area planning studies shall be conducted over as broad a region as feasible, including adjacent Canadian systems who are members of NPCC, or its successor organization, and, as appropriate, MAAC and Reliability First, or their successor organizations . . . ” (Attachment K, § 6.3)

Interregional Planning and Studies

The ISO is participating in numerous national and interregional planning activities with the U.S. Department of Energy, the Northeast Power Coordinating Council, and other balancing authority areas in the United States and Canada. The aim of these projects, as described in this section, is to ensure the coordination of planning efforts to enhance the widespread reliability of the interregional electric power system. The ISO also conducts studies with other entities within and outside the region and with neighboring areas to conduct production cost studies, to investigate the challenges to and possibilities for integrating renewable resources, and to address other common issues affecting the planning of the overall system.

The OATT Attachment K requires the ISO to identify and resolve interregional planning issues, as identified in Needs Assessments and Solution Studies.

## Studies of the Eastern Interconnection

The Energy Policy Act of 2005 (EPAct) (which among other things amends the Federal Power Act) requires the DOE and FERC to implement several reliability provisions. The requirements include ensuring the reliability of the transmission infrastructure by the establishment of National Interest Electric Transmission Corridors (NIETCs) and the implementation of enforceable reliability standards administered by the North American Electric Reliability Corporation.

### U.S. DOE Study of National Interest Electric Transmission Corridors

Based in part on the 2006 Congestion Study of the Eastern Interconnection, DOE designated the Mid-Atlantic Area National Corridor from south of the Washington, DC, area, to north of the area between Utica and Albany, New York. That corridor omits all areas of New England.

Section 216(h)(9)(C) of EPAct requires DOE to consult regularly with, among others, transmission organizations (i.e., ISOs, RTOs, independent transmission providers [TPs], or other FERC-approved transmission organizations). DOE was required to study the congestion of the U.S. electric power system and issued a December 2009 report. The report shows little congestion in New England, and DOE removed New England as “an area of concern.” According to DOE, this is the result of the successful development of resources and transmission facilities, where and when they are needed. As of April 2010, DOE did not designate new NIETCs. Further, a NIETC provision in the American Recovery and Reinvestment Act of 2009 (i.e., the federal economic stimulus bill), Section 409, requires an analysis of significant areas of renewable resources constrained by lack of access to adequate transmission capacity.

ISO New England and other planning authorities have participated in several DOE workshops on NIETCs. The ISO supported a DOE study of the Eastern Interconnection that showed that New England has less congestion than other areas of the country. The ISO will continue to monitor future DOE studies and coordinate activities with other ISOs and RTOs as well as policymakers and electric power industry stakeholders in New England.

### Eastern Interconnection Planning Collaborative

In August 2009, an agreement to form the Eastern Interconnection Planning Collaborative was implemented, for which 26 planning authorities in the Eastern Interconnection, representing over 95% of the Eastern Interconnection load, have now signed on. At the same time the EIPC was forming, DOE issued a Funding Opportunity Announcement (FOA) for analysis work for the Eastern Interconnection. The FOA funding was allocated to two categories—Topic A funding is for analysis work, and Topic B funding is providing grants for state participation. The EIPC submitted a proposal in fall 2009, and that December, DOE selected the EIPC to perform the work under Topic A. In response to the funding under Topic B, the states formed the Eastern Interconnection States Planning Council (EISPC) and submitted a proposal that DOE also selected.

The entire EIPC membership will support the Topic A analysis work, with eight of the 26 EIPC members taking on a role of principle investigator, which reflects a lead role in the contractual arrangements under the FOA. The EIPC has contracted with Charles River Associates to support the analysis work and with The Keystone Center to manage the stakeholder process.

The EIPC proposal was founded on the established planning expertise existing in the EIPC membership and will use the individual Regional System Plans as a basis for building an interconnection-wide model for the analysis work. The work in 2010 is focusing on developing the model in preparation for scenario analysis work and on the formation of the Stakeholder Steering Committee, which is required under the FOA to drive the inputs for the analysis work. The EIPC proposal calls for the analysis to be discussed in a final report to be issued by summer 2012. The Stakeholder Steering Committee was announced in July and will meet to agree on assumptions for inputs to the analysis, which is scheduled to begin in late 2010.

### Electric Reliability Organization Overview

The Federal Power Act directed FERC to establish one Electric Reliability Organization (ERO) with the statutory responsibilities to establish and enforce standards for the North American power system and periodically publish reliability reports. FERC designated the North American Electric Reliability Corporation as the ERO. As the RTO for New England, the ISO is charged with making sure its operations comply with applicable NERC standards. In addition, the ISO has participated in regional and interregional studies required for compliance.

Through its committee structure, NERC regularly publishes reports that assess the reliability of the North American electric power system. Annual long-term reliability assessments evaluate the future adequacy of the power system in the United States and Canada for a 10-year period. The reports project electricity supply and demand, evaluate resource and transmission system adequacy, and discuss key issues and trends that could affect reliability. Summer and winter assessments evaluate the adequacy of electricity supplies in the United States and Canada for the upcoming summer and winter peak-demand periods. Special regional, interregional, or interconnection-wide assessments are conducted as needed.

## Interregional Coordination

The ISO is participating in the ISO/RTO Council, an association of the North American Independent System Operators and Regional Transmission Organizations. The ISO also is actively participating in NPCC interregional planning activities, the Joint ISO/RTO Planning Committee (JIPC), and a number of other activities designed to reduce seams issues with other ISOs and RTOs.

### IRC Activities

Created in April 2003, the ISO/RTO Council is an industry group consisting of the 10 functioning ISOs and RTOs in North America. These ISOs and RTOs serve two-thirds of the electricity customers in the United States and more than 50% of Canada’s population. The IRC works collaboratively to develop effective processes, tools, and standard methods for improving competitive electricity markets across North America. In fulfilling this mission, the IRC balances reliability considerations with market practices that encourage the addition of needed resources. As a result, each ISO/RTO manages efficient, robust markets that provide competitive and reliable electricity service, consistent with its individual market and reliability criteria.

While the IRC members have different authorities, they have many planning responsibilities in common because of their similar missions to independently and fairly administer an open, transparent planning process consistent with established FERC policy. As part of the ISO/RTO authorization to operate, each ISO/RTO has led an open, transparent planning effort among its participants. In addition, with the implementation of Order No. 890, ISOs/RTOs have upgraded their planning processes to meet FERC’s objectives. Specifically, the transmission planning process must provide for coordination, openness, transparency, information exchange, comparability, dispute resolution, regional coordination, economic planning studies, and cost allocation (see Section 2.1). This ensures a level playing field for infrastructure development efficiently driven by competition and meeting all reliability requirements.

The IRC has coordinated filings with FERC on many issues, such as those concerning the administration of the ISO’s Generator Interconnection Queue and other technical issues. For example, the IRC has identified issues and is acting to address the challenges of integrating demand resources and wind generation and, through its representatives, is leveraging the efforts of NERC’s Integrating Variable Generation Task Force (see Sections 9.1.2 and 9.3.1.1). The IRC has representation on other NERC task forces and committees.

In response to a FERC request, the IRC is preparing a report summarizing the performance metrics the ISOs and RTOs use for compliance with national and regional reliability standards, market administration and performance, and organizational effectiveness.

### Northeast Power Coordinating Council

The Northeast Power Coordinating Council is one of eight regional entities located throughout the United States, Canada, and portions of Mexico responsible for enhancing and promoting the reliable and efficient operation of the interconnected power system. The NPCC’s geographic area is northeastern North America and includes New York, the six New England states, Ontario, Québec, and the Maritime provinces in Canada. Pursuant to separate agreements NPCC has with its members and NERC and by a Memorandum of Understanding with the applicable Canadian authorities, the NPCC provides the following activities and services to its geographic area:

Statutory activities—develop regional reliability standards; assess compliance with and enforce these standards; coordinate system planning, design, and operation; and assess reliability

Nonstatutory criteria services—establish regionally specific criteria and monitor and enforce compliance with these criteria

ISO New England plans and operates the New England system in compliance with NPCC criteria, standards, guidelines, and procedures. The ISO also participates in NPCC interregional studies and planning initiatives.

#### NPCC Criteria and NERC Standards

To meet all reliability objectives for the Northeast, the NPCC criteria must be at least as stringent as the NERC requirements. The NPCC membership currently is bound through the execution of the NPCC Membership Agreement to adhere to these criteria, and ISO New England also includes, by reference, NPCC criteria in its governing documents (e.g., Transmission Operating Agreement). In addition, NERC has delegated to NPCC the authority to create regional standards to enhance the reliability of the international interconnected power system in northeastern North America.

The NPCC enforces the ISO’s compliance with NPCC criteria. Using NERC’s Uniform Compliance Monitoring and Enforcement Program, the NPCC also assesses and enforces the ISO’s compliance with NERC’s reliability standards. Additionally, the NPCC monitors and enforces registered entities’ (e.g., generator owners, transmission owners, and load-serving entities) compliance with NERC standards within New England. This includes the need for system protection and other equipment upgrades required of power system facilities.

#### Coordinated Planning

The NPCC initiates studies of its geographic areas and coordinates member-system plans to facilitate interregional improvements to reliability. The NPCC also evaluates its areas’ assessments, resource reviews, and interim and comprehensive transmission system reviews. The NPCC conducts short-term assessments to ensure that developments in one region do not have significant adverse effects on other regions. As a member of NPCC, ISO New England fully participates in NPCC-coordinated interregional studies with its neighboring areas.

### Northeastern ISO/RTO Planning Coordination Protocol

ISO New England, NYISO, and PJM follow a planning protocol to enhance the coordination of planning activities and address planning seams issues among the interregional balancing authority areas. Hydro-Québec TransÉnergie, the Independent Electric System Operator (IESO) of Ontario, the New Brunswick System Operator (NBSO), and New Brunswick Power participate on a limited basis to share data and information. The key elements of the protocol are to establish procedures that accomplish the following tasks:

Exchange data and information to ensure the proper coordination of databases and planning models for both individual and joint planning activities conducted by all parties

Coordinate interconnection requests likely to have cross-border impacts

Analyze firm transmission service requests likely to have cross-border impacts

Develop the Northeast Coordinated System Plan

Allocate the costs associated with projects having cross-border impacts consistent with each party’s tariff and applicable federal or provincial regulatory policy

To implement the protocol, the group formed the Joint ISO/RTO Planning Committee and the Inter-Area Planning Stakeholder Advisory Committee open stakeholder group. Through the open stakeholder process, the JIPC has addressed several interregional, balancing authority area issues. The Northeast Coordinated System Plan summarizes completed and ongoing work activities conducted by the JIPC:

The study of transmission upgrades, including improvements in the Plattsburgh, NY–VT area

The coordination of interconnection queue studies and transmission improvements to ensure reliable interregional planning

Cross-border transmission security issues, including the consideration of loss-of-source (LOS) contingencies in New England

Studies aimed at investigating generator-deliverability and load-deliverability issues

Market efficiency analyses, reflecting coordinated models of the three ISO/RTOs and neighboring regions

Reporting on the effects of environmental regulations, including the integration of wind and other renewable resources, as well as the effect of demand-side resources on interregional operations and planning

The JIPC recognizes the need for further work based on input from the IPSAC. Future plans call for conducting additional interregional economic analyses that may identify potential transmission bottlenecks and trigger the need for transmission planning analyses. In addition, cross-border transmission cost allocation discussions are planned for NYISO and PJM. The ISO and its stakeholders are participating in these discussions for informational purposes. The ISO has not received a request to change the OATT and would only do so through the normal regional stakeholder process before engaging with entities outside New England. The need for these discussions would likely be triggered by the need for specific interregional projects or a new order issued by FERC. The ISO/RTOs regularly report on the status of seams issues including the schedules for addressing the cross-border planning issues.

## Summary of Interregional Planning

ISO New England’s planning activities are closely coordinated with neighboring systems and across the Eastern Interconnection. The ISO has achieved full compliance with all required planning standards and has successfully implemented the northeastern ISO/RTO Planning Protocol, which has further improved interregional planning among neighboring areas. Sharing capacity resources with other systems, particularly to meet environmental emission requirements, will likely become increasingly necessary. Thus, identifying the potential impacts that proposed resources and transmission projects could have on both New England and neighboring systems is beneficial to support the reliable and economic performance of the overall system.

# State, Regional and Federal Initiatives

“In addition, the RSP shall also provide information on a broad variety of power system requirements that serves as input for reviewing the design of the markets and the overall economic performance of the system.” (Attachment K, Overview)

“The ISO shall reflect proposed market responses in the regional system planning process . . . Specifically, the ISO shall incorporate or update information regarding resources in Needs Assessments that have been proposed and (i) have cleared in a Forward Capacity Auction pursuant to Market Rule 1 of the ISO Tariff, (ii) have been selected in, and are contractually bound by, a state-sponsored Request for Proposals . . .” (Attachment K,  § 4.2(a))

State, regional, and federal initiatives and policies have a significant impact on the electricity markets, specifically influencing the timing, type, and location of resources and transmission infrastructure developed to meet system needs. The New England states have continually worked together to identify, discuss and work on energy issues of common interest. Even with this history of cooperation, each state has a unique set of energy policy objectives and goals. This section presents recently implemented laws, policies, and initiatives that affect regional system planning.

## State Initiatives, Activities, and Policies

Over the past few years, the New England states have implemented numerous energy policies and initiatives. Though each state is unique, the states have consistently focused on policies and initiatives that advance energy efficiency, increase the development of renewable resources, and reduce pollutants from certain generating facilities.

### Connecticut

In August 2010, the Connecticut Department of Public Utility Control approved the second Integrated Resource Plan developed by the state’s electric utilities and the Connecticut Energy Advisory Board pursuant to legislation passed in 2007. The DPUC determined that Connecticut meets regional reliability requirements and will have sufficient resources during the plan’s 10-year planning horizon; thus, it should not procure additional resources at this time. However, the integrated resource planning process is considering near-term options for additional investment in demand-side management and long-term options for developing nuclear power in the region as an overall strategy to promote non-carbon-emitting resources. The state’s utilities are required to submit plans biennially to the Connecticut Energy Advisory Board (CEAB).

In recent years, Connecticut has issued several RFPs for providing financial incentives for the development of capacity and peaking resources in the state, which requires these resources to participate in the New England wholesale electricity market. This participation has contributed to the large amount of generating resources clearing in the FCM in Connecticut (see Section 4.2.2).

### Maine

Over the past few years, Maine has established aggressive wind generation goals for the state:

- 2,000 MW of installed capacity by 2015

- 3,000 MW  of installed capacity by 2020, including 300 MW or more from offshore generation

- 8,000 MW of installed capacity by 2030, including 5,000 MW from generation facilities located offshore

In 2006, the MPUC was given the authority to direct electric utilities to enter into long-term electric generation contracts to bring benefits to Maine ratepayers by providing, among other things, renewable capacity and energy fuel diversity. Last year, the Maine PUC approved a long-term contract. The contract is for electric energy and capacity from an in-state wind project for a 20-year term. Similarly, legislation was passed in 2010 that provides the Maine PUC with the ability to direct one or more electric utilities to enter into a contract of up to 20 years for the installed capacity, associated renewable energy, and renewable energy credits of one or more deep-water offshore wind energy pilot projects or tidal energy demonstration projects.

Earlier this year, Efficiency Maine Trust released the Triennial Plan of the Efficiency Maine Trust 2011–2013. This three-year plan is designed to help Maine’s consumers save energy and money, meet environmental goals, and stimulate the state’s economy. To achieve these objectives, EMT plans to launch a public-awareness campaign for energy conservation; provide incentives for consumers to use energy-efficient devices; promote renewable energy heating options, such as biomass instead of heating oil; and continue to support customer-side wind and solar facilities. The plan’s goal is to achieve the following:

- 3.3 trillion Btu of annual energy savings starting in 2013

- A better than 4:1 benefit-to-cost ratio for dollars invested by the EMT

- Reductions in nearly 300,000 tons of carbon dioxide by 2013

- $840 million in energy saving to consumers

### Massachusetts

Pursuant to the 2008 Green Communities Act, electricity distribution companies in the state are required to develop three-year plans that promote energy efficiency. These plans were filed with the Massachusetts DPU in 2009 and were approved in early 2010. The plans call for the investment of $1.2 billion in efficiency measures over three years, with funding coming from system benefit and energy-efficiency charges on ratepayer bills, RGGI allowances, FCM revenues, and other funding sources. Collectively, the utilities’ annual energy-efficiency goals amount to a total statewide savings goal of 2,649,000 MWh for 2010 to 2012. The three-year programs are intended to reduce peak electricity demand by more than 400 MW and reduce greenhouse gas emissions by nearly 15 million tons.

In June 2009, the Massachusetts DPU adopted amended net-metering rules, and in August 2009, it issued its model net-metering tariff and the net-metering tariffs for the state's investor-owned utilities, which became effective in December 2009. The state's investor-owned utilities must offer net metering, but municipal utilities are not obligated to do so. The aggregate capacity for all four utilities for net metering is limited to 1% of each utility’s peak load, or 110 MW total.  As of August 2010, the state had 32.3 MW of net metering, which reduces the state’s energy consumption.

In June 2010, the DPU issued an order adopting emergency regulations reversing a rule that state utilities sign long-term renewable energy contracts only with in-state generators. As part of the Green Communities Act, utilities were required to seek long-term contracts twice in five years from projects within the state to finance the development of renewable energy generation. However, because of a legal challenge claiming the in-state rule violated the Commerce Clause of the U.S. Constitution by discriminating against out-of-state developers, the DPU opened the RFP to bids coming from outside the state’s borders.

Since 2002, biomass technology for generating electricity has qualified for incentives under the Massachusetts Renewable Portfolio Standard. However, in December 2009, the Department of Energy Resources suspended new biomass facilities from qualifying for the RPS, pending results of a study of greenhouse gas impacts. Under the Global Warming Solutions Act, Massachusetts is required to reduce greenhouse gas emissions across the economy 80% by 2050. In June 2010, the DOER released the Biomass Sustainability and Carbon Policy Study, which found that the use of biomass for heating and CHP facilities would result in a 25% reduction in greenhouse gas emissions in 2050 relative to oil, but biomass-fired electricity would result in 3% increase in emissions over coal-fired electricity in 2050. As a result of these findings, DOER will hold public meetings and conduct a policymaking process to discuss potential changes to the state RPS and other policy options concerning biomass and greenhouse gas impacts.

Massachusetts also has a goal to develop 2,000 MW of wind power by 2020.

### New Hampshire

In 2008, Governor Lynch signed legislation forming the North Country Transmission Commission, which urged transmission upgrades to facilitate the development of renewable projects in northern New Hampshire. Last year, the governor signed into law legislation that allows the North Country Transmission Commission to develop a proposal to upgrade the transmission system in northernmost New Hampshire. In April 2010, a consultant was selected to help develop recommendations that will form the basis for an action plan to pay for upgrading the transmission system. The plan anticipates the integration of an additional 400 MW of new renewable energy generation on the Coos Loop. This plan is to be completed by the end of 2010.

### Rhode Island

In recent years, Rhode Island has set aggressive renewable energy goals, such as deriving 15% of the state’s energy from wind. To achieve this goal, the state signed a joint development agreement with Deepwater Wind to construct and operate two offshore wind farms. In late 2009, National Grid signed a 20-year Power Purchase Agreement (PPA) with Deep Water that calls for the utility to purchase the energy generated from the smaller of the two proposed offshore wind farms at a cost of 24.4¢/kWh in the first full year of operation (expected in 2013), and escalating 3.5% per year thereafter.

On March 30, 2010, the Rhode Island Public Utilities Commission rejected the PPA for what it determined was too high a price for the energy output from the proposed wind facility. The PUC also determined that the proposed project—according to long-term contracting standards set in statute—was not “commercially reasonable.”

Pursuant to enacted legislation requiring National Grid and Deepwater Wind to amend the original PPA to result in lower prices, a revised agreement was filed with the PUC on June 30, 2010. Although the new PPA includes the same starting price of 24.4¢/kWh, it includes provisions that allow the price to be reduced if project costs are lower than originally estimated. In deciding whether or not to approve the amended PPA, the PUC must determine whether it is “commercially reasonable” and also consider the positive effects of the project on economic development and the potential environmental benefits.

### Vermont

The U.S. Nuclear Regulatory Commission (NRC) has direct jurisdiction over radiological safety at Vermont Yankee (VY) nuclear power plant, whose existing permit is set to expire in 2012. The NRC staff gave preliminary approval to Vermont Yankee’s request to extend its license for 20 years, but it is uncertain when the NRC will make its final determination. On March 23, 2009, the NRC announced that it will delay indefinitely its final decision on the relicensing of VY. Vermont law currently states that no nuclear plant will be relicensed until the Vermont general assembly approves and determines that the operation of the plant will promote the general welfare. In 2009, the Vermont Senate rejected legislation that would have determined that the continued operation of VY promotes the state’s general welfare. As of the completion of the 2010 Vermont legislative session, the full legislature also had not determined that the operation of Vermont Yankee promotes the general welfare.

In 2009, VELCO was awarded almost $69 million from the DOE for a smart grid project designed to expand the deployment of Vermont smart meters from the current 28,000 to 300,000.

Earlier this year, Vermont’s two largest utilities, Green Mountain Power and Central Vermont Public Service, signed a Memorandum of Understanding with Hydro-Québec (HQ) for a new power supply contract beginning in 2012 and ending in 2038. The agreement includes a price-smoothing mechanism that will shield customers from market fluctuations. One of the key provisions of the agreement calls for the Vermont legislature to enact legislation to designate large hydroelectric facilities, which would include HQ power, as renewable resources. The legislature passed, and the governor signed into a law, a bill that allows large-scale hydro facilities to be considered renewable resources.

## Regional Initiatives

Several regional initiatives that seek to improve the regional energy markets, coordinate regional studies, and enhance resource adequacy and system planning currently are taking place or have recently concluded. Entities in the New England states are also actively pursuing smart grid projects.

### Coordination among the New England States

The six New England states are actively involved in the ISO’s regional planning process individually and through the New England States Committee on Electricity. NESCOE serves as a forum for representatives from the states to participate in the ISO's decision-making processes, including those dealing with resource adequacy and system planning and expansion issues. In addition to NESCOE, the ISO works collaboratively with the state consumer advocates, the New England Conference of Public Utilities Commissioners (NECPUC), and the New England Governors’ Conference (NEGC) and their representatives.

The New England states have become active participants in the creation of interconnection-wide planning for the Eastern Interconnection. The Eastern Interconnection States Planning Council (EISPC) is an organization of states in the Eastern Interconnection, including representatives from New England, responsible for participating with the planning authorities that are part of the Eastern Interconnection Planning Collaborative (see Section 11.1.2). ISO New England, NESCOE, and NEPOOL work closely to coordinate New England’s participation in all EISPC and EIPC activities.

### Regional Policy Development

The ISO’s 2009 New England 2030 Power System Study provided the technical analysis and information necessary for the governors and stakeholders to consider renewable resource options, their estimated costs, and potential outcomes (see Section 10.1). This study is a complement to the Governors’ Renewable Energy Blueprint, which identifies regulatory mechanisms available to advance renewable resource development in New England, including the potential for the states to synchronize their power procurement and long-term power contract activities and to coordinate siting reviews of proposed interstate transmission facilities. The report is not a final determination on the issue of coordinated procurement and emphasizes that an important next step is consultation with the region’s stakeholders to receive input on the report.

The blueprint emphasizes the need for a partnership between the federal government and the New England states to facilitate the delivery of low-carbon, secure, cost-effective sources of electricity to New England consumers that would help meet state and federal policy objectives.

Building on the 2009 New England 2030 Power System Study and the New England Governors’ Regional Blueprint, NESCOE submitted a request of the ISO for an economic study in 2010. NESCOE’s study request seeks to develop a baseline for the states to evaluate renewable power expansion scenarios for the region (See Section 10.3)

In September 2009, the NEGC adopted a resolution identifying the vast potential for cost-effective renewable resources, particularly wind power. The NEGC resolution directs state regulators and policymakers to support the development of New England’s renewable resources and to consider potential mechanisms for coordinating the procurement of renewable resources. The NEGC also adopted a similar resolution jointly with the eastern Canadian premiers, initiating a dialogue between the states and provinces to consider potential terms and conditions for regional procurement and a sample regional RFP. The joint resolution pledges cooperation by both regions to enhance opportunities for the development of cost-effective renewable resources. It also directs the New England states to explore opportunities to coordinate state siting for interstate transmission. The governors and premiers also adopted resolutions on climate change and energy efficiency at the 33rd Annual Conference of the New England Governors and Eastern Canadian Premiers (NEG/ECP).

The states formed a Renewable Procurement Work Group (RPWG) to meet the directives of the 2009 resolutions. The working group includes state representatives from across New England who oversee current competitive power procurement processes or who administer such procurement, as well as NESCOE managers and staff, state energy policy officials, and staff of the New England Governors' Conference. The RPWG is examining the Renewable Portfolio Standards for each of the states, including the eligibility of resources across the region and the timing of power procurement, to identify opportunities to coordinate such procurement.

At the 34th Annual Conference of the NEG/ECP, NESCOE submitted a report to the New England Governors summarizing the work of the RPWG on coordinating the procurement of renewable resources. The report assesses power procurement practices, contract authority, and renewable resource eligibility across the six states. It also looks at the general terms and conditions that may be applicable for developing regionwide procurement options and processes. Additionally, the report identifies obstacles that may be encountered in pursuing coordinated procurement, as well as potential solutions, and introduces the idea of a model regional RFP for renewable resources. To enable the broadest set of resources to be considered, the contract length, resource types, and pricing structure of such an RFP would need to be flexible. The report emphasizes that the primary objective in coordinating the procurement and development of renewable resources is to select the most cost-effective renewable resources for consumers in areas with competitive markets and processes. At the conference, the governors and premiers also adopted resolutions on energy efficiency and solar power.

### Forward Capacity Market Updates

FERC has set for paper hearing proposed changes to the FCM, which address several issues, including the Alternative Price Rule, the modeling of capacity zones, and the proper value of the cost of new entry. The first brief was filed with FERC on July 1, 2010, and the second brief was filed with FERC on September 1, 2010.

### Price-Responsive Demand

The ISO has initiated work with NEPOOL stakeholders and state utility regulators to develop a policy and program design for future price-responsive demand programs. As part of this effort, the ISO will provide information and support to the New England states, as available resources permit, and will participate in forums and proceedings on dynamic retail pricing as requested by state public utility regulators.

### Consumer Liaison Group

In early 2009, the ISO initiated the RTO Responsiveness and Governance Working Group to address ISO’s responsiveness to stakeholders and customers. One of the major themes that came from the RTO Responsiveness and Governance Working Group was a desire by consumers for the ISO to provide greater transparency about the impacts of ISO activities on consumer costs. In response to this, the ISO and stakeholders created the Consumer Liaison Group (CLG).

The CLG was established to create a forum for the flow of information between the ISO and New England’s electricity users. Among other things, the benefit of the CLG is that consumers and their representatives gain a better understanding of ISO initiatives, market developments, and cost impacts associated with major initiatives. The CLG also allows the ISO to gain a better understanding of consumer interests and concerns.

The CLG, which first met in July 2009 and held two subsequent meetings that year, is scheduled to meet four times in 2010. At these meetings and with the guidance of the CLG Coordinating Committee, CLG members identified and discussed important consumer issues, established a governance structure to guide the group, and refined CLG objectives to ensure that the group meets the informational needs of consumers. Significant time was allotted at the first three meetings to discuss transmission investment, wholesale electricity market pricing, and the components of wholesale and retails costs.

FERC Commissioner Philip Moeller was a special guest at the CLG’s December 2009 meeting. Paul Hibbard, the then Chairman of the Massachusetts Department of Public Utilities, and Mary Healey, Consumer Counsel for the State of Connecticut and President of the National Association of State Utility Consumer Advocates, presented at the February and May 2010 meetings, respectively.

On July 30, 2010, the ISO released its report about the CLG, which summarizes the goals and structure of the CLG, 2009 CLG activities, major ISO activities and initiatives from 2009, and goals for the CLG in 2010.

### Regional Smart Grid Projects

As discussed in Section 9.1, the ISO is implementing several smart grid projects, including one involving the expansion of phasor measurement units. Towns, businesses, and utilities in New England also are actively pursuing and conducting smart grid projects and were selected to receive approximately $225 million total in DOE smart grid investment grants. Other DOE Smart Grid Investment Grant awards in New England are as follows:

- Connecticut—Connecticut Municipal Electric Energy Cooperative was awarded $9 million to build a regional smart meter network including five municipal utilities and at least 13,000 time-varying meters that will allow customers to control their electricity use.

- Maine—Central Maine Power Company was awarded approximately $96 million to install 650,000 smart meters for all its customers.

- Massachusetts—

  - Honeywell International was awarded $11.4 million to provide automated peak-pricing response for almost 700 commercial and industrial (C&I) customers.

  - NSTAR was awarded $10.1 million to expand capabilities to allow for “self-healing” to reduce system outages.

  - The Town of Danvers was awarded $8.5 million to deploy 12,000 smart meters, upgrade cybersecurity, and automate outage management.

  - Marblehead Municipal Light was awarded $1.3 million to install 10,000 smart meters and develop a pilot program for real-time price and load management.

  - Vineyard Energy Project was awarded $0.8 million to deploy a range of technologies.

- New Hampshire—The New Hampshire Electric Cooperative was awarded $15.8 million to install 75,000 smart meters that will use two-way communications to help reduce energy use.

- Vermont—VELCO was awarded $68.9 million to expand the deployment of smart meters from the current 28,000 to 300,000.

## ISO Initiatives

Each year, the ISO engages in numerous energy-related initiatives with regional stakeholders. Recent ISO initiatives are detailed below.

### Project Cost Estimation and Controls Working Group

To address concerns about transmission project cost estimates and cost overruns, in late 2008, the ISO, NECPUC, and the region’s transmission owners established the Project Cost Estimation and Controls Working Group. The group was formed to develop recommendations leading to more consistent and transparent estimates for proposed transmission projects.

As a result of this stakeholder working group, the Project Cost Estimating Guidelines were established and incorporated as Attachment D into ISO Planning Procedure No. 4 (PP 4), Procedure for Pool Supported PTF Cost Review. These guidelines were developed for a number of reasons:

- Provide consistent cost engineering terms and definitions

- Provide a standardized approach to cost estimating in the region

- Improve the ability of the region’s transmission owners to provide common estimates

- Increase project cost transparency

- Provide regular information about the transmission investments made in the region and their impact on rates

“The RSP shall, among other things . . . (iii) specify the physical characteristics of the physical solutions that can meet the needs defined in the Needs Assessments and include information on market responses that can address them; (iv) provide sufficient information to allow Market Participants to assess the quantity, general locations, operating characteristics and required availability criteria of the type of incremental supply or demand-side resources, or merchant transmission projects, that would satisfy the identified needs or that may serve to modify, offset or defer proposed regulated transmission upgrades.” (Attachment K, § 3.1)

A workshop was held in January 2010, further instructing transmission owners on how to use the templates included in the guidelines and suggesting ways to report their costs periodically as a project moves through its lifecycle.

Further revisions to the guidelines and PP 4 were implemented in 2010 to provide greater consistency among transmission owners and to improve cost reporting. The costs of large, complex projects using the guideline templates have been discussed and reviewed at several PAC meetings in 2010. To date, all transmission owners have used these templates to report to the PAC on the costs associated with nine projects.

### RSP Planning Process Updates

The ISO and stakeholders discussed the regional planning process at the March 8, 2010, PAC meeting. While generally satisfied with the current planning process, stakeholders provided many comments. One suggestion was for the ISO to consider state energy-efficiency program goals more fully when identifying long-term resource adequacy and transmission system needs. Another suggestion was to provide additional information on nontransmission alternatives (NTAs) as a supplement to Needs Assessments, which currently provide critical load levels.

Stakeholders also have requested an examination of the continued degradation of the regional load factor. The possible retirement of aging, environmentally challenged generating units is another factor some stakeholders wish to be considered as part of the transmission planning process. These issues and changes in processes will be discussed with the PAC and other stakeholder groups as required.

In early 2009, the ISO set up an informal working group, the Regional Energy-Efficiency Initiative (REEI), to collect information about state and utility energy-efficiency programs and initiatives, to improve its understanding of the long-run impact of energy-efficiency programs, and to develop the most complete data set possible to serve as a resource for future analysis. In general, the states are eager to have the ISO’s planning process more fully reflect their investments in energy-efficiency programs (see Section 8.4).

Because Needs Assessments must comply with reliability requirements, the ISO and its stakeholders must understand several technical issues before fully considering the state energy-efficiency goals as inputs to the planning process, most notably, the process for establishing and modifying the load forecast. Three of these issues are the realization rate, which is the percentage of actual savings achieved compared with the planned savings; the elimination of the double accounting of energy-efficiency savings with FCM resources; and the expected future success rates of the programs. Plans call for the ISO convening the PAC to discuss these and other issues. On the basis of this discussion and related analysis, the ISO and regional stakeholders will then determine how the state energy-efficiency programs may serve as inputs into the planning process.

RSP10 provides considerable information on NTAs that can meet system needs. This includes general quantities and locations for meeting resource adequacy and operating reserve requirements (see Sections 4 and 5). In addition, RSP provides information on fuel diversity and environmental issues as well as those associated with planning new technologies (Sections 7, 8, and 9). The RSP also summarizes how the need for major transmission improvements would change for various changes in supply and demand resource expansions and retirements, including the redevelopment of “brownfield” sites (Section 10). Finally, RSP discusses transmission system needs, ranging from those of relatively small load pockets through the interregional system (Section 6 and Section 11). In accordance with ISO procedures for administering FCM and transmission planning studies, RSP10 gives full consideration to resources with state contracts, such as those participating in state RFP processes.

With due consideration of Critical Energy Infrastructure Information and Information Policy restrictions, power system planning professionals currently can use detailed information posted in reports and obtain technical databases for conducting their own analyses. This information includes critical load levels, key contingencies, and their system response. While this information assists market participants and the states in developing nontransmission alternatives, it is the ISO’s goal to include additional information on NTAs in future RSPs that can be more readily understood by nontechnical audiences.

Although the existing planning process has served the region well, the ISO will examine ways to improve the process and provide additional information to stakeholders. Detailed system analyses, showing the amounts and locations of hypothetical resources that would relieve transmission constraints, and the identification of critical load levels have been identified as useful information. Plans call for holding discussions with the PAC as the best means of deciding which information would be of greatest use to stakeholders. Stakeholder requests for process changes necessitating modifications to the OATT could only be considered through the usual stakeholder processes and approvals that are outside the PAC’s responsibilities.

## Federal Initiatives

On June 17, 2010, FERC issued a Notice of Proposed Rulemaking (NOPR) proposing to build on its Order No. 890 open-access transmission reforms to create a closer link between regional electricity transmission planning processes and cost allocation to help ensure that needed transmission facilities actually are built. 

According to FERC, the NOPR is based on three years of monitoring the implementation of Order No. 890, assessing information from three regional technical conferences, and examining more than 150 sets of comments filed in response to an October 2009 Request for Comment on Transmission Planning and Cost Allocation. In the NOPR, FERC seeks comments on the following proposed requirements:

- Transmission providers must identify and establish cost allocation methods for beneficiaries of new transmission facilities to establish a closer link between cost allocation and regional transmission planning.

- Transmission planning must account for system needs driven by public policy requirements established by state or federal laws or regulations, such as Renewable Portfolio Standards.

- Neighboring transmission planning regions must improve their coordination with each other regarding proposed facilities within or interconnecting two adjacent regions that could address transmission needs more efficiently than separately planned intraregional facilities.

- Provisions that give an undue advantage to an incumbent developer must be removed from FERC-approved tariffs or agreements so that sponsors of transmission projects have the right, consistent with state or local laws or regulations, to build and own facilities selected for inclusion in regional transmission plans.

A significant aspect of the NOPR is that public policy requirements, such as state-mandated Renewable Portfolio Standards, may be taken into account in transmission planning.

The ISO submitted comments to FERC on the NOPR on September 29, 2010.Additionally, the ISO submitted comments to FERC as part of the ISO/RTO Council.

Several other federal bills are under consideration to address greenhouse gas emissions, renewable energy standards, and FERC authority to site transmission. The ISO and its regional stakeholders will continue monitoring these legislative activities and update planning studies and processes as may be required.

## Summary of Regional Initiatives

The ISO works with a wide variety of state policymakers and other regional stakeholders through its planning process. Economic studies provide information to stakeholders, especially policymakers who have established state goals for promoting the use of renewable and energy-efficiency resources. Several other state initiatives, such as the use of power purchase agreements and RFPs, have influenced the region’s resource mix through the expansion of resources.

While regional initiatives, such as the formation of the CLG and the improved transparency of transmission cost estimates, have enhanced the planning process, the ISO continues to work with stakeholders to make further improvements to the planning process and the RSP. Two of these major initiatives are the consideration of the use of state energy-efficiency goals and the provision of additional information on nontransmisison alternatives meeting system needs.

The FERC NOPR on the planning process and federal legislative activities will likely affect the New England planning process as well.

# Conclusions and Key Findings

The ISO’s 2010 Regional System Plan discusses several major results of interest to the region’s stakeholders. Success of the Forward Capacity Market and the locational Forward Reserve Market and other factors have resulted in the development of generation and demand resources expected to meet the capacity needs of the New England region over the 10-year planning horizon, assuming no major resource retirements. The economic recession has slowed the growth in summer peak load levels, and RSP10 shows an expected delay of the peaks anticipated in RSP09 by one-and-one-half to two years. While the region has been successful in building needed transmission, the lower load levels and the development of resources where and when they are needed may delay the need for selected transmission projects. The region will continue to depend on natural gas for approximately 40% of its electric energy, but the ISO, regional stakeholders, and the natural gas industry have taken measures to improve the reliability of gas plants and the diversity of the gas supply resources.

Environmental initiatives, such as the Regional Greenhouse Gas Initiative and Renewable Portfolio Standards, are encouraging the development of clean, renewable resources in the region. As a result of economic incentives provided by the wholesale power markets and state policies, wind plants in New England are anticipated to see large growth, and demand resources and energy efficiency are expected to increase. New England has a long history of integrating new technologies into the system, and smart grid improvements are being developed to improve the electric power system’s performance and operating flexibility. Economic studies have shown the effects of scenarios that increase renewable resources and demand resources in the region and imports from Canada. These studies have helped provide guidance to policymakers and developers of supply and demand resources and merchant transmission.

The transmission system in New England has evolved significantly over the past several years. From 2002 through 2010, over 300 transmission projects will have been placed in service, and a number are under construction or well into the siting process. Along with the reliability improvements they bring to the system, these transmission upgrades support market efficiency, and the region has seen a significant reduction in congestion costs and other out-of-merit charges, such as second-contingency and voltage-control payments. According to DOE, because of the region’s successful “multi-faceted approach” that has spurred investment in new supply- and demand-side resources, as well as planning and development of extensive transmission upgrades, the system currently experiences little system congestion, and it has removed New England as “an area of concern” for the identification of National Interest Electric Transmission Corridors. Additionally, merchant transmission facilities are in various stages of development in the region and have the potential to provide access to renewable resources in remote areas of New England and neighboring regions.

## RSP Tariff Requirements

Attachment K of the OATT specifies that the RSP must discuss the assessment of the system needs of the pool transmission facilities, the results of such assessments, and projected transmission system improvements. The RSP also must identify the projected annual and peak demands for electric energy for a five- to 10-year horizon, the needs for resources over this period, and how such resources are expected to be provided. Additionally, the RSP must include sufficient information to allow market participants, including merchant transmission project developers, to assess several factors to assist them in meeting identified system needs or to modify, offset, or defer proposed regulated transmission upgrades. These factors include the quantity, general locations, operating characteristics, and required availability criteria of incremental supply- and demand-side resources.

As required by the tariff, the ISO works closely with the region’s stakeholders through an open and transparent process. In particular, members of the PAC advise the ISO on the scope of work, assumptions, and draft results for the RSP and supporting studies. These studies include Needs Assessments and Solution Studies. Stakeholders can use this detailed information and conduct independent studies using databases available from the ISO to better identify specific locations for market resource development and merchant transmission as alternatives to regulated transmission solutions.

As part of the planning process, the ISO approves transmission projects to meet identified system needs, for which resource alternatives and merchant transmission are insufficient. The transmission projects are included in the ISO’s RSP Project List.

The ISO has continually met all the requirements of Attachment K of the OATT.

## RSP10 Outlook

RS10 draws the following conclusions about the outlook for New England’s electric power system over the next 10 years:

Forecasts for the Annual and Peak Use of Electric Energy—The RSP10 10-year forecast for electric energy demand is lower than the RSP09 forecast, indicating a 0.9% average growth rate in the annual use of electric energy and a long-term 1.4% average growth rate in summer peak use. By the end of the 10-year period, the 50/50 summer peak would be about 530 MW lower than the RSP09 50/50 forecast for 2018.

Capacity Need and Resource Development—Resources with capacity supply obligations in the Forward Capacity Market are exceeding the “representative” 34,818 MW value for capacity resources needed by 2019. Assuming that the over 35,000 MW of resources that cleared the third Forward Capacity Auction remain in commercial operation, New England will have adequate resources through 2019.

Operating Reserve—RSP10 anticipates that the infrastructure required to meet the reliability requirements will be developed successfully and will improve the economical performance of the system from 2010 through 2014. The SWCT and BOSTON import areas may not need any representative operating reserves because of transmission improvements to these areas. The Greater Connecticut import area still has the greatest representative operating reserve need of up to 1,250 MW. The addition of the NEEWS Interstate Reliability Project would reduce the need for locational operating reserves in Greater Connecticut by approximately 50%, while also addressing other system needs. The Demand-Response Reserves Pilot program will offer additional information on the performance of demand resources in providing operating reserve.

Transmission System—Transmission studies have been completed and show the system needs and transmission additions required for the ISO’s continued compliance with NERC and NPCC reliability standards and criteria. An additional 38 projects were placed in service in 2009, and an additional 34 projects are expected to be placed in service in 2010. The completed transmission projects are required for providing reliable electric service to load throughout the system and for meeting the demand in areas with significant load growth.

Transmission improvements already have reduced the costs of second-contingency and voltage-control payments to generation that must run for reliability reasons, especially in Lower SEMA. Additional transmission improvements are planned in that area and other load pockets to improve reliability by further reducing the reliance on must-run generation.

- The need for the Interstate Reliability Project portion of NEEWS has been determined, and the final alternatives are under development. The need for the 345 kV portions of the Central Connecticut Reliability Project portion of NEEWS is under study. Plans call for discussing both these studies with the PAC by the first quarter of 2011. The other portions of NEEWS in Springfield and Rhode Island should proceed as planned to serve load reliably in those areas. The MPRP, a project adding major 345 kV facilities from the north to southern parts of Maine, has received most of its approvals from the Maine PUC. Other transmission projects are necessary to serve demand reliably in load pockets, reduce dependencies on must-run generation, and meet load growth throughout the system. The ISO will proceed with projects identified as planned in the RSP Project List.

Fuel Diversity—New England will continue to remain dependent on natural gas as the dominant fuel for the region, which provides over 40% of the region’s electric energy. Continued enhancement of the regional and interregional natural gas infrastructure serving New England and its neighboring systems, including new pipelines, LNG terminals, and new natural gas sources, will help expand and diversify the region’s natural gas supply. Converting gas-fired generation to dual-fuel capability improves reliability and reduces exposure to volatile natural gas prices during shortage periods. Other risk factors have been mitigated through modifications to operating procedures. Modifications to market rules are planned to address resource unit commitment uncertainties and to facilitate the commitment of supplemental or replacement reserves during natural gas shortages. Environmental initiatives are promoting the development of renewable resources and energy efficiency, which would help increase system fuel diversity.

Environmental Initiatives—While subject to revisions, the U.S. Clean Air Interstate Rule, the Clean Water Act Section 316b specifying cooling water intake requirements, and the Regional Greenhouse Gas Initiative are environmental requirements that will affect or are affecting the region’s generators. Power plant options for complying with Section 316b could require capital improvements in thermal discharge systems, including the addition of cooling towers. Compliance with air emission initiatives may require several actions by power plant owners. These could include improving emission control systems, which add capital costs; procuring emission allowances and switching to cleaner fuels, which would increase operating costs; and reducing the permissible run times of the plant, which would reduce revenues from the market. The ISO monitors environmental initiatives, their effects on generating plant operations, and their effects on the overall planning and operation of the power system.

Environmental Performance—The 2008 average emissions for New England generators show a continual decline from previous years. The marginal emission rates have declined as natural gas has become the dominant portion of generation. Compared with 1999, the 2008 average emission rate for SO2 has declined by 67%, the NOX rate by 62%, and the CO2 rate by 12%. Further reductions in emissions are supported by state policies and the ISO markets.

RGGI allowance auctions to date have provided over $177 million to the six New England states, and over 93% of these funds are targeted for the state energy-efficiency programs. New England’s preliminary CO2 emissions for 2009 are approximately 30% below the cap of 55.8 million tons.

Renewable Portfolio Standards and Related Policies—An ISO analysis based on the 2010 energy forecast shows that Renewable Portfolio Standards and other related goals would result in total demand for renewable resources and energy efficiency reaching 25.5% of New England’s total projected energy use by 2017 and 30.4% by 2020. If only 40% of the renewable energy projects in the ISO’s Generator Interconnection Queue (as of April 1, 2010) were built, the electric energy from these projects would meet the projected demand for renewable energy in New England up to 2013. However, other resources, such as resources from adjacent balancing authority areas; new renewable projects in New England not yet in the queue; small, behind-the-meter projects; and existing generators switching to eligible renewable fuels, could fill the RPS compliance need beyond 2013. Other options could fill any shortfalls of need, such as making Alternative Compliance Payments, which also serve as a price cap on the cost of Renewable Energy Certificates.

Integration of New Technologies and Smart Grid—The ISO is undertaking a detailed wind integration study of up to 12,000 MW of potential wind development. This will assist the ISO in planning for the reliable integration of a large amount of variable-output resources into the ISO’s system planning and operations as well as New England’s wholesale electricity markets. The ISO also is taking steps to integrate active demand resources, which currently represent over 1,800 MW system capacity for 2012, into system operations and the markets. Because some New England states now have future targets for solar installations, the ISO is following the developments of solar photovoltaic installations in the region.

The federal Energy Independence and Security Act of 2007 is calling for a major increase in the use of smart grid technologies to improve the operation and planning of the electricity grid. The ISO already is experienced in using some smart grid technologies and currently is using smart grid technologies to improve data acquisition, analysis, control, and efficiency of the electric power grid. Funding from the American Recovery and Reinvestment Act of 2009 is supporting additional installations and applications of phasor measurement systems on the New England system. Considerable research and development are needed to benefit fully from these technologies, however, and the ISO and its stakeholders are examining the use of phasor measurement units, FACTS, dynamic line ratings, and thermal and electricity storage technologies, such as plug-in electric vehicles. All these technologies have the potential to support the reliable and economical operation and planning of the grid and will facilitate the successful integration of renewable energy resources.

Economic Planning Studies—In response to a request by the New England governors, the ISO provided technical support to the governors for developing a “blueprint” for integrating large-scale renewable energy resources into the region’s electric power grid. The primary findings of the 2030 Power System Study indicate that New England has significant potential for onshore and offshore wind resources that could be developed and added to the electric power system with appropriate transmission expansion. Renewable and low-carbon-emitting resources located nearby in eastern Canada could be available to New England with transmission expansions to the Québec and New Brunswick power systems.

In April 2010, the ISO received a request from NESCOE to supplement the 2030 Power System Study. This study would analyze (1) the market-sourced replacement or repowering of older coal- and oil-fired generators, and (2) the replacement of the same fossil units through the competitive procurement of renewable resources from New England, neighboring Canadian provinces, or both areas.

The ISO is also conducting joint production cost studies with PJM and NYISO, examining several scenarios for the 2013 system. The goal of the study is to identify potential transmission bottlenecks that may constrain interregional power transfers and show the effects of relieving those transmission constraints.

Interregional Planning—ISO New England’s planning activities are closely coordinated among the six New England states as well as with neighboring systems and the federal government. The Northeastern ISO/RTO Planning Protocol has improved interregional planning among the ISO’s neighboring areas, as summarized in the Northeast Coordinated System Plan. Sharing capacity resources with other systems, particularly to meet environmental emission requirements, will likely become increasingly necessary. Identifying the potential impacts that proposed generating units and transmission projects could have on neighboring systems is beneficial for systemwide reliability and economic performance. The ISO has coordinated system plans and proactively initiated planning studies with other regions. The Eastern Interconnection Planning Collaborative is coordinating plans across the entire Eastern Interconnection, seeking to promote wide-area technical planning studies.

Regional and State Initiatives—The ISO continues to work with stakeholders to improve the RSP and the planning process. Two of these major initiatives will consider the use of the state energy-efficiency goals and the provision of additional information on how nontransmission alternatives can play a role in meeting system needs.

Active involvement and participation by all regional stakeholders, including public officials, state agencies, market participants, and other PAC members, are key elements of an open, transparent, and successful planning process. The ISO has continued to work with other representatives of the New England states, primarily through the PAC but also through designated representative organizations, such as the New England Committee of Public Utilities Commissioners, the New England States Committee on Electricity, and the New England Governors’ Conference. The ISO also coordinates study activities on a national level with DOE, FERC, NERC, and other organizations.

In conclusion, ISO New England’s 2010 Regional System Plan presents a comprehensive assessment of the region’s electricity system needs for 2010 through 2019 and fully meets the OATT Attachment K requirements for regional planning.

# Appendix A
RSP Project List

RSP10 incorporates information from the June 2010 RSP Project List. The June 2010 and other RSP Project Lists are Excel files available at http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/projects/index.html.

# Appendix B
List of Acronyms and Abbreviations

| Acronym/Abbreviation | Description |
| --- | --- |
| AC | Administrative Committee |
| ACEEE | American Council for an Energy-Efficient Economy |
| ACP | Alternative Compliance Payment |
| AEO | Annual Energy Outlook |
| AGT | Algonquin Gas Transmission |
| AMRXY | 20XY Annual Markets Report |
| APS | Alternative Portfolio Standard |
| ARA | Annual Reconfiguration Auction |
| ARR | Auction Revenue Rights |
| ARRA | American Recovery and Reinvestment Act of 2009 |
| ATR | Alternative Technology Regulation (Pilot Program) |
| avg. | average |
| BACT | best available control technology |
| BAT | best available technology |
| Bcf; Bcf/d | billion cubic feet; billion cubic feet per day |
| BHE | 1) RSP subarea of Northeastern Maine 2) Bangor Hydro Electric (Company) |
| BOSTON | RSP subarea of Greater Boston, including the North Shore |
| Btu | British thermal unit(s) |
| C&I | commercial and industrial |
| CAGR | compound annual growth rate |
| CAIR | Clean Air Interstate Rule |
| CATR | Comprehensive Area Transmission Review of the New England Transmission System |
| CEAB | Connecticut Energy Advisory Board |
| CEEF | Connecticut Energy Efficiency Fund |
| CEII | Critical Energy Infrastructure Information |
| CELT | capacity, energy, loads, and transmission |
| 2009 CELT Report | 2009–2018 Forecast Report of Capacity, Energy, Loads, and Transmission |
| 2010 CELT Report | 2010–2019 Forecast Report of Capacity, Energy, Loads, and Transmission |
| CFE | communications front end |
| CHP | combined heat and power |
| CLG | Consumer Liaison Group |
| CMA/NEMA | RSP subarea comprising central Massachusetts and northeastern Massachusetts |
| CMP | Central Maine Power (Company) |
| C.M.R.; CMR | Code of Massachusetts Regulations |
| CO2 | carbon dioxide |
| CONE | cost of new entry |
| CPCN | Certificate of Public Convenience and Necessity |
| CRS | Congressional Research Service |
| CSO | capacity supply obligation |
| CT | 1) State of Connecticut 2) RSP subarea that includes northern and eastern Connecticut 3) Connecticut load zone |
| CT DPUC | Connecticut Department of Public Utility Control |
| DARD | dispatchable asset-related demand |
| DC | District of Columbia; direct current |
| D.C. Cir. | District of Columbia Circuit (Court) |
| DCT | double-circuit tower |
| DDE | demand-designated entity |
| DE | Delaware |
| DEP | Department of Environmental Protection (Maine, New Jersey) |
| DG | distributed generation |
| DLN | dry, low nitrogen oxide |
| DLR | dynamic line rating |
| DOE | U.S. Department of Energy |
| DOER | Department of Energy Resources (Massachusetts) |
| DOMAC | Distrigas of Massachusetts |
| DPUC | Department of Public Utility Control (Connecticut) |
| DRR Pilot | Demand-Response Reserve Pilot Program |
| ECMB | Energy Conservation Management Board |
| EE | energy efficiency |
| EEAC | Energy Efficiency Advisory Council (MA) |
| EERF | Energy-Efficiency Reconciliation Factor |
| EERS | Electric Efficiency Resource Standard |
| EGOC | Electric/Gas Operations Committee |
| EIA | Energy Information Administration (U.S. DOT) |
| EIPC | Eastern Interconnection Planning Collaborative |
| EISPC | Eastern Interconnection States Planning Council |
| EMS | Energy Management System |
| EPA | U.S. Environmental Protection Agency |
| EPAct | Energy Policy Act of 2005 |
| EPRI | Electric Power Research Institute |
| ERCOT | Electric Reliability Council of Texas |
| ERO | Electric Reliability Organization |
| EV | Efficiency Vermont |
| EWITS | Eastern Wind Integration and Transmission Study (U.S. DOE, NREL) |
| FACTS | Flexible Alternating-Current Transmission System |
| FAQ | frequently asked question |
| FCA | Forward Capacity Auction |
| FCA #N | Nth Forward Capacity Auction |
| FCM | Forward Capacity Market |
| FERC | Federal Energy Regulatory Commission |
| FIT | feed-in tariff |
| FOA | Funding Opportunity Announcement |
| FRM | Forward Reserve Market |
| FTR | Financial Transmission Rights |
| GCA | Green Communities Act (MA) |
| GDF | Gaz de France |
| GDP | gross domestic product |
| GE F-Class | General Electric’s F class of gas turbines |
| GHG | greenhouse gas |
| G.L. | general law |
| GPS | global positioning satellite |
| Greater Connecticut | RSP study area that includes the RSP subareas of NOR, SWCT, and CT |
| Greater Southwest Connecticut | RSP study area that includes the southwestern and western portions of Connecticut and comprises the SWCT and NOR subareas |
| GRI | Greater Rhode Island |
| GSRP | Greater Springfield Reliability Project |
| GT | gas turbine |
| GW | gigawatt(s) |
| GWh | gigawatt-hour(s) |
| HEDD | High Electric Demand Day |
| HQ | Hydro-Québec Balancing Authority Area |
| HQICC | Hydro-Québec Installed Capability Credit |
| H.R. | House of Representatives |
| HVAC | heating, ventilation, and air conditioning |
| HVDC | high-voltage direct current |
| HY | hydraulic turbine |
| IBCS OS | Internet-Based Communication System Open Solution |
| ICAP | installed capacity |
| ICR | Installed Capacity Requirement |
| IEEE | Institute of Electrical and Electronics Engineers |
| IESO | Independent Electric System Operator (Ontario, Canada) |
| IGTS | Iroquois Gas Transmission System |
| IMO | Independent Electricity Market Operator of Ontario |
| IPSAC | Inter-Area Planning Stakeholder Advisory Committee |
| IRC | ISO/RTO Council |
| IREMM | Interregional Electric Market Model |
| IRP | Interstate Reliability Plan |
| ISO | Independent System Operator of New England; ISO New England |
| ISO/RTO | Independent System Operator/Regional Transmission Organization |
| ISOs | Independent System Operators |
| IVGTF | Integrating Variable Generation Task Force (NERC) |
| JIPC | Joint ISO/RTO Planning Committee |
| kton | kiloton(s) |
| kV | kilovolt(s) |
| kW | kilowatt(s) |
| kWh | kilowatt-hour(s) |
| lb | pound(s) |
| LDC | local distribution company |
| LFG | landfill gas |
| LLC | limited liability company |
| LMP | locational marginal price |
| LNG | liquefied natural gas |
| LOLE | loss-of-load expectation |
| LOS | loss of source |
| Lower SEMA; LSM | Lower southeastern Massachusetts |
| LRA | local resource adequacy |
| LSE | load-serving entity |
| LSR | local sourcing requirement |
| M&NE | Maritimes and Northeast (Pipeline) |
| MA | Massachusetts |
| MAAC | Mid-Atlantic Area Council |
| MA DOER | Massachusetts Department of Energy Resources |
| MA DPU | Massachusetts Department of Public Utilities |
| MAOP | maximum allowable operating pressure |
| MARS | Minimum-Area Reliability Simulation Program (General Electric) |
| max | maximum |
| MCL | maximum capacity limit |
| MD | Maryland |
| ME | 1) State of Maine 2) RSP subarea that includes western and central Maine and Saco Valley, New Hampshire 3) Maine load zone |
| MEA | Marginal Emissions Analysis |
| MEPCO | Maine Electric Power Company, Inc. |
| METU | Market Efficiency Transmission Upgrade |
| MISO | Midwest Independent System Operator |
| mils | one thousandth of a dollar |
| M/LCC | Master/Local Control Center |
| M/LCC2 | Master/Local Control Center Procedure No. 2, Abnormal Conditions Alert |
| MMBtu | million British thermal unit(s) |
| mo. | month(es) |
| MOU | Memorandum of Understanding |
| MPRP | Maine Power Reliability Program |
| MPS | Maine Public Service |
| MPUC | Maine Public Utilities Commission |
| MSW | municipal solid waste |
| mton | million ton(s) |
| MVAR | megavolt-ampere(s) reactive |
| MW | megawatt(s) |
| MWh | megawatt-hour(s) |
| N-1 | first-contingency loss |
| N-1-1 | second-contingency loss |
| na | not applicable |
| NAAQS | National Ambient Air Quality Standards |
| NAESB | North American Energy Standards Board |
| NB | New Brunswick |
| n.d. | no date |
| NBSO | New Brunswick System Operator |
| NCPC | Net Commitment-Period Compensation |
| NECPUC | New England Conference of Public Utilities Commissioners |
| NEEWS | New England East–West Solution |
| NEGC | New England Governors' Conference |
| NEG/ECP | New England Governors/Eastern Canadian Premiers |
| NEITC | New England Independent Transmission Company |
| NEL | net energy for load |
| NEMA | 1) RSP subarea for Northeast Massachusetts 2) Northeast Massachusetts load zone |
| NEMA/Boston | Combined load zone that includes Northeast Massachusetts and the Boston area |
| NEPGA | New England Power Generators Association |
| NEPOOL | New England Power Pool |
| NERC | North American Electric Reliability Corporation |
| NESCOE | New England States Committee on Electricity |
| NEWIS | New England Wind Integration Study |
| NG | natural gas |
| NGA | Northeast Gas Association |
| NGCC | natural gas combined cycle |
| NGRID | National Grid |
| NH | 1) State of New Hampshire 2) RSP subarea comprising northern, eastern, and central New Hampshire; eastern Vermont; and southwestern Maine 3) New Hampshire load zone |
| NIETC | National Interest Electric Transmission Corridors |
| NIST | National Institute of Standards and Technology |
| NJ | New Jersey |
| NMISA | Northern Maine Independent System Administrator, Inc. |
| NNC | Norwalk Harbor–Northport Cable |
| NNE | northern New England |
| No. | number |
| NOR | RSP subarea that includes Norwalk and Stamford, Connecticut |
| NO2 | nitrogen dioxide |
| NOX | nitrogen oxide(s) |
| NPCC | Northeast Power Coordinating Council, Inc. |
| NREL | National Renewable Energy Laboratory (U.S. DOE) |
| NRI | Northeast Reliability Interconnection |
| NTA | nontransmission alternative |
| Nuc | nuclear |
| NWVT | Northwest Vermont |
| NY | New York Balancing Authority Area |
| NYISO | New York Independent System Operator |
| NYPA | New York Power Authority |
| NYSERDA | New York State Energy Research Development Authority |
| O3 | ozone |
| OATT | Open Access Transmission Tariff |
| OP 4 | ISO Operating Procedure No. 4, Action during a Capacity Deficiency |
| OP 7 | ISO Operating Procedure No. 7, Action in an Emergency |
| OP 8 | ISO Operating Procedure No. 8, Operating Reserve and Regulation |
| OP 19 | ISO Operating Procedure No. 19, Transmission Operations |
| OP 21 | ISO Operating Procedure No. 21, Action during an Energy Emergency |
| OPA | Ontario Power Authority |
| OTC | Ozone Transport Commission |
| PA | Pennsylvania |
| PAC | Planning Advisory Committee |
| PDC | phasor data concentrator |
| PDR | passive demand resource |
| PER | peak energy rent |
| PEV | plug-in electric vehicle |
| PJM | PJM Interconnection LLC, the RTO for all or parts of Delaware, Illinois, Indiana, Kentucky, Maryland, Michigan, New Jersey, North Carolina, Ohio, Pennsylvania, Tennessee, Virginia, and the District of Columbia |
| PM2.5 | fine particulates |
| PMU | phasor measurement unit |
| pnode | pricing node |
| PNGTS | Portland Natural Gas Transmission System |
| PP 3 | ISO Planning ISO Planning Procedure No. 3, Reliability Standards for the New England Area Bulk Power Supply System |
| PP 4 | ISO Planning Procedure No. 4, Procedure for Pool-Supported PTF Cost Review |
| PP 10 | ISO Planning Procedure No. 10, Planning Procedure to Support the Forward Capacity Market |
| PPA | Power Purchase Agreement |
| ppb | part(s) per billion |
| PSPC | Power Supply Planning Committee |
| PTF | pool transmission facility |
| PTO | participating transmission owner |
| Pub. L. | public law |
| PUC | Public Utilities Commission |
| PV | photovoltaic |
| queue (the) | ISO Generator Interconnection Queue |
| RC | Reliability Committee |
| REC | Renewable Energy Certificate |
| REEI | Regional Energy-Efficiency Initiative (ISO New England) |
| Renw | renewable |
| Resid | residual |
| RFP | request for proposal |
| RGGI | Regional Greenhouse Gas Initiative |
| RI | 1) State of Rhode Island 2) RSP subarea that includes the part of Rhode Island bordering Massachusetts 3) Rhode Island load zone |
| RIRP | Rhode Island Reliability Project |
| RNS | Regional Network Service |
| RPS | Renewable Portfolio Standard |
| RSP | Regional System Plan |
| RSPXY | 20XY Regional System Plan |
| RTDR | real-time demand response |
| RTEG | real-time emergency generation |
| RTO | Regional Transmission Organization |
| RTPRP | Real-Time Price-Response Program |
| RTU | remote terminal unit |
| RWK | Rumford–Woodstock–Kimball Road |
| S. | Senate (U.S.) |
| SB | Senate Bill |
| SBC | system benefits charge |
| SCC | seasonal claimed capability |
| SCADA | System Control and Data Acquisition |
| SEMA | 1) RSP subarea comprising southeastern Massachusetts and Newport, Rhode Island 2) Southeastern Massachusetts load zone |
| Sess. | Session (Congress) |
| SIDU | synchrophasor infrastructure and data utilization |
| SLR | static line rating |
| SMD | Standard Market Design |
| SME | RSP subarea for Southeastern Maine |
| SO2 | sulfur dioxide |
| SOEP | Sable Offshore Energy Project |
| SPEED | Sustainably Priced Energy Enterprise Development |
| SPS | special protection system |
| sq. | square |
| S-REC | Solar Renewable Energy Credit |
| ST | steam |
| SWCT | RSP subarea for Southwest Connecticut |
| TBD | to be determined |
| Tcf | trillion cubic feet |
| TGP | Tennessee Gas Pipeline |
| TO | transmission owner |
| TP | transmission provider |
| TRC | Tradable Renewable Credit; Technical Review Committee |
| TSA | transmission security analysis |
| UDS | Unit Dispatch System |
| U.S. | United States |
| V2G | vehicle to grid |
| VELCO | Vermont Electric Power Company |
| VFT | variable-frequency transformer |
| VT | 1) State of Vermont 2) RSP subarea that includes Vermont and southwestern New Hampshire 3) Vermont load zone |
| 20XY VT LRP | 20XY Vermont Long-Range Plan |
| WCMA | Western/Central Massachusetts load zone |
| WMA | RSP subarea for Western Massachusetts |
| WMECO | Western Massachusetts Electric Company |
| WMPPXY | Wholesale Markets Projects Plan 20XY |

ISO New England Open Access Transmission Tariff, Section II, Attachment K, “Regional System Planning Process” (December 7, 2007); http://www.iso-ne.com/regulatory/tariff/sect_2/oatt/2-1-09_sect_ii.pdf. ISO New England Inc. Transmission, Markets, and Services Tariff, Part II, Section 48 (2010); http://www.iso-ne.com/regulatory/tariff/index.html.

NEPOOL was formed by the region’s private and municipal utilities to foster cooperation and coordination among the utilities in the six-state region and ensure a dependable supply of electricity. Today, NEPOOL members serve as ISO stakeholders and market participants. More information on NEPOOL participants is available at
http://www.iso-ne.com/committees/nepool_part/index.html.

Past RSPs are archived at http://www.iso-ne.com/trans/rsp/index.html. For access to supporting reports, contact ISO Customer Service at 413-540-4220.

This total includes seven projects in 2002, 26 projects in 2003, 30 projects in 2004, 51 projects in 2005, 55 projects in 2006, 36 projects in 2007, and 64 projects in 2008 based on the June 2010 RSP Project List. An additional 38 projects were placed in service in 2009, and an additional 34 projects are expected to be placed in service in 2010.

The ISO’s 2010–2019 Forecast Report of Capacity, Energy, Loads, and Transmission (May 18, 2010); copies of all CELT reports are located at http://www.iso-ne.com/trans/celt/index.html.

DOE, 2009 National Electric Transmission Congestion Study (December 2009); http://www.congestion09.anl.gov/documents/docs/Congestion_Study_2009.pdf.

PAC materials and meeting minutes are available at http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/index.html.

ISO New England Inc. Transmission, Markets, and Services Tariff, Part II, Section 48 (ISO tariff) (2010); http://www.iso-ne.com/regulatory/tariff/index.html. Information on NERC requirements is available at http://www.nerc.com. Information on NPCC is available at http://www.npcc.org/.

ISO New England Open Access Transmission Tariff, Section II, Attachment K, “Regional System Planning Process” (December 7, 2007); http://www.iso-ne.com/regulatory/tariff/sect_2/oatt/2-1-09_sect_ii.pdf.

In general, supply resources are generating units that use nuclear energy, fossil fuels (such as natural gas, oil, or coal), or renewable fuels (such as water, wind, or the sun) to produce electricity. Demand resources are measures that reduce consumer demand for electricity from the power system, such as using energy-efficient appliances and lighting, advanced cooling and heating technologies, electronic devices to cycle air conditioners on and off, and equipment to shift load to off-peak hours of demand. They also include using distributed generation (DG) (i.e., electricity generated on site).

Other demand resources consist of three types of demand resources: energy efficiency, load management, and distributed generation. These types of resources typically are nondispatchable and tend to reduce end-use demand on the electricity network across many hours but usually not in direct response to changing hourly wholesale prices. Refer to the ISO’s 2009 Regional System Plan (RSP09), Section 4.2.4.3, (October 15, 2009) for additional information on ODRs; http://www.iso-ne.com/trans/rsp/2009/index.

Weather-normalized results are those that would have been observed had the weather been the same as the long-term average weather.

A capacity commitment period runs from June 1 through May 31 of the following year. Existing capacity resources are required to participate in the FCA and are automatically entered into the capacity auction. However, these resources may indicate a desire to be removed from the FCA by submitting a delist bid before the existing-capacity qualification deadline.

Order on Forward Capacity Market Revisions and Related Complaints, FERC Docket Nos. ER10-787-000, EL10-50-000, and EL10-57-000 (April 23, 2010); http://www.iso-ne.com/regulatory/ferc/orders/2010/apr/er10-787-000_el10-50_el10-57_order_fcm_redesign.pdf.

To conduct some RSP studies, the region is divided into various areas related to their electrical system characteristics. Greater Connecticut is an area that has boundaries similar to the State of Connecticut but is slightly smaller because of electrical system limitations near Connecticut’s borders with western Massachusetts and Rhode Island. Greater Southwest Connecticut includes southwestern and western portions of Connecticut. The BOSTON area (all capitalized) includes the city of Boston and northeast Massachusetts. (See Figure 2-2.)

The ISO develops the representative operating-reserve requirements of these major import areas as ranges to account for future uncertainties about the availability of resources, load variations due to weather, and other factors.

In-merit generation is when the generators with the lowest-price offers are committed and dispatched first, and increasingly higher-priced generators are brought on line as demand increases. Out-of-merit dispatch is when higher-priced generators are committed and dispatched before lower-priced resources to respect system reliability requirements, which results in increased costs to load.

Demand response in wholesale electricity markets occurs when market participants reduce their consumption of electric energy from the network in exchange for compensation based on market prices.

The ISO is subject to audits, which must prove compliance with all planning requirements. The last NERC/NPCC audit report, Compliance Audit Report Public Version: ISO New England Inc. April 20 to April 24, 2009 (May 7, 2009; posted  January 5, 2010), is available at http://www.npcc.org/compliance2/AuditSpot.aspx.

The current update of the RSP Project List is available at http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/projects/index.html.

Cost estimates without transmission cost allocation approval are subject to wide ranges of accuracy and change as projects progress through various stages of implementation. The $5 billion cost estimate has a range $3.8 to $6.2 billion based on projects that are proposed, planned, and under construction. See the June 2010 RSP Project List presentation, slide 9, at http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/projects/2010/june_proj_list_slides.pdf.

Participating transmission owners’ (PTOs’) annual informational filing regarding ISO tariff charges in effect as of June 1, 2010, pursuant to FERC Docket Nos. RT04-2-000, et al.(July 30, 2010);
http://iso-ne.com/regulatory/ferc/ptoac/2010/jun10_sch_9_1_info_filing.pdf.
PTO presentation to the RC and TC (August 16–17, 2010) explaining the basis of the RNS rate; http://www.iso-ne.com/committees/comm_wkgrps/trans_comm/tariff_comm/mtrls/2010/aug16172010/a11_2010_rns_rates_presentation.pdf. Second presentation projecting the RNS rate for five years using a number of assumptions; http://www.iso-ne.com/committees/comm_wkgrps/trans_comm/tariff_comm/mtrls/2010/aug16172010/a11_rns_rate_forecast_%202010_2014.pdf.

Load pockets are areas of the system where the transmission capability is insufficient to import power from other parts of the system and load must rely on local generation. The ISO is studying changes in the export-transfer capability from Maine to New Hampshire.

A second contingency is when a power system element is unavailable and another contingency occurs.

The 2009 Northeast Coordinated System Plan (ISO New England, New York ISO [NYISO], and PJM Interconnection [PJM], May 24, 2010) summarizes several interregional planning activities. The report is available at http://iso-ne.com/committees/comm_wkgrps/othr/ipsac/ncsp/index.html. PJM is the RTO for all or parts of Delaware, Illinois, Indiana, Kentucky, Maryland, Michigan, New Jersey, North Carolina, Ohio, Pennsylvania, Tennessee, Virginia, and the District of Columbia.

The Eastern Interconnection consists of the interconnected transmission and distribution infrastructure that synchronously operates east of the Rocky Mountains, excluding the portion of the system located in the Electric Reliability Council of Texas (ERCOT) and Québec. Additional information on the EIPC is available at http://www.eipconline.com/.

Improvements include a new liquefied natural gas (LNG) terminal in St. John, New Brunswick; the Northeast Gateway Project and Neptune LNG terminals, both offshore of Gloucester, MA; increased sources of natural gas from shale, such as the Marcellus Shale discoveries, and developments in Atlantic Canada (Deep Panuke); and several improvements to natural gas pipelines and storage facilities.

System operating concerns experienced in the cold snap of 2004 have largely been addressed. Final Report on Electricity Supply Conditions in New England during the January 14–16, 2004 “Cold Snap” (October 12, 2004); http://www.iso-ne.com/pubs/spcl_rpts/2004/final_report_jan2004_cold_snap.pdf.

Air emission regulations cover nitrous oxides (NOX), particulates, sulfur dioxide (SO2), mercury, and greenhouse gases, such as carbon dioxide (CO2).

2008 New England Electric Generator Air Emissions Report (August 18, 2010);
http://www.iso-ne.com/genrtion_resrcs/reports/emission/index.html.

According to  the National Electrical Manufacturers Association and the Congressional Research Service, the goal of the smart grid is to use advanced, information-based technologies to increase power grid efficiency, reliability, and flexibility, and reduce the rate at which additional electric utility infrastructure needs to be built. For additional information, see the ISO’s Overview of the Smart Grid—Policies, Initiatives, and Needs (February 17, 2009); http://www.iso-ne.com/pubs/whtpprs/smart_grid_report_021709_final.pdf.

The ISO Generator Interconnection Queue (queue) includes those generators that have submitted requests to interconnect to the ISO New England electric power system.

Active demand resources reduce load in response to a request from the ISO to do so for system reliability reasons or in response to a price signal. Passive demand resources are principally designed to save electric energy use and are in place at all times without requiring direction from the ISO.

Another economic study requested in 2009 by ISO New England stakeholders, as well as stakeholders from NYISO and PJM, is analyzing a series of scenarios for 2013 to account for planned load, resource expansions and retirements, and transmission configurations that could affect these regions. The study will focus primarily on the NYISO and ISO New England systems. Refer to April and May 2009 PAC materials at
http://iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/mtrls/2009/index.html, and May 2009 discussions held with the Inter-Area Planning Stakeholder Advisory Committee (IPSAC) at
http://iso-ne.com/committees/comm_wkgrps/othr/ipsac/mtrls/2009/may72009/index.html.

NESCOE is the FERC-approved regional-state committee for providing advisory input to the ISO regarding the development of the RSP.

Transmission Planning and Cost Allocation by Transmission Owning and Operating Public Utilities, Notice of Proposed Rulemaking, FERC Docket No. RM12-23-000 (June 17, 2010); http://ferc.gov/whats-new/comm-meet/2010/061710/E-9.pdf.

Any stakeholder can designate a representative to the PAC by providing written notice to the ISO. PAC materials (2001–2010) are available at http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/index.html.

NEPOOL was formed by the region’s private and municipal utilities to foster cooperation and coordination among the utilities in the six-state region and ensure a dependable supply of electricity. Today, NEPOOL members serve as ISO stakeholders and market participants. More information on NEPOOL participants is available at
http://www.iso-ne.com/committees/nepool_part/index.html.

Supply resources are generating units that use nuclear energy, fossil fuels (such as gas, oil, or coal), or renewable fuels (such as water, wind, or the sun) to produce electricity. In general, demand resources are measures that reduce consumer demand for electricity from the power system, such as the use of energy-efficient appliances and lighting, advanced cooling and heating technologies, electronic devices to cycle air conditioners on and off, and equipment to shift load to off-peak hours of demand. Other measures include the use of electricity generated on site (i.e., distributed generation, or DG). Demand resources also include installed measures, such as equipment, services, and strategies that reduce end-use demand on the electricity network during specific performance hours. ISO New England Inc. Transmission, Markets, and Services Tariff (ISO tariff), Part II, Section 48 (2010); http://www.iso-ne.com/regulatory/tariff/index.html.

Renewable sources of energy are those that are naturally replenished, such as solar, hydro, wind, selected biomass (e.g., wood and wood-waste solids and gas), geothermal, ocean thermal, and tidal sources of power. Other fuel sources that can be regarded as renewable resources include landfill gas (LFG) (i.e., the gas that results from decomposition in landfills and either is collected, cleaned, and used for generation or is vented or flared) and refuse (municipal solid waste). Some states consider fuel cells to be renewable.

Load is the demand for electricity measured in megawatts (MW).

PAC materials and meeting minutes are available at
http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/index.html.

A merchant transmission facility is an independently developed and funded facility subject to the operational control of the ISO, pursuant to an operating agreement specific to each facility (refer to Section 6.2.3.4).

In response to stakeholder requests, the ISO will provide additional information on NTAs as part of future RSPs.

The current list is available at http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/projects/index.html.

Recent and archived RSP materials are available at http://www.iso-ne.com/trans/rsp/index.html. The AMR is available at http://www.iso-ne.com/markets/mkt_anlys_rpts/annl_mkt_rpts/. The Needs Assessments and Solution Studies that have been presented to the PAC and posted on the ISO Web site can be obtained by contacting ISO Customer Service at 413-540-4220.

Stakeholders also can obtain publicly available network models of the transmission system through the FERC 715 process, which requires transmitting utilities that operate facilities rated at or above 100 kV to submit information to FERC annually; see http://www.ferc.gov/docs-filing/eforms/form-715/overview.asp. The ISO Information Policy, Attachment D of the ISO tariff, addresses the requirements for controlling the disclosure of CEII and confidential information; see http://www.iso-ne.com/regulatory/tariff/attach_d/index.html.

A balancing authority area is a group of generation, transmission, and loads within the metered boundaries of the entity (balancing authority) that maintains the load-resource balance within the area. Balancing authority areas were formerly referred to as control areas. Further information is available in the NERC glossary at http://www.nerc.com/docs/standards/rs/Glossary_12Feb08.pdf.

Preventing Undue Discrimination and Preference in Transmission Service, Final Rule, FERC Order No. 890, Docket Nos. RM05-17-000 and RM05-25-000 (February 16, 2007); http://www.ferc.gov/whats-new/comm-meet/2007/021507/E-1.pdf. NERC Reliability Standards (Princeton, NJ: NERC, 2010); http://www.nerc.com/page.php?cid=2|20. NPCC Regional Standards (New York: NPCC, 2010); http://www.npcc.org/regStandards/Overview.aspx. ISO New England Planning Procedures (2010); http://www.iso-ne.com/rules_proceds/isone_plan/index.html. ISO New England Operating Procedures (2010); http://www.iso-ne.com/rules_proceds/operating/index.html.

The ISO is not responsible for portions of northern and eastern Maine. The Northern Maine Independent System Administrator, Inc. (NMISA) is a nonprofit entity responsible for the administration of the northern Maine transmission system and electric power markets in Aroostook and Washington counties, which has a peak load of approximately 130 MW; see http://www.nmisa.com.

In exchange for compensation based on wholesale electricity prices, customers in ISO demand-resource programs reduce load continuously or quickly, when instructed, to enhance system reliability or in response to price signals. The 1,900 MW of ISO demand resources do not include energy efficiency provided by other customer-based programs that are outside the ISO markets or are otherwise unknown to ISO. See Section 4.2.1.1 for more details on demand resources.

For more information on New England wholesale electricity markets, see the ISO’s 2009 Annual Markets Report (AMR09) (May 18, 2010); http://www.iso-ne.com/markets/mktmonmit/rpts/index.html.

Installed capacity is the megawatt capability of a generating unit, dispatchable load, external resource or transaction, or demand resource that qualifies as a participant in the ISO’s Forward Capacity Market according to the market rules. Additional information is available at http://www.iso-ne.com/markets/othrmkts_data/fcm/index.html.

Regulation is the capability of specially equipped generators to increase or decrease their generation output every four seconds in response to signals they receive from the ISO to control slight changes on the system.

Unloaded operating capacity is operational capacity not generating electric energy but able to convert to generating energy. A contingency is the sudden loss of a generation or transmission resource. A system’s first contingency (N-1) is when the power element (facility) with the largest impact on system reliability is lost. A second contingency 
(N-1-1) takes place after a first contingency has occurred and is the loss of the facility that then has the largest impact on the system.

Load zones can also have the same boundaries as reliability regions, which are intended to reflect the operating characteristics of, and the major constraints on, the New England transmission system. See Market Rule 1, Section III.2.7 of the ISO tariff; http://www.iso-ne.com/regulatory/tariff/sect_3/_mr1_sect_1-12.pdf.

The ISO tariff allows loads that meet specified requirements to request and receive nodal pricing.

Real-time emergency generation is distributed generation the ISO calls on to operate during certain voltage-reduction or more severe actions but must limit its operation to comply with the generation’s federal, state, or local air quality permit(s) or combination of permits.

The distribution of generation resources by RSP subarea is available in the ISO’s presentation, “New England System Plan System Overview,” slide 12 (March 31, 2009);
http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/mtrls/2009/mar312009/a_system_overview.pdf.

The ISO’s Capacity, Energy, Load, and Transmission (CELT) Reports and associated documentation contain more detailed information on short- and long-run forecast methodologies, models, and inputs; weather normalization; regional, state, subarea, and load-zone forecasts of annual electric energy use and peak loads; high- and low-forecast bandwidths; and retail electricity prices. They are available at “CELT Forecasting Details 2010;” http://www.iso-ne.com/trans/celt/fsct_detail/index.html. Also see 2010–2019 Forecast Report of Capacity, Energy, Loads, and Transmission (May 18, 2010); http://www.iso-ne.com/trans/celt/report/.

Refer to PAC materials presented on March 18, 2010;
http://iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/mtrls/2010/mar182010/index.html.

RSP09 (October 15, 2009); http://www.iso-ne.com/trans/rsp/2009/index.

Moody’s Analytics, Inc., Economy.com (2009); http://www.economy.com/default.asp. Electricity load forecasters throughout the United States and New England use Moody’s economic forecasts.

The increase in electric energy savings attributable to active demand resources (i.e., demand-response resources that reduce peak load; see Section 4.2.1.1) is insignificant.

The compound annual growth rate (CAGR) is calculated as follows:

The inflation rate was obtained from Moody’s Analytics, Economy.com, as part of its November 2009 economic forecast.
Order Accepting in Part and Modifying in Part Standard Market Design Filing and Dismissing Compliance Filing, FERC Docket Nos. ER02-2330-000 and EL00-62-039 (September 20, 2002), 37. For background information, see Explanatory Statement in Support of Settlement Agreement of the Settling Parties and Request for Expedited Consideration and Settlement Agreement Resolving All Issues, FERC Docket Nos. ER03-563-000, -030, -055 (filed March 6, 2006; as amended March 7, 2006). Refer to AMR09, Section 2.2 and Section 4, for more information on the FCM;
http://www.iso-ne.com/markets/mkt_anlys_rpts/annl_mkt_rpts/index.html.

Peak energy rent reduces capacity market payments for all capacity resources, typically when electricity demand is high and prices in the electric energy markets go above the PER threshold price (i.e., an estimate of the electric energy cost of the most expensive resource on the system). Section 4.2.2 contains additional information on the FCA.

American Recovery and Reinvestment Act of 2009, Stimulus Bill, U.S. Public Law 111-5, H.R. 1, S. 1 (February 17, 2009); http://www.gpo.gov/fdsys/pkg/PLAW-111publ5/content-detail.html. Several articles by Moody’s Analytics, Economy.com, detail and explain its forecast and are available at “Economy.com January 2009 Economic Forecasting Articles;”
http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/mtrls/2009/feb252009/index.html.

Office of Energy Efficiency and Renewable Energy, DOE, “Appliances and Commercial Equipment Standards Program” Web site (April 24, 2009); http://www1.eere.energy.gov/buildings/appliance_standards/.

Details of the loads are available at “CELT Forecasting Details 2010;”
http://www.iso-ne.com/trans/celt/fsct_detail/index.html. Also see the full 2010 CELT report; http://www.iso-ne.com/trans/celt/report/.

For additional information, refer to the pricing node tables available at “Settlement Model Information;”
http://www.iso-ne.com/stlmnts/stlmnt_mod_info/index.html.

2010–2019 Forecast Report of Capacity, Energy, Loads, and Transmission;
http://www.iso-ne.com/trans/celt/report/index.html.

Increased energy savings attributable to other demand resources (ODRs) reduced the growth in weather-normalized electric energy consumption by 50% from 2008 to 2009. Other demand resources consist of energy-efficiency measures, load management, and distributed generation. These types of demand resources typically are nondispatchable and tend to reduce end-use demand on the electricity network across many hours but usually not in direct response to changing hourly wholesale prices. Refer to the ISO’s 2009 Regional System Plan (RSP09) (October 15, 2009), Section 4.2.4.3, for additional information on ODRs; http://www.iso-ne.com/trans/rsp/2009/index.

A capacity supply obligation is a requirement for a resource to provide capacity, or a portion of capacity, to satisfy a portion of the ISO’s Installed Capacity Requirement that is acquired through an FCA, a reconfiguration auction, or a CSO bilateral contract through which a market participant may transfer all or part of its CSO to another entity.

See the PAC agenda summary at http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/mins/index.html.

The queue includes the requests submitted by generators to interconnect to the ISO New England electric power system.

Deterministic analyses are snapshots of assumed specific conditions that do not attempt to quantify the likelihood that these conditions will actually materialize. The results are based on analyzing a set of conditions representing a specific scenario.

Probabilistic analyses use statistical estimates of the likelihood of an event taking place and explicitly recognize that the inputs are uncertain.

Not meeting this criterion could result in a penalty, currently being developed by the NPCC, for the New England Balancing Authority Area. Additional information is available at http://www.npcc.org/documents/regStandards/Criteria.aspx. However, the amount procured may exceed the ICR as a result of price floors established during the development of the FCM—in which case, all the resources offered to the market would clear below the established floor price—or because the size of the marginal resource that cleared in the auction was larger than the amount needed. The FCM rules allow for intermediate adjustments to the amount of procured capacity to account for expected changes in system conditions.

Tie-line benefits account for both the transmission-transfer capability of the tie lines and the emergency capacity assistance that may be available from neighboring systems when and if New England would need it.

A bus is a point of interconnection to the system. Internal transmission constraints are addressed through the modeling of local sourcing requirements (LSRs) and maximum capacity limits (MCLs); see Section 4.1.2.

For the 2010/2011 ICR calculations, the purchases and sales data are based on the values published in the ISO’s 2010 CELT Report; http://www.iso-ne.com/trans/celt/index.html.

Established ICR values refer to the values that either have been approved by FERC or have been filed with FERC for approval. Representative net ICR values are the representative ICRs for the region, minus the tie-reliability benefits associated with the Hydro-Québec Phase I/II Interface (termed HQICCs). As defined in the ISO’s tariff, the HQICC is a monthly value that reflects the annual installed capacity benefits of the HQ Interconnection, as determined by the ISO using a standard methodology on file with FERC. The ISO calculates representative net ICR values solely to inform New England stakeholders; these values have not and will not be filed with FERC for approval. Capacity commitment periods, also referred to as capability years, run from June 1 through May 31of the following year.

The most recent version of this presentation is available at
http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/mtrls/2010/apr272010/icr_values.pdf.

Resulting reserves are the amount of capacity in excess of the forecast 50/50 peak load. Percent resulting reserves =
[{(Net ICR − 50/50 peak load) ÷ 50/50 peak load} × 100].

The ISO submitted the ICR filing to FERC on May 4, 2010; it is available at
http://www.iso-ne.com/regulatory/ferc/filings/2010/may/er10-___-000_05-04-10_icr_2013-2014.pdf.

The 2011/2012 ICR, filed September 9, 2008, and based on the 2008 load forecast, is available at http://www.iso-ne.com/regulatory/ferc/filings/2008/sep/er08-1512-000_9-9-08_2011-2012_icr_filing.pdf. The 2010/2011 ICR for the annual reconfiguration auction (not the primary FCA) was filed January 30, 2009, and also used the 2008 load forecast;
http://www.iso-ne.com/regulatory/ferc/filings/2009/jan/er09-640-000_1-30-09_icr_filing.pdf.

The rule changes pertain only to import-constrained load zones. Each export-constrained load zone is modeled as a separate capacity zone in the FCA; the ISO did not propose any change to these provisions.

To enhance the regional system planning process, the ISO is also analyzing the impact of proposed transmission topology changes on FCM zonal configuration and requirements, identifying emerging issues that may require changes in zonal configuration, identifying effective solutions to local security and reliability needs, and developing projections of zonal configurations under alternate expansion strategies.

The capacity commitment period requirements for 2010/2011 to 2013/2014 are available in the FERC filings at http://www.iso-ne.com/regulatory/ferc/filings/2008/sep/er08-1512-000_9-9-08_2011-2012_icr_filing.pdf;
http://www.iso-ne.com/regulatory/ferc/filings/2009/jan/er09-640-000_1-30-09_icr_filing.pdf;
http://www.iso-ne.com/regulatory/ferc/filings/2009/jul/er09-___-000_7-7-09_2012-2013_icr_values.pdf; and 
http://www.iso-ne.com/regulatory/ferc/filings/2010/may/er10-___-000_05-04-10_icr_2013-2014.pdf. FERC has approved the actual values.

The ISO’s 2009 Annual Markets Report, Section 2.2 (May 18, 2010), describes the FCM in more detail. The report is available at http://www.iso-ne.com/markets/mkt_anlys_rpts/annl_mkt_rpts/index.html.

Although FCA #4 was held in August 2010, results are not yet publically available for inclusion in RSP10.

Real-time emergency generators are required to begin operating within 30 minutes, which results in increasing supply on the New England grid, and also to continue that operation until receiving a dispatch instruction allowing them to shut down.

Various types of delist bids exist, including static, dynamic, permanent, export, and several others. Refer to AMR09, Section 2.2.3, for the more information on delist bids; http://www.iso-ne.com/markets/mkt_anlys_rpts/annl_mkt_rpts/index.html.

Internal Market Monitoring Unit Review of the Forward Capacity Market Auction Results and Design Elements, 15, Table 3-1, Quantity Rule (filed with FERC June 5, 2009); http://www.iso-ne.com/regulatory/ferc/filings/2009/jun/er09-1282-000_06-05-09_market_monitor_report_for_fcm.pdf.

2010 CELT Report, Section 3.1; http://www.iso-ne.com/trans/celt/report/2010/2010_celt_report.xls.

Under certain conditions, Market Rule 1 allows generators that repower or perform environmental upgrades to be classified as “new.” For FCA #3, there were no repowering projects, and a majority of the new projects, approximately 87%, were environmental upgrades to existing generators.

Because FCA #4 results were preliminary at the time of RSP10’s information deadline, they are not included in the analyses conducted for this report. The preliminary results are available at 
http://www.iso-ne.com/nwsiss/pr/2010/final_fca4_release_08062010.pdf.

The May 4, 2010, filing, Informational Filing for Qualification in the Forward Capacity Market, is available at http://www.iso-ne.com/markets/othrmkts_data/fcm/cal_results/index.html.

Operating Procedure No. 4, Action during a Capacity Deficiency (June 1, 2010);
http://www.iso-ne.com/rules_proceds/operating/isone/op4/index.html. Operating Procedure No.7, Action in an Emergency (August 19, 2008); http://www.iso-ne.com/rules_proceds/operating/isone/op7/index.html.

To obtain 2,500 MW of load and capacity relief, ISO system operators would need to implement Actions 1 through 13 of OP 4, which include allowing the depletion of the 30-minute and partial depletion of the 10-minute reserve (1,000 MW), scheduling market participants’ submitted emergency transactions and arranging emergency purchases between balancing authority areas (1,600 MW–2,000 MW), and implementing 5% voltage reductions (450 MW).

These amounts are consistent and achievable through the use of OP 4 actions that can provide over 3,000 MW through the use of tie benefits, 5% voltage reduction, and the depletion of the 10-minute operating reserve (to the minimum level of 200 MW).

The projects that have been proposed but discontinued faced problems during their development associated with financing, licensing, insufficient market incentives, or other issues. More information on interconnection projects is available at “Interconnection Status” (April 1, 2010); http://www.iso-ne.com/genrtion_resrcs/nwgen_inter/status/index.html.

ISO Operating Procedure No. 8, Operating Reserve and Regulation (June 5, 2009);
http://www.iso-ne.com/rules_proceds/operating/isone/op8/op8_rto_final.pdf.

ISO Operating Procedure No. 19, Transmission Operations (April 13, 2007);
http://www.iso-ne.com/rules_proceds/operating/isone/op19/op19_rto_final.pdf.

Market Rule 1, Standard Market Design (Section III of the ISO tariff) (2010) defines the types of reserves that can meet these requirements; http://www.iso-ne.com/regulatory/tariff/sect_3/index.html.

Economic-merit order (i.e., in merit or in merit order) is when the generators with the lowest-price offers are committed and dispatched first, and increasingly higher-priced generators are brought on line as demand increases. Out-of-merit dispatch is when generators are run less economically to respect system reliability requirements.

Baseload generating units satisfy all or part of the minimum load of the system and, as a consequence, produce electric energy continuously and at a constant rate. These units usually are economic to operate day to day. Intermediate-load generating units are used during the transition between baseload and peak-load requirements. These units come on line during intermediate load levels and ramp up and down to follow the system load that peaks during the day and is at its lowest in the middle of the night. A peaking unit is designed to start up quickly on demand and operate for only a few hours, typically during system peak days, which amounts to a few hundred hours per year.

In some circumstances, when transmission contingencies are more severe than generation contingencies, shedding some load may be acceptable.

This dispatch and telemetry configuration is very similar to the dispatch of generating resources. The specifications of the system are identified in ISO Operating Procedure No. 18, Metering and Telemetry Criteria, Appendix G: Demand Response RTU (June 1, 2010); http://www.iso-ne.com/rules_proceds/operating/isone/op18/index.html.

ISO New England commissioned KEMA to perform a study of several aspects of its DRR pilot program, including baseline modeling. A series of alternatives also were evaluated to ensure that the forecasting methodology was appropriate.

RSP09, Section 10; http://www.iso-ne.com/trans/rsp/2009/index.html. Planning Advisory Committee materials and report; http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/index.html.

The Eastern Interconnection consists of the interconnected transmission and distribution infrastructure that synchronously operates east of the Rocky Mountains, excluding the portion of the system located in the Electric Reliability Council of Texas (ERCOT) and Québec.

See the OATT, Section II.B, Attachment N, “Procedures for Regional System Plan Upgrades;”
http://www.iso-ne.com/regulatory/tariff/sect_2/oatt/index.html.

ISO practices and procedures are available at http://www.iso-ne.com/trans/services/types_apps/.

The Network Capability Interconnection Standard is an energy-only standard that includes the minimum criteria required to permit a generator to connect to the transmission system so that it does not have any adverse impacts on reliability, stability, or the operation of the system, including the degradation of transfer capability for interfaces affected by the generating facility. The Capacity Capability Interconnection Standard is a capacity and energy standard that includes the same criteria as the Network Capability Interconnection Standard but also includes criteria to ensure intrazonal deliverability by avoiding the redispatch of other capacity network resources. Before October 29, 1998, Generator Interconnection-Related Upgrades included cost responsibility for additional upgrades beyond those required to satisfy the minimum interconnection standard. The standard are defined in the OATT, Section 22; http://www.iso-ne.com/regulatory/tariff/sect_2/sch22/1-24-10-sched_22.pdf.

NEMA Upgrades are located in the Northeast Massachusetts Reliability Region and were scheduled and placed in service by June 30, 2004. The OATT, Schedule 12A, lists the NEMA Upgrades; http://www.iso-ne.com/regulatory/tariff/sect_1/sec_1.pdf.

The filing for the addition or modification to the transmission upgrade must be in accordance with the OATT, Section II.47.2, on a date after the RSP Project List (as of the date of that application) already has documented the addition or modification, other than as an Elective Transmission Upgrade.

This part of the ISO tariff covers the review of participants’ proposed plans. Approval of projects pursuant to Section I.3.9 of the tariff is the recognition that the proposed project can be implemented without significantly degrading the performance of the system; it is not an endorsement of the need for or associated costs of the project. See http://www.iso-ne.com/regulatory/tariff/sect_1/09-8-19_section_1.pdf.

PAC materials and meeting minutes are available at
http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/index.html. The RSP Project List is available at http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/projects/index.html.

The $5 billion cost estimate is based on projects that are proposed, planned, and under construction and has a range of $3.8 to $6.2 billion.

For background information, refer to “RNS Rate Effective June 1, 2010,” by the PTO AC Rates Working Group, presented at the NEPOOL RC and TC Joint Summer Meeting (August 16–17, 2010); http://www.iso-ne.com/committees/comm_wkgrps/trans_comm/tariff_comm/mtrls/2010/aug16172010/a11_2010_rns_rates_presentation.pdf.

One exception is that Aroostook and Washington Counties in Maine are served radially from New Brunswick.

Further details about individual transmission projects can be obtained by contacting ISO Customer Service at (413) 540-4220. As part of the PAC materials, the ISO includes study schedules of system performance Needs Assessments and Solutions Studies.

The flows vary with system conditions, as shown by the 2009 data where the flows were northbound about 20% of the time; see http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/mtrls/2010/jan212010/lmp_and_interface.pdf.

New Hampshire Transmission System Needs Assessment (October 1, 2009);
http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/reports/2009/final_nh_needs_report.pdf.
New Hampshire Transmission Needs Assessment Update Presentation (July 6, 2009);
http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2009/jul162009/nh_needs.pdf.

2010 CELT Report; http://www.iso-ne.com/trans/celt/index.html.

2006 Vermont Transmission System Long-Range Plan (June 30, 2006); http://www.velco.com/LongRange/Documents/abridged_2006_plan%5B1%5D.pdf.

Vermont Transmission System Needs Assessment Study Scope (October 15, 2008); http://www.iso-ne.com/trans/sys_studies/rsp_docs/pres/2008/final_vermont_transmission_system_needs_assessment__study_scope_oct152008.pdf.

2009 Vermont Transmission System Long-Range Plan (July 1, 2009); http://www.velco.com/LongRange/Pages/2009Long-RangeTransmissionPlan.aspx.

Vermont Transmission Reliability Report Need Analysis (February 8, 2010);
http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/reports/2010/final_vt_report.pdf.

Vermont Transmission System Needs Assessment Presentation (February 25, 2009); http://w ww.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2009/feb252009/vermont_needs.pdf.

Southern Loop/Coolidge Connector Presentation (January 17, 2008);
http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/mtrls/2008/jan172008/avelcosouthernloop.pdf.
Vermont Southern Loop/Coolidge Connector Update Presentation (January 15, 2008); http://www.iso-ne.com/trans/sys_studies/rsp_docs/pres/2008/avtsoloop.pdf). Vermont Coolidge Connecter Presentation (July 16, 2009); http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2009/jul162009/vermont.pdf.

Overview—New Hampshire Second Deerfield Autotransformer Presentation (June 4, 2008); http://www.iso-ne.com/trans/sys_studies/rsp_docs/pres/2008/deerfield_area.pdf. New Hampshire Second Deerfield Autotransformer—Update to June 2008 Presentation (December 16, 2008); http://www.iso-ne.com/trans/sys_studies/rsp_docs/pres/2008/deerfield.pdf. Second 345/115-kV Deerfield Autotransformer Proposed Plan Application Analysis Report (June 16, 2009); http://www.iso-ne.com/committees/comm_wkgrps/relblty_comm/relblty/ceii/ceii_mtrls/2009/jun162009/2nd_deerfield_txfmr_rev1_ppa.zip.

Littleton Substation Reconfiguration Project Presentation (July 6, 2009); http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2009/jul162009/littleton.pdf.

Maine Power Reliability Program (MPRP) Steady State Needs Assessment Presentation (May 14, 2007); http://www.iso-ne.com/trans/sys_studies/rsp_docs/pres/2007/maine_power_reliability_program_steady_state_needs_assessment.pdf). Final Report Maine Power Reliability Program Needs Assessment of the Maine Transmission System (June 19, 2007; http://www.iso-ne.com/trans/sys_studies/rsp_docs/pres/2007/maine_power_reliability_program_needs_assessment_final_report.pdf.

Maine Power Reliability Program (MPRP) Transmission Alternatives—Revised Presentation (January 24, 2008); http://www.iso-ne.com/trans/sys_studies/rsp_docs/pres/2008/amprprevised.pdf. Final Report Maine Power Reliability Program Transmission Alternatives Assessment for the Maine Transmission System (June 10, 2008); http://www.iso-ne.com/trans/sys_studies/rsp_docs/pres/2008/mprp_final_report.pdf. The Maine Power Reliability Program Transmission Alternatives Assessment for the Maine Transmission System (May 30, 2008) describes the original version of this project in more detail. The CMP Maine Power Reliability Program Proposed Plan Application Analyses Addendum Report (February 6, 2009) updates the project descriptions.

Central Maine Power Company and Public Service of New Hampshire, Request for Certificate of Public Convenience and Necessity for the Maine Power Reliability Program Consisting of the Construction of Approximately 350 miles of 345 kV and 115 kV Transmission Lines, Maine PUC Docket No. 2008-255 (July 31, 2008); http://www.cmpco.com/OurCompany/MPRP_CPCN_APPLCTN.html.

PSNH and CMP Joint Supplemental Filing with Respect to Termination of Section 3022 Adjacent to Existing Three Rivers Substation, Maine PUC Docket No. 2008-255 (July 26, 2010). The report is available at http://mpuc.informe.org/easyfile/easyweb.php?func=easyweb_query. (Enter "2008255" into the "Case ID" on the search page and locate the filings for July 26, 2010, to access the entry for "Three Rivers Substation.")

Bangor Hydro’s Northern System Review Presentation (June 4, 2008);
http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2008/bhe.pdf.

New Hampshire 10-Year Study-Transmission Alternatives (January 21, 2009); http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2009/jan212009/a_nh_alternative_assessment.pdf.

Greater Hartford Reliability Study (March 18, 2010);
http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2010/mar182010/greaterhartford.pdf.

New England East–West Solution (NEEWS) Rhode Island and Springfield Current Needs Assessments (June 17, 2009); http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2009/jun172009/neews.pdf.

Southern New England Transmission Reliability Needs Analysis Report. Both public (redacted) and private versions of this report are available on the ISO's Web site. Contact ISO Customer Services at (413) 540-4220 for additional information.

Greater Boston Area Transmission Needs Assessment (July 8, 2010);
http://iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/reports/index.html.

Greater Boston Study Needs Assessment/Solutions (March 18, 2010);
http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/mtrls/2010/mar182010/gb_needs_solutions.pdf.

Western Massachusetts (MA) Transmission Planning Studies (November 6, 2007);
http://www.iso-ne.com/trans/sys_studies/rsp_docs/pres/2007/western_massachusetts_transmission_planning_studies.pdf. Pittsfield-Greenfield, MA Area Transmission Needs Assessment and the appendices to this report (June 29, 2010);
https://iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/reports/2010/pitts-green_assess.pdf and
http://iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/reports/index.html.

Greater Hartford Area Reliability Study (March 18, 2010);
http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2010/mar182010/greaterhartford.pdf.

New England East–West Solution (June 2008); http://www.iso-ne.com/trans/sys_studies/rsp_docs/pres/2008/neews_options_final_protect.pdf. A number of the less complex Rhode Island improvements, which were put on an accelerated schedule, came to be known as the advanced NEEWS upgrades for Rhode Island. These were merged with other upgrades into what became the Greater Rhode Island Project. This project is discussed further below.

Merrimack/North Shore Area Transmission Reliability Study Steady State Analysis to Support Proposed Plan Application (April 2006); http://www.iso-ne.com/committees/comm_wkgrps/relblty_comm/relblty/mtrls/2008/feb142008/zip3_wakefield.zip.

Mystic 345 kV, 160 MVAR Shunt Reactor Project Transmission Facilities Proposed Plan Steady State Analysis (July 1, 2008); http://www.iso-ne.com/committees/comm_wkgrps/relblty_comm/relblty/ceii/2008/aug/mystic_reactor_study_report.pdf.

E-205E 230 kV Line Refurbishment (August 19, 2009);
http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/ceii/mtrls/2009/aug192009/a_ngrid.pdf.

Western Massachusetts Transmission Reinforcements 2007 to 2017 (September 2007);
http://www.iso-ne.com/committees/comm_wkgrps/relblty_comm/relblty/mtrls/2007/oct102007/zip2_western_ma_ppa.zip.

Slawek Szymanowski, Auburn St. Substation Upgrades System Impact Study (National Grid, November 2007) and Sandeep Baidwan and Ahmet Oztepe, Auburn St. Substation and Area Transmission System Reliability Study (National Grid, July 2007);  http://www.iso-ne.com/committees/comm_wkgrps/relblty_comm/relblty/mtrls/2007/dec192007/index.html (Zip 3 Study Reports).

Lower SEMA Short Term Upgrades System Impact Study Steady State Analysis (May 3, 2007);
http://www.iso-ne.com/committees/comm_wkgrps/relblty_comm/relblty/mtrls/2007/aug82007/zip1b_study-reports.zip.

Greater Rhode Island Transmission Reinforcements (March 2008);
http://www.iso-ne.com/committees/comm_wkgrps/relblty_comm/relblty/mtrls/2008/apr152008/zip1_gri-study-reports.zip.

Steady State and Short Circuit Analysis for the System Impact Study of the Grand Avenue Project (November 21, 2008); http://www.iso-ne.com/committees/comm_wkgrps/relblty_comm/relblty/ceii/2008/dec/grand_avenue_project_steady_state_report.pdf.

ISO Planning Procedure No. 10 (PP 10), System Planning Activities Conducted to Support the Forward Capacity Market (July 2009); http://www.iso-ne.com/rules_proceds/isone_plan/pp10_r6.pdf.

Order on Forward Capacity Auction Results Filing, FERC Docket No, ER10-186-000 (February 26, 2010);
http://www.iso-ne.com/regulatory/ferc/orders/2010/feb/er10-186-000_2-26-10_order_accept_3rd_fca_results.pdf.

The results of the fourth FCA, which commenced on August 3, 2010, were not made public before publishing RSP10. ISO New England Inc., Informational Filing for Qualification in the Forward Capacity Market, FERC Docket No. ER10-___-000 (May 4, 2010); http://www.iso-ne.com/regulatory/ferc/filings/2010/may/er10-___-000_05-04-10_4th_fca_info_filing.pdf.

See RSP10 2009 Historical Market Data: Locational Marginal Prices, Interface MW Flows (January 21, 2010); http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/mtrls/2010/jan212010/lmp_and_interface.pdf.

Net Commitment-Period Compensation (NCPC) provides “make-whole” payments to market participants with resources whose operating costs exceed energy revenues over the 24-hour dispatch day. NCPC is paid to resources for providing first- and second-contingency voltage support and control and distribution system protection in either the Day-Ahead or Real-Time Energy Markets. The accounting for the provision of these services is performed daily and considers a resource’s total offer amount for generation, including start-up fees and no-load fees, compared with its total energy market value during the day. If the total value is less than the offer amount, the difference is credited to the market participant. For more information, see Market Rule 1, Section III, Appendix F: Net Commitment-Period Compensation Accounting; http://www.iso-ne.com/regulatory/tariff/sect_3/.

The NCPC second-contingency payments to generators in SEMA were $143.5 million in 2008 and $13.9 million in 2009. The NCPC voltage payments to generators in SEMA were $6.9 million in 2008 and $3.9 million in 2009. See the “NCPC Credits Summary 2010” Web page; http://www.iso-ne.com/markets/othrmkts_data/ncpc/ncpc_sum/index.html.

On the basis of the June 2010 RSP Project List, this total includes seven projects in 2002, 26 projects in 2003, 30 projects in 2004, 51 projects in 2005, 55 projects in 2006, 36 projects in 2007, and 64 projects in 2008. An additional 38 projects were placed in service in 2009, and an additional 34 projects are expected to be placed in service in 2010.

Cost estimates without transmission cost allocation approval are subject to wide ranges of accuracy and change as projects progress. Many projects, especially those in the early stages of development, do not have cost estimates.

All the ISO’s CELT reports are available at http://www.iso-ne.com/trans/celt/index.html. The summer installed capacity total includes existing generation and expected generation capacity additions but not Hydro-Québec Interconnection Capability Credits (HQICC), demand-response resources, or external purchases and sales. The 2010 CELT Report, Section 2.1, “Generator List with Existing and Expected Seasonal Claimed Capability (SCC),” contains details on 2010 summer installed capacity.

The renewable resource fuel sources include landfill gas, other biomass gas, refuse (municipal solid waste), wood and wood-waste solids, wind, solar, black liquor, and tire-derived fuels.

Operating Procedure No. 4, Action during a Capacity Deficiency (June 1, 2010);
http://www.iso-ne.com/rules_proceds/operating/isone/op4/index.html.

Energy Information Administration (EIA), DOE, “Intrastate Natural Gas Pipeline Segment” Web page (n.d.) and “Intrastate Natural Gas Pipeline Companies” spreadsheet (2007)); http://www.eia.doe.gov/pub/oil_gas/natural_gas/analysis_publications/ngpipeline/intrastate.html.

Marcellus Shale, a geographic formation in the Appalachian basin, extends from Virginia into Ohio, Pennsylvania, and New York.

EnCana, “Offshore—Deep Panuke” Web page (2009); http://www.encana.com/operations/canada/deeppanuke/; in-service date status obtained from the Northeast Gas Association (NGA) (June 29, 2010).

The satisfaction of the 45% peak-day requirement is a combination of vaporization at Distrigas in Everett, MA, and vaporization from all New England gas local distribution companies’ (LDCs’) satellite LNG tanks serving their service territory peak-day requirements. Distrigas is the primary, sole-source supplier of LNG liquid trucking in the region.

“GDF” stands for Gaz de France. GDF SUEZ Energy North America, “LNG Operations” Web site (2009); http://www.suezenergyna.com/ourcompanies/lngna.shtml.

Distragas transmittal to the ISO, June 28, 2010.

Excelerate Energy, “Northeast Gateway Deepwater Port” Web page (n.d.); http://www.excelerateenergy.com/northeast.html.

The Canaport LNG project is a Canadian Limited Partnership between subsidiaries of Irving Oil Limited (25% owner) and Respol (75% owner). See Canaport LNG Web site (2008); http://www.canaportlng.com/index.php.

More information on the Brunswick Pipeline is available at http://www.brunswickpipeline.com/home/index.cfm.The M&NE Pipeline (http://www.mnpp.com/us/) can receive approximately 0.85 Bcf/d of natural gas from Canada for delivery into New England from various Canadian supply points, which include deepwater production from the Sable Offshore Energy Project and the upcoming (in 2011) Deep Panuke Project, along with land-based production from Corridor Resources’ McCully gas field and regasified LNG from the Canaport facility.

Distragas transmittal to the ISO, June 28, 2010.

NGA, 2009 Statistical Guide (December 2009).

NGA Web site (2010); http://www.northeastgas.org.

NGA, Regional Market Update (December 2009).

While most of New England’s geology is unsuitable for underground gas storage, aboveground LNG tanks can store natural gas for the region.

Spectra Energy, “Steckman Ridge” Web page (2009); http://www.spectraenergy.com/what_we_do/businesses/us/assets/steckman/.

NGA, “FERC Approves Wyckoff Gas Storage Commencement of Partial Service,” NGA News (July 2009) Issue 7, Vol. 7.

Thomas Corners began accepting interruptible gas injections on November 3, 2009, and firm gas injections on April 1, 2010.

American Recovery and Reinvestment Act of 2009, Stimulus Bill, U.S. Public Law 111-5, H.R. 1, S. 1 (February 17, 2009). http://www.wealthdaily.com/articles/renewable-energy-stimulus/1706.

See Section 4.2.1.1 for demand-resource participation in the FCM; Section 8.4 for summaries of the state goals for energy efficiency; Section 9 for information on the ISO’s plans for integrating renewable resources, demand resources, and smart grid technologies.

The price of input fuels has a large impact on the cost of providing electric energy. In 2009, natural-gas-fired generation set the LMP 60% of the time. Thus, when the average price of natural gas decreased considerably in 2009, the cost for providing electricity also decreased. For more information on electricity costs and natural gas prices for 2007 to 2009, refer to the ISO’s 2009 Annual Markets Report (AMR09), Section 1.3.1.1,  3.1.2.2, and 3.3.6.6 (May 18, 2010); http://www.iso-ne.com/markets/mkt_anlys_rpts/annl_mkt_rpts/index.html.

During the week of July 4, 2008, the average price of imported crude oil was $142.52/barrel. This price declined to $32.98/barrel in the last week of 2008 (AMR08, Section 1.1.5);
http://www.iso-ne.com/markets/mktmonmit/rpts/other/amr08_final_061709.pdf.

“ISO New England Interconnection Status” (April 1, 2010);
http://www.iso-ne.com/genrtion_resrcs/nwgen_inter/status/index.html.

This includes projects that are proposing direct interconnection to the ISO system. The renewables include wind, hydro, landfill gas, biomass, and fuel cells.

Since the occurrence of the January 2004 cold snap, over 2,600 MW of single-fuel, gas-only stations have added secondary (liquid) fuel capability. Cold Snap Report (October 2004);
http://www.iso-ne.com/pubs/spcl_rpts/2004/final_report_jan2004_cold_snap.pdf.

ISO New England’s 2010 Wholesale Markets Projects Plan (WMPP10) (March 19, 2010), 9;
http://www.iso-ne.com/pubs/whlsle_mkt_pln/isone_2010_wmp_031810.pdf.

Ibid.

Typically, the newer class of dry, low-NOX (DLN) gas-fired combustion turbines is rated as “GE F-Class” and higher. This can also be considered a “rate-of-change” issue.

In response to the cold snap of January 2004, Market Rule 1, Appendix H: Operations during Cold Weather Conditions, was developed. In response to the oil and gas infrastructure damage in the Gulf of Mexico from hurricanes Katrina and Rita in fall 2005, ISO Operating Procedure No. 21 (OP 21), Actions during an Energy Emergency, was developed; http://www.iso-ne.com/rules_proceds/operating/isone/op21/index.html.

Regional natural gas prices are from the Intercontinental Exchange (ICE) (June 24, 2010); https://www.theice.com/homepage.jhtml.

Other oxides of nitrogen (NOX) also contribute to the formation of ozone. The status of these environmental regulatory activities and coverage of proposed changes to EPA’s NAAQS, mercury, and coal combustion products is discussed in more detail in the 2009 Northeast Coordinated System Plan, developed by ISO New England, NYISO, and PJM Interconnection LLC (PJM) (May 24, 2010), 47–61; http://www.iso-ne.com/committees/comm_wkgrps/othr/ipsac/reports/index.html. (PJM is the RTO for all or parts of Delaware, Illinois, Indiana, Kentucky, Maryland, Michigan, New Jersey, North Carolina, Ohio, Pennsylvania, Tennessee, Virginia, and the District of Columbia.)

Refer to the Ozone Transport Commission’s Memorandum of Understanding Among the States of the Ozone Transport Commission Concerning the Incorporation of High Electric Demand Day Emission Reduction Strategies into Ozone Attainment State Implementation Planning, MOU-07-01 (March 2, 2007); http://www.otcair.org/document.asp?Fview=Formal%20Actions#.

EPA, Cooling Water Intake Structures, CWA Section 316b; Phase I—New Facilities. Fact Sheet. EPA-821-F-01-01 (November 2001); http://www.epa.gov/waterscience/316b/phase1/316bph1fs.html.

EPA’s regulatory actions related to visibility are summarized at http://www.epa.gov/air/visibility/actions.html. Additional information is available at “EPA’s Regional Haze Program” Web page (2009); http://www.epa.gov/air/visibility/program.html.

NESHAPs are emission standards set in EPA’s Clean Air Act, § 112, for air pollutants not covered by NAAQS that may cause an increase in fatalities or a serious illness. The standards require the maximum degree of emission reduction that EPA determines to be achievable (i.e., the maximum achievable control technology; MACT). For additional information, see “National Emission Standard for Hazardous Air Pollutants” Web page (2010); http://www.epa.gov/apti/course422/apc4e.html.

Hazardous and Solid Waste Management System; Identification and Listing of Special Wastes; Disposal of Coal Combustion Residuals from Electric Utilities, Proposed Rule, EPA-HQ-RCRA-2009-0640; FRL, Federal Register, vol. 75, No. 118 (June 21, 2010); http://www.epa.gov/epawaste/nonhaz/industrial/special/fossil/ccr-rule/ccr-rule-prop.pdf. Also see http://www.epa.gov/waste/nonhaz/industrial/special/fossil/ccr-rule/index.htm.

Ozone Transport Commission, MOU Among the States of the Ozone Transport Commission Concerning the Incorporation of High Electric Demand Days Emission Reduction Strategies into Ozone Attainment State Implementation Planning, MOU 07-01 (March 2, 2007). New York, New Jersey, Pennsylvania, Maryland, and Delaware also have commitments totaling 123.2 tons of NOX reductions; http://www.otcair.org/document.asp?Fview=Formal%20Actions#.

North Carolina v. EPA, No. 05-1244, Slip Op. (D.C. Cir., July 11, 2008); http://pacer.cadc.uscourts.gov/docs/common/opinions/200807/05-1244-1127017.pdf.

Office of Air and Radiation, EPA, “EPA Clean Air Markets—Data and Maps, Emissions, Preliminary Quick Reports” Web pages; http://camddataandmaps.epa.gov/gdm/index.cfm?fuseaction=emissions.wizard.

“Uncertainty clouds KGL release,” Carbon Market North America, Vol. 5, Issue 16 (April 23, 2010); http://www.pointcarbon.com/news/cmna/1.1439092.

Under RGGI, one allowance equals the limited right to emit one ton of CO2.

Environment Northeast, RGGI Auction Tracker Web site (2010); http://www.env-ne.org/resources/open/p/id/715.

RGGI Memorandum of Understanding, Section 6D (December 20, 2005); http://rggi.org/docs/mou_12_20_05.pdf.

U.S. Congress, American Clean Energy and Security Act of 2009, H.R. 2454, 111th Cong., 1st Sess. (2009).

EPA, “Climate Change Regulatory Initiatives” Web page, “Greenhouse Gases Reporting Program” (2010); http://www.epa.gov/climatechange/emissions/ghgrulemaking.html.

Office of Air and Radiation, EPA, “Fact Sheet—Proposed Rule: Prevention of Significant Deterioration and Title V Greenhouse Gas Tailoring Rule” (2009); http://www.epa.gov/NSR/fs20090930action.html.

Michael J. Bradley, Susan F. Tierney, et al., Ensuring a Clean, Modern Electric Generating Fleet while Maintaining Electric System Reliability (M.J. Bradley and Associates and Analysis Group, August 2010); http://www.mjbradley.com/documents/MJBAandAnalysisGroupReliabilityReportAugust2010.pdf.

Whitman and Requardt Associates, LLP, The Handy-Whitman Index of Public Construction Costs, Bulletin No. 168: 1912 to July1, 2008 (2008); http://www.scribd.com/doc/9501599/Handy-Whitman-Index-Electrical.

2008 New England Electric Generator Air Emissions Report (August 18, 2010);
http://www.iso-ne.com/genrtion_resrcs/reports/emission/index.html.

Office of Air and Radiation, EPA, “Clean Air Markets Data and Maps, Emissions” Web pages (2010); http://camddataandmaps.epa.gov/gdm/index.cfm?fuseaction=emissions.wizard.

Hydro and pumped hydro were not considered to be incremental and were excluded from the 500 MW.

On the peak day, August 8, 2007, a higher peak hourly NOX rate was calculated: 2.75 tons/hour, or 11 lbs/MWh. The lowest peak emissions occurred on July 18, 2008, at 0.6 tons/hour (2 lbs/MWh).

American Council for an Energy-Efficient Economy (ACEEE), 2009 State Energy Efficiency Scorecard (October 2009); http://www.aceee.org/pubs/e097.htm.

See the ISO’s Forward Capacity Auction Results Filing, FERC Docket No, ER10-___-000 (October 30, 2009); http://www.iso-ne.com/regulatory/ferc/filings/2009/oct/er10-___-000_10-29-09_fca_3_results_filing.pdf.

CT Energy Conservation Management Board, An Investment in Connecticut Energy Efficiency (March 1, 2010); http://www.ctsavesenergy.org/files/Final%202009%20Legislative%20Report%202.19.10.pdf.

Commonwealth of Massachusetts, An Act Relative to Green Communities, Chapter 169 of the Acts of 2008 (July 2, 2008); http://www.mass.gov/legis/laws/seslaw08/sl080169.htm.

National Grid, NSTAR, Unitil, and Western Massachusetts Electric, 2010–2012 Massachusetts Joint Statewide Three-Year Electric Energy Efficiency Plan (October 29, 2009); http://www.ma-eeac.org/docs/DPU-filing/ElectricPlanFinalOct09.pdf.

Massachusetts Department of Public Utilities Order 09-116 through 09-120 (January 28, 2010); http://www.env.state.ma.us/dpu/docs/electric/09-116/12810dpuord.pdf.

Commonwealth of Massachusetts, An Act Relative to Green Communities, § 116(a)(1) (2008); http://www.mass.gov/legis/laws/seslaw08/sl080169.htm.

The Narragansett Electric Company d/b/a National Grid Gas and Electric Energy Efficiency Program Plans for 2009, RI and Providence Plantations, RI PUC Docket No. 4000 (n.d); http://www.ripuc.org/eventsactions/docket/4000-NGrid-Ord19608(4-6-09).pdf or http://www.ripuc.org/eventsactions/docket/4000page.html.

“Efficiency Vermont,” Slide 4, presentation at the ISO’s Regional Energy-Efficiency Initiative (REEI) (March 5, 2009).

ACEEE, Vermont Utility Sector Policies (2010); http://www.aceee.org/energy/state/vermont/vt_utility.htm.

Efficiency Vermont, Year 2009 Savings Claim (April 1, 2010); http://www.efficiencyvermont.com/stella/filelib/EfficiencyVermont2009_SavingsClaim_Final.pdf.

GDS Associates, Additional Opportunities for Energy Efficiency in New Hampshire Final Report (January 2009); http://www.puc.nh.gov/Electric/GDS%20Report/NH%20Additional%20EE%20Opportunities%20Study%202-19-09%20-%20Final.pdf.

2010 Core Energy Efficiency Programs, DE 09-170, Order Approving Revised 2010 Core Budgets, NH PUC Order No. 25,099 (April 30, 2010); http://www.puc.state.nh.us/Regulatory/Orders/2010orders/25099e.pdf. Also, Maureen Reno (Utility Analyst, NH PUC), in telephone conversation with Eric Wilkinson (ISO New England), August 26, 2010.

Efficiency Maine Web site (n.d.); http://www.efficiencymaine.com/.

Efficiency Maine Trust Web site (2010); http://www.efficiencymainetrust.org/triennial.html.

EMT, Draft Triennial Plan of the Efficiency Maine Trust 2011–2013 (April 5, 2010); http://www.efficiencymainetrust.org/docs/TriPlan_Final_Draft_100405.pdf.

Efficiency Maine Trust Web site (2010); http://www.efficiencymainetrust.org/.

Retail competitive suppliers are load-serving entities (LSEs), such as electric utility distribution companies that sell basic electrical energy service to end-use customers, except for municipally owned utilities.

MA DOER, Biomass Sustainability and Carbon Policy Study (June 2010); http://www.mass.gov/?pageID=eoeeaterminal&L=4&L0=Home&L1=Energy%2c+Utilities+%26+Clean+Technologies&L2=Renewable+Energy&L3=Biomass&sid=Eoeea&b=terminalcontent&f=doer_arra_bscps&csid=Eoeea and Clarification of Suspension of Biomass Energy from Qualification in the Renewable Energy Portfolio Standard Program (December 22, 2009); http://www.mass.gov/Eoeea/docs/doer/renewables/biomass/biomass-suspend-clarify-2009dec22.pdf. Ian Bowles (Secretary, Massachusetts Executive Office of Energy and Environmental Affairs) in letter on biomass sustainability and carbon regulations to the MA DOER, July 7, 2010; http://www.mass.gov/Eoeea/docs/eea/biomass/070710_biomass_sustainablity_carbon_regs_letter.pdf.

Maine Public Utilities Commission Revised Rules 65.407 Chapter 311 Portfolio Requirement (Effective November 6, 2007).

Maine’s RPS allows FERC-qualifying facilities (i.e., efficient cogeneration plants) to count toward meeting its goal of having renewable resources provide 30% of its electricity use. Maine’s many paper mills typically meet this goal.

Renewable Energy Portfolio Standard—Class I 225 [CMR 14.05 (1)(4)(a)];  http://www.mass.gov/Eoeea/docs/doer/renewables/solar/225CMR1400Jan8-2010.pdf.

The electric energy consumption target for CHP technology is based on the megawatt-hours of fuel energy savings a CHP facility can experience compared with the amount of fuel separate energy facilities would use (e.g., an electric  purchase from the ISO grid and a boiler each requiring its own fuel). To meet the target, the CHP would need to be more fuel efficient providing electricity and heat than the separate electric energy purchase from the ISO grid and boiler providing the same energy applications as the CHP facility. Flywheels are large rotating masses that can store electric energy, which can be called on to provide power for relatively brief periods.

Stretch Energy Code, 780 CMR Appendix 120 AA (Commonwealth of Massachusetts, 2009); http://www.mass.gov/Eeops/docs/dps/inf/appendix_120_aa_jul09_09_final.pdf.

The ISO projections did not account for customers still on “standard offer” contracts for the next several years because these offers are not subject to the RPS until the contracts expire.

The calculation is based on the exemption of municipal loads through 2020.

The ISO’s Renewable Portfolio Standard projection calculator provides regional goals and electric energy production by renewable resource type. Users can insert their own input assumptions in these spreadsheets, which are available at http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/eag/usr_sprdshts/index.html.

The ISO recognizes that each state must certify the resources to meet the RPS requirements. These state-certified RPS projects include generators connected to the grid, behind the meter, and in adjacent balancing areas (where allowed).

New renewable energy projects generally do not enter the queue until they are within two to five years of their intended commercial operation date.

The ISO’s Renewable Portfolio Standard projection calculator provides regional goals and electric energy production by renewable resource type. Users can insert their own input assumptions in these spreadsheets, which are available at http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/eag/usr_sprdshts/index.html.

Robert Grace, “Renewable Energy Resources in New England . . . Will They Be There When We Need Them,” presentation at the Northeast Energy and Commerce Association 15th Annual New England Energy Conference, Newport, RI (May 12, 2008).

MA DOER, Annual RPS Compliance Report for 2008 (July 29, 2009); http://www.mass.gov/Eoeea/docs/doer/rps/rps-2008annual-rpt.pdf.

The ISO’s Renewable Portfolio Standard projection calculator provides regional goals and electric energy production by renewable resource type. Users can insert their own input assumptions in these spreadsheets, which are available at http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/eag/usr_sprdshts/index.html.

New England has the potential for developing over 215 GW of wind generation (see Section 9.3). New England also has cooperated regionally to promote the development of renewables and import them from the neighboring Canadian provinces (see Section 12.2.2).

A more detailed discussion of smart grid technology is available at the IEEE Smart Grid Web site (2010); http://smartgrid.ieee.org/.

U.S. Congress, Energy Independence and Security Act of 2007 (January 4, 2007); http://frwebgate.access.gpo.gov/cgi-bin/getdoc.cgi?dbname=110_cong_bills&docid=f:h6enr.txt.pdf.

Preventing Undue Discrimination and Preference in Transmission Service, Final Rule, FERC Order No. 890, Docket Nos. RM05-17-000 and RM05-25-000 (February 16, 2007); http://www.ferc.gov/whats-new/comm-meet/2007/021507/E-1.pdf. “Alternative Technology Regulation Pilot Program Frequently Asked Questions” Web page (2009); http://www.iso-ne.com/support/faq/atr/index.html.

Beacon Power has installed 2 MW of flywheels, which have provided regulation services from a location in Tyngsboro, Massachusetts. “Beacon Power Connects Second Megawatt of Regulation Service,” Business Wire (July 20, 2009); http://www.businesswire.com/portal/site/home/permalink/?ndmViewId=news_view&newsId=20090720005598&newsLang=en. V2G technology involves electric vehicles that can store electric energy and supply it for electric energy or ancillary services (e.g., regulation services and spinning reserves).

As of May 3, 2010, the five PMUs were located at Orrington, ME; Scobie Pond, NH; and Pequonnock, Manchester, and Long Mountain, CT.

The IEEE defines FACTS as flexible alternating-current transmission systems that incorporate power electronics-based controllers and other static controllers to enhance controllability and power-transfer capability. See http://www.ieee-pes.org/nari-hingorani-facts-award.

Michael Henderson and Donald Ramey, “Planning Issues for FACTS,” presentation at the IEEE Power Engineering Society General Meeting, Tampa (June 2007). Also see “Transmission System Application Requirements for FACTS Controllers Special Publication 06TP178,” produced by the IEEE Power Engineering Society Working Group 15.05.13.

Customers may become fatigued with frequent operation as a demand-response resource and not want to respond when required. For example, a customer in the business of making a product may prefer fulfilling an order rather than repeatedly reducing energy consumption and delaying production.

Gross-up rules give credit for customer actions that both reduce load at the customer’s meter and reduce power system losses.

ISO New England Inc. and New England Power Pool FERC Filing, Tariff Revisions Regarding Elimination of the Reserve Margin Gross-Up for Demand Resources, FERC Docket No. ER09-___-000 (October 31, 2008);
http://www.iso-ne.com/regulatory/ferc/filings/2008/oct/er09-209-000_10-31-08_dr_gross-up_filing.pdf.

For more information, see ISO New England Operating Procedure No. 4, Action during a Capacity Deficiency (April 29, 2010); http://www.iso-ne.com/rules_proceds/operating/future_fcm/op4_fcm_draft.pdf.

See the 2009 Northeast Coordinated System Plan, Chapter 8 (May 24, 2010) for a summary of wind integration studies and issues; http://www.iso-ne.com/committees/comm_wkgrps/othr/ipsac/ncsp/2010/ncsp09final.pdf.

NERC, Special Report: Accommodating High Levels of Variable Generation (April 2009); http://www.nerc.com/files/IVGTF_Report_041609.pdf.

IVGTF materials are posted at http://www.nerc.com/filez/ivgtf.html.

ISO/RTO Council, Variable Energy Resources, System Operation and Wholesale Markets, white paper (April 12, 2010); http://www.iso-ne.com/regulatory/ferc/filings/2010/apr/rm10-11-000_4-12-10_irc_ver_comments.pdf.

Load-following regulation adjusts generators minute by minute to meet continuous changes in load demand. Reserve requirements account for the loss of any generating facility, including variable generation, and sudden reductions in production by variable generation (see Section 5).

The 3,100 MW of wind includes wind projects in the queue, including affected non-FERC queue projects, as of April 1, 2010.

2009 Northeast Coordinated System Plan (May 24, 2010);
http://iso-ne.com/committees/comm_wkgrps/othr/ipsac/ncsp/index.html.

The RFP is available at http://www.iso-ne.com/aboutiso/vendor/exhibits/index.html.

The NEWIS methodology is discussed in more detail in RSP09; http://www.iso-ne.com/trans/rsp/2009/rsp09_final.pdf.

See NEWIS materials at the PAC materials Web sites for December 17, 2008; June 17, August 18, and November 18, 2009; and January 21 and May 25, 2010; http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/mtrls/index.html.

GE Energy Application and Systems Engineering, et al, Technical Requirements for Wind Generation Interconnection and Integration (November 3, 2009);
http://iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/reports/2009/newis_report.pdf.

Insolation is the measure of solar radiation energy received on a given surface area in a given time, expressed in common usage in either watts/sq. meter (power) or kWh/m2/day (energy).

Richard Chelboski, presentation at the NECA Annual Renewable Energy Conference, Boston, MA (March 3, 2010); http://www.necanews.org/dev/documents/100303_chleboski_richard_4.pdf.

New England Electricity Scenario Analysis Report (August 2, 2007);
http://www.iso-ne.com/committees/comm_wkgrps/othr/sas/mtrls/elec_report/scenario_analysis_final.pdf.

NERC, Special Report: Accommodating High Levels of Variable Generation (April 2009), 27; http://www.nerc.com/files/IVGTF_Report_041609.pdf.

Larry Sherwood, U. S. Solar Market Trends 2008 (Interstate Renewable Energy Council, July 2009); http://irecusa.org/fileadmin/user_upload/NationalOutreachDocs/SolarTrendsReports/IREC_Solar_Market_Trends_Report_2008.pdf.

Bill Opalka, “Shaping the Future of Power,” Renewablebiz Daily (April 20, 2010); http://www.renewablesbiz.com/article/10/04/shaping-future-power.

Commonwealth of Massachusetts, An Act Relative to Green Communities, Chapter 169 of the Acts of 2008 (July 2, 2008); http://www.mass.gov/legis/laws/seslaw08/sl080169.htm.

MA DOER, “Solar PV Installation FAQ” Web page (n.d.);
http://www.mass.gov/Eoeea/docs/doer/renewables/solar/solar-tip.pdf.

NREL, DOE, 2008 Solar Market Report (January 2010); http://www.nrel.gov/applying_technologies/pdfs/2008_solar_market_report.pdf.

OPA, “Renewable Energy Fee-In Tariff Program” Web page (2010); http://fit.powerauthority.on.ca/Page.asp?PageID=1115&SiteNodeID=1052.

OPA, “Ontario Announces 184 Large-Scale Energy Projects,” news release (April 8, 2010); http://fit.powerauthority.on.ca/Storage/100/10986_Apr_8_News_Release_FINAL.pdf.

Under Attachment K, §4.1(a)(v), the ISO also could initiate an economic study.

PAC materials are available at http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/reports/index.html. The final results of the economic studies will be available at the same link.

ISO Planning Advisory Committee; http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/mtrls/index.html. See materials for the April, May, and June 2010 PAC meetings.

Midwest ISO, PJM, Southwest Power Pool, and Tennessee Valley Authority, Joint Coordinated System Plan 2008 (JCSP08) (2008); http://www.jcspstudy.org/. DOE, NREL, Eastern Wind Integration and Transmission Study (EWITS) (January 2010); http://www.nrel.gov/wind/systemsintegration/pdfs/2010/ewits_final_report.pdf.

New England 2030 Power System Study: Report to the New England Governors, Scenario Analysis of Renewable Resource Development (February 2010);
http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/reports/2010/economicstudyreportfinal_022610.pdf.
New England Governors’ Conference (NEGC), New England Governors’ Renewable Energy Blueprint (September 15, 2009); http://www.nescoe.com/Blueprint.html.

See April and May 2009 PAC materials at
http://iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/mtrls/2009/index.html, and May 2009 materials from the Inter-Area Planning Stakeholder Advisory Committee at 
http://iso-ne.com/committees/comm_wkgrps/othr/ipsac/mtrls/2009/may72009/index.html. Also see the IPSAC Web sites at http://www.interiso.com and http://www.iso-ne.com/committees/comm_wkgrps/othr/ipsac/index.html.

IREMM is a simulation tool the ISO has used in past production cost analyses for developing hourly, chronological system-production costs, and other metrics.

The onshore and offshore wind in BHE, ME, and SME was modeled in BHE. The results of the study will then provide additional information on various transmission limitations arising from different locations of wind development within the three load bubbles.

PROMOD, GridView, MAPS, and other programs provide more detailed production cost representations of the transmission network than IREMM. For more information on the IREMM and detailed production cost program scopes of work and the differences between IREMM and these detailed production cost programs, see the June 2009 IPSAC presentation; http://iso-ne.com/committees/comm_wkgrps/othr/ipsac/mtrls/2009/jun302009/index.html) and the 2009 Northeast Coordinated System Plan (see Section 11.2.3).

ISO New England 2009 Regional System Plan (October 15, 2009); http://www.iso-ne.com/trans/rsp/2009/rsp09_final.pdf.

NYISO, New York 2008 Reliability Needs Assessment (RNA) (December 10, 2007); http://www.nyiso.com/public/webdocs/services/planning/reliability_assessments/2008_RNA__Supporting_FINAL_REPORT_12_12.pdf. 2008 New York ISO Comprehensive Reliability Plan (July 15, 2008) (developed in response to the 2008 RNA); http://www.nyiso.com/public/webdocs/newsroom/press_releases/2008/2008_Comprensive_Reliability_Plan_Final_Report_07152008.pdf. New York 2009 Reliability Needs Assessment (January 13, 2009); http://www.nyiso.com/public/webdocs/newsroom/press_releases/2009/RNA_2009_Final_1_13_09.pdf. PJM, PJM 2007 RTEP Plan (February 27, 2008); http://www.pjm.com/documents/reports/rtep-report.aspx.

ISO New England 2009 CELT Report 2009–2018 Forecast Report of Capacity, Energy, Loads, and Transmission (April 15, 2009); http://www.iso-ne.com/trans/celt/report/2009/index.html.

Refer to RSP09, Table 4-7; http://www.iso-ne.com/trans/rsp/2009/index. Operating Procedure No. 4, Action during a Capacity Deficiency (March 5, 2008); http://www.iso-ne.com/rules_proceds/operating/isone/op4/index.html.

EIA, DOE, Form EIA-860 Database Annual Electric Generator Report (2010); http://www.eia.doe.gov/cneaf/electricity/page/eia860.html.

NYISO, 2009 Load and Capacity Data “Gold Book,” (April 2009); http://www.nyiso.com/public/webdocs/services/planning/planning_data_reference_documents/2009_LoadCapacityData_PUBLIC.pdf . PJM, PJM Load Forecast Report (January 2009); http://green.dc.gov/green/lib/green/pdfs/2009-pjm-load-report.pdf.

ISO generic generator dispatch cost spreadsheets provide production costs and emission rates for given fuel costs and emission allowances. Users can make their own input assumptions in these spreadsheets, which are available at
http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/eag/usr_sprdshts/index.html.

EIA, DOE, 2009 Annual Energy Outlook, DOE/EIA-0383 (June 2009); http://www.eia.doe.gov/oiaf/archive/aeo09/index.html.

Also see the ISO’s 2009 Annual Markets Report, Section 2.6;
http://www.iso-ne.com/markets/mktmonmit/rpts/other/amr09_final_051810.pdf.

Auction Revenue Rights are a mechanism used to distribute some of FTR auction revenue to congestion-paying load-serving entities and transmission customers that have supported the transmission system.

Emissions could be well below the cap in the short term. This is the case with RGGI CO2 emissions; see Section 8.1.2.

NESCOE is the FERC-approved regional-state committee for providing advisory input to the ISO regarding the development of the RSP.

The undersea cable is assumed to use HVDC voltage-source converter technology.

See the PAC presentation materials (April 27, 2010);
http://www.iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/mtrls/2010/apr272010/index.html.

See additional details of the scope of work and assumptions available at
http://iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/mtrls/2010/jun162010/economic_studies.pdf.

The use of various metrics provided by the economic studies, such as energy revenues to resources by type, can be compared with the resource production costs and carrying charges derived from the representative capital costs to determine the economic viability of specific expansion scenarios.

The Brattle Group, Connecticut Light and Power, United Illuminating, Integrated Resource Plan for Connecticut (January 1, 2010); http://www.ctenergy.org/pdf/2010IRP.pdf.

New England Electricity Scenario Analysis Report (August 2, 2007);
http://www.iso-ne.com/committees/comm_wkgrps/othr/sas/mtrls/elec_report/scenario_analysis_final.pdf.

“Update on Generic Capital Costs of New Resources,” PAC presentation (January 21, 2010);
http://iso-ne.com/committees/comm_wkgrps/prtcpnts_comm/pac/mtrls/2010/jan212010/generic_resource_costs.pdf.

Ryan Wiser and Mark Bolinger, 2009 Wind Technologies Market Report (DOE, Lawrence Berkley National Laboratory, August 2010); http://eetd.lbl.gov/ea/ems/reports/lbnl-3716e.pdf.

Energy Policy Act of 2005, U.S. Public Law. 109-58, Title XII, Subtitle B, 119 Stat. 594 (2005) (amending the Federal Power Act to add a new § 216).

National Interest Electric Transmission Corridors and Congestion Study documents are available at http://nietc.anl.gov/documents/index.cfm. The 2006 Congestion Study of the Eastern Interconnection (August 2006) is available at http://nietc.anl.gov/documents/docs/Congestion_Study_2006-9MB.pdf.

A map of the Mid-Atlantic Area National Corridor is available at http://nietc.anl.gov/documents/docs/NIETC_MidAtlantic_Area_Corridor_Map.pdf.

DOE, 2009 National Electric Transmission Congestion Study (DOE, December 2009); http://congestion09.anl.gov/documents/docs/Congestion_Study_2009.pdf.

American Recovery and Reinvestment Act of 2009, Stimulus Bill, U.S. Public Law 111-5, H.R. 1, S. 1 (February 17, 2009); http://www.gpo.gov/fdsys/pkg/PLAW-111publ5/content-detail.html.

Workshop materials are available at the DOE Web site, “2009 National Electric Transmission Congestion Study” (n.d); http://congestion09.anl.gov//.

Open Access Technology International, Inc. Assessment of Historical Transmission Congestion in the Eastern Interconnection (DOE, July 1, 2009); http://www.congestion09.anl.gov/documents/docs/EasternInterconnection.pdf.

See http://www.eipconline.com/.

See the EIPC Final DOE Statement of Project Objectives (July 14, 2010); http://www.eipconline.com/Documents/SOPO_14Jul10_DE-OE0000343.pdf.

The “NERC Company Overview: FAQs” Web page (2010) provides information about NERC as the ERO; http://www.nerc.com/page.php?cid=1|7|114.

Preventing Undue Discrimination and Preference in Transmission Service, Final Rule, FERC Order No. 890, Docket Nos. RM05-17-000 and RM05-25-000 (February 16, 2007); http://www.ferc.gov/whats-new/comm-meet/2007/021507/E-1.pdf. Also see Open Access Transmission Tariff Reform, FERC Order No. 890 Final Rule (2007); http://www.ferc.gov/industries/electric/indus-act/oatt-reform/sum-compl-filing.asp. While not FERC jurisdictional, the Canadian ISO/RTO processes are intended to comply with Order 890 requirements.

As full members, New Brunswick and Nova Scotia also ensure that NPCC reliability issues are addressed for Prince Edward Island.

Additional information about the protocol is available at http://www.interiso.com/public/document/Northeastern%20ISO-RTO%20Planning%20Protocol.pdf.

See the IPSAC Web sites at http://www.interiso.com and
http://www.iso-ne.com/committees/comm_wkgrps/othr/ipsac/index.html.

2009 Northeast Coordinated System Plan (May 24, 2010); http://iso-ne.com/committees/comm_wkgrps/othr/ipsac/index.html.

The Seams Report is available at http://www.iso-ne.com/regulatory/seams/2008/index.html.

DPUC Review of the Integrated Resource Plan, CT DPUC Docket No. 08-07-01 (February 18, 2009); http://www.dpuc.state.ct.us/FINALDEC.NSF/0d1e102026cb64d98525644800691cfe/e38fd40db43adb3a85257562007065bc?OpenDocument. An Act Concerning Electricity and Energy Efficiency, Connecticut House Bill 7432; Public Act 07-242) (Approved June 4, 2007). See the CEAB Web site for additional information; http://www.ctenergy.org/.

Maine Revised Statutes, Title 35-A § 3404, 2 (A) and (B); http://www.mainelegislature.org/legis/statutes/35-A/title35-Asec3404.html. Also, An Act to Implement the Recommendations of the Governor's Ocean Energy Task Force, Maine Public Law, 124th Maine Legislature LD 1810 (April 7, 2010); http://www.mainelegislature.org/legis/bills/bills_124th/billpdfs/SP071001.pdf).

Maine PUC, Request for Proposal Issued by MPUC for Long-Term Contracting of Electric Power Supply (February 23, 2010); http://www.maine.gov/tools/whatsnew/index.php?topic=puc-pressreleases&id=92548&v=article08.

An Act To Implement the Recommendations of the Governor's Ocean Energy Task Force, Maine Public Law 615, LD 1810 (2010); http://www.mainelegislature.org/legis/bills/bills_124th/chapters/PUBLIC615.asp.

EMT, Triennial Plan of the Efficiency Maine Trust 2011–2013 (April 2010); http://www.efficiencymainetrust.org/docs/EMT_Final_Tri_Plan.pdf.

Commonwealth of Massachusetts, An Act Relative to Green Communities, Chapter 169 of the Acts of 2008 (July 2, 2008); http://www.mass.gov/legis/laws/seslaw08/sl080169.htm.

National Grid, NSTAR, Unitil, and Western Massachusetts Electric, 2010–2012 Massachusetts Joint Statewide Three-Year Electric Energy Efficiency Plan (October 29, 2009); http://www.ma-eeac.org/docs/DPU-filing/ElectricPlanFinalOct09.pdf.

Order Instituting a Rulemaking pursuant to G.L. c. 30A, § 2 and 220 C.M.R. § 2.00 et seq. to Implement the Net Metering Provisions of An Act Relative to Green Communities . . . MA DPU 08-75-A Order Adopting Final Regulations (June 26, 2009); http://www.env.state.ma.us/dpu/docs/gas/08-75/62609dpuord.pdf. Investigation by the Department of Public Utilities to Develop Tariffs Governing Net Metering Under An Act Relative to Green Communities, St. 2008, c. 169, § 78. MA DPU 09-03-A Order Adopting Model Net Metering Tariff (August 20, 2009); http://www.env.state.ma.us/dpu/docs/electric/09-03/82009noiord.pdf. Unitil, National Grid, NSTAR, and Western Massachusetts Electric Company are the investor-owned utilities in Massachusetts.

Order Adopting Emergency Regulations, MA DPU 10-58 (June 9, 2010); http://www.env.state.ma.us/dpu/docs/electric/10-58/6910dpuord.pdf.

Commonwealth of Massachusetts, An Act Establishing the Global Warming Solutions Act, Chapter 298 of the Acts of 2008 (August 7, 2008); http://www.mass.gov/legis/laws/seslaw08/sl080298.htm.

MA DOER, Biomass Sustainability and Carbon Policy Study (June 2010); http://www.mass.gov/?pageID=eoeeaterminal&L=4&L0=Home&L1=Energy,+Utilities+%26+Clean+Technologies&L2=Renewable+Energy&L3=Biomass&sid=Eoeea&b=terminalcontent&f=doer_arra_bscps&csid=Eoeea.

Commonwealth of Massachusetts, “Governor Patrick Sets New Goals for Wind Power,” press release (January 13, 2009); http://www.mass.gov/?pageID=gov3pressrelease&L=1&L0=Home&sid=Agov3&b=pressrelease&f=090113_Goals_Wind_Power&csid=Agov3.

An Act Establishing a Commission to Develop a Plan for the Expansion of Transmission Capacity in the North Country, NH SB 383 (2008); http://www.gencourt.state.nh.us/legislation/2008/SB0383.html. An Act Relative to the Commission to Develop a Plan for the Expansion of Transmission Capacity in the North Country, NH.SB 85 (2009); http://www.gencourt.state.nh.us/legislation/2009/SB0085.html. The 2009 bill extends the life of the commission created pursuant to SB 383. North Country Transmission Commission information is available at http://www.puc.nh.gov/TransmissionCommission.htm.

NH Office of Energy Planning, “Action Plan contracted for Coos Loop Transmission Lines,” press release (April 29, 2010); http://www.puc.state.nh.us/Transmission%20Commission/2010-04-29%20Press%20Release%20-%20KEMA%20selected%20to%20do%20transmission%20lines%20action%20plan.pdf.

An Act Relating to Public Utilities and Carriers—Contracting Standard for Renewable Energy, RI Senate Bill 2819, Sub A as amended, Chap. 32 (June 15, 2010);  http://dirac.rilin.state.ri.us/BillStatus/WebClass1.ASP?WCI=BillStatus&WCE=ifrmBillStatus&WCU. Review of Amended Power Purchase Agreement Between The Narragansett Electric Company d/b/a National Grid and Deepwater Wind Block Island, LLC Pursuant to R.I.G.L. § 39-26.1-7, National Grid Filing to the RI PUC, Docket 4185 (June 30, 2010); http://www.ripuc.org/eventsactions/docket/4185-Amended%20PPA%20(PUC%206-30-10).pdf.

Vermont Statutes Annotated, Title 30, § 248(e); http://www.leg.state.vt.us/statutes/fullsection.cfm?Title=30&Chapter=005&Section=00248.

Central Vermont Public Service, “Preliminary Vermont-Hydro-Québec Agreement Reached” (March 11, 2010); http://www.cvps.com/AboutUs/news/viewStory.aspx?story_id=264.

See Vermont H.781 (2010); http://www.leg.state.vt.us/docs/2010/bills/Passed/H-781.pdf.

For more information, see www.nescoe.com.

FERC, Wholesale Power Market Platform, SMD Notice of Proposed Rulemaking white paper, FERC Docket No. RM01-12-000 (April 28, 2003).

EIPC, “Sector Caucus Voting Results,” Web page (2010); http://www.eipconline.com/SelectionProcess.aspx.

NEGC, New England Governors’ Renewable Energy Blueprint (September 15, 2009); http://www.nescoe.com/Blueprint.html.

NEGC Resolution Adopting the Governors’ Renewable Energy Blueprint (September 15, 2009); www.negc.org.

NEG-ECP Resolution Concerning Renewable Energy (September 15, 2009); www.negc.org.

The 33rd Annual Conference of the New England Governors and Eastern Canadian Premiers (NEG/ECP) took place in Saint John, New Brunswick, on September 15, 2009.

The 34th Annual Conference of the NEG/ECP took place in Lenox, Massachusetts, on July 12, 2010. NESCOE, Report to the New England Governors on Coordinated Renewable Procurement (July 12, 2010); http://www,nescoe.com. On September 2, 2010, the ISO submitted comments to NESCOE on this report, which are available at http://www.nescoe.com/uploads/ISO_NE_Comments_to_NESCOE-2.pdf.

Additional information about the NEG/ECP conferences is available at http://www.negc.org/premiers.html.

The Alternative Price Rule ensures that the capacity clearing price reflects the cost of new entry (CONE) in an FCA when entry of new resources was prevented because of the presence of out-of-market capacity. This rule sets the clearing price at the lesser of the CONE or the price at which the last new capacity offer left the auction. The rule and the determination of the CONE are described in detail in Market Rule I, Section II.13.2.4 and III.13.2.7.8; http://www.iso-ne.com/regulatory/tariff/sect_3/index.html.

ISO New England Inc. and New England Power Pool, Docket Nos. ER10-787-000, EL10-50-000, and EL10-57-000 (consolidated) FERC filing (July 1, 2010); http://www.iso-ne.com/regulatory/ferc/filings/2010/jul/er10-787-000_07-01-10_fcm_first_brief.pdf. ISO New England Inc. and New England Power Pool, Docket Nos. ER10-787-000, EL10-50-000, and EL10-57-000 (consolidated) FERC filing (September 1, 2010); http://www.iso-ne.com/regulatory/ferc/filings/2010/sep/er10-787-000_09-01-10_second_fcm_redesign_brief.pdf.

Starting in fall 2008 and through spring 2009, the ISO and regional stakeholders worked on the issue of price-responsive demand treatment and participation in the energy market. On March 18, 2010, FERC issued a Notice of Proposed Rulemaking (NOPR), Demand-Response Compensation in Organized Wholesale Energy Markets, 130 FERC ¶ 61,213, Docket RM10-17-000. In this NOPR FERC seeks comments on a proposal that would require ISOs and RTOs to pay demand-response providers the full LMP for demand reductions in all hours when demand-response resources reduced energy consumption. The results of the NOPR process will provide the region with guidance on this issue.

Real-time pricing refers to retail prices that change hourly (or subhourly) based on changes in hourly wholesale power costs. Critical-peak pricing is a type of dynamic pricing whereby the majority of kilowatt-hour usage is priced according to time of use; during hours when the system is experiencing high peak demand, electric energy usage is subject to higher hourly prices. Variable-peak pricing is a type of time-of-use rate in which the on-peak rate changes daily to reflect average day-ahead wholesale market prices during predetermined on-peak hours.

For more information on the RTO Responsiveness and Governance Working Group, see
http://www.iso-ne.com/committees/comm_wkgrps/othr/rto/mtrls/index.html.

For more information on the CLG, see http://www.iso-ne.com/committees/comm_wkgrps/othr/clg/index.html.

ISO New England’s 2009 Report on the Consumer Liaison Group (July 30, 2010);
http://www.iso-ne.com/committees/comm_wkgrps/othr/clg/mtrls/2010/aug52010/2009_clg_report_final.pdf.

DOE, Recovery Act Selections for Smart Grid Investment Grant Awards, by State, table (2010); http://www.energy.gov/recovery/smartgrid_maps/SGIGSelections_State.pdf.

ISO Planning Procedure No. 4, Procedure for Pool Supported PTF Cost Review, Attachment D (August 2009); http://www.iso-ne.com/rules_proceds/isone_plan/. Draft Project Cost Estimating Guidelines (April 27, 2009);
http://www.iso-ne.com/rules_proceds/isone_plan/pp4_0_attachment_d.pdf.

EPA defines brownfields as real property, the expansion, redevelopment, or reuse of which may be complicated by the presence or potential presence of a hazardous substance, pollutant, or contaminant.

Transmission Planning and Cost Allocation by Transmission Owning and Operating Public Utilities, Notice of Proposed Rulemaking, FERC Docket No. RM12-23-000 (June 17, 2010); http://ferc.gov/whats-new/comm-meet/2010/061710/E-9.pdf.

Comments of ISO New England Inc. Transmission Planning and Cost Allocation by Transmission Owning and Operation Public Utilities, FERC Docket No. RM10-23-000 (September 29, 2010);
http://www.iso-ne.com/regulatory/ferc/filings/2010/sep/rm10-23-000_9-29-10_iso_nopr_comments.pdf.

Comments of the ISO/RTO Council, Transmission Planning and Cost Allocation by Transmission Owning and Operation Public Utilities, FERC Docket No. RM10-23-000 (September 28, 2010);
http://www.iso-ne.com/regulatory/ferc/filings/2010/sep/rm10-23-000_9-28-10_irc_nopr_comments.pdf.